## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_145_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_145_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_145_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_145_0_node_7 | 20 | n |  | TRUE
4 | bus_MV_145_0_node_263 | 20 | n |  | TRUE
5 | bus_MV_145_0_node_231 | 20 | n |  | TRUE
6 | bus_MV_145_0_node_262 | 20 | n |  | TRUE
7 | bus_MV_145_0_node_254 | 20 | n |  | TRUE
8 | bus_MV_145_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_145_0_node_117 | 20 | n |  | TRUE
10 | bus_MV_145_0_node_3 | 20 | n |  | TRUE
11 | bus_MV_145_0_node_8 | 20 | n |  | TRUE
12 | bus_MV_145_0_node_6 | 20 | n |  | TRUE
13 | bus_MV_145_0_node_275 | 20 | n |  | TRUE
14 | bus_MV_145_0_node_13 | 20 | n |  | TRUE
15 | bus_MV_145_0_node_9 | 20 | n |  | TRUE
16 | bus_MV_145_0_node_226 | 20 | n |  | TRUE
17 | bus_MV_145_0_node_255 | 20 | n |  | TRUE
18 | bus_MV_145_0_node_252 | 20 | n |  | TRUE
19 | bus_MV_145_0_node_12 | 20 | n |  | TRUE
20 | bus_MV_145_0_node_118 | 20 | n |  | TRUE
21 | bus_MV_145_0_node_119 | 20 | n |  | TRUE
22 | bus_MV_145_0_node_120 | 20 | n |  | TRUE
23 | bus_MV_145_0_node_116 | 20 | n |  | TRUE
24 | bus_MV_145_0_node_122 | 20 | n |  | TRUE
25 | bus_MV_145_0_node_56 | 20 | n |  | TRUE
26 | bus_MV_145_0_node_115 | 20 | n |  | TRUE
27 | bus_MV_145_0_node_227 | 20 | n |  | TRUE
28 | bus_MV_145_0_node_10 | 20 | n |  | TRUE
29 | bus_MV_145_0_node_11 | 20 | n |  | TRUE
30 | bus_MV_145_0_node_46 | 20 | n |  | TRUE
31 | bus_MV_145_0_node_14 | 20 | n |  | TRUE
32 | bus_MV_145_0_node_15 | 20 | n |  | TRUE
33 | bus_MV_145_0_node_123 | 20 | n |  | TRUE
34 | bus_MV_145_0_node_233 | 20 | n |  | TRUE
35 | bus_MV_145_0_node_20 | 20 | n |  | TRUE
36 | bus_MV_145_0_node_126 | 20 | n |  | TRUE
37 | bus_MV_145_0_node_51 | 20 | n |  | TRUE
38 | bus_MV_145_0_node_16 | 20 | n |  | TRUE
39 | bus_MV_145_0_node_18 | 20 | n |  | TRUE
40 | bus_MV_145_0_node_17 | 20 | n |  | TRUE
41 | bus_MV_145_0_node_19 | 20 | n |  | TRUE
42 | bus_MV_145_0_node_127 | 20 | n |  | TRUE
43 | bus_MV_145_0_node_125 | 20 | n |  | TRUE
44 | bus_MV_145_0_node_242 | 20 | n |  | TRUE
45 | bus_MV_145_0_node_21 | 20 | n |  | TRUE
46 | bus_MV_145_0_node_22 | 20 | n |  | TRUE
47 | bus_MV_145_0_node_124 | 20 | n |  | TRUE
48 | bus_MV_145_0_node_251 | 20 | n |  | TRUE
49 | bus_MV_145_0_node_32 | 20 | n |  | TRUE
50 | bus_MV_145_0_node_131 | 20 | n |  | TRUE
51 | bus_MV_145_0_node_23 | 20 | n |  | TRUE
52 | bus_MV_145_0_node_151 | 20 | n |  | TRUE
53 | bus_MV_145_0_node_152 | 20 | n |  | TRUE
54 | bus_MV_145_0_node_132 | 20 | n |  | TRUE
55 | bus_MV_145_0_node_24 | 20 | n |  | TRUE
56 | bus_MV_145_0_node_25 | 20 | n |  | TRUE
57 | bus_MV_145_0_node_26 | 20 | n |  | TRUE
58 | bus_MV_145_0_node_27 | 20 | n |  | TRUE
59 | bus_MV_145_0_node_28 | 20 | n |  | TRUE
60 | bus_MV_145_0_node_29 | 20 | n |  | TRUE
61 | bus_MV_145_0_node_154 | 20 | n |  | TRUE
62 | bus_MV_145_0_node_155 | 20 | n |  | TRUE
63 | bus_MV_145_0_node_94 | 20 | n |  | TRUE
64 | bus_MV_145_0_node_153 | 20 | n |  | TRUE
65 | bus_MV_145_0_node_92 | 20 | n |  | TRUE
66 | bus_MV_145_0_node_30 | 20 | n |  | TRUE
67 | bus_MV_145_0_node_31 | 20 | n |  | TRUE
68 | bus_MV_145_0_node_33 | 20 | n |  | TRUE
69 | bus_MV_145_0_node_34 | 20 | n |  | TRUE
70 | bus_MV_145_0_node_35 | 20 | n |  | TRUE
71 | bus_MV_145_0_node_257 | 20 | n |  | TRUE
72 | bus_MV_145_0_node_256 | 20 | n |  | TRUE
73 | bus_MV_145_0_node_36 | 20 | n |  | TRUE
74 | bus_MV_145_0_node_37 | 20 | n |  | TRUE
75 | bus_MV_145_0_node_38 | 20 | n |  | TRUE
76 | bus_MV_145_0_node_146 | 20 | n |  | TRUE
77 | bus_MV_145_0_node_39 | 20 | n |  | TRUE
78 | bus_MV_145_0_node_134 | 20 | n |  | TRUE
79 | bus_MV_145_0_node_41 | 20 | n |  | TRUE
80 | bus_MV_145_0_node_276 | 20 | n |  | TRUE
81 | bus_MV_145_0_node_107 | 20 | n |  | TRUE
82 | bus_MV_145_0_node_112 | 20 | n |  | TRUE
83 | bus_MV_145_0_node_113 | 20 | n |  | TRUE
84 | bus_MV_145_0_node_111 | 20 | n |  | TRUE
85 | bus_MV_145_0_node_109 | 20 | n |  | TRUE
86 | bus_MV_145_0_node_105 | 20 | n |  | TRUE
87 | bus_MV_145_0_node_42 | 20 | n |  | TRUE
88 | bus_MV_145_0_node_110 | 20 | n |  | TRUE
89 | bus_MV_145_0_node_45 | 20 | n |  | TRUE
90 | bus_MV_145_0_node_157 | 20 | n |  | TRUE
91 | bus_MV_145_0_node_158 | 20 | n |  | TRUE
92 | bus_MV_145_0_node_44 | 20 | n |  | TRUE
93 | bus_MV_145_0_node_80 | 20 | n |  | TRUE
94 | bus_MV_145_0_node_47 | 20 | n |  | TRUE
95 | bus_MV_145_0_node_49 | 20 | n |  | TRUE
96 | bus_MV_145_0_node_52 | 20 | n |  | TRUE
97 | bus_MV_145_0_node_48 | 20 | n |  | TRUE
98 | bus_MV_145_0_node_50 | 20 | n |  | TRUE
99 | bus_MV_145_0_node_53 | 20 | n |  | TRUE
100 | bus_MV_145_0_node_232 | 20 | n |  | TRUE
101 | bus_MV_145_0_node_54 | 20 | n |  | TRUE
102 | bus_MV_145_0_node_55 | 20 | n |  | TRUE
103 | bus_MV_145_0_node_64 | 20 | n |  | TRUE
104 | bus_MV_145_0_node_290 | 20 | n |  | TRUE
105 | bus_MV_145_0_node_268 | 20 | n |  | TRUE
106 | bus_MV_145_0_node_60 | 20 | n |  | TRUE
107 | bus_MV_145_0_node_61 | 20 | n |  | TRUE
108 | bus_MV_145_0_node_62 | 20 | n |  | TRUE
109 | bus_MV_145_0_node_100 | 20 | n |  | TRUE
110 | bus_MV_145_0_node_97 | 20 | n |  | TRUE
111 | bus_MV_145_0_node_238 | 20 | n |  | TRUE
112 | bus_MV_145_0_node_98 | 20 | n |  | TRUE
113 | bus_MV_145_0_node_65 | 20 | n |  | TRUE
114 | bus_MV_145_0_node_66 | 20 | n |  | TRUE
115 | bus_MV_145_0_node_67 | 20 | n |  | TRUE
116 | bus_MV_145_0_node_71 | 20 | n |  | TRUE
117 | bus_MV_145_0_node_73 | 20 | n |  | TRUE
118 | bus_MV_145_0_node_173 | 20 | n |  | TRUE
119 | bus_MV_145_0_node_85 | 20 | n |  | TRUE
120 | bus_MV_145_0_node_68 | 20 | n |  | TRUE
121 | bus_MV_145_0_node_69 | 20 | n |  | TRUE
122 | bus_MV_145_0_node_70 | 20 | n |  | TRUE
123 | bus_MV_145_0_node_236 | 20 | n |  | TRUE
124 | bus_MV_145_0_node_75 | 20 | n |  | TRUE
125 | bus_MV_145_0_node_169 | 20 | n |  | TRUE
126 | bus_MV_145_0_node_250 | 20 | n |  | TRUE
127 | bus_MV_145_0_node_235 | 20 | n |  | TRUE
128 | bus_MV_145_0_node_74 | 20 | n |  | TRUE
129 | bus_MV_145_0_node_170 | 20 | n |  | TRUE
130 | bus_MV_145_0_node_72 | 20 | n |  | TRUE
131 | bus_MV_145_0_node_171 | 20 | n |  | TRUE
132 | bus_MV_145_0_node_172 | 20 | n |  | TRUE
133 | bus_MV_145_0_node_76 | 20 | n |  | TRUE
134 | bus_MV_145_0_node_77 | 20 | n |  | TRUE
135 | bus_MV_145_0_node_78 | 20 | n |  | TRUE
136 | bus_MV_145_0_node_79 | 20 | n |  | TRUE
137 | bus_MV_145_0_node_96 | 20 | n |  | TRUE
138 | bus_MV_145_0_node_81 | 20 | n |  | TRUE
139 | bus_MV_145_0_node_249 | 20 | n |  | TRUE
140 | bus_MV_145_0_node_95 | 20 | n |  | TRUE
141 | bus_MV_145_0_node_82 | 20 | n |  | TRUE
142 | bus_MV_145_0_node_83 | 20 | n |  | TRUE
143 | bus_MV_145_0_node_84 | 20 | n |  | TRUE
144 | bus_MV_145_0_node_86 | 20 | n |  | TRUE
145 | bus_MV_145_0_node_89 | 20 | n |  | TRUE
146 | bus_MV_145_0_node_103 | 20 | n |  | TRUE
147 | bus_MV_145_0_node_162 | 20 | n |  | TRUE
148 | bus_MV_145_0_node_87 | 20 | n |  | TRUE
149 | bus_MV_145_0_node_88 | 20 | n |  | TRUE
150 | bus_MV_145_0_node_176 | 20 | n |  | TRUE
151 | bus_MV_145_0_node_159 | 20 | n |  | TRUE
152 | bus_MV_145_0_node_104 | 20 | n |  | TRUE
153 | bus_MV_145_0_node_102 | 20 | n |  | TRUE
154 | bus_MV_145_0_node_90 | 20 | n |  | TRUE
155 | bus_MV_145_0_node_161 | 20 | n |  | TRUE
156 | bus_MV_145_0_node_149 | 20 | n |  | TRUE
157 | bus_MV_145_0_node_147 | 20 | n |  | TRUE
158 | bus_MV_145_0_node_160 | 20 | n |  | TRUE
159 | bus_MV_145_0_node_108 | 20 | n |  | TRUE
160 | bus_MV_145_0_node_99 | 20 | n |  | TRUE
161 | bus_MV_145_0_node_277 | 20 | n |  | TRUE
162 | bus_MV_145_0_node_237 | 20 | n |  | TRUE
163 | bus_MV_145_0_node_101 | 20 | n |  | TRUE
164 | bus_MV_145_0_node_174 | 20 | n |  | TRUE
165 | bus_MV_145_0_node_175 | 20 | n |  | TRUE
166 | bus_MV_145_0_node_177 | 20 | n |  | TRUE
167 | bus_MV_145_0_node_106 | 20 | n |  | TRUE
168 | bus_MV_145_0_node_114 | 20 | n |  | TRUE
169 | bus_MV_145_0_node_148 | 20 | n |  | TRUE
170 | bus_MV_145_0_node_128 | 20 | n |  | TRUE
171 | bus_MV_145_0_node_129 | 20 | n |  | TRUE
172 | bus_MV_145_0_node_130 | 20 | n |  | TRUE
173 | bus_MV_145_0_node_136 | 20 | n |  | TRUE
174 | bus_MV_145_0_node_133 | 20 | n |  | TRUE
175 | bus_MV_145_0_node_135 | 20 | n |  | TRUE
176 | bus_MV_145_0_node_137 | 20 | n |  | TRUE
177 | bus_MV_145_0_node_142 | 20 | n |  | TRUE
178 | bus_MV_145_0_node_144 | 20 | n |  | TRUE
179 | bus_MV_145_0_node_156 | 20 | n |  | TRUE
180 | bus_MV_145_0_node_278 | 20 | n |  | TRUE
181 | bus_MV_145_0_node_140 | 20 | n |  | TRUE
182 | bus_MV_145_0_node_145 | 20 | n |  | TRUE
183 | bus_MV_145_0_node_279 | 20 | n |  | TRUE
184 | bus_MV_145_0_node_143 | 20 | n |  | TRUE
185 | bus_MV_145_0_node_138 | 20 | n |  | TRUE
186 | bus_MV_145_0_node_139 | 20 | n |  | TRUE
187 | bus_MV_145_0_node_141 | 20 | n |  | TRUE
188 | bus_MV_145_0_node_259 | 20 | n |  | TRUE
189 | bus_MV_145_0_node_258 | 20 | n |  | TRUE
190 | bus_MV_145_0_node_228 | 20 | n |  | TRUE
191 | bus_MV_145_0_node_229 | 20 | n |  | TRUE
192 | bus_MV_145_0_node_230 | 20 | n |  | TRUE
193 | bus_MV_145_0_node_234 | 20 | n |  | TRUE
194 | bus_MV_145_0_node_239 | 20 | n |  | TRUE
195 | bus_MV_145_0_node_240 | 20 | n |  | TRUE
196 | bus_MV_145_0_node_241 | 20 | n |  | TRUE
197 | bus_HV_145_0_node_151 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_145_0_load_0 | 0 | 0.11839 | 0.057339 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_145_0_load_263 | 4 | 0.16123 | 0.078088 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_145_0_load_262 | 6 | 0.12364 | 0.059882 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_145_0_load_254 | 7 | 0.079107 | 0.038313 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_145_0_load_3 | 10 | 0.12899 | 0.062472 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_145_0_load_275 | 13 | 0.09754 | 0.047241 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_145_0_load_226 | 16 | 0.071977 | 0.03486 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_145_0_load_255 | 17 | 0.12699 | 0.061503 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_145_0_load_252 | 18 | 0.12218 | 0.059174 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_145_0_load_120 | 22 | 0.16375 | 0.079308 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_145_0_load_122 | 24 | 0.16209 | 0.078506 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_145_0_load_115 | 26 | 0.10878 | 0.052685 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_145_0_load_10 | 28 | 0.11134 | 0.053926 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_145_0_load_46 | 30 | 0.079125 | 0.038322 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_145_0_load_123 | 33 | 0.094458 | 0.045748 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_145_0_load_233 | 34 | 0.16296 | 0.078923 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_145_0_load_20 | 35 | 0.16093 | 0.077944 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_145_0_load_51 | 37 | 0.31395 | 0.15205 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_145_0_load_16 | 38 | 0.11635 | 0.056349 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_145_0_load_18 | 39 | 0.069878 | 0.033843 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_145_0_load_127 | 42 | 0.14144 | 0.068502 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_145_0_load_125 | 43 | 0.15852 | 0.076773 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_145_0_load_242 | 44 | 0.22941 | 0.11111 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_145_0_load_124 | 47 | 0.15355 | 0.07437 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_145_0_load_251 | 48 | 0.099547 | 0.048213 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_145_0_load_23 | 51 | 0.12817 | 0.062077 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_145_0_load_151 | 52 | 0.13356 | 0.064687 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_145_0_load_27 | 58 | 0.12211 | 0.059142 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_145_0_load_29 | 60 | 0.12379 | 0.059952 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_145_0_load_154 | 61 | 0.13846 | 0.06706 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_145_0_load_30 | 66 | 0.14832 | 0.071834 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_145_0_load_33 | 68 | 0.098613 | 0.047761 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_145_0_load_257 | 71 | 0.12411 | 0.060108 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_145_0_load_36 | 73 | 0.11901 | 0.057637 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_145_0_load_146 | 76 | 0.14132 | 0.068442 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_145_0_load_39 | 77 | 0.15735 | 0.076208 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_145_0_load_276 | 80 | 0.087067 | 0.042168 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_145_0_load_107 | 81 | 0.1119 | 0.054194 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_145_0_load_111 | 84 | 0.12146 | 0.058827 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_145_0_load_109 | 85 | 0.099024 | 0.047959 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_145_0_load_105 | 86 | 0.13704 | 0.06637 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_145_0_load_42 | 87 | 0.1488 | 0.072067 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_145_0_load_110 | 88 | 0.07678 | 0.037186 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_145_0_load_157 | 90 | 0.088101 | 0.042669 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_145_0_load_80 | 93 | 0.1523 | 0.073765 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_145_0_load_47 | 94 | 0.12556 | 0.060809 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_145_0_load_53 | 99 | 0.12321 | 0.059676 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_145_0_load_232 | 100 | 0.084547 | 0.040948 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_145_0_load_64 | 103 | 0.16086 | 0.077906 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_145_0_load_290 | 104 | 0.1617 | 0.078315 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_145_0_load_268 | 105 | 0.15146 | 0.073356 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_145_0_load_60 | 106 | 0.11927 | 0.057764 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_145_0_load_97 | 110 | 0.072403 | 0.035066 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_145_0_load_238 | 111 | 0.13706 | 0.06638 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_145_0_load_65 | 113 | 0.10355 | 0.05015 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_145_0_load_66 | 114 | 0.12212 | 0.059148 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_145_0_load_67 | 115 | 1.534 | 0.74295 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_145_0_load_173 | 118 | 0.099355 | 0.04812 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_145_0_load_68 | 120 | 0.1301 | 0.063011 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_145_0_load_69 | 121 | 0.11352 | 0.054981 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_145_0_load_169 | 125 | 0.078213 | 0.03788 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_145_0_load_250 | 126 | 0.74125 | 0.359 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_145_0_load_74 | 128 | 0.22408 | 0.10853 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_145_0_load_72 | 130 | 0.11914 | 0.057704 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_145_0_load_171 | 131 | 0.098198 | 0.04756 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_145_0_load_76 | 133 | 0.15205 | 0.073642 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_145_0_load_96 | 137 | 0.090628 | 0.043893 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_145_0_load_249 | 139 | 0.097324 | 0.047136 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_145_0_load_95 | 140 | 0.15114 | 0.0732 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_145_0_load_82 | 141 | 0.15261 | 0.073914 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_145_0_load_162 | 147 | 0.11702 | 0.056676 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_145_0_load_176 | 150 | 0.11239 | 0.054431 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_145_0_load_159 | 151 | 0.13321 | 0.064515 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_145_0_load_104 | 152 | 0.1003 | 0.048577 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_145_0_load_90 | 154 | 0.15796 | 0.076502 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_145_0_load_161 | 155 | 0.13654 | 0.066131 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_145_0_load_147 | 157 | 0.13973 | 0.067675 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_145_0_load_160 | 158 | 0.092235 | 0.044672 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_145_0_load_108 | 159 | 0.15914 | 0.077074 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_145_0_load_277 | 161 | 0.14013 | 0.067869 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_145_0_load_237 | 162 | 0.4095 | 0.19833 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_145_0_load_101 | 163 | 0.067495 | 0.032689 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_145_0_load_177 | 166 | 0.137 | 0.066352 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_145_0_load_106 | 167 | 0.082209 | 0.039816 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_145_0_load_114 | 168 | 0.12054 | 0.058382 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_145_0_load_148 | 169 | 0.1011 | 0.048963 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_145_0_load_128 | 170 | 0.15201 | 0.073623 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_145_0_load_130 | 172 | 0.14409 | 0.069786 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_145_0_load_137 | 176 | 0.10445 | 0.050589 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_145_0_load_142 | 177 | 0.15657 | 0.075831 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_145_0_load_156 | 179 | 0.12524 | 0.060659 | 0 | 0 |  | 1 | TRUE | wye
91 | MV_145_0_load_278 | 180 | 0.12086 | 0.058534 | 0 | 0 |  | 1 | TRUE | wye
92 | MV_145_0_load_279 | 183 | 0.10005 | 0.048458 | 0 | 0 |  | 1 | TRUE | wye
93 | MV_145_0_load_143 | 184 | 0.094464 | 0.045751 | 0 | 0 |  | 1 | TRUE | wye
94 | MV_145_0_load_138 | 185 | 0.16125 | 0.078097 | 0 | 0 |  | 1 | TRUE | wye
95 | MV_145_0_load_259 | 188 | 0.13828 | 0.06697 | 0 | 0 |  | 1 | TRUE | wye
96 | MV_145_0_load_229 | 191 | 0.19677 | 0.095301 | 0 | 0 |  | 1 | TRUE | wye
97 | MV_145_0_load_230 | 192 | 0.10859 | 0.052591 | 0 | 0 |  | 1 | TRUE | wye
98 | MV_145_0_load_234 | 193 | 1.29 | 0.6248 | 0 | 0 |  | 1 | TRUE | wye
99 | MV_145_0_load_241 | 196 | 0.44928 | 0.2176 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 52 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_145_0_line_0 |  | 0 | 1 | 0.068154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_145_0_line_1 |  | 1 | 2 | 0.11851 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_145_0_line_2 |  | 1 | 3 | 0.3859 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_145_0_line_3 |  | 2 | 6 | 0.009658 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_145_0_line_4 |  | 3 | 7 | 0.053631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_145_0_line_5 |  | 3 | 8 | 0.20321 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_145_0_line_6 |  | 4 | 5 | 0.1016 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_145_0_line_7 |  | 5 | 190 | 0.021824 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_145_0_line_8 |  | 6 | 9 | 0.04878 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_145_0_line_9 |  | 8 | 11 | 0.37509 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_145_0_line_10 |  | 8 | 10 | 0.018052 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_145_0_line_11 |  | 9 | 26 | 0.039839 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_145_0_line_12 |  | 11 | 15 | 0.78057 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_145_0_line_13 |  | 11 | 16 | 0.042537 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_145_0_line_14 |  | 12 | 13 | 0.10295 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_145_0_line_15 |  | 12 | 14 | 0.24636 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_145_0_line_16 |  | 14 | 18 | 0.044852 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_145_0_line_17 |  | 14 | 19 | 0.11416 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_145_0_line_18 |  | 15 | 17 | 0.075083 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_145_0_line_19 |  | 16 | 27 | 0.033218 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_145_0_line_20 |  | 19 | 33 | 0.02849 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_145_0_line_21 |  | 19 | 29 | 0.11038 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_145_0_line_22 |  | 20 | 21 | 0.25802 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_145_0_line_23 |  | 20 | 22 | 0.014862 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_145_0_line_24 |  | 20 | 23 | 0.21282 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_145_0_line_25 |  | 21 | 24 | 0.042612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_145_0_line_26 |  | 23 | 26 | 0.070185 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_145_0_line_27 |  | 24 | 25 | 0.007535 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_145_0_line_28 |  | 25 | 102 | 0.096782 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_145_0_line_29 |  | 27 | 190 | 0.04419 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_145_0_line_30 |  | 28 | 29 | 0.027279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_145_0_line_31 |  | 28 | 30 | 0.15198 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_145_0_line_32 |  | 29 | 31 | 0.38047 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_145_0_line_33 |  | 29 | 32 | 0.56781 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_145_0_line_34 |  | 31 | 34 | 0.024596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_145_0_line_35 |  | 32 | 35 | 0.13169 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_145_0_line_36 |  | 32 | 36 | 0.19577 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_145_0_line_37 |  | 34 | 37 | 0.090372 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_145_0_line_38 |  | 35 | 42 | 0.022601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_145_0_line_39 |  | 35 | 41 | 0.033264 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_145_0_line_40 |  | 36 | 44 | 0.036886 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_145_0_line_41 |  | 36 | 45 | 0.16008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_145_0_line_42 |  | 37 | 95 | 0.059878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_145_0_line_43 |  | 38 | 39 | 0.033073 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_145_0_line_44 |  | 38 | 40 | 0.030888 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_145_0_line_45 |  | 40 | 41 | 0.030549 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_145_0_line_46 |  | 43 | 44 | 0.10945 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_145_0_line_47 |  | 45 | 46 | 0.15195 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
48 | MV_145_0_line_48 |  | 45 | 47 | 0.032271 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_145_0_line_49 |  | 46 | 48 | 0.049041 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
50 | MV_145_0_line_50 |  | 47 | 49 | 0.051164 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_145_0_line_51 |  | 48 | 50 | 0.015837 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
52 | MV_145_0_line_52 |  | 49 | 67 | 0.05385 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_145_0_line_53 |  | 50 | 171 | 0.17416 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
54 | MV_145_0_line_54 |  | 51 | 52 | 0.14445 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_145_0_line_55 |  | 52 | 53 | 0.065208 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
56 | MV_145_0_line_56 |  | 52 | 54 | 0.019304 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
57 | MV_145_0_line_57 |  | 53 | 64 | 0.014435 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
58 | MV_145_0_line_58 |  | 54 | 171 | 0.32559 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
59 | MV_145_0_line_59 |  | 55 | 56 | 0.028822 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_145_0_line_60 |  | 55 | 57 | 0.036358 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_145_0_line_61 |  | 56 | 58 | 0.039159 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_145_0_line_62 |  | 56 | 59 | 0.030577 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_145_0_line_63 |  | 57 | 60 | 0.010873 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_145_0_line_64 |  | 59 | 61 | 0.025605 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_145_0_line_65 |  | 61 | 62 | 0.019269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_145_0_line_66 |  | 61 | 63 | 0.049298 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
67 | MV_145_0_line_67 |  | 61 | 64 | 0.0269 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
68 | MV_145_0_line_68 |  | 62 | 179 | 0.022233 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_145_0_line_69 |  | 63 | 65 | 0.066489 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
70 | MV_145_0_line_70 |  | 65 | 155 | 0.034406 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
71 | MV_145_0_line_71 |  | 65 | 154 | 0.029313 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_145_0_line_72 |  | 66 | 67 | 0.049225 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_145_0_line_73 |  | 68 | 69 | 0.026414 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_145_0_line_74 |  | 69 | 70 | 0.092835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_145_0_line_75 |  | 70 | 71 | 0.005094 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_145_0_line_76 |  | 71 | 72 | 0.020387 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_145_0_line_77 |  | 72 | 189 | 0.076854 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_145_0_line_78 |  | 73 | 74 | 0.008206 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_145_0_line_79 |  | 74 | 75 | 0.15864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_145_0_line_80 |  | 75 | 77 | 0.068035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_145_0_line_81 |  | 76 | 77 | 0.13401 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
82 | MV_145_0_line_82 |  | 76 | 78 | 0.033797 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_145_0_line_83 |  | 78 | 175 | 0.15365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_145_0_line_84 |  | 79 | 80 | 0.024778 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_145_0_line_85 |  | 79 | 81 | 0.092666 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
86 | MV_145_0_line_86 |  | 81 | 85 | 0.038019 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
87 | MV_145_0_line_87 |  | 81 | 84 | 0.041525 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
88 | MV_145_0_line_88 |  | 81 | 86 | 0.0020549 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_145_0_line_89 |  | 82 | 83 | 0.020887 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
90 | MV_145_0_line_90 |  | 82 | 84 | 0.0204 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
91 | MV_145_0_line_91 |  | 83 | 168 | 0.027337 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_145_0_line_92 |  | 83 | 169 | 0.033197 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
93 | MV_145_0_line_93 |  | 85 | 93 | 0.023248 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
94 | MV_145_0_line_94 |  | 85 | 92 | 0.036683 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_145_0_line_95 |  | 86 | 167 | 0.038991 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
96 | MV_145_0_line_96 |  | 87 | 88 | 0.022387 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
97 | MV_145_0_line_97 |  | 88 | 89 | 0.02289 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_145_0_line_98 |  | 89 | 90 | 0.029326 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_145_0_line_99 |  | 89 | 92 | 0.029365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_145_0_line_100 |  | 90 | 91 | 0.005694 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_145_0_line_101 |  | 91 | 138 | 0.034482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_145_0_line_102 |  | 93 | 135 | 0.033387 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
103 | MV_145_0_line_103 |  | 94 | 95 | 0.002575 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_145_0_line_104 |  | 95 | 96 | 0.080762 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_145_0_line_105 |  | 96 | 100 | 0.062044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_145_0_line_106 |  | 96 | 97 | 0.058339 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
107 | MV_145_0_line_107 |  | 97 | 98 | 0.095229 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_145_0_line_108 |  | 98 | 99 | 0.027609 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_145_0_line_109 |  | 99 | 101 | 0.036506 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
110 | MV_145_0_line_110 |  | 101 | 102 | 0.18802 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_145_0_line_111 |  | 102 | 103 | 0.039364 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_145_0_line_112 |  | 104 | 105 | 0.33702 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
113 | MV_145_0_line_113 |  | 105 | 195 | 0.088952 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
114 | MV_145_0_line_114 |  | 106 | 107 | 0.01274 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_145_0_line_115 |  | 107 | 108 | 0.14489 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_145_0_line_116 |  | 108 | 109 | 0.061386 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_145_0_line_117 |  | 108 | 110 | 0.029271 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_145_0_line_118 |  | 109 | 111 | 0.031199 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_145_0_line_119 |  | 110 | 112 | 0.01591 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_145_0_line_120 |  | 111 | 162 | 0.06385 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_145_0_line_121 |  | 112 | 160 | 0.064542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_145_0_line_122 |  | 113 | 114 | 0.02871 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_145_0_line_123 |  | 113 | 115 | 0.065756 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_145_0_line_124 |  | 114 | 116 | 0.044494 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_145_0_line_125 |  | 116 | 117 | 0.021969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_145_0_line_126 |  | 117 | 124 | 0.061764 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_145_0_line_127 |  | 117 | 128 | 0.036152 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
128 | MV_145_0_line_128 |  | 118 | 119 | 0.007079 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_145_0_line_129 |  | 119 | 146 | 0.071855 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
130 | MV_145_0_line_130 |  | 119 | 142 | 0.12502 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
131 | MV_145_0_line_131 |  | 120 | 121 | 0.0091564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_145_0_line_132 |  | 121 | 122 | 0.034914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_145_0_line_133 |  | 122 | 123 | 0.10144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_145_0_line_134 |  | 122 | 124 | 0.069658 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_145_0_line_135 |  | 122 | 125 | 0.018897 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
136 | MV_145_0_line_136 |  | 123 | 126 | 0.022207 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_145_0_line_137 |  | 123 | 127 | 0.1087 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_145_0_line_138 |  | 124 | 129 | 0.029571 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
139 | MV_145_0_line_139 |  | 127 | 193 | 0.026123 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_145_0_line_140 |  | 128 | 130 | 0.013039 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_145_0_line_141 |  | 129 | 131 | 0.0084895 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
142 | MV_145_0_line_142 |  | 129 | 132 | 0.048043 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_145_0_line_143 |  | 131 | 165 | 0.034515 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
144 | MV_145_0_line_144 |  | 132 | 166 | 0.005327 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_145_0_line_145 |  | 133 | 134 | 0.043019 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
146 | MV_145_0_line_146 |  | 134 | 135 | 0.011797 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_145_0_line_147 |  | 135 | 136 | 0.023254 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
148 | MV_145_0_line_148 |  | 136 | 137 | 0.017947 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
149 | MV_145_0_line_149 |  | 137 | 140 | 0.020588 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
150 | MV_145_0_line_150 |  | 138 | 139 | 0.020278 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_145_0_line_151 |  | 140 | 145 | 0.019174 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
152 | MV_145_0_line_152 |  | 141 | 142 | 0.016737 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
153 | MV_145_0_line_153 |  | 141 | 143 | 0.020956 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
154 | MV_145_0_line_154 |  | 142 | 144 | 0.16058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_145_0_line_155 |  | 143 | 145 | 0.12842 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
156 | MV_145_0_line_156 |  | 144 | 147 | 0.019757 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_145_0_line_157 |  | 145 | 149 | 0.083449 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_145_0_line_158 |  | 146 | 152 | 0.042761 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_145_0_line_159 |  | 146 | 153 | 0.003663 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
160 | MV_145_0_line_160 |  | 148 | 149 | 0.1029 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_145_0_line_161 |  | 148 | 150 | 0.010751 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_145_0_line_162 |  | 149 | 151 | 0.03392 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
163 | MV_145_0_line_163 |  | 152 | 160 | 0.039743 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_145_0_line_164 |  | 153 | 163 | 0.039375 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
165 | MV_145_0_line_165 |  | 155 | 156 | 0.02668 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
166 | MV_145_0_line_166 |  | 156 | 157 | 0.035065 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
167 | MV_145_0_line_167 |  | 157 | 169 | 0.026687 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
168 | MV_145_0_line_168 |  | 158 | 159 | 0.019585 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
169 | MV_145_0_line_169 |  | 159 | 167 | 0.010738 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_145_0_line_170 |  | 160 | 161 | 0.067878 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
171 | MV_145_0_line_171 |  | 162 | 194 | 0.071487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_145_0_line_172 |  | 163 | 164 | 0.037433 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
173 | MV_145_0_line_173 |  | 164 | 165 | 0.009985 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
174 | MV_145_0_line_174 |  | 170 | 171 | 0.056478 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_145_0_line_175 |  | 171 | 172 | 0.011647 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_145_0_line_176 |  | 172 | 173 | 0.010528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_145_0_line_177 |  | 173 | 178 | 0.16482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
178 | MV_145_0_line_178 |  | 174 | 175 | 0.16343 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
179 | MV_145_0_line_179 |  | 174 | 176 | 0.043685 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
180 | MV_145_0_line_180 |  | 175 | 177 | 0.039507 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
181 | MV_145_0_line_181 |  | 176 | 179 | 0.10285 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
182 | MV_145_0_line_182 |  | 176 | 180 | 0.081461 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
183 | MV_145_0_line_183 |  | 177 | 181 | 0.042219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
184 | MV_145_0_line_184 |  | 178 | 184 | 0.031781 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
185 | MV_145_0_line_185 |  | 178 | 182 | 0.27639 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
186 | MV_145_0_line_186 |  | 181 | 186 | 0.044289 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
187 | MV_145_0_line_187 |  | 182 | 183 | 0.033172 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
188 | MV_145_0_line_188 |  | 185 | 186 | 0.050406 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
189 | MV_145_0_line_189 |  | 186 | 187 | 0.071061 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
190 | MV_145_0_line_190 |  | 187 | 188 | 0.049576 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
191 | MV_145_0_line_191 |  | 188 | 189 | 0.030847 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
192 | MV_145_0_line_192 |  | 190 | 191 | 0.069941 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
193 | MV_145_0_line_193 |  | 191 | 192 | 0.043644 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
194 | MV_145_0_line_194 |  | 194 | 195 | 0.1145 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
195 | MV_145_0_line_195 |  | 195 | 196 | 0.022271 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_145_0_trafo_151 | 25 MVA 110/20 kV | 197 | 52 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2722832.5995 | 1204196.2564
1 | 2722767.9145 | 1204217.1533
2 | 2722832.1986 | 1204316.6833
3 | 2722382.5873 | 1204238.1166
4 | 2722479.4327 | 1203953.1433
5 | 2722379.1221 | 1203971.0006
6 | 2722840.1371 | 1204322.184
7 | 2722361.2012 | 1204189.5309
8 | 2722287.0991 | 1204254.8623
9 | 2722863.9793 | 1204364.7398
10 | 2722289.32 | 1204272.7545
11 | 2722247.1561 | 1204015.7651
12 | 2722771.107 | 1205008.5817
13 | 2722683.4764 | 1204960.856
14 | 2722942.4232 | 1205185.6175
15 | 2721911.4089 | 1203556.848
16 | 2722286.8986 | 1204005.9342
17 | 2721842.0245 | 1203528.1553
18 | 2722913.3674 | 1205151.4491
19 | 2723024.9549 | 1205215.0394
20 | 2723032.6618 | 1204445.5287
21 | 2723126.3039 | 1204583.8962
22 | 2723043.6981 | 1204435.5753
23 | 2722927.5817 | 1204454.3494
24 | 2723108.1176 | 1204621.8165
25 | 2723112.2104 | 1204628.1501
26 | 2722884.6392 | 1204398.835
27 | 2722315.7496 | 1203989.4719
28 | 2723050.4678 | 1205284.4397
29 | 2723077.3189 | 1205289.6748
30 | 2723027.0098 | 1205434.6031
31 | 2723348.6123 | 1205102.731
32 | 2723484.161 | 1205401.5029
33 | 2723052.6459 | 1205208.3382
34 | 2723352.2727 | 1205078.4216
35 | 2723559.3978 | 1205509.5841
36 | 2723543.7127 | 1205587.9982
37 | 2723373.5427 | 1204990.5886
38 | 2723620.8662 | 1205549.7549
39 | 2723620.6049 | 1205582.827
40 | 2723602.2947 | 1205525.0739
41 | 2723574.8793 | 1205538.7057
42 | 2723540.9527 | 1205522.6454
43 | 2723408.7691 | 1205644.1636
44 | 2723510.973 | 1205604.9894
45 | 2723613.074 | 1205727.1836
46 | 2723741.4706 | 1205808.16
47 | 2723595.41 | 1205754.2162
48 | 2723779.9707 | 1205838.5365
49 | 2723593.2399 | 1205804.6206
50 | 2723793.4306 | 1205846.9442
51 | 2724052.8989 | 1205869.3462
52 | 2724148.443 | 1205977.681
53 | 2724204.4996 | 1206010.9944
54 | 2724138.5044 | 1205994.2425
55 | 2724284.8798 | 1205958.0711
56 | 2724269.6702 | 1205982.5732
57 | 2724304.5731 | 1205927.6135
58 | 2724304.7611 | 1206000.028
59 | 2724253.5545 | 1206008.5798
60 | 2724299.9007 | 1205917.7976
61 | 2724240.7296 | 1206030.7409
62 | 2724230.7466 | 1206047.2347
63 | 2724285.3825 | 1206051.9086
64 | 2724216.9374 | 1206018.381
65 | 2724323.7447 | 1206063.8719
66 | 2723605.4998 | 1205890.0614
67 | 2723625.9204 | 1205845.2724
68 | 2723618.773 | 1206290.0952
69 | 2723645.2625 | 1206289.7768
70 | 2723733.0611 | 1206312.3239
71 | 2723736.552 | 1206316.0436
72 | 2723756.2483 | 1206316.0629
73 | 2724087.3229 | 1206542.2288
74 | 2724093.6429 | 1206547.4419
75 | 2724123.9999 | 1206417.1293
76 | 2724113.3006 | 1206254.5276
77 | 2724175.4665 | 1206373.2439
78 | 2724094.523 | 1206226.4271
79 | 2724315.5984 | 1206205.4434
80 | 2724291.3768 | 1206200.224
81 | 2724397.4065 | 1206161.9185
82 | 2724344.042 | 1206193.1596
83 | 2724334.3319 | 1206174.6544
84 | 2724362.381 | 1206184.2237
85 | 2724413.2436 | 1206196.4815
86 | 2724396.5505 | 1206160.0504
87 | 2724411.3425 | 1206278.5266
88 | 2724433.291 | 1206282.9333
89 | 2724429.4244 | 1206260.3896
90 | 2724458.2356 | 1206254.9193
91 | 2724458.9772 | 1206249.2749
92 | 2724424.1611 | 1206231.5024
93 | 2724434.9289 | 1206187.9714
94 | 2723401.8399 | 1204934.9261
95 | 2723400.4557 | 1204937.0991
96 | 2723321.5792 | 1204922.5365
97 | 2723340.0122 | 1204867.1865
98 | 2723297.2086 | 1204794.9703
99 | 2723271.325 | 1204785.1619
100 | 2723295.2241 | 1204978.7049
101 | 2723237.1885 | 1204772.2254
102 | 2723176.894 | 1204652.5245
103 | 2723207.6626 | 1204676.7663
104 | 2725349.6893 | 1206328.8136
105 | 2725034.9435 | 1206208.3108
106 | 2724827.3574 | 1206064.7466
107 | 2724839.575 | 1206068.4382
108 | 2724819.4869 | 1206205.6562
109 | 2724836.4734 | 1206258.1181
110 | 2724791.3123 | 1206212.2802
111 | 2724842.8183 | 1206288.6629
112 | 2724778.5478 | 1206221.6794
113 | 2724531.0862 | 1206456.2473
114 | 2724549.4521 | 1206434.1802
115 | 2724489.0338 | 1206506.7984
116 | 2724577.9148 | 1206399.9813
117 | 2724595.7503 | 1206387.0881
118 | 2724627.3456 | 1206273.8167
119 | 2724624.0991 | 1206267.522
120 | 2724587.0158 | 1206476.5207
121 | 2724595.4431 | 1206472.9401
122 | 2724628.3451 | 1206462.3258
123 | 2724650.9203 | 1206561.2059
124 | 2724632.7296 | 1206404.3064
125 | 2724647.1455 | 1206460.4168
126 | 2724629.8996 | 1206568.5393
127 | 2724645.4082 | 1206650.6146
128 | 2724590.5017 | 1206351.3187
129 | 2724661.4576 | 1206396.9672
130 | 2724577.9057 | 1206354.6876
131 | 2724659.3009 | 1206388.7563
132 | 2724680.7915 | 1206389.1984
133 | 2724519.7676 | 1206191.8986
134 | 2724478.7006 | 1206179.0881
135 | 2724466.8935 | 1206178.3303
136 | 2724466.1296 | 1206155.1411
137 | 2724463.9753 | 1206137.3271
138 | 2724463.1528 | 1206215.0469
139 | 2724482.4599 | 1206221.2474
140 | 2724459.4028 | 1206117.2721
141 | 2724558.0435 | 1206150.7212
142 | 2724568.6445 | 1206163.6967
143 | 2724544.2143 | 1206134.9429
144 | 2724652.7714 | 1206095.7451
145 | 2724451.7112 | 1206099.754
146 | 2724673.4321 | 1206268.4637
147 | 2724654.081 | 1206076.0352
148 | 2724494.1948 | 1206000.5863
149 | 2724460.9667 | 1206043.7598
150 | 2724504.8503 | 1205998.9406
151 | 2724427.0488 | 1206044.1532
152 | 2724704.2865 | 1206238.7743
153 | 2724670.7921 | 1206271.0105
154 | 2724347.8037 | 1206049.9067
155 | 2724306.5832 | 1206093.6928
156 | 2724324.6466 | 1206113.3283
157 | 2724294.7502 | 1206131.7866
158 | 2724400.0614 | 1206094.5626
159 | 2724389.7927 | 1206111.2391
160 | 2724732.4724 | 1206266.8734
161 | 2724779.8653 | 1206315.4674
162 | 2724902.5472 | 1206311.2313
163 | 2724661.0859 | 1206309.1703
164 | 2724653.9428 | 1206345.9158
165 | 2724650.6494 | 1206355.3432
166 | 2724685.2059 | 1206386.1994
167 | 2724388.5053 | 1206121.8982
168 | 2724354.3795 | 1206156.0133
169 | 2724317.1976 | 1206146.2205
170 | 2723841.3034 | 1205906.5357
171 | 2723887.9474 | 1205928.7777
172 | 2723882.2959 | 1205938.9682
173 | 2723877.1896 | 1205948.1804
174 | 2724092.2047 | 1206071.9614
175 | 2724024.9436 | 1206191.1545
176 | 2724122.0834 | 1206100.0483
177 | 2723987.6822 | 1206204.5797
178 | 2723789.7399 | 1206037.6569
179 | 2724219.2272 | 1206066.265
180 | 2724174.5995 | 1206162.3209
181 | 2723973.8649 | 1206164.7292
182 | 2723816.8585 | 1206098.3653
183 | 2723843.0744 | 1206088.9129
184 | 2723790.9069 | 1206069.4163
185 | 2723893.0561 | 1206171.9967
186 | 2723939.681 | 1206191.1507
187 | 2723885.5046 | 1206236.2161
188 | 2723845.1425 | 1206264.9006
189 | 2723823.3258 | 1206286.7647
190 | 2722358.1241 | 1203976.9415
191 | 2722375.1367 | 1204044.2154
192 | 2722376.0906 | 1204082.8447
193 | 2724621.0686 | 1206660.1015
194 | 2724970.3579 | 1206331.853
195 | 2724955.6236 | 1206248.5699
196 | 2724934.867 | 1206240.4965
197 | 2724148.443 | 1205977.681

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98965 | 0.018422 | 0.11839 | 0.057339
1 | 0.98966 | 0.018327 | 0 | 0
2 | 0.98981 | 0.017238 | 0 | 0
3 | 0.98901 | 0.01275 | 0 | 0
4 | 0.98839 | 0.017418 | 0.16123 | 0.078088
5 | 0.98841 | 0.017225 | 0 | 0
6 | 0.98983 | 0.017396 | 0.12364 | 0.059882
7 | 0.98901 | 0.0128 | 0.079107 | 0.038313
8 | 0.98881 | 0.01422 | 0 | 0
9 | 0.98993 | 0.018265 | 0 | 0
10 | 0.9888 | 0.014248 | 0.12899 | 0.062472
11 | 0.98849 | 0.016517 | 0 | 0
12 | 0.99418 | -0.00096512 | 0 | 0
13 | 0.99417 | -0.00085163 | 0.09754 | 0.047241
14 | 0.99423 | -0.00061675 | 0 | 0
15 | 0.98837 | 0.017263 | 0 | 0
16 | 0.98846 | 0.016776 | 0.071977 | 0.03486
17 | 0.98835 | 0.017145 | 0.12699 | 0.061503
18 | 0.99422 | -0.00068384 | 0.12218 | 0.059174
19 | 0.99426 | -0.00089001 | 0 | 0
20 | 0.99048 | 0.016707 | 0 | 0
21 | 0.99094 | 0.013275 | 0 | 0
22 | 0.99048 | 0.016736 | 0.16375 | 0.079308
23 | 0.99015 | 0.019195 | 0 | 0
24 | 0.99101 | 0.012718 | 0.16209 | 0.078506
25 | 0.99103 | 0.012605 | 0 | 0
26 | 0.98999 | 0.017844 | 0.10878 | 0.052685
27 | 0.98844 | 0.016951 | 0 | 0
28 | 0.9943 | -0.0011993 | 0.11134 | 0.053926
29 | 0.99431 | -0.0012613 | 0 | 0
30 | 0.99428 | -0.0013474 | 0.079125 | 0.038322
31 | 0.99308 | 0.0083953 | 0 | 0
32 | 0.99649 | -0.018348 | 0 | 0
33 | 0.99426 | -0.00092294 | 0.094458 | 0.045748
34 | 0.99301 | 0.0090279 | 0.16296 | 0.078923
35 | 0.99637 | -0.019165 | 0.16093 | 0.077944
36 | 0.99782 | -0.0080472 | 0 | 0
37 | 0.9926 | 0.0058131 | 0.31395 | 0.15205
38 | 0.99634 | -0.0191 | 0.11635 | 0.056349
39 | 0.99634 | -0.019073 | 0.069878 | 0.033843
40 | 0.99635 | -0.019028 | 0 | 0
41 | 0.99636 | -0.019094 | 0 | 0
42 | 0.99636 | -0.019126 | 0.14144 | 0.068502
43 | 0.99776 | -0.0080878 | 0.15852 | 0.076773
44 | 0.9978 | -0.0078766 | 0.22941 | 0.11111
45 | 0.99861 | -0.014405 | 0 | 0
46 | 0.99895 | -0.010368 | 0 | 0
47 | 0.9986 | -0.014294 | 0.15355 | 0.07437
48 | 0.9992 | -0.0040867 | 0.099547 | 0.048213
49 | 0.99859 | -0.014209 | 0 | 0
50 | 0.99922 | -0.0039772 | 0 | 0
51 | 0.99996 | -0.00022479 | 0.12817 | 0.062077
52 | 1 | 0 | -16.4463 | -7.6904
53 | 0.99949 | -0.028262 | 0 | 0
54 | 0.99997 | -0.00015723 | 0 | 0
55 | 0.99931 | -0.028842 | 0 | 0
56 | 0.99932 | -0.028882 | 0 | 0
57 | 0.99931 | -0.028789 | 0 | 0
58 | 0.99931 | -0.028826 | 0.12211 | 0.059142
59 | 0.99933 | -0.028966 | 0 | 0
60 | 0.9993 | -0.028773 | 0.12379 | 0.059952
61 | 0.99934 | -0.028882 | 0.13846 | 0.06706
62 | 0.9993 | -0.028583 | 0 | 0
63 | 0.99918 | -0.029491 | 0 | 0
64 | 0.99944 | -0.028479 | 0 | 0
65 | 0.99897 | -0.030309 | 0 | 0
66 | 0.99856 | -0.014204 | 0.14832 | 0.071834
67 | 0.99858 | -0.014116 | 0 | 0
68 | 0.99852 | -0.026057 | 0.098613 | 0.047761
69 | 0.99852 | -0.026088 | 0 | 0
70 | 0.99853 | -0.026187 | 0 | 0
71 | 0.99853 | -0.026192 | 0.12411 | 0.060108
72 | 0.99854 | -0.026243 | 0 | 0
73 | 0.9985 | -0.027446 | 0.11901 | 0.057637
74 | 0.9985 | -0.027458 | 0 | 0
75 | 0.99852 | -0.027663 | 0 | 0
76 | 0.9986 | -0.027226 | 0.14132 | 0.068442
77 | 0.99853 | -0.02774 | 0.15735 | 0.076208
78 | 0.99863 | -0.027038 | 0 | 0
79 | 0.99765 | -0.094419 | 0 | 0
80 | 0.99765 | -0.094445 | 0.087067 | 0.042168
81 | 0.99767 | -0.09432 | 0.1119 | 0.054194
82 | 0.99804 | -0.07345 | 0 | 0
83 | 0.9981 | -0.073208 | 0 | 0
84 | 0.99792 | -0.080386 | 0.12146 | 0.058827
85 | 0.99746 | -0.10612 | 0.099024 | 0.047959
86 | 0.99767 | -0.094308 | 0.13704 | 0.06637
87 | 0.9974 | -0.10615 | 0.1488 | 0.072067
88 | 0.9974 | -0.10611 | 0.07678 | 0.037186
89 | 0.99741 | -0.10617 | 0 | 0
90 | 0.9974 | -0.10624 | 0.088101 | 0.042669
91 | 0.9974 | -0.10624 | 0 | 0
92 | 0.99743 | -0.10631 | 0 | 0
93 | 0.9974 | -0.10636 | 0.1523 | 0.073765
94 | 0.99244 | 0.0070152 | 0.12556 | 0.060809
95 | 0.99244 | 0.0070112 | 0 | 0
96 | 0.99224 | 0.0085135 | 0 | 0
97 | 0.99204 | 0.0068368 | 0 | 0
98 | 0.99181 | 0.0085333 | 0 | 0
99 | 0.99175 | 0.0090278 | 0.12321 | 0.059676
100 | 0.99224 | 0.0085743 | 0.084547 | 0.040948
101 | 0.99163 | 0.0080428 | 0 | 0
102 | 0.99122 | 0.011162 | 0 | 0
103 | 0.99121 | 0.011238 | 0.16086 | 0.077906
104 | 0.99535 | -0.10417 | 0.1617 | 0.078315
105 | 0.99545 | -0.1035 | 0.15146 | 0.073356
106 | 0.99592 | -0.10691 | 0.11927 | 0.057764
107 | 0.99592 | -0.10693 | 0 | 0
108 | 0.99594 | -0.10712 | 0 | 0
109 | 0.99584 | -0.10619 | 0 | 0
110 | 0.99599 | -0.1076 | 0.072403 | 0.035066
111 | 0.99579 | -0.10571 | 0.13706 | 0.06638
112 | 0.99602 | -0.10788 | 0 | 0
113 | 0.99554 | -0.12193 | 0.10355 | 0.05015
114 | 0.9956 | -0.12249 | 0.12212 | 0.059148
115 | 0.99541 | -0.12072 | 1.534 | 0.74295
116 | 0.9957 | -0.12343 | 0 | 0
117 | 0.99575 | -0.12389 | 0 | 0
118 | 0.99648 | -0.10998 | 0.099355 | 0.04812
119 | 0.99648 | -0.10999 | 0 | 0
120 | 0.9957 | -0.12338 | 0.1301 | 0.063011
121 | 0.9957 | -0.1234 | 0.11352 | 0.054981
122 | 0.99571 | -0.1235 | 0 | 0
123 | 0.99544 | -0.12104 | 0 | 0
124 | 0.99592 | -0.12544 | 0 | 0
125 | 0.99571 | -0.12352 | 0.078213 | 0.03788
126 | 0.99542 | -0.12085 | 0.74125 | 0.359
127 | 0.99527 | -0.11936 | 0 | 0
128 | 0.99573 | -0.12405 | 0.22408 | 0.10853
129 | 0.99599 | -0.12469 | 0 | 0
130 | 0.99573 | -0.12403 | 0.11914 | 0.057704
131 | 0.996 | -0.12464 | 0.098198 | 0.04756
132 | 0.99598 | -0.12461 | 0 | 0
133 | 0.9973 | -0.10674 | 0.15205 | 0.073642
134 | 0.99731 | -0.10667 | 0 | 0
135 | 0.99732 | -0.10669 | 0 | 0
136 | 0.99726 | -0.10691 | 0 | 0
137 | 0.99722 | -0.10709 | 0.090628 | 0.043893
138 | 0.9974 | -0.1062 | 0 | 0
139 | 0.99739 | -0.10617 | 0.097324 | 0.047136
140 | 0.99717 | -0.10728 | 0.15114 | 0.0732
141 | 0.99679 | -0.10879 | 0.15261 | 0.073914
142 | 0.99675 | -0.10894 | 0 | 0
143 | 0.99683 | -0.10861 | 0 | 0
144 | 0.99673 | -0.10874 | 0 | 0
145 | 0.99712 | -0.10746 | 0 | 0
146 | 0.99633 | -0.11058 | 0 | 0
147 | 0.99672 | -0.10871 | 0.11702 | 0.056676
148 | 0.99708 | -0.10711 | 0 | 0
149 | 0.9971 | -0.10723 | 0 | 0
150 | 0.99708 | -0.10709 | 0.11239 | 0.054431
151 | 0.99709 | -0.10729 | 0.13321 | 0.064515
152 | 0.99623 | -0.10973 | 0.1003 | 0.048577
153 | 0.99632 | -0.1106 | 0 | 0
154 | 0.99897 | -0.030254 | 0.15796 | 0.076502
155 | 0.99875 | -0.042637 | 0.13654 | 0.066131
156 | 0.99858 | -0.052062 | 0 | 0
157 | 0.99848 | -0.052482 | 0.13973 | 0.067675
158 | 0.99763 | -0.094457 | 0.092235 | 0.044672
159 | 0.99764 | -0.094435 | 0.15914 | 0.077074
160 | 0.99615 | -0.10898 | 0 | 0
161 | 0.99613 | -0.1091 | 0.14013 | 0.067869
162 | 0.99569 | -0.10483 | 0.4095 | 0.19833
163 | 0.99619 | -0.11771 | 0.067495 | 0.032689
164 | 0.99607 | -0.12438 | 0 | 0
165 | 0.99606 | -0.12444 | 0 | 0
166 | 0.99598 | -0.1246 | 0.137 | 0.066352
167 | 0.99764 | -0.094467 | 0.082209 | 0.039816
168 | 0.9981 | -0.073169 | 0.12054 | 0.058382
169 | 0.99831 | -0.061773 | 0.1011 | 0.048963
170 | 0.99945 | -0.0026581 | 0.15201 | 0.073623
171 | 0.99946 | -0.0027585 | 0 | 0
172 | 0.99946 | -0.00272 | 0.14409 | 0.069786
173 | 0.99946 | -0.0027032 | 0 | 0
174 | 0.99894 | -0.029627 | 0 | 0
175 | 0.99871 | -0.027733 | 0 | 0
176 | 0.999 | -0.030126 | 0.10445 | 0.050589
177 | 0.99868 | -0.027443 | 0.15657 | 0.075831
178 | 0.99941 | -0.0024179 | 0 | 0
179 | 0.99926 | -0.028237 | 0.12524 | 0.060659
180 | 0.99898 | -0.030245 | 0.12086 | 0.058534
181 | 0.99865 | -0.02721 | 0 | 0
182 | 0.99938 | -0.0021588 | 0 | 0
183 | 0.99938 | -0.0021198 | 0.10005 | 0.048458
184 | 0.99941 | -0.0024543 | 0.094464 | 0.045751
185 | 0.99861 | -0.026867 | 0.16125 | 0.078097
186 | 0.99862 | -0.026963 | 0 | 0
187 | 0.99859 | -0.026692 | 0 | 0
188 | 0.99857 | -0.026498 | 0.13828 | 0.06697
189 | 0.99856 | -0.026427 | 0 | 0
190 | 0.98841 | 0.017186 | 0 | 0
191 | 0.98839 | 0.017439 | 0.19677 | 0.095301
192 | 0.98838 | 0.017496 | 0.10859 | 0.052591
193 | 0.99522 | -0.11896 | 1.29 | 0.6248
194 | 0.99562 | -0.10419 | 0 | 0
195 | 0.99551 | -0.10316 | 0 | 0
196 | 0.9955 | -0.10304 | 0.44928 | 0.2176
197 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.11839 | -0.057339 | 0.11839 | 0.055746 | 1.3326e-06 | -0.0015934 | 0.0038371 | 0.0038171 | 0.0038371 | 0.98965 | 0.018422 | 0.98966 | 0.018327 | 1.7441
1 | -0.99305 | -0.4371 | 0.99321 | 0.43438 | 0.0001583 | -0.0027247 | 0.031648 | 0.031616 | 0.031648 | 0.98966 | 0.018327 | 0.98981 | 0.017238 | 14.3856
2 | 0.87466 | 0.38136 | -0.87412 | -0.38147 | 0.00053272 | -0.00011724 | 0.027833 | 0.027838 | 0.027838 | 0.98966 | 0.018327 | 0.98901 | 0.01275 | 13.2561
3 | -0.99321 | -0.43438 | 0.99322 | 0.43438 | 1.72e-05 | -5.2262e-07 | 0.031616 | 0.031616 | 0.031616 | 0.98981 | 0.017238 | 0.98983 | 0.017396 | 15.0551
4 | 0.079107 | 0.037061 | -0.079107 | -0.038313 | 4.6835e-07 | -0.0012524 | 0.0025498 | 0.0025655 | 0.0025655 | 0.98901 | 0.01275 | 0.98901 | 0.0128 | 1.1662
5 | 0.79502 | 0.34441 | -0.79484 | -0.34911 | 0.00017388 | -0.0046933 | 0.025289 | 0.025344 | 0.025344 | 0.98901 | 0.01275 | 0.98881 | 0.01422 | 11.5202
6 | -0.16123 | -0.078088 | 0.16124 | 0.075719 | 3.6921e-06 | -0.0023688 | 0.0052323 | 0.0052025 | 0.0052323 | 0.98839 | 0.017418 | 0.98841 | 0.017225 | 2.3783
7 | -0.16124 | -0.075719 | 0.16124 | 0.075211 | 7.8762e-07 | -0.00050884 | 0.0052025 | 0.0051962 | 0.0052025 | 0.98841 | 0.017225 | 0.98841 | 0.017186 | 2.3648
8 | -1.1169 | -0.49426 | 1.117 | 0.49427 | 0.00011027 | 1.2007e-05 | 0.03562 | 0.035619 | 0.03562 | 0.98983 | 0.017396 | 0.98993 | 0.018265 | 16.9617
9 | 0.66585 | 0.28706 | -0.66563 | -0.29574 | 0.00022547 | -0.0086867 | 0.021169 | 0.021271 | 0.021271 | 0.98881 | 0.01422 | 0.98849 | 0.016517 | 9.6687
10 | 0.12899 | 0.06205 | -0.12899 | -0.062472 | 4.2136e-07 | -0.00042129 | 0.0041788 | 0.0041841 | 0.0041841 | 0.98881 | 0.01422 | 0.9888 | 0.014248 | 1.9019
11 | -1.117 | -0.49427 | 1.117 | 0.49336 | 6.7455e-05 | -0.00091218 | 0.035619 | 0.035608 | 0.035619 | 0.98993 | 0.018265 | 0.98999 | 0.017844 | 16.1904
12 | 0.12701 | 0.043214 | -0.12699 | -0.061417 | 1.6769e-05 | -0.018203 | 0.0039179 | 0.0041201 | 0.0041201 | 0.98849 | 0.016517 | 0.98837 | 0.017263 | 1.8728
13 | 0.53862 | 0.25253 | -0.5386 | -0.25352 | 1.7151e-05 | -0.00098725 | 0.017373 | 0.017385 | 0.017385 | 0.98849 | 0.016517 | 0.98846 | 0.016776 | 7.9023
14 | 0.097541 | 0.044812 | -0.09754 | -0.047241 | 1.348e-06 | -0.0024291 | 0.0031168 | 0.0031469 | 0.0031469 | 0.99418 | -0.00096512 | 0.99417 | -0.00085163 | 1.4304
15 | -0.097541 | -0.044812 | 0.097546 | 0.044524 | 4.2593e-06 | -0.00028803 | 0.0031168 | 0.0031133 | 0.0031168 | 0.99418 | -0.00096512 | 0.99423 | -0.00061675 | 1.4842
16 | 0.12218 | 0.059122 | -0.12218 | -0.059174 | 1.2414e-06 | -5.2151e-05 | 0.003941 | 0.0039417 | 0.0039417 | 0.99423 | -0.00061675 | 0.99422 | -0.00068384 | 1.877
17 | -0.21973 | -0.10365 | 0.21973 | 0.10095 | 7.5476e-06 | -0.0026922 | 0.0070539 | 0.0070209 | 0.0070539 | 0.99423 | -0.00061675 | 0.99426 | -0.00089001 | 3.2063
18 | 0.12699 | 0.061417 | -0.12699 | -0.061503 | 2.2715e-06 | -8.6136e-05 | 0.0041201 | 0.0041212 | 0.0041212 | 0.98837 | 0.017263 | 0.98835 | 0.017145 | 1.9625
19 | 0.46663 | 0.21866 | -0.46662 | -0.21943 | 1.005e-05 | -0.00077191 | 0.01505 | 0.015059 | 0.015059 | 0.98846 | 0.016776 | 0.98844 | 0.016951 | 6.8451
20 | 0.094459 | 0.045715 | -0.094458 | -0.045748 | 4.7128e-07 | -3.3327e-05 | 0.0030468 | 0.0030472 | 0.0030472 | 0.99426 | -0.00089001 | 0.99426 | -0.00092294 | 1.4511
21 | -0.31419 | -0.14667 | 0.31421 | 0.14407 | 1.4887e-05 | -0.0026009 | 0.010067 | 0.010036 | 0.010067 | 0.99426 | -0.00089001 | 0.99431 | -0.0012613 | 4.576
22 | -1.3902 | -0.62019 | 1.3909 | 0.61434 | 0.00067692 | -0.0058458 | 0.044366 | 0.044295 | 0.044366 | 0.99048 | 0.016707 | 0.99094 | 0.013275 | 20.1665
23 | 0.16375 | 0.07896 | -0.16375 | -0.079308 | 5.5744e-07 | -0.00034795 | 0.0052984 | 0.0053028 | 0.0053028 | 0.99048 | 0.016707 | 0.99048 | 0.016736 | 2.4104
24 | 1.2264 | 0.54123 | -1.226 | -0.54608 | 0.00043436 | -0.0048546 | 0.039071 | 0.039129 | 0.039129 | 0.99048 | 0.016707 | 0.99015 | 0.019195 | 17.7861
25 | -1.3909 | -0.61434 | 1.391 | 0.61338 | 0.00011158 | -0.00096603 | 0.044295 | 0.044283 | 0.044295 | 0.99094 | 0.013275 | 0.99101 | 0.012718 | 20.134
26 | 1.226 | 0.54608 | -1.2258 | -0.54605 | 0.00019147 | 3.7798e-05 | 0.039129 | 0.03913 | 0.03913 | 0.99015 | 0.019195 | 0.98999 | 0.017844 | 18.6335
27 | -1.5531 | -0.69188 | 1.5531 | 0.69171 | 2.4673e-05 | -0.00016937 | 0.049526 | 0.049524 | 0.049526 | 0.99101 | 0.012718 | 0.99103 | 0.012605 | 22.512
28 | -1.5531 | -0.69171 | 1.5534 | 0.68954 | 0.00031672 | -0.002176 | 0.049524 | 0.049497 | 0.049524 | 0.99103 | 0.012605 | 0.99122 | 0.011162 | 22.511
29 | 0.46662 | 0.21943 | -0.4666 | -0.22046 | 1.339e-05 | -0.0010268 | 0.015059 | 0.015072 | 0.015072 | 0.98844 | 0.016951 | 0.98841 | 0.017186 | 6.8509
30 | -0.19047 | -0.092069 | 0.19047 | 0.091426 | 1.372e-06 | -0.00064351 | 0.0061421 | 0.0061339 | 0.0061421 | 0.9943 | -0.0011993 | 0.99431 | -0.0012613 | 2.7918
31 | 0.079127 | 0.038144 | -0.079125 | -0.038322 | 1.7628e-06 | -0.00017827 | 0.0025503 | 0.0025525 | 0.0025525 | 0.9943 | -0.0011993 | 0.99428 | -0.0013474 | 1.2155
32 | 2.5316 | 1.1396 | -2.5282 | -1.1476 | 0.0033043 | -0.0079899 | 0.080602 | 0.080709 | 0.080709 | 0.99431 | -0.0012613 | 0.99308 | 0.0083953 | 36.686
33 | -3.0362 | -1.3751 | 3.0433 | 1.3638 | 0.0070867 | -0.011331 | 0.096769 | 0.096609 | 0.096769 | 0.99431 | -0.0012613 | 0.99649 | -0.018348 | 43.9861
34 | 2.5282 | 1.1476 | -2.528 | -1.1481 | 0.00021391 | -0.00051566 | 0.080709 | 0.080716 | 0.080716 | 0.99308 | 0.0083953 | 0.99301 | 0.0090279 | 36.6892
35 | 0.48866 | 0.23365 | -0.4886 | -0.23377 | 5.7776e-05 | -0.0001199 | 0.015691 | 0.015693 | 0.015693 | 0.99649 | -0.018348 | 0.99637 | -0.019165 | 7.4729
36 | -3.532 | -1.5974 | 3.5364 | 1.5999 | 0.0043985 | 0.0025227 | 0.1123 | 0.11229 | 0.1123 | 0.99649 | -0.018348 | 0.99782 | -0.0080472 | 53.4745
37 | 2.3651 | 1.0692 | -2.3642 | -1.0687 | 0.00091673 | 0.00046787 | 0.075454 | 0.075456 | 0.075456 | 0.99301 | 0.0090279 | 0.9926 | 0.0058131 | 35.9312
38 | 0.14144 | 0.067967 | -0.14144 | -0.068502 | 6.2462e-07 | -0.00053553 | 0.0045465 | 0.0045532 | 0.0045532 | 0.99637 | -0.019165 | 0.99636 | -0.019126 | 2.0697
39 | 0.18623 | 0.087861 | -0.18623 | -0.088649 | 1.5832e-06 | -0.00078799 | 0.0059659 | 0.0059757 | 0.0059757 | 0.99637 | -0.019165 | 0.99636 | -0.019094 | 2.7162
40 | 0.38794 | 0.18688 | -0.38793 | -0.18775 | 7.6489e-06 | -0.00087457 | 0.012458 | 0.012469 | 0.012469 | 0.99782 | -0.0080472 | 0.9978 | -0.0078766 | 5.6676
41 | -3.9243 | -1.7868 | 3.9276 | 1.784 | 0.0033244 | -0.0028222 | 0.12475 | 0.1247 | 0.12475 | 0.99782 | -0.0080472 | 0.99861 | -0.014405 | 56.7037
42 | 2.0502 | 0.91667 | -2.0499 | -0.91798 | 0.0003411 | -0.0013072 | 0.065315 | 0.065331 | 0.065331 | 0.9926 | 0.0058131 | 0.99244 | 0.0070112 | 29.696
43 | 0.069878 | 0.03306 | -0.069878 | -0.033843 | 2.2246e-07 | -0.00078383 | 0.0022398 | 0.0022496 | 0.0022496 | 0.99634 | -0.0191 | 0.99634 | -0.019073 | 1.0225
44 | -0.18622 | -0.089408 | 0.18623 | 0.089373 | 1.9713e-06 | -3.537e-05 | 0.0059852 | 0.0059847 | 0.0059852 | 0.99634 | -0.0191 | 0.99635 | -0.019028 | 2.8501
45 | -0.18623 | -0.089373 | 0.18623 | 0.088649 | 1.4585e-06 | -0.00072365 | 0.0059847 | 0.0059757 | 0.0059847 | 0.99635 | -0.019028 | 0.99636 | -0.019094 | 2.7203
46 | -0.15852 | -0.076773 | 0.15852 | 0.076646 | 5.0624e-06 | -0.00012692 | 0.0050958 | 0.0050942 | 0.0050958 | 0.99776 | -0.0080878 | 0.9978 | -0.0078766 | 2.4266
47 | -4.2295 | -1.9269 | 4.2308 | 1.9226 | 0.0013242 | -0.0042377 | 0.13436 | 0.13429 | 0.13436 | 0.99861 | -0.014405 | 0.99895 | -0.010368 | 37.115
48 | 0.30188 | 0.14288 | -0.30188 | -0.14365 | 4.0198e-06 | -0.00076716 | 0.0096548 | 0.0096643 | 0.0096643 | 0.99861 | -0.014405 | 0.9986 | -0.014294 | 4.3929
49 | -4.2308 | -1.9226 | 4.2317 | 1.9235 | 0.00081191 | 0.00086715 | 0.13429 | 0.13429 | 0.13429 | 0.99895 | -0.010368 | 0.9992 | -0.0040867 | 38.3697
50 | 0.14832 | 0.069277 | -0.14832 | -0.070495 | 1.5345e-06 | -0.0012177 | 0.0047324 | 0.0047474 | 0.0047474 | 0.9986 | -0.014294 | 0.99859 | -0.014209 | 2.1579
51 | -4.3312 | -1.9717 | 4.3313 | 1.9708 | 9.2496e-05 | -0.00094141 | 0.13749 | 0.13748 | 0.13749 | 0.9992 | -0.0040867 | 0.99922 | -0.0039772 | 21.5498
52 | 0.14832 | 0.070495 | -0.14832 | -0.071776 | 1.6257e-06 | -0.0012816 | 0.0047474 | 0.0047634 | 0.0047634 | 0.99859 | -0.014209 | 0.99858 | -0.014116 | 2.1652
53 | -4.3313 | -1.9708 | 4.3323 | 1.9604 | 0.0010161 | -0.010356 | 0.13748 | 0.13735 | 0.13748 | 0.99922 | -0.0039772 | 0.99946 | -0.0027585 | 21.5479
54 | -0.12817 | -0.062077 | 0.12818 | 0.061907 | 4.3478e-06 | -0.00016971 | 0.0041113 | 0.0041091 | 0.0041113 | 0.99996 | -0.00022479 | 1 | 0 | 1.9577
55 | 11.4787 | 5.4534 | -11.4756 | -5.4451 | 0.003133 | 0.0083349 | 0.36686 | 0.36686 | 0.36686 | 1 | 0 | 0.99949 | -0.028262 | 56.8773
56 | 4.8254 | 2.1646 | -4.8253 | -2.1657 | 0.00013905 | -0.0011346 | 0.15267 | 0.15269 | 0.15269 | 1 | 0 | 0.99997 | -0.00015723 | 23.9319
57 | 11.4756 | 5.4451 | -11.475 | -5.4457 | 0.00060032 | -0.00056796 | 0.36686 | 0.36687 | 0.36687 | 0.99949 | -0.028262 | 0.99944 | -0.028479 | 57.5031
58 | 4.8253 | 2.1657 | -4.8229 | -2.1848 | 0.0023491 | -0.019123 | 0.15269 | 0.15293 | 0.15293 | 0.99997 | -0.00015723 | 0.99946 | -0.0027585 | 23.9699
59 | -0.12379 | -0.058826 | 0.12379 | 0.058139 | 6.0182e-07 | -0.00068703 | 0.0039591 | 0.0039506 | 0.0039591 | 0.99931 | -0.028842 | 0.99932 | -0.028882 | 1.7996
60 | 0.12379 | 0.058826 | -0.12379 | -0.059693 | 7.6289e-07 | -0.00086666 | 0.0039591 | 0.0039699 | 0.0039699 | 0.99931 | -0.028842 | 0.99931 | -0.028789 | 1.8045
61 | 0.12211 | 0.058209 | -0.12211 | -0.059142 | 8.0071e-07 | -0.00093344 | 0.0039078 | 0.0039195 | 0.0039195 | 0.99932 | -0.028882 | 0.99931 | -0.028826 | 1.7816
62 | -0.2459 | -0.11635 | 0.2459 | 0.11562 | 2.518e-06 | -0.00072832 | 0.0078584 | 0.0078494 | 0.0078584 | 0.99932 | -0.028882 | 0.99933 | -0.028966 | 3.572
63 | 0.12379 | 0.059693 | -0.12379 | -0.059952 | 2.2897e-07 | -0.00025918 | 0.0039699 | 0.0039732 | 0.0039732 | 0.99931 | -0.028789 | 0.9993 | -0.028773 | 1.806
64 | -0.2459 | -0.11562 | 0.24591 | 0.11559 | 2.8107e-06 | -2.8765e-05 | 0.0078494 | 0.0078491 | 0.0078494 | 0.99933 | -0.028966 | 0.99934 | -0.028882 | 3.7378
65 | 1.448 | 0.67256 | -1.4479 | -0.673 | 5.4721e-05 | -0.00044321 | 0.046119 | 0.046125 | 0.046125 | 0.99934 | -0.028882 | 0.9993 | -0.028583 | 20.9658
66 | 9.6415 | 4.5915 | -9.6401 | -4.5938 | 0.0014498 | -0.0022765 | 0.30848 | 0.30852 | 0.30852 | 0.99934 | -0.028882 | 0.99918 | -0.029491 | 48.3572
67 | -11.4739 | -5.4467 | 11.475 | 5.4457 | 0.0011188 | -0.0010581 | 0.36689 | 0.36687 | 0.36689 | 0.99934 | -0.028882 | 0.99944 | -0.028479 | 57.5064
68 | 1.4479 | 0.673 | -1.4479 | -0.67351 | 6.3155e-05 | -0.00051134 | 0.046125 | 0.046131 | 0.046131 | 0.9993 | -0.028583 | 0.99926 | -0.028237 | 20.9688
69 | 9.6401 | 4.5938 | -9.6381 | -4.5969 | 0.0019559 | -0.0030685 | 0.30852 | 0.30857 | 0.30857 | 0.99918 | -0.029491 | 0.99897 | -0.030309 | 48.3653
70 | 9.4802 | 4.5211 | -9.479 | -4.5181 | 0.0011315 | 0.0029952 | 0.30351 | 0.30351 | 0.30351 | 0.99897 | -0.030309 | 0.99875 | -0.042637 | 47.0555
71 | 0.15796 | 0.075804 | -0.15796 | -0.076502 | 1.0048e-06 | -0.00069814 | 0.005063 | 0.0050717 | 0.0050717 | 0.99897 | -0.030309 | 0.99897 | -0.030254 | 2.3053
72 | -0.14832 | -0.071834 | 0.14832 | 0.071776 | 1.9903e-06 | -5.735e-05 | 0.0047641 | 0.0047634 | 0.0047641 | 0.99856 | -0.014204 | 0.99858 | -0.014116 | 2.2686
73 | -0.098613 | -0.047761 | 0.098614 | 0.047132 | 3.5296e-07 | -0.00062869 | 0.0031677 | 0.0031598 | 0.0031677 | 0.99852 | -0.026057 | 0.99852 | -0.026088 | 1.4399
74 | -0.098614 | -0.047132 | 0.098615 | 0.044922 | 1.2268e-06 | -0.0022096 | 0.0031598 | 0.0031328 | 0.0031598 | 0.99852 | -0.026088 | 0.99853 | -0.026187 | 1.4363
75 | -0.098615 | -0.044922 | 0.098615 | 0.044801 | 6.6702e-08 | -0.00012125 | 0.0031328 | 0.0031314 | 0.0031328 | 0.99853 | -0.026187 | 0.99853 | -0.026192 | 1.424
76 | -0.22272 | -0.10491 | 0.22272 | 0.10442 | 1.3776e-06 | -0.00048493 | 0.0071174 | 0.0071115 | 0.0071174 | 0.99853 | -0.026192 | 0.99854 | -0.026243 | 3.2352
77 | -0.22272 | -0.10442 | 0.22273 | 0.1026 | 5.1725e-06 | -0.0018281 | 0.0071115 | 0.0070892 | 0.0071115 | 0.99854 | -0.026243 | 0.99856 | -0.026427 | 3.2325
78 | -0.11901 | -0.057637 | 0.11901 | 0.057442 | 1.5999e-07 | -0.00019529 | 0.0038228 | 0.0038204 | 0.0038228 | 0.9985 | -0.027446 | 0.9985 | -0.027458 | 1.7377
79 | -0.11901 | -0.057442 | 0.11901 | 0.053666 | 3.0533e-06 | -0.0037755 | 0.0038204 | 0.0037742 | 0.0038204 | 0.9985 | -0.027458 | 0.99852 | -0.027663 | 1.7365
80 | -0.11901 | -0.053666 | 0.11901 | 0.052047 | 1.2872e-06 | -0.0016193 | 0.0037742 | 0.0037552 | 0.0037742 | 0.99852 | -0.027663 | 0.99853 | -0.02774 | 1.7155
81 | 0.27638 | 0.12811 | -0.27636 | -0.12826 | 1.8519e-05 | -0.00014792 | 0.0088061 | 0.008808 | 0.008808 | 0.9986 | -0.027226 | 0.99853 | -0.02774 | 4.1943
82 | -0.41769 | -0.19655 | 0.41771 | 0.19652 | 1.0723e-05 | -3.3519e-05 | 0.013345 | 0.013344 | 0.013345 | 0.9986 | -0.027226 | 0.99863 | -0.027038 | 6.3546
83 | -0.41771 | -0.19652 | 0.41774 | 0.19287 | 3.6403e-05 | -0.003648 | 0.013344 | 0.013299 | 0.013344 | 0.99863 | -0.027038 | 0.99871 | -0.027733 | 6.0655
84 | 0.087067 | 0.042139 | -0.087067 | -0.042168 | 3.4588e-07 | -2.9224e-05 | 0.0027989 | 0.0027993 | 0.0027993 | 0.99765 | -0.094419 | 0.99765 | -0.094445 | 1.333
85 | -0.087067 | -0.042139 | 0.087068 | 0.04203 | 1.2927e-06 | -0.0001093 | 0.0027989 | 0.0027975 | 0.0027989 | 0.99765 | -0.094419 | 0.99767 | -0.09432 | 1.3328
86 | 8.1841 | 3.8858 | -8.1831 | -3.8833 | 0.0009327 | 0.0024558 | 0.26214 | 0.26214 | 0.26214 | 0.99767 | -0.09432 | 0.99746 | -0.10612 | 40.6423
87 | -8.8537 | -4.2095 | 8.8549 | 4.2127 | 0.0011928 | 0.0031505 | 0.28366 | 0.28366 | 0.28366 | 0.99767 | -0.09432 | 0.99792 | -0.080386 | 43.9788
88 | 0.47063 | 0.22756 | -0.47063 | -0.22761 | 6.2772e-07 | -4.8648e-05 | 0.015126 | 0.015127 | 0.015127 | 0.99767 | -0.09432 | 0.99767 | -0.094308 | 6.8757
89 | -8.9769 | -4.2731 | 8.9775 | 4.2721 | 0.00053368 | -0.0010068 | 0.28757 | 0.28755 | 0.28757 | 0.99804 | -0.07345 | 0.9981 | -0.073208 | 45.073
90 | 8.9769 | 4.2731 | -8.9763 | -4.2715 | 0.00060225 | 0.0015914 | 0.28757 | 0.28757 | 0.28757 | 0.99804 | -0.07345 | 0.99792 | -0.080386 | 44.5839
91 | 0.12054 | 0.057732 | -0.12054 | -0.058382 | 5.465e-07 | -0.00065006 | 0.0038656 | 0.0038738 | 0.0038738 | 0.9981 | -0.073208 | 0.9981 | -0.073169 | 1.7608
92 | -9.098 | -4.3298 | 9.099 | 4.3325 | 0.0010065 | 0.0026607 | 0.29142 | 0.29141 | 0.29142 | 0.9981 | -0.073208 | 0.99831 | -0.061773 | 45.1807
93 | 7.6731 | 3.6391 | -7.6727 | -3.6403 | 0.00043397 | -0.0012088 | 0.24578 | 0.24579 | 0.24579 | 0.99746 | -0.10612 | 0.9974 | -0.10636 | 38.5258
94 | 0.41103 | 0.19629 | -0.41102 | -0.19632 | 1.1358e-05 | -3.6454e-05 | 0.013182 | 0.013183 | 0.013183 | 0.99746 | -0.10612 | 0.99743 | -0.10631 | 6.2776
95 | 0.33359 | 0.16124 | -0.33358 | -0.16128 | 7.9853e-06 | -4.1328e-05 | 0.010721 | 0.010722 | 0.010722 | 0.99767 | -0.094308 | 0.99764 | -0.094467 | 5.1055
96 | -0.1488 | -0.072067 | 0.1488 | 0.072041 | 9.1326e-07 | -2.6014e-05 | 0.0047852 | 0.0047849 | 0.0047852 | 0.9974 | -0.10615 | 0.9974 | -0.10611 | 2.2787
97 | -0.22558 | -0.10923 | 0.22558 | 0.10868 | 1.6065e-06 | -0.00054322 | 0.007254 | 0.0072472 | 0.007254 | 0.9974 | -0.10611 | 0.99741 | -0.10617 | 3.2973
98 | 0.18543 | 0.088336 | -0.18543 | -0.088369 | 1.8465e-06 | -3.3671e-05 | 0.0059446 | 0.005945 | 0.005945 | 0.99741 | -0.10617 | 0.9974 | -0.10624 | 2.831
99 | -0.41101 | -0.19702 | 0.41102 | 0.19632 | 6.8175e-06 | -0.00069549 | 0.013192 | 0.013183 | 0.013192 | 0.99741 | -0.10617 | 0.99743 | -0.10631 | 5.9962
100 | 0.097324 | 0.0457 | -0.097324 | -0.045836 | 7.3683e-08 | -0.00013522 | 0.0031119 | 0.0031136 | 0.0031136 | 0.9974 | -0.10624 | 0.9974 | -0.10624 | 1.4153
101 | 0.097324 | 0.045836 | -0.097324 | -0.046654 | 4.4772e-07 | -0.00081889 | 0.0031136 | 0.0031238 | 0.0031238 | 0.9974 | -0.10624 | 0.9974 | -0.1062 | 1.4199
102 | 7.5203 | 3.5665 | -7.5197 | -3.5683 | 0.00059875 | -0.0017495 | 0.2409 | 0.24092 | 0.24092 | 0.9974 | -0.10636 | 0.99732 | -0.10669 | 37.7622
103 | -0.12556 | -0.060809 | 0.12556 | 0.060749 | 5.6612e-08 | -6.0538e-05 | 0.0040579 | 0.0040571 | 0.0040579 | 0.99244 | 0.0070152 | 0.99244 | 0.0070112 | 1.8445
104 | 1.9243 | 0.85723 | -1.9239 | -0.85901 | 0.00040498 | -0.0017787 | 0.061276 | 0.061299 | 0.061299 | 0.99244 | 0.0070112 | 0.99224 | 0.0085135 | 27.863
105 | 0.084547 | 0.03949 | -0.084547 | -0.040948 | 6.1455e-07 | -0.0014583 | 0.0027148 | 0.0027331 | 0.0027331 | 0.99224 | 0.0085135 | 0.99224 | 0.0085743 | 1.2423
106 | 1.8394 | 0.81952 | -1.839 | -0.81937 | 0.00035674 | 0.0001549 | 0.058584 | 0.058585 | 0.058585 | 0.99224 | 0.0085135 | 0.99204 | 0.0068368 | 27.8976
107 | 1.839 | 0.81937 | -1.8386 | -0.82147 | 0.00043653 | -0.0021076 | 0.058585 | 0.058611 | 0.058611 | 0.99204 | 0.0068368 | 0.99181 | 0.0085333 | 26.6416
108 | 1.8386 | 0.82147 | -1.8384 | -0.82208 | 0.00012663 | -0.00061084 | 0.058611 | 0.058619 | 0.058619 | 0.99181 | 0.0085333 | 0.99175 | 0.0090278 | 26.6451
109 | 1.7152 | 0.76241 | -1.715 | -0.76233 | 0.00019416 | 7.8756e-05 | 0.054636 | 0.054637 | 0.054637 | 0.99175 | 0.0090278 | 0.99163 | 0.0080428 | 26.0175
110 | 1.715 | 0.76233 | -1.7143 | -0.76652 | 0.00075001 | -0.00419 | 0.054637 | 0.054689 | 0.054689 | 0.99163 | 0.0080428 | 0.99122 | 0.011162 | 24.8586
111 | 0.16086 | 0.076983 | -0.16086 | -0.077906 | 1.4206e-06 | -0.000923 | 0.0051935 | 0.0052052 | 0.0052052 | 0.99122 | 0.011162 | 0.99121 | 0.011238 | 2.366
112 | -0.1617 | -0.078315 | 0.16172 | 0.077927 | 1.6289e-05 | -0.00038845 | 0.0052108 | 0.0052058 | 0.0052108 | 0.99535 | -0.10417 | 0.99545 | -0.1035 | 2.4813
113 | -0.31318 | -0.15128 | 0.31319 | 0.15119 | 1.612e-05 | -9.5136e-05 | 0.010086 | 0.010085 | 0.010086 | 0.99545 | -0.1035 | 0.99551 | -0.10316 | 4.8029
114 | -0.11927 | -0.057764 | 0.11927 | 0.057463 | 2.507e-07 | -0.00030163 | 0.0038412 | 0.0038374 | 0.0038412 | 0.99592 | -0.10691 | 0.99592 | -0.10693 | 1.746
115 | -0.11927 | -0.057463 | 0.11927 | 0.054032 | 2.8168e-06 | -0.0034304 | 0.0038374 | 0.0037953 | 0.0038374 | 0.99592 | -0.10693 | 0.99594 | -0.10712 | 1.7443
116 | 1.3095 | 0.62501 | -1.3094 | -0.62642 | 0.00014502 | -0.0014106 | 0.042058 | 0.042077 | 0.042077 | 0.99594 | -0.10712 | 0.99584 | -0.10619 | 19.1257
117 | -1.4288 | -0.67904 | 1.4289 | 0.67837 | 8.2144e-05 | -0.00066889 | 0.045853 | 0.045844 | 0.045853 | 0.99594 | -0.10712 | 0.99599 | -0.1076 | 20.8423
118 | 1.3094 | 0.62642 | -1.3093 | -0.62713 | 7.3756e-05 | -0.00071681 | 0.042077 | 0.042086 | 0.042086 | 0.99584 | -0.10619 | 0.99579 | -0.10571 | 19.1299
119 | -1.5013 | -0.71344 | 1.5013 | 0.71307 | 4.9291e-05 | -0.00036222 | 0.048176 | 0.048171 | 0.048176 | 0.99599 | -0.1076 | 0.99602 | -0.10788 | 21.8982
120 | 1.1722 | 0.56075 | -1.1721 | -0.56223 | 0.00012103 | -0.0014756 | 0.037671 | 0.03769 | 0.03769 | 0.99579 | -0.10571 | 0.99569 | -0.10483 | 17.1318
121 | -1.5013 | -0.71307 | 1.5015 | 0.7116 | 0.00019986 | -0.0014697 | 0.048171 | 0.048152 | 0.048171 | 0.99602 | -0.10788 | 0.99615 | -0.10898 | 21.896
122 | -1.6378 | -0.79161 | 1.6379 | 0.79096 | 0.00010662 | -0.0006478 | 0.052746 | 0.052738 | 0.052746 | 0.99554 | -0.12193 | 0.9956 | -0.12249 | 23.9755
123 | 1.5342 | 0.74146 | -1.534 | -0.74295 | 0.0002144 | -0.0014922 | 0.04941 | 0.04943 | 0.04943 | 0.99554 | -0.12193 | 0.99541 | -0.12072 | 22.468
124 | -1.76 | -0.85011 | 1.7602 | 0.84911 | 0.00019073 | -0.00099654 | 0.056672 | 0.056659 | 0.056672 | 0.9956 | -0.12249 | 0.9957 | -0.12343 | 25.76
125 | -1.7602 | -0.84911 | 1.7603 | 0.84862 | 9.414e-05 | -0.00049214 | 0.056659 | 0.056652 | 0.056659 | 0.9957 | -0.12343 | 0.99575 | -0.12389 | 25.754
126 | -2.1035 | -1.0145 | 2.1039 | 1.0132 | 0.00037786 | -0.0013503 | 0.067704 | 0.067686 | 0.067704 | 0.99575 | -0.12389 | 0.99592 | -0.12544 | 30.7746
127 | 0.34323 | 0.16589 | -0.34323 | -0.16592 | 7.8679e-06 | -3.7864e-05 | 0.011052 | 0.011052 | 0.011052 | 0.99575 | -0.12389 | 0.99573 | -0.12405 | 5.263
128 | -0.099355 | -0.04812 | 0.099355 | 0.047952 | 9.6613e-08 | -0.0001678 | 0.0031981 | 0.0031959 | 0.0031981 | 0.99648 | -0.10998 | 0.99648 | -0.10999 | 1.4537
129 | 6.5057 | 3.1094 | -6.5048 | -3.1134 | 0.00096908 | -0.0039366 | 0.20889 | 0.20894 | 0.20894 | 0.99648 | -0.10999 | 0.99633 | -0.11058 | 32.75
130 | -6.6051 | -3.1574 | 6.6068 | 3.1506 | 0.0017368 | -0.0068239 | 0.21208 | 0.21199 | 0.21208 | 0.99648 | -0.10999 | 0.99675 | -0.10894 | 33.2421
131 | -0.1301 | -0.063011 | 0.1301 | 0.062795 | 2.1458e-07 | -0.00021668 | 0.0041911 | 0.0041883 | 0.0041911 | 0.9957 | -0.12338 | 0.9957 | -0.1234 | 1.905
132 | -0.24362 | -0.11778 | 0.24363 | 0.11695 | 2.865e-06 | -0.00082561 | 0.0078453 | 0.0078349 | 0.0078453 | 0.9957 | -0.1234 | 0.99571 | -0.1235 | 3.566
133 | 2.0322 | 0.97796 | -2.0316 | -0.98019 | 0.00057921 | -0.0022287 | 0.065385 | 0.065415 | 0.065415 | 0.99571 | -0.1235 | 0.99544 | -0.12104 | 29.7341
134 | -2.354 | -1.1328 | 2.3546 | 1.1313 | 0.0005333 | -0.0014911 | 0.075739 | 0.075718 | 0.075739 | 0.99571 | -0.1235 | 0.99592 | -0.12544 | 34.4268
135 | 0.078213 | 0.037858 | -0.078213 | -0.03788 | 2.137e-07 | -2.2232e-05 | 0.0025192 | 0.0025195 | 0.0025195 | 0.99571 | -0.1235 | 0.99571 | -0.12352 | 1.1998
136 | 0.74127 | 0.35848 | -0.74125 | -0.359 | 1.6908e-05 | -0.00052037 | 0.023878 | 0.023885 | 0.023885 | 0.99544 | -0.12104 | 0.99542 | -0.12085 | 10.8568
137 | 1.2904 | 0.6217 | -1.2901 | -0.6242 | 0.00025057 | -0.0024971 | 0.041537 | 0.041569 | 0.041569 | 0.99544 | -0.12104 | 0.99527 | -0.11936 | 18.8951
138 | -4.4585 | -2.1444 | 4.4588 | 2.1436 | 0.00029369 | -0.00079284 | 0.1434 | 0.14339 | 0.1434 | 0.99592 | -0.12544 | 0.99599 | -0.12469 | 39.6143
139 | 1.2901 | 0.6242 | -1.29 | -0.6248 | 6.0274e-05 | -0.00059992 | 0.041569 | 0.041577 | 0.041577 | 0.99527 | -0.11936 | 0.99522 | -0.11896 | 18.8986
140 | 0.11914 | 0.057395 | -0.11914 | -0.057704 | 2.5614e-07 | -0.00030858 | 0.003834 | 0.0038379 | 0.0038379 | 0.99573 | -0.12405 | 0.99573 | -0.12403 | 1.7445
141 | -4.5958 | -2.2087 | 4.5958 | 2.2082 | 5.7292e-05 | -0.00049689 | 0.14779 | 0.14778 | 0.14779 | 0.99599 | -0.12469 | 0.996 | -0.12464 | 23.1642
142 | 0.137 | 0.065088 | -0.137 | -0.066226 | 1.2435e-06 | -0.0011375 | 0.0043961 | 0.0044104 | 0.0044104 | 0.99599 | -0.12469 | 0.99598 | -0.12461 | 2.0047
143 | -4.694 | -2.2558 | 4.6943 | 2.2538 | 0.00024295 | -0.0020147 | 0.15094 | 0.15092 | 0.15094 | 0.996 | -0.12464 | 0.99606 | -0.12444 | 23.6588
144 | 0.137 | 0.066226 | -0.137 | -0.066352 | 1.3838e-07 | -0.00012613 | 0.0044104 | 0.004412 | 0.004412 | 0.99598 | -0.12461 | 0.99598 | -0.1246 | 2.0054
145 | -0.15205 | -0.073642 | 0.15205 | 0.073592 | 1.8327e-06 | -4.9932e-05 | 0.0048902 | 0.0048896 | 0.0048902 | 0.9973 | -0.10674 | 0.99731 | -0.10667 | 2.3287
146 | -0.15205 | -0.073592 | 0.15205 | 0.073312 | 3.7624e-07 | -0.00028004 | 0.0048896 | 0.0048861 | 0.0048896 | 0.99731 | -0.10667 | 0.99732 | -0.10669 | 2.2225
147 | 7.3677 | 3.4949 | -7.3673 | -3.4962 | 0.00040036 | -0.0012277 | 0.23604 | 0.23605 | 0.23605 | 0.99732 | -0.10669 | 0.99726 | -0.10691 | 36.9992
148 | 7.3673 | 3.4962 | -7.367 | -3.4971 | 0.00030903 | -0.00094741 | 0.23605 | 0.23607 | 0.23607 | 0.99726 | -0.10691 | 0.99722 | -0.10709 | 37.0014
149 | 7.2764 | 3.4532 | -7.276 | -3.4543 | 0.00034585 | -0.0010916 | 0.23315 | 0.23317 | 0.23317 | 0.99722 | -0.10709 | 0.99717 | -0.10728 | 36.547
150 | 0.097324 | 0.046654 | -0.097324 | -0.047136 | 2.6467e-07 | -0.00048157 | 0.0031238 | 0.0031298 | 0.0031298 | 0.9974 | -0.1062 | 0.99739 | -0.10617 | 1.4226
151 | 7.1249 | 3.3811 | -7.1246 | -3.3821 | 0.00030885 | -0.001024 | 0.22831 | 0.22832 | 0.22832 | 0.99717 | -0.10728 | 0.99712 | -0.10746 | 35.7873
152 | 6.7241 | 3.2021 | -6.7239 | -3.203 | 0.00024061 | -0.00090934 | 0.21569 | 0.2157 | 0.2157 | 0.99679 | -0.10879 | 0.99675 | -0.10894 | 33.8088
153 | -6.8767 | -3.276 | 6.877 | 3.2748 | 0.00031509 | -0.0011309 | 0.2206 | 0.22058 | 0.2206 | 0.99679 | -0.10879 | 0.99683 | -0.10861 | 34.5764
154 | 0.11702 | 0.052399 | -0.11702 | -0.056207 | 2.9926e-06 | -0.0038081 | 0.0037134 | 0.0037599 | 0.0037599 | 0.99675 | -0.10894 | 0.99673 | -0.10874 | 1.709
155 | -6.877 | -3.2748 | 6.879 | 3.2679 | 0.0019299 | -0.0069336 | 0.22058 | 0.22048 | 0.22058 | 0.99683 | -0.10861 | 0.99712 | -0.10746 | 34.5739
156 | 0.11702 | 0.056207 | -0.11702 | -0.056676 | 3.7344e-07 | -0.00046852 | 0.0037599 | 0.0037658 | 0.0037658 | 0.99673 | -0.10874 | 0.99672 | -0.10871 | 1.7117
157 | 0.2456 | 0.11423 | -0.2456 | -0.11621 | 6.872e-06 | -0.0019789 | 0.0078418 | 0.0078662 | 0.0078662 | 0.99712 | -0.10746 | 0.9971 | -0.10723 | 3.5755
158 | 1.7423 | 0.82611 | -1.7421 | -0.82707 | 0.00017822 | -0.00096051 | 0.055868 | 0.055881 | 0.055881 | 0.99633 | -0.11058 | 0.99623 | -0.10973 | 25.4004
159 | 4.7625 | 2.2873 | -4.7625 | -2.2875 | 2.6523e-05 | -0.00021353 | 0.15308 | 0.15308 | 0.15308 | 0.99633 | -0.11058 | 0.99632 | -0.1106 | 23.9937
160 | -0.11239 | -0.054176 | 0.11239 | 0.051734 | 1.7774e-06 | -0.0024421 | 0.0036121 | 0.003582 | 0.0036121 | 0.99708 | -0.10711 | 0.9971 | -0.10723 | 1.6419
161 | 0.11239 | 0.054176 | -0.11239 | -0.054431 | 1.8743e-07 | -0.00025514 | 0.0036121 | 0.0036154 | 0.0036154 | 0.99708 | -0.10711 | 0.99708 | -0.10709 | 1.6433
162 | 0.13321 | 0.064475 | -0.13321 | -0.064515 | 1.1096e-06 | -3.9564e-05 | 0.0042846 | 0.0042851 | 0.0042851 | 0.9971 | -0.10723 | 0.99709 | -0.10729 | 2.0405
163 | 1.6418 | 0.7785 | -1.6417 | -0.77939 | 0.00014712 | -0.00089805 | 0.052652 | 0.052663 | 0.052663 | 0.99623 | -0.10973 | 0.99615 | -0.10898 | 23.9379
164 | 4.7625 | 2.2875 | -4.7621 | -2.2866 | 0.0003294 | 0.00083177 | 0.15308 | 0.15308 | 0.15308 | 0.99632 | -0.1106 | 0.99619 | -0.11771 | 23.7334
165 | 9.3425 | 4.4519 | -9.3416 | -4.4497 | 0.00085223 | 0.0022549 | 0.29912 | 0.29912 | 0.29912 | 0.99875 | -0.042637 | 0.99858 | -0.052062 | 46.3758
166 | 9.3416 | 4.4497 | -9.3407 | -4.4513 | 0.00096956 | -0.0016508 | 0.29912 | 0.29915 | 0.29915 | 0.99858 | -0.052062 | 0.99848 | -0.052482 | 46.8889
167 | 9.2009 | 4.3837 | -9.2001 | -4.3815 | 0.00082723 | 0.0021877 | 0.29466 | 0.29466 | 0.29466 | 0.99848 | -0.052482 | 0.99831 | -0.061773 | 45.6841
168 | -0.092235 | -0.044672 | 0.092236 | 0.044649 | 3.0683e-07 | -2.3077e-05 | 0.0029655 | 0.0029652 | 0.0029655 | 0.99763 | -0.094457 | 0.99764 | -0.094435 | 1.4121
169 | -0.25137 | -0.12172 | 0.25137 | 0.12147 | 9.359e-07 | -0.00025489 | 0.0080816 | 0.0080784 | 0.0080816 | 0.99764 | -0.094435 | 0.99764 | -0.094467 | 3.6735
170 | 0.14013 | 0.06779 | -0.14013 | -0.067869 | 2.4617e-06 | -7.8867e-05 | 0.0045112 | 0.0045122 | 0.0045122 | 0.99615 | -0.10898 | 0.99613 | -0.1091 | 2.1487
171 | 0.76263 | 0.3639 | -0.76257 | -0.36558 | 5.7328e-05 | -0.001675 | 0.024499 | 0.02452 | 0.02452 | 0.99569 | -0.10483 | 0.99562 | -0.10419 | 11.1454
172 | 4.6946 | 2.254 | -4.6943 | -2.2532 | 0.00030433 | 0.00076703 | 0.15091 | 0.15091 | 0.15091 | 0.99619 | -0.11771 | 0.99607 | -0.12438 | 23.3966
173 | 4.6943 | 2.2532 | -4.6943 | -2.2538 | 7.0268e-05 | -0.00058288 | 0.15091 | 0.15092 | 0.15092 | 0.99607 | -0.12438 | 0.99606 | -0.12444 | 23.6545
174 | -0.15201 | -0.073623 | 0.15201 | 0.072276 | 1.7882e-06 | -0.0013465 | 0.0048785 | 0.0048616 | 0.0048785 | 0.99945 | -0.0026581 | 0.99946 | -0.0027585 | 2.2175
175 | 0.33862 | 0.15212 | -0.33862 | -0.1524 | 1.788e-06 | -0.00027725 | 0.010722 | 0.010725 | 0.010725 | 0.99946 | -0.0027585 | 0.99946 | -0.00272 | 4.8751
176 | 0.19453 | 0.082611 | -0.19453 | -0.082861 | 5.2396e-07 | -0.00025094 | 0.0061043 | 0.0061071 | 0.0061071 | 0.99946 | -0.00272 | 0.99946 | -0.0027032 | 2.776
177 | 0.19453 | 0.082861 | -0.19452 | -0.08679 | 8.2673e-06 | -0.0039285 | 0.0061071 | 0.0061525 | 0.0061525 | 0.99946 | -0.0027032 | 0.99941 | -0.0024179 | 2.7966
178 | 1.0969 | 0.50477 | -1.0967 | -0.50858 | 0.00026602 | -0.0038141 | 0.034894 | 0.034941 | 0.034941 | 0.99894 | -0.029627 | 0.99871 | -0.027733 | 15.8824
179 | -1.0969 | -0.50477 | 1.097 | 0.50375 | 7.0984e-05 | -0.0010198 | 0.034894 | 0.034881 | 0.034894 | 0.99894 | -0.029627 | 0.999 | -0.030126 | 15.8609
180 | 0.67891 | 0.31571 | -0.67888 | -0.31664 | 2.4715e-05 | -0.00093348 | 0.021642 | 0.021653 | 0.021653 | 0.99871 | -0.027733 | 0.99868 | -0.027443 | 9.8424
181 | -1.3223 | -0.61277 | 1.3226 | 0.61285 | 0.00032498 | 8.0988e-05 | 0.042113 | 0.042112 | 0.042113 | 0.999 | -0.030126 | 0.99926 | -0.028237 | 20.0539
182 | 0.12086 | 0.058438 | -0.12086 | -0.058534 | 2.1848e-06 | -9.5684e-05 | 0.0038792 | 0.0038804 | 0.0038804 | 0.999 | -0.030126 | 0.99898 | -0.030245 | 1.8478
183 | 0.52231 | 0.24081 | -0.5223 | -0.24181 | 1.559e-05 | -0.0010007 | 0.016625 | 0.016637 | 0.016637 | 0.99868 | -0.027443 | 0.99865 | -0.02721 | 7.5625
184 | 0.094464 | 0.045713 | -0.094464 | -0.045751 | 5.2037e-07 | -3.757e-05 | 0.0030312 | 0.0030317 | 0.0030317 | 0.99941 | -0.0024179 | 0.99941 | -0.0024543 | 1.4437
185 | 0.10006 | 0.041077 | -0.10005 | -0.047667 | 3.688e-06 | -0.00659 | 0.0031241 | 0.0032013 | 0.0032013 | 0.99941 | -0.0024179 | 0.99938 | -0.0021588 | 1.4551
186 | 0.5223 | 0.24181 | -0.52228 | -0.24286 | 1.6379e-05 | -0.0010497 | 0.016637 | 0.01665 | 0.01665 | 0.99865 | -0.02721 | 0.99862 | -0.026963 | 7.5683
187 | 0.10005 | 0.047667 | -0.10005 | -0.048458 | 4.5524e-07 | -0.0007909 | 0.0032013 | 0.0032112 | 0.0032112 | 0.99938 | -0.0021588 | 0.99938 | -0.0021198 | 1.4596
188 | -0.16125 | -0.078097 | 0.16125 | 0.076898 | 1.7999e-06 | -0.0011996 | 0.0051793 | 0.0051643 | 0.0051793 | 0.99861 | -0.026867 | 0.99862 | -0.026963 | 2.3542
189 | 0.36103 | 0.16597 | -0.36102 | -0.16765 | 1.2539e-05 | -0.0016882 | 0.011486 | 0.011507 | 0.011507 | 0.99862 | -0.026963 | 0.99859 | -0.026692 | 5.2304
190 | 0.36102 | 0.16765 | -0.36101 | -0.16883 | 8.7742e-06 | -0.0011777 | 0.011507 | 0.011521 | 0.011521 | 0.99859 | -0.026692 | 0.99857 | -0.026498 | 5.2369
191 | 0.22273 | 0.10186 | -0.22273 | -0.1026 | 2.067e-06 | -0.00073378 | 0.0070803 | 0.0070892 | 0.0070892 | 0.99857 | -0.026498 | 0.99856 | -0.026427 | 3.2224
192 | 0.30537 | 0.14524 | -0.30536 | -0.14687 | 9.1258e-06 | -0.0016287 | 0.009876 | 0.0098965 | 0.0098965 | 0.98841 | 0.017186 | 0.98839 | 0.017439 | 4.4984
193 | 0.10859 | 0.051573 | -0.10859 | -0.052591 | 7.2086e-07 | -0.0010178 | 0.003511 | 0.0035238 | 0.0035238 | 0.98839 | 0.017439 | 0.98838 | 0.017496 | 1.6017
194 | 0.76257 | 0.36558 | -0.76248 | -0.36826 | 9.2027e-05 | -0.0026823 | 0.02452 | 0.024554 | 0.024554 | 0.99562 | -0.10419 | 0.99551 | -0.10316 | 11.1609
195 | 0.44929 | 0.21707 | -0.44928 | -0.2176 | 6.2276e-06 | -0.00052514 | 0.014469 | 0.014476 | 0.014476 | 0.99551 | -0.10316 | 0.9955 | -0.10304 | 6.5799

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 16.5799 | 7.7551

## res_load
| p_mw | q_mvar
0 | 0.11839 | 0.057339
1 | 0.16123 | 0.078088
2 | 0.12364 | 0.059882
3 | 0.079107 | 0.038313
4 | 0.12899 | 0.062472
5 | 0.09754 | 0.047241
6 | 0.071977 | 0.03486
7 | 0.12699 | 0.061503
8 | 0.12218 | 0.059174
9 | 0.16375 | 0.079308
10 | 0.16209 | 0.078506
11 | 0.10878 | 0.052685
12 | 0.11134 | 0.053926
13 | 0.079125 | 0.038322
14 | 0.094458 | 0.045748
15 | 0.16296 | 0.078923
16 | 0.16093 | 0.077944
17 | 0.31395 | 0.15205
18 | 0.11635 | 0.056349
19 | 0.069878 | 0.033843
20 | 0.14144 | 0.068502
21 | 0.15852 | 0.076773
22 | 0.22941 | 0.11111
23 | 0.15355 | 0.07437
24 | 0.099547 | 0.048213
25 | 0.12817 | 0.062077
26 | 0.13356 | 0.064687
27 | 0.12211 | 0.059142
28 | 0.12379 | 0.059952
29 | 0.13846 | 0.06706
30 | 0.14832 | 0.071834
31 | 0.098613 | 0.047761
32 | 0.12411 | 0.060108
33 | 0.11901 | 0.057637
34 | 0.14132 | 0.068442
35 | 0.15735 | 0.076208
36 | 0.087067 | 0.042168
37 | 0.1119 | 0.054194
38 | 0.12146 | 0.058827
39 | 0.099024 | 0.047959
40 | 0.13704 | 0.06637
41 | 0.1488 | 0.072067
42 | 0.07678 | 0.037186
43 | 0.088101 | 0.042669
44 | 0.1523 | 0.073765
45 | 0.12556 | 0.060809
46 | 0.12321 | 0.059676
47 | 0.084547 | 0.040948
48 | 0.16086 | 0.077906
49 | 0.1617 | 0.078315
50 | 0.15146 | 0.073356
51 | 0.11927 | 0.057764
52 | 0.072403 | 0.035066
53 | 0.13706 | 0.06638
54 | 0.10355 | 0.05015
55 | 0.12212 | 0.059148
56 | 1.534 | 0.74295
57 | 0.099355 | 0.04812
58 | 0.1301 | 0.063011
59 | 0.11352 | 0.054981
60 | 0.078213 | 0.03788
61 | 0.74125 | 0.359
62 | 0.22408 | 0.10853
63 | 0.11914 | 0.057704
64 | 0.098198 | 0.04756
65 | 0.15205 | 0.073642
66 | 0.090628 | 0.043893
67 | 0.097324 | 0.047136
68 | 0.15114 | 0.0732
69 | 0.15261 | 0.073914
70 | 0.11702 | 0.056676
71 | 0.11239 | 0.054431
72 | 0.13321 | 0.064515
73 | 0.1003 | 0.048577
74 | 0.15796 | 0.076502
75 | 0.13654 | 0.066131
76 | 0.13973 | 0.067675
77 | 0.092235 | 0.044672
78 | 0.15914 | 0.077074
79 | 0.14013 | 0.067869
80 | 0.4095 | 0.19833
81 | 0.067495 | 0.032689
82 | 0.137 | 0.066352
83 | 0.082209 | 0.039816
84 | 0.12054 | 0.058382
85 | 0.1011 | 0.048963
86 | 0.15201 | 0.073623
87 | 0.14409 | 0.069786
88 | 0.10445 | 0.050589
89 | 0.15657 | 0.075831
90 | 0.12524 | 0.060659
91 | 0.12086 | 0.058534
92 | 0.10005 | 0.048458
93 | 0.094464 | 0.045751
94 | 0.16125 | 0.078097
95 | 0.13828 | 0.06697
96 | 0.19677 | 0.095301
97 | 0.10859 | 0.052591
98 | 1.29 | 0.6248
99 | 0.44928 | 0.2176

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1