## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_150_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_150_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_150_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_150_0_node_4 | 20 | n |  | TRUE
4 | bus_MV_150_0_node_67 | 20 | n |  | TRUE
5 | bus_MV_150_0_node_68 | 20 | n |  | TRUE
6 | bus_MV_150_0_node_62 | 20 | n |  | TRUE
7 | bus_MV_150_0_node_71 | 20 | n |  | TRUE
8 | bus_MV_150_0_node_188 | 20 | n |  | TRUE
9 | bus_MV_150_0_node_80 | 20 | n |  | TRUE
10 | bus_MV_150_0_node_61 | 20 | n |  | TRUE
11 | bus_MV_150_0_node_33 | 20 | n |  | TRUE
12 | bus_MV_150_0_node_34 | 20 | n |  | TRUE
13 | bus_MV_150_0_node_81 | 20 | n |  | TRUE
14 | bus_MV_150_0_node_5 | 20 | n |  | TRUE
15 | bus_MV_150_0_node_6 | 20 | n |  | TRUE
16 | bus_MV_150_0_node_7 | 20 | n |  | TRUE
17 | bus_MV_150_0_node_8 | 20 | n |  | TRUE
18 | bus_MV_150_0_node_39 | 20 | n |  | TRUE
19 | bus_MV_150_0_node_37 | 20 | n |  | TRUE
20 | bus_MV_150_0_node_165 | 20 | n |  | TRUE
21 | bus_MV_150_0_node_47 | 20 | n |  | TRUE
22 | bus_MV_150_0_node_55 | 20 | n |  | TRUE
23 | bus_MV_150_0_node_38 | 20 | n |  | TRUE
24 | bus_MV_150_0_node_166 | 20 | n |  | TRUE
25 | bus_MV_150_0_node_9 | 20 | n |  | TRUE
26 | bus_MV_150_0_node_11 | 20 | n |  | TRUE
27 | bus_MV_150_0_node_12 | 20 | n |  | TRUE
28 | bus_MV_150_0_node_10 | 20 | n |  | TRUE
29 | bus_MV_150_0_node_13 | 20 | n |  | TRUE
30 | bus_MV_150_0_node_63 | 20 | n |  | TRUE
31 | bus_MV_150_0_node_45 | 20 | n |  | TRUE
32 | bus_MV_150_0_node_14 | 20 | n |  | TRUE
33 | bus_MV_150_0_node_31 | 20 | n |  | TRUE
34 | bus_MV_150_0_node_72 | 20 | n |  | TRUE
35 | bus_MV_150_0_node_50 | 20 | n |  | TRUE
36 | bus_MV_150_0_node_32 | 20 | n |  | TRUE
37 | bus_MV_150_0_node_30 | 20 | n |  | TRUE
38 | bus_MV_150_0_node_49 | 20 | n |  | TRUE
39 | bus_MV_150_0_node_48 | 20 | n |  | TRUE
40 | bus_MV_150_0_node_51 | 20 | n |  | TRUE
41 | bus_MV_150_0_node_54 | 20 | n |  | TRUE
42 | bus_MV_150_0_node_15 | 20 | n |  | TRUE
43 | bus_MV_150_0_node_17 | 20 | n |  | TRUE
44 | bus_MV_150_0_node_16 | 20 | n |  | TRUE
45 | bus_MV_150_0_node_20 | 20 | n |  | TRUE
46 | bus_MV_150_0_node_19 | 20 | n |  | TRUE
47 | bus_MV_150_0_node_197 | 20 | n |  | TRUE
48 | bus_MV_150_0_node_79 | 20 | n |  | TRUE
49 | bus_MV_150_0_node_21 | 20 | n |  | TRUE
50 | bus_MV_150_0_node_78 | 20 | n |  | TRUE
51 | bus_MV_150_0_node_27 | 20 | n |  | TRUE
52 | bus_MV_150_0_node_24 | 20 | n |  | TRUE
53 | bus_MV_150_0_node_22 | 20 | n |  | TRUE
54 | bus_MV_150_0_node_23 | 20 | n |  | TRUE
55 | bus_MV_150_0_node_28 | 20 | n |  | TRUE
56 | bus_MV_150_0_node_25 | 20 | n |  | TRUE
57 | bus_MV_150_0_node_29 | 20 | n |  | TRUE
58 | bus_MV_150_0_node_26 | 20 | n |  | TRUE
59 | bus_MV_150_0_node_36 | 20 | n |  | TRUE
60 | bus_MV_150_0_node_187 | 20 | n |  | TRUE
61 | bus_MV_150_0_node_73 | 20 | n |  | TRUE
62 | bus_MV_150_0_node_74 | 20 | n |  | TRUE
63 | bus_MV_150_0_node_35 | 20 | n |  | TRUE
64 | bus_MV_150_0_node_41 | 20 | n |  | TRUE
65 | bus_MV_150_0_node_42 | 20 | n |  | TRUE
66 | bus_MV_150_0_node_83 | 20 | n |  | TRUE
67 | bus_MV_150_0_node_40 | 20 | n |  | TRUE
68 | bus_MV_150_0_node_198 | 20 | n |  | TRUE
69 | bus_MV_150_0_node_43 | 20 | n |  | TRUE
70 | bus_MV_150_0_node_44 | 20 | n |  | TRUE
71 | bus_MV_150_0_node_46 | 20 | n |  | TRUE
72 | bus_MV_150_0_node_207 | 20 | n |  | TRUE
73 | bus_MV_150_0_node_52 | 20 | n |  | TRUE
74 | bus_MV_150_0_node_206 | 20 | n |  | TRUE
75 | bus_MV_150_0_node_53 | 20 | n |  | TRUE
76 | bus_MV_150_0_node_196 | 20 | n |  | TRUE
77 | bus_MV_150_0_node_148 | 20 | n |  | TRUE
78 | bus_MV_150_0_node_149 | 20 | n |  | TRUE
79 | bus_MV_150_0_node_150 | 20 | n |  | TRUE
80 | bus_MV_150_0_node_56 | 20 | n |  | TRUE
81 | bus_MV_150_0_node_57 | 20 | n |  | TRUE
82 | bus_MV_150_0_node_75 | 20 | n |  | TRUE
83 | bus_MV_150_0_node_58 | 20 | n |  | TRUE
84 | bus_MV_150_0_node_170 | 20 | n |  | TRUE
85 | bus_MV_150_0_node_168 | 20 | n |  | TRUE
86 | bus_MV_150_0_node_59 | 20 | n |  | TRUE
87 | bus_MV_150_0_node_60 | 20 | n |  | TRUE
88 | bus_MV_150_0_node_70 | 20 | n |  | TRUE
89 | bus_MV_150_0_node_64 | 20 | n |  | TRUE
90 | bus_MV_150_0_node_65 | 20 | n |  | TRUE
91 | bus_MV_150_0_node_66 | 20 | n |  | TRUE
92 | bus_MV_150_0_node_77 | 20 | n |  | TRUE
93 | bus_MV_150_0_node_69 | 20 | n |  | TRUE
94 | bus_MV_150_0_node_190 | 20 | n |  | TRUE
95 | bus_MV_150_0_node_88 | 20 | n |  | TRUE
96 | bus_MV_150_0_node_82 | 20 | n |  | TRUE
97 | bus_MV_150_0_node_189 | 20 | n |  | TRUE
98 | bus_MV_150_0_node_99 | 20 | n |  | TRUE
99 | bus_MV_150_0_node_85 | 20 | n |  | TRUE
100 | bus_MV_150_0_node_86 | 20 | n |  | TRUE
101 | bus_MV_150_0_node_205 | 20 | n |  | TRUE
102 | bus_MV_150_0_node_87 | 20 | n |  | TRUE
103 | bus_MV_150_0_node_211 | 20 | n |  | TRUE
104 | bus_MV_150_0_node_97 | 20 | n |  | TRUE
105 | bus_MV_150_0_node_98 | 20 | n |  | TRUE
106 | bus_MV_150_0_node_96 | 20 | n |  | TRUE
107 | bus_MV_150_0_node_89 | 20 | n |  | TRUE
108 | bus_MV_150_0_node_90 | 20 | n |  | TRUE
109 | bus_MV_150_0_node_91 | 20 | n |  | TRUE
110 | bus_MV_150_0_node_94 | 20 | n |  | TRUE
111 | bus_MV_150_0_node_213 | 20 | n |  | TRUE
112 | bus_MV_150_0_node_208 | 20 | n |  | TRUE
113 | bus_MV_150_0_node_92 | 20 | n |  | TRUE
114 | bus_MV_150_0_node_93 | 20 | n |  | TRUE
115 | bus_MV_150_0_node_210 | 20 | n |  | TRUE
116 | bus_MV_150_0_node_215 | 20 | n |  | TRUE
117 | bus_MV_150_0_node_101 | 20 | n |  | TRUE
118 | bus_MV_150_0_node_102 | 20 | n |  | TRUE
119 | bus_MV_150_0_node_209 | 20 | n |  | TRUE
120 | bus_MV_150_0_node_143 | 20 | n |  | TRUE
121 | bus_MV_150_0_node_126 | 20 | n |  | TRUE
122 | bus_MV_150_0_node_100 | 20 | n |  | TRUE
123 | bus_MV_150_0_node_186 | 20 | n |  | TRUE
124 | bus_MV_150_0_node_185 | 20 | n |  | TRUE
125 | bus_MV_150_0_node_212 | 20 | n |  | TRUE
126 | bus_MV_150_0_node_214 | 20 | n |  | TRUE
127 | bus_MV_150_0_node_103 | 20 | n |  | TRUE
128 | bus_MV_150_0_node_104 | 20 | n |  | TRUE
129 | bus_MV_150_0_node_142 | 20 | n |  | TRUE
130 | bus_MV_150_0_node_105 | 20 | n |  | TRUE
131 | bus_MV_150_0_node_110 | 20 | n |  | TRUE
132 | bus_MV_150_0_node_177 | 20 | n |  | TRUE
133 | bus_MV_150_0_node_164 | 20 | n |  | TRUE
134 | bus_MV_150_0_node_106 | 20 | n |  | TRUE
135 | bus_MV_150_0_node_107 | 20 | n |  | TRUE
136 | bus_MV_150_0_node_108 | 20 | n |  | TRUE
137 | bus_MV_150_0_node_136 | 20 | n |  | TRUE
138 | bus_MV_150_0_node_111 | 20 | n |  | TRUE
139 | bus_MV_150_0_node_137 | 20 | n |  | TRUE
140 | bus_MV_150_0_node_131 | 20 | n |  | TRUE
141 | bus_MV_150_0_node_132 | 20 | n |  | TRUE
142 | bus_MV_150_0_node_135 | 20 | n |  | TRUE
143 | bus_MV_150_0_node_133 | 20 | n |  | TRUE
144 | bus_MV_150_0_node_134 | 20 | n |  | TRUE
145 | bus_MV_150_0_node_171 | 20 | n |  | TRUE
146 | bus_MV_150_0_node_191 | 20 | n |  | TRUE
147 | bus_MV_150_0_node_115 | 20 | n |  | TRUE
148 | bus_MV_150_0_node_116 | 20 | n |  | TRUE
149 | bus_MV_150_0_node_152 | 20 | n |  | TRUE
150 | bus_MV_150_0_node_156 | 20 | n |  | TRUE
151 | bus_MV_150_0_node_109 | 20 | n |  | TRUE
152 | bus_MV_150_0_node_175 | 20 | n |  | TRUE
153 | bus_MV_150_0_node_121 | 20 | n |  | TRUE
154 | bus_MV_150_0_node_130 | 20 | n |  | TRUE
155 | bus_MV_150_0_node_112 | 20 | n |  | TRUE
156 | bus_MV_150_0_node_113 | 20 | n |  | TRUE
157 | bus_MV_150_0_node_122 | 20 | n |  | TRUE
158 | bus_MV_150_0_node_146 | 20 | n |  | TRUE
159 | bus_MV_150_0_node_172 | 20 | n |  | TRUE
160 | bus_MV_150_0_node_117 | 20 | n |  | TRUE
161 | bus_MV_150_0_node_144 | 20 | n |  | TRUE
162 | bus_MV_150_0_node_145 | 20 | n |  | TRUE
163 | bus_MV_150_0_node_183 | 20 | n |  | TRUE
164 | bus_MV_150_0_node_147 | 20 | n |  | TRUE
165 | bus_MV_150_0_node_184 | 20 | n |  | TRUE
166 | bus_MV_150_0_node_140 | 20 | n |  | TRUE
167 | bus_MV_150_0_node_120 | 20 | n |  | TRUE
168 | bus_MV_150_0_node_162 | 20 | n |  | TRUE
169 | bus_MV_150_0_node_153 | 20 | n |  | TRUE
170 | bus_MV_150_0_node_155 | 20 | n |  | TRUE
171 | bus_MV_150_0_node_154 | 20 | n |  | TRUE
172 | bus_MV_150_0_node_163 | 20 | n |  | TRUE
173 | bus_MV_150_0_node_200 | 20 | n |  | TRUE
174 | bus_MV_150_0_node_201 | 20 | n |  | TRUE
175 | bus_MV_150_0_node_118 | 20 | n |  | TRUE
176 | bus_MV_150_0_node_127 | 20 | n |  | TRUE
177 | bus_MV_150_0_node_158 | 20 | n |  | TRUE
178 | bus_MV_150_0_node_199 | 20 | n |  | TRUE
179 | bus_MV_150_0_node_129 | 20 | n |  | TRUE
180 | bus_MV_150_0_node_125 | 20 | n |  | TRUE
181 | bus_MV_150_0_node_173 | 20 | n |  | TRUE
182 | bus_MV_150_0_node_157 | 20 | n |  | TRUE
183 | bus_MV_150_0_node_159 | 20 | n |  | TRUE
184 | bus_MV_150_0_node_123 | 20 | n |  | TRUE
185 | bus_MV_150_0_node_124 | 20 | n |  | TRUE
186 | bus_MV_150_0_node_176 | 20 | n |  | TRUE
187 | bus_MV_150_0_node_138 | 20 | n |  | TRUE
188 | bus_MV_150_0_node_139 | 20 | n |  | TRUE
189 | bus_MV_150_0_node_193 | 20 | n |  | TRUE
190 | bus_MV_150_0_node_192 | 20 | n |  | TRUE
191 | bus_MV_150_0_node_178 | 20 | n |  | TRUE
192 | bus_MV_150_0_node_151 | 20 | n |  | TRUE
193 | bus_MV_150_0_node_194 | 20 | n |  | TRUE
194 | bus_MV_150_0_node_169 | 20 | n |  | TRUE
195 | bus_MV_150_0_node_195 | 20 | n |  | TRUE
196 | bus_MV_150_0_node_167 | 20 | n |  | TRUE
197 | bus_MV_150_0_node_160 | 20 | n |  | TRUE
198 | bus_MV_150_0_node_174 | 20 | n |  | TRUE
199 | bus_MV_150_0_node_179 | 20 | n |  | TRUE
200 | bus_MV_150_0_node_180 | 20 | n |  | TRUE
201 | bus_MV_150_0_node_181 | 20 | n |  | TRUE
202 | bus_MV_150_0_node_182 | 20 | n |  | TRUE
203 | bus_MV_150_0_node_204 | 20 | n |  | TRUE
204 | bus_HV_150_0_node_172 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_150_0_load_0 | 0 | 0.13267 | 0.064255 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_150_0_load_67 | 4 | 0.11084 | 0.053685 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_150_0_load_62 | 6 | 0.091075 | 0.04411 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_150_0_load_188 | 8 | 0.069645 | 0.03373 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_150_0_load_80 | 9 | 0.14643 | 0.070919 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_150_0_load_33 | 11 | 0.10158 | 0.049198 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_150_0_load_81 | 13 | 0.10649 | 0.051578 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_150_0_load_5 | 14 | 0.11232 | 0.054399 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_150_0_load_37 | 19 | 0.13615 | 0.065941 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_150_0_load_165 | 20 | 0.18594 | 0.090054 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_150_0_load_47 | 21 | 0.091724 | 0.044424 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_150_0_load_55 | 22 | 0.13258 | 0.064209 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_150_0_load_9 | 25 | 0.15441 | 0.074786 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_150_0_load_11 | 26 | 0.3419 | 0.16559 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_150_0_load_10 | 28 | 0.37676 | 0.18247 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_150_0_load_63 | 30 | 0.090151 | 0.043662 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_150_0_load_72 | 34 | 0.070675 | 0.03423 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_150_0_load_50 | 35 | 0.31963 | 0.1548 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_150_0_load_30 | 37 | 0.1176 | 0.056955 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_150_0_load_48 | 39 | 0.1591 | 0.077054 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_150_0_load_54 | 41 | 0.12305 | 0.059595 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_150_0_load_15 | 42 | 0.14391 | 0.069698 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_150_0_load_197 | 47 | 0.16132 | 0.078128 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_150_0_load_79 | 48 | 0.10864 | 0.052616 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_150_0_load_78 | 50 | 0.053492 | 0.025907 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_150_0_load_22 | 53 | 0.14224 | 0.068889 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_150_0_load_29 | 57 | 0.1292 | 0.062573 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_150_0_load_187 | 60 | 0.15848 | 0.076754 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_150_0_load_73 | 61 | 0.086791 | 0.042035 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_150_0_load_35 | 63 | 0.12725 | 0.061629 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_150_0_load_41 | 64 | 0.14585 | 0.070641 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_150_0_load_198 | 68 | 0.11346 | 0.054953 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_150_0_load_44 | 70 | 0.15589 | 0.075503 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_150_0_load_207 | 72 | 0.14938 | 0.072346 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_150_0_load_206 | 74 | 0.069352 | 0.033589 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_150_0_load_196 | 76 | 0.07948 | 0.038494 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_150_0_load_148 | 77 | 0.16252 | 0.078711 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_150_0_load_56 | 80 | 0.14827 | 0.071809 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_150_0_load_75 | 82 | 0.068635 | 0.033241 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_150_0_load_58 | 83 | 0.11195 | 0.05422 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_150_0_load_170 | 84 | 0.24052 | 0.11649 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_150_0_load_59 | 86 | 0.055527 | 0.026893 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_150_0_load_70 | 88 | 0.085683 | 0.041498 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_150_0_load_64 | 89 | 0.14333 | 0.06942 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_150_0_load_65 | 90 | 0.096529 | 0.046751 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_150_0_load_190 | 94 | 0.085092 | 0.041212 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_150_0_load_88 | 95 | 0.14491 | 0.070185 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_150_0_load_99 | 98 | 0.10019 | 0.048526 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_150_0_load_85 | 99 | 0.081704 | 0.039571 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_150_0_load_211 | 103 | 0.05586 | 0.027054 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_150_0_load_98 | 105 | 0.096506 | 0.04674 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_150_0_load_96 | 106 | 0.091551 | 0.04434 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_150_0_load_89 | 107 | 0.091809 | 0.044465 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_150_0_load_208 | 112 | 0.13395 | 0.064873 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_150_0_load_92 | 113 | 0.13559 | 0.06567 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_150_0_load_210 | 115 | 0.064673 | 0.031323 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_150_0_load_215 | 116 | 0.15665 | 0.075867 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_150_0_load_209 | 119 | 0.08809 | 0.042664 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_150_0_load_143 | 120 | 0.15059 | 0.072935 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_150_0_load_185 | 124 | 0.059474 | 0.028804 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_150_0_load_212 | 125 | 0.077242 | 0.03741 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_150_0_load_214 | 126 | 0.077733 | 0.037648 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_150_0_load_103 | 127 | 0.078724 | 0.038128 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_150_0_load_142 | 129 | 0.079331 | 0.038422 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_150_0_load_177 | 132 | 0.1646 | 0.079717 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_150_0_load_106 | 134 | 0.082292 | 0.039856 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_150_0_load_136 | 137 | 0.060026 | 0.029072 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_150_0_load_137 | 139 | 0.10106 | 0.048946 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_150_0_load_131 | 140 | 0.058994 | 0.028572 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_150_0_load_171 | 145 | 0.15857 | 0.076797 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_150_0_load_191 | 146 | 0.070745 | 0.034263 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_150_0_load_115 | 147 | 0.13226 | 0.064056 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_150_0_load_152 | 149 | 0.15021 | 0.072748 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_150_0_load_109 | 151 | 0.1249 | 0.060493 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_150_0_load_175 | 152 | 0.15625 | 0.075676 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_150_0_load_121 | 153 | 0.10595 | 0.051316 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_150_0_load_112 | 155 | 0.13495 | 0.065359 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_150_0_load_122 | 157 | 0.098719 | 0.047812 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_150_0_load_172 | 159 | 0.072307 | 0.03502 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_150_0_load_144 | 161 | 0.11419 | 0.055304 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_150_0_load_183 | 163 | 0.14514 | 0.070296 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_150_0_load_184 | 165 | 0.12132 | 0.058756 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_150_0_load_162 | 168 | 0.14323 | 0.069367 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_150_0_load_163 | 172 | 0.14818 | 0.071769 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_150_0_load_200 | 173 | 0.13491 | 0.06534 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_150_0_load_201 | 174 | 0.12168 | 0.05893 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_150_0_load_127 | 176 | 0.11545 | 0.055913 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_150_0_load_199 | 178 | 0.14058 | 0.068088 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_150_0_load_173 | 181 | 0.1324 | 0.064123 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_150_0_load_123 | 184 | 0.1314 | 0.063638 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_150_0_load_176 | 186 | 0.38235 | 0.18518 | 0 | 0 |  | 1 | TRUE | wye
91 | MV_150_0_load_138 | 187 | 0.11229 | 0.054387 | 0 | 0 |  | 1 | TRUE | wye
92 | MV_150_0_load_193 | 189 | 0.12324 | 0.059688 | 0 | 0 |  | 1 | TRUE | wye
93 | MV_150_0_load_178 | 191 | 0.067546 | 0.032714 | 0 | 0 |  | 1 | TRUE | wye
94 | MV_150_0_load_194 | 193 | 0.078247 | 0.037897 | 0 | 0 |  | 1 | TRUE | wye
95 | MV_150_0_load_169 | 194 | 2.481 | 1.2016 | 0 | 0 |  | 1 | TRUE | wye
96 | MV_150_0_load_160 | 197 | 0.085528 | 0.041423 | 0 | 0 |  | 1 | TRUE | wye
97 | MV_150_0_load_174 | 198 | 0.13438 | 0.065083 | 0 | 0 |  | 1 | TRUE | wye
98 | MV_150_0_load_179 | 199 | 0.16242 | 0.078664 | 0 | 0 |  | 1 | TRUE | wye
99 | MV_150_0_load_204 | 203 | 0.1372 | 0.066447 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 159 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_150_0_line_0 |  | 0 | 1 | 0.078541 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_150_0_line_1 |  | 1 | 2 | 0.34676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_150_0_line_2 |  | 1 | 3 | 0.24865 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
3 | MV_150_0_line_3 |  | 2 | 7 | 0.044867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_150_0_line_4 |  | 2 | 8 | 0.088345 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_150_0_line_5 |  | 3 | 6 | 0.017304 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
6 | MV_150_0_line_6 |  | 4 | 5 | 0.10907 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
7 | MV_150_0_line_7 |  | 4 | 6 | 0.64505 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
8 | MV_150_0_line_8 |  | 5 | 93 | 0.16417 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
9 | MV_150_0_line_9 |  | 7 | 9 | 0.024395 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_150_0_line_10 |  | 7 | 10 | 0.42081 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_150_0_line_11 |  | 9 | 96 | 0.14481 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_150_0_line_12 |  | 10 | 88 | 0.23277 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_150_0_line_13 |  | 10 | 87 | 0.81515 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_150_0_line_14 |  | 11 | 12 | 0.10257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_150_0_line_15 |  | 12 | 13 | 0.76491 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_150_0_line_16 |  | 13 | 66 | 0.046653 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_150_0_line_17 |  | 14 | 15 | 0.10876 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_150_0_line_18 |  | 15 | 16 | 0.10448 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
19 | MV_150_0_line_19 |  | 15 | 17 | 0.13044 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
20 | MV_150_0_line_20 |  | 16 | 18 | 0.25141 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
21 | MV_150_0_line_21 |  | 16 | 19 | 0.020323 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
22 | MV_150_0_line_22 |  | 17 | 20 | 0.044763 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
23 | MV_150_0_line_23 |  | 18 | 21 | 0.079407 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_150_0_line_24 |  | 18 | 22 | 0.22476 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_150_0_line_25 |  | 19 | 23 | 0.030607 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
26 | MV_150_0_line_26 |  | 20 | 24 | 0.035633 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
27 | MV_150_0_line_27 |  | 22 | 45 | 0.028103 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_150_0_line_28 |  | 23 | 67 | 0.47073 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
29 | MV_150_0_line_29 |  | 24 | 85 | 0.034562 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
30 | MV_150_0_line_30 |  | 25 | 26 | 0.039956 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_150_0_line_31 |  | 25 | 27 | 0.19559 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
32 | MV_150_0_line_32 |  | 25 | 28 | 0.10184 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
33 | MV_150_0_line_33 |  | 27 | 29 | 0.30025 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
34 | MV_150_0_line_34 |  | 28 | 30 | 1.8198 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
35 | MV_150_0_line_35 |  | 29 | 32 | 0.6063 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_150_0_line_36 |  | 29 | 33 | 0.19535 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
37 | MV_150_0_line_37 |  | 30 | 31 | 1.8745 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
38 | MV_150_0_line_38 |  | 31 | 71 | 0.64855 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_150_0_line_39 |  | 31 | 70 | 0.017668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_150_0_line_40 |  | 32 | 34 | 0.039407 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_150_0_line_41 |  | 32 | 35 | 0.048382 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_150_0_line_42 |  | 33 | 36 | 0.11247 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
43 | MV_150_0_line_43 |  | 33 | 37 | 0.022798 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_150_0_line_44 |  | 34 | 38 | 0.17145 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_150_0_line_45 |  | 35 | 39 | 0.033359 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_150_0_line_46 |  | 36 | 64 | 0.061418 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
47 | MV_150_0_line_47 |  | 38 | 73 | 0.069762 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_150_0_line_48 |  | 39 | 40 | 0.054618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_150_0_line_49 |  | 40 | 41 | 0.064454 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_150_0_line_50 |  | 42 | 43 | 0.015347 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_150_0_line_51 |  | 42 | 44 | 0.075787 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_150_0_line_52 |  | 43 | 45 | 0.13753 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_150_0_line_53 |  | 44 | 46 | 0.050995 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_150_0_line_54 |  | 46 | 47 | 0.02653 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_150_0_line_55 |  | 47 | 51 | 0.021833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_150_0_line_56 |  | 48 | 49 | 0.043939 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_150_0_line_57 |  | 48 | 50 | 0.39249 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_150_0_line_58 |  | 49 | 51 | 0.15643 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_150_0_line_59 |  | 50 | 62 | 0.94829 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
60 | MV_150_0_line_60 |  | 51 | 52 | 0.18075 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_150_0_line_61 |  | 52 | 55 | 0.1878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_150_0_line_62 |  | 52 | 53 | 0.029159 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_150_0_line_63 |  | 53 | 54 | 0.049729 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_150_0_line_64 |  | 54 | 56 | 0.053252 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_150_0_line_65 |  | 55 | 60 | 0.039426 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_150_0_line_66 |  | 55 | 58 | 0.15348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_150_0_line_67 |  | 56 | 57 | 0.016063 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_150_0_line_68 |  | 58 | 59 | 0.36432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_150_0_line_69 |  | 59 | 63 | 0.029626 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_150_0_line_70 |  | 61 | 62 | 0.21339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_150_0_line_71 |  | 64 | 65 | 0.069018 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
72 | MV_150_0_line_72 |  | 65 | 69 | 0.099647 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
73 | MV_150_0_line_73 |  | 66 | 96 | 0.13223 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
74 | MV_150_0_line_74 |  | 67 | 68 | 0.052106 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
75 | MV_150_0_line_75 |  | 68 | 69 | 0.042955 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
76 | MV_150_0_line_76 |  | 71 | 72 | 0.077216 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_150_0_line_77 |  | 73 | 74 | 0.038344 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_150_0_line_78 |  | 73 | 75 | 0.30417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_150_0_line_79 |  | 75 | 76 | 0.093 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_150_0_line_80 |  | 77 | 78 | 0.022045 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
81 | MV_150_0_line_81 |  | 78 | 79 | 0.28977 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
82 | MV_150_0_line_82 |  | 79 | 192 | 0.19296 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
83 | MV_150_0_line_83 |  | 79 | 189 | 0.024206 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
84 | MV_150_0_line_84 |  | 80 | 81 | 0.005761 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_150_0_line_85 |  | 80 | 82 | 0.11803 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
86 | MV_150_0_line_86 |  | 81 | 83 | 0.020028 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_150_0_line_87 |  | 83 | 84 | 0.028002 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_150_0_line_88 |  | 84 | 85 | 0.015071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_150_0_line_89 |  | 85 | 196 | 0.13168 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
90 | MV_150_0_line_90 |  | 86 | 87 | 0.15568 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_150_0_line_91 |  | 89 | 90 | 0.11383 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_150_0_line_92 |  | 90 | 91 | 0.074843 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_150_0_line_93 |  | 91 | 92 | 0.14196 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
94 | MV_150_0_line_94 |  | 91 | 93 | 0.11432 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
95 | MV_150_0_line_95 |  | 92 | 94 | 0.097106 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
96 | MV_150_0_line_96 |  | 93 | 95 | 0.093449 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_150_0_line_97 |  | 94 | 97 | 0.052881 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
98 | MV_150_0_line_98 |  | 97 | 98 | 1.6289 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
99 | MV_150_0_line_99 |  | 98 | 122 | 0.078854 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
100 | MV_150_0_line_100 |  | 98 | 123 | 3.0303 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
101 | MV_150_0_line_101 |  | 99 | 100 | 0.029338 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
102 | MV_150_0_line_102 |  | 99 | 101 | 0.75315 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
103 | MV_150_0_line_103 |  | 100 | 102 | 0.41574 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
104 | MV_150_0_line_104 |  | 101 | 103 | 0.12151 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
105 | MV_150_0_line_105 |  | 102 | 104 | 0.71902 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
106 | MV_150_0_line_106 |  | 102 | 105 | 0.13668 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
107 | MV_150_0_line_107 |  | 103 | 126 | 0.64531 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
108 | MV_150_0_line_108 |  | 103 | 125 | 1.0345 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
109 | MV_150_0_line_109 |  | 104 | 106 | 0.19393 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
110 | MV_150_0_line_110 |  | 106 | 120 | 1.4111 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
111 | MV_150_0_line_111 |  | 107 | 108 | 0.058516 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
112 | MV_150_0_line_112 |  | 108 | 109 | 0.35307 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_150_0_line_113 |  | 108 | 110 | 0.37798 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
114 | MV_150_0_line_114 |  | 109 | 111 | 0.30363 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_150_0_line_115 |  | 109 | 112 | 0.017395 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
116 | MV_150_0_line_116 |  | 110 | 115 | 0.076305 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
117 | MV_150_0_line_117 |  | 110 | 114 | 0.16831 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_150_0_line_118 |  | 111 | 116 | 0.005934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_150_0_line_119 |  | 113 | 114 | 0.00751 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_150_0_line_120 |  | 116 | 201 | 0.056022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_150_0_line_121 |  | 117 | 118 | 0.77202 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_150_0_line_122 |  | 117 | 119 | 0.006873 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_150_0_line_123 |  | 118 | 125 | 0.15523 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
124 | MV_150_0_line_124 |  | 118 | 122 | 0.90294 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
125 | MV_150_0_line_125 |  | 120 | 121 | 0.066371 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
126 | MV_150_0_line_126 |  | 121 | 180 | 0.7764 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
127 | MV_150_0_line_127 |  | 123 | 124 | 0.16219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_150_0_line_128 |  | 126 | 203 | 0.062887 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
129 | MV_150_0_line_129 |  | 126 | 202 | 0.031315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_150_0_line_130 |  | 127 | 128 | 0.018388 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_150_0_line_131 |  | 127 | 129 | 0.16631 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
132 | MV_150_0_line_132 |  | 128 | 130 | 0.069293 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_150_0_line_133 |  | 128 | 131 | 0.25007 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
134 | MV_150_0_line_134 |  | 129 | 138 | 0.003723 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_150_0_line_135 |  | 130 | 132 | 0.054463 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
136 | MV_150_0_line_136 |  | 131 | 151 | 0.047473 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
137 | MV_150_0_line_137 |  | 132 | 133 | 0.045727 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_150_0_line_138 |  | 133 | 171 | 0.11345 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_150_0_line_139 |  | 134 | 135 | 0.032056 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_150_0_line_140 |  | 135 | 136 | 0.20283 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_150_0_line_141 |  | 135 | 137 | 1.354 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
142 | MV_150_0_line_142 |  | 136 | 138 | 0.27025 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_150_0_line_143 |  | 136 | 139 | 0.029512 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
144 | MV_150_0_line_144 |  | 137 | 142 | 0.051858 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_150_0_line_145 |  | 140 | 141 | 0.17827 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_150_0_line_146 |  | 141 | 142 | 0.51847 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_150_0_line_147 |  | 142 | 143 | 1.0713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_150_0_line_148 |  | 143 | 144 | 0.075244 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_150_0_line_149 |  | 144 | 145 | 0.068976 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_150_0_line_150 |  | 144 | 146 | 0.050632 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
151 | MV_150_0_line_151 |  | 147 | 148 | 0.027097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_150_0_line_152 |  | 147 | 149 | 0.10002 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
153 | MV_150_0_line_153 |  | 147 | 150 | 0.27272 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
154 | MV_150_0_line_154 |  | 148 | 167 | 0.24022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_150_0_line_155 |  | 149 | 168 | 0.12288 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
156 | MV_150_0_line_156 |  | 149 | 169 | 0.025678 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
157 | MV_150_0_line_157 |  | 150 | 173 | 0.009515 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_150_0_line_158 |  | 152 | 153 | 0.24985 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
159 | MV_150_0_line_159 |  | 152 | 154 | 0.044749 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_150_0_line_160 |  | 153 | 167 | 0.02433 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_150_0_line_161 |  | 154 | 179 | 0.066582 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_150_0_line_162 |  | 155 | 156 | 0.064106 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
163 | MV_150_0_line_163 |  | 155 | 157 | 0.14486 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
164 | MV_150_0_line_164 |  | 156 | 158 | 0.4525 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
165 | MV_150_0_line_165 |  | 156 | 159 | 0.88609 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
166 | MV_150_0_line_166 |  | 157 | 160 | 0.019535 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
167 | MV_150_0_line_167 |  | 158 | 163 | 0.057205 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_150_0_line_168 |  | 159 | 166 | 0.66876 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
169 | MV_150_0_line_169 |  | 160 | 175 | 0.099851 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
170 | MV_150_0_line_170 |  | 161 | 162 | 0.060703 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
171 | MV_150_0_line_171 |  | 161 | 163 | 0.22659 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
172 | MV_150_0_line_172 |  | 162 | 164 | 0.41787 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_150_0_line_173 |  | 164 | 165 | 0.045814 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
174 | MV_150_0_line_174 |  | 166 | 191 | 0.06215 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
175 | MV_150_0_line_175 |  | 166 | 188 | 0.27249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_150_0_line_176 |  | 168 | 172 | 0.13662 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
177 | MV_150_0_line_177 |  | 169 | 170 | 0.10172 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
178 | MV_150_0_line_178 |  | 170 | 177 | 0.12049 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
179 | MV_150_0_line_179 |  | 170 | 178 | 0.025991 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
180 | MV_150_0_line_180 |  | 171 | 172 | 0.062071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
181 | MV_150_0_line_181 |  | 173 | 174 | 0.088246 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
182 | MV_150_0_line_182 |  | 175 | 176 | 0.039664 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
183 | MV_150_0_line_183 |  | 176 | 179 | 0.14697 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
184 | MV_150_0_line_184 |  | 176 | 180 | 0.015711 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
185 | MV_150_0_line_185 |  | 177 | 181 | 0.026265 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
186 | MV_150_0_line_186 |  | 179 | 186 | 0.016473 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
187 | MV_150_0_line_187 |  | 180 | 185 | 0.26935 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
188 | MV_150_0_line_188 |  | 181 | 182 | 0.29019 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
189 | MV_150_0_line_189 |  | 181 | 183 | 0.12982 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
190 | MV_150_0_line_190 |  | 182 | 197 | 0.050962 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
191 | MV_150_0_line_191 |  | 183 | 198 | 0.017472 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
192 | MV_150_0_line_192 |  | 184 | 185 | 0.069175 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
193 | MV_150_0_line_193 |  | 187 | 188 | 0.06561 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
194 | MV_150_0_line_194 |  | 189 | 190 | 0.010058 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
195 | MV_150_0_line_195 |  | 190 | 191 | 1.1939 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
196 | MV_150_0_line_196 |  | 192 | 193 | 0.11533 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
197 | MV_150_0_line_197 |  | 193 | 195 | 0.12556 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
198 | MV_150_0_line_198 |  | 194 | 195 | 0.67219 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
199 | MV_150_0_line_199 |  | 194 | 196 | 0.005432 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
200 | MV_150_0_line_200 |  | 199 | 200 | 0.0098706 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
201 | MV_150_0_line_201 |  | 200 | 201 | 0.33091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
202 | MV_150_0_line_202 |  | 200 | 202 | 0.22439 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_150_0_trafo_172 | 25 MVA 110/20 kV | 204 | 159 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2741148.0889 | 1217123.1197
1 | 2741225.3535 | 1217109.0159
2 | 2741537.648 | 1217061.3616
3 | 2741011.715 | 1217236.2426
4 | 2740426.8659 | 1217516.4029
5 | 2740342.6131 | 1217585.6654
6 | 2741001.0948 | 1217222.5576
7 | 2741568.4969 | 1217029.2004
8 | 2741530.3983 | 1217149.4084
9 | 2741589.3484 | 1217041.862
10 | 2741812.1132 | 1216696.8105
11 | 2741735.0384 | 1217980.2316
12 | 2741807.9344 | 1217910.3398
13 | 2741734.5176 | 1217148.9587
14 | 2744410.0775 | 1217976.9206
15 | 2744515.328 | 1218004.3179
16 | 2744561.7988 | 1217921.3292
17 | 2744607.149 | 1218038.686
18 | 2744317.6109 | 1217863.5164
19 | 2744560.7783 | 1217901.4318
20 | 2744638.2637 | 1218070.865
21 | 2744241.2502 | 1217840.9594
22 | 2744351.4627 | 1217641.321
23 | 2744588.9463 | 1217896.7
24 | 2744662.211 | 1218097.2395
25 | 2745200.4181 | 1217571.1155
26 | 2745229.6336 | 1217598.3728
27 | 2745068.994 | 1217715.9554
28 | 2745270.3217 | 1217497.0541
29 | 2744923.1724 | 1217827.9484
30 | 2746797.8628 | 1216508.0108
31 | 2745079.1048 | 1217256.0722
32 | 2745134.3711 | 1218207.4267
33 | 2744816.1483 | 1217667.0081
34 | 2745157.7861 | 1218176.4622
35 | 2745153.8511 | 1218251.7138
36 | 2744734.5853 | 1217673.1542
37 | 2744800.1777 | 1217650.7394
38 | 2745316.9178 | 1218112.6493
39 | 2745174.7474 | 1218277.7166
40 | 2745132.173 | 1218311.93
41 | 2745082.3721 | 1218270.8374
42 | 2744432.8323 | 1217508.1248
43 | 2744429.6581 | 1217523.1386
44 | 2744490.9282 | 1217459.458
45 | 2744378.8032 | 1217647.8245
46 | 2744524.7029 | 1217421.2552
47 | 2744544.6557 | 1217404.0021
48 | 2744352.0676 | 1217324.9442
49 | 2744395.8635 | 1217329.8204
50 | 2743985.299 | 1217185.1967
51 | 2744543.2552 | 1217382.2272
52 | 2744578.5357 | 1217261.0789
53 | 2744587.8995 | 1217233.905
54 | 2744551.9895 | 1217199.5044
55 | 2744712.8507 | 1217269.0456
56 | 2744509.8305 | 1217168.7667
57 | 2744501.0208 | 1217182.198
58 | 2744705.6311 | 1217180.4609
59 | 2744804.1771 | 1217420.0715
60 | 2744733.6908 | 1217302.5138
61 | 2744183.3536 | 1216070.9423
62 | 2744060.1766 | 1216239.8641
63 | 2744790.699 | 1217445.5659
64 | 2744696.9278 | 1217624.5535
65 | 2744654.2733 | 1217570.2935
66 | 2741765.1383 | 1217113.9685
67 | 2744565.6574 | 1217480.5662
68 | 2744617.7587 | 1217479.8963
69 | 2744651.3503 | 1217506.7902
70 | 2745066.9533 | 1217243.2654
71 | 2744805.9015 | 1217080.5549
72 | 2744747.7034 | 1217131.2958
73 | 2745342.4702 | 1218061.3837
74 | 2745313.0144 | 1218036.733
75 | 2745545.4904 | 1218027.5319
76 | 2745594.7845 | 1218106.3931
77 | 2744819.2146 | 1218981.0708
78 | 2744797.6364 | 1218984.4715
79 | 2744624.8103 | 1219199.0591
80 | 2744726.0509 | 1218066.4298
81 | 2744730.3466 | 1218070.2819
82 | 2744786.9008 | 1217965.2987
83 | 2744716.6762 | 1218084.9191
84 | 2744697.5634 | 1218105.3835
85 | 2744687.2765 | 1218116.3979
86 | 2741537.1176 | 1216743.3355
87 | 2741464.3957 | 1216718.8106
88 | 2741840.1055 | 1216482.7064
89 | 2740269.4287 | 1217370.1943
90 | 2740169.5717 | 1217424.8242
91 | 2740146.3739 | 1217481.7821
92 | 2740013.8942 | 1217498.6268
93 | 2740235.0102 | 1217553.9835
94 | 2739920.1093 | 1217473.4474
95 | 2740215.4584 | 1217601.8749
96 | 2741723.9021 | 1216988.3369
97 | 2739882.425 | 1217436.9321
98 | 2738312.7126 | 1217872.0604
99 | 2739325.025 | 1219556.9681
100 | 2739353.6461 | 1219563.7765
101 | 2738585.0383 | 1219697.1594
102 | 2739687.5335 | 1219541.4882
103 | 2738554.4179 | 1219579.5707
104 | 2740191.8881 | 1219654.4642
105 | 2739561.6967 | 1219488.1385
106 | 2740378.3438 | 1219707.8001
107 | 2737158.728 | 1219400.0801
108 | 2737100.2692 | 1219397.499
109 | 2737382.7567 | 1219447.4704
110 | 2736809.1964 | 1219156.3626
111 | 2737576.3547 | 1219611.1192
112 | 2737371.6784 | 1219434.0593
113 | 2736800.8787 | 1219030.011
114 | 2736799.6457 | 1219037.411
115 | 2736765.8897 | 1219219.1873
116 | 2737578.9604 | 1219605.786
117 | 2737997.373 | 1218427.7446
118 | 2738411.0197 | 1218408.7895
119 | 2737997.0772 | 1218434.6102
120 | 2741596.7078 | 1220419.7522
121 | 2741655.2241 | 1220451.3927
122 | 2738249.818 | 1217911.6095
123 | 2738040.5244 | 1214854.0053
124 | 2738052.5999 | 1214703.071
125 | 2738377.3148 | 1218560.3113
126 | 2737941.4347 | 1219781.2482
127 | 2741911.5023 | 1221218.9607
128 | 2741916.7121 | 1221201.3253
129 | 2741754.5978 | 1221163.8214
130 | 2741979.3826 | 1221198.1051
131 | 2741738.7162 | 1221025.6697
132 | 2742028.959 | 1221175.5566
133 | 2742071.3693 | 1221158.1643
134 | 2741477.6252 | 1221350.7505
135 | 2741452.0199 | 1221370.0372
136 | 2741509.9968 | 1221245.8972
137 | 2740624.7442 | 1222441.9162
138 | 2741754.1241 | 1221160.1292
139 | 2741500.552 | 1221217.9378
140 | 2740034.0684 | 1222135.7466
141 | 2740164.4763 | 1222245.0188
142 | 2740573.6502 | 1222433.9919
143 | 2740108.2926 | 1222792.7412
144 | 2740071.1022 | 1222743.8801
145 | 2740017.0861 | 1222702.2014
146 | 2740120.9774 | 1222735.1573
147 | 2742284.2635 | 1220865.6289
148 | 2742309.6561 | 1220855.9829
149 | 2742247.3462 | 1220958.5824
150 | 2742374.2201 | 1221123.0883
151 | 2741693.7682 | 1221040.9466
152 | 2741940.2091 | 1220643.1964
153 | 2742173.4701 | 1220732.7139
154 | 2741981.2538 | 1220625.9153
155 | 2742435.996 | 1220601.6847
156 | 2742490.4914 | 1220567.6812
157 | 2742291.1522 | 1220599.4098
158 | 2742883.8709 | 1220791.3077
159 | 2743100.5545 | 1219925.0429
160 | 2742274.1888 | 1220609.1796
161 | 2743091.3619 | 1220683.4182
162 | 2743036.3364 | 1220709.0519
163 | 2742922.0502 | 1220834.0048
164 | 2743229.5745 | 1220965.5718
165 | 2743200.9006 | 1220929.8405
166 | 2743739.0061 | 1220124.0851
167 | 2742181.8353 | 1220755.5665
168 | 2742130.5492 | 1220920.4059
169 | 2742255.4699 | 1220982.9417
170 | 2742348.1423 | 1220953.5862
171 | 2742038.3811 | 1221053.3211
172 | 2742016.2821 | 1220995.2999
173 | 2742378.3952 | 1221131.6287
174 | 2742421.2233 | 1221208.7856
175 | 2742200.9957 | 1220617.2943
176 | 2742185.8709 | 1220580.613
177 | 2742374.1048 | 1220869.3456
178 | 2742349.3657 | 1220979.5488
179 | 2742046.0624 | 1220625.9161
180 | 2742190.8422 | 1220565.7078
181 | 2742370.0652 | 1220843.3935
182 | 2742638.1829 | 1220954.4147
183 | 2742492.4477 | 1220886.6905
184 | 2742175.9921 | 1220432.6839
185 | 2742245.031 | 1220426.0153
186 | 2742037.0556 | 1220614.0133
187 | 2743869.186 | 1220367.9602
188 | 2743861.4619 | 1220302.8064
189 | 2744609.8605 | 1219218.1237
190 | 2744601.4066 | 1219212.636
191 | 2743789.2669 | 1220087.7001
192 | 2744556.7139 | 1219093.6266
193 | 2744512.4579 | 1218987.5171
194 | 2744597.8293 | 1218207.2939
195 | 2744474.8093 | 1218868.1345
196 | 2744593.6692 | 1218203.801
197 | 2742637.7959 | 1221004.7597
198 | 2742504.5976 | 1220874.1037
199 | 2737870.4009 | 1219683.2773
200 | 2737864.4266 | 1219691.1345
201 | 2737631.1517 | 1219626.5311
202 | 2737914.5286 | 1219765.9346
203 | 2737919.8651 | 1219840.3205
204 | 2743100.5545 | 1219925.0429

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98438 | -0.79015 | 0.13267 | 0.064255
1 | 0.9844 | -0.79002 | 0 | 0
2 | 0.98416 | -0.78868 | 0 | 0
3 | 0.9846 | -0.78426 | 0 | 0
4 | 0.9851 | -0.76576 | 0.11084 | 0.053685
5 | 0.98516 | -0.76185 | 0 | 0
6 | 0.98461 | -0.78417 | 0.091075 | 0.04411
7 | 0.98413 | -0.78853 | 0 | 0
8 | 0.98414 | -0.78875 | 0.069645 | 0.03373
9 | 0.98411 | -0.78865 | 0.14643 | 0.070919
10 | 0.98406 | -0.7887 | 0 | 0
11 | 0.98382 | -0.79041 | 0.10158 | 0.049198
12 | 0.98384 | -0.79053 | 0 | 0
13 | 0.98399 | -0.78937 | 0.10649 | 0.051578
14 | 0.98522 | -0.75719 | 0.11232 | 0.054399
15 | 0.98524 | -0.75704 | 0 | 0
16 | 0.98511 | -0.75785 | 0 | 0
17 | 0.98541 | -0.75599 | 0 | 0
18 | 0.985 | -0.75844 | 0 | 0
19 | 0.98509 | -0.75796 | 0.13615 | 0.065941
20 | 0.98547 | -0.75563 | 0.18594 | 0.090054
21 | 0.98499 | -0.75835 | 0.091724 | 0.044424
22 | 0.98446 | -0.76267 | 0.13258 | 0.064209
23 | 0.98507 | -0.75812 | 0 | 0
24 | 0.98552 | -0.75533 | 0 | 0
25 | 0.98392 | -0.77508 | 0.15441 | 0.074786
26 | 0.9839 | -0.77491 | 0.3419 | 0.16559
27 | 0.984 | -0.77469 | 0 | 0
28 | 0.98387 | -0.77817 | 0.37676 | 0.18247
29 | 0.98413 | -0.77404 | 0 | 0
30 | 0.9834 | -0.80679 | 0.090151 | 0.043662
31 | 0.98273 | -0.82546 | 0 | 0
32 | 0.98349 | -0.76873 | 0 | 0
33 | 0.98426 | -0.77329 | 0 | 0
34 | 0.98348 | -0.76865 | 0.070675 | 0.03423
35 | 0.98343 | -0.76911 | 0.31963 | 0.1548
36 | 0.98434 | -0.77282 | 0 | 0
37 | 0.98426 | -0.77332 | 0.1176 | 0.056955
38 | 0.98343 | -0.76912 | 0 | 0
39 | 0.98342 | -0.769 | 0.1591 | 0.077054
40 | 0.98341 | -0.76893 | 0 | 0
41 | 0.9834 | -0.76883 | 0.12305 | 0.059595
42 | 0.9842 | -0.76061 | 0.14391 | 0.069698
43 | 0.98422 | -0.76079 | 0 | 0
44 | 0.98406 | -0.76175 | 0 | 0
45 | 0.98442 | -0.76236 | 0 | 0
46 | 0.98399 | -0.76125 | 0 | 0
47 | 0.98396 | -0.76099 | 0.16132 | 0.078128
48 | 0.98385 | -0.76129 | 0.10864 | 0.052616
49 | 0.98386 | -0.76141 | 0 | 0
50 | 0.98374 | -0.7622 | 0.053492 | 0.025907
51 | 0.98394 | -0.76082 | 0 | 0
52 | 0.98381 | -0.75983 | 0 | 0
53 | 0.9838 | -0.75974 | 0.14224 | 0.068889
54 | 0.98379 | -0.75982 | 0 | 0
55 | 0.98374 | -0.75935 | 0 | 0
56 | 0.98378 | -0.75974 | 0 | 0
57 | 0.98377 | -0.75972 | 0.1292 | 0.062573
58 | 0.98372 | -0.75922 | 0 | 0
59 | 0.98366 | -0.75876 | 0 | 0
60 | 0.98373 | -0.75943 | 0.15848 | 0.076754
61 | 0.98356 | -0.76349 | 0.086791 | 0.042035
62 | 0.98359 | -0.76368 | 0 | 0
63 | 0.98365 | -0.75872 | 0.12725 | 0.061629
64 | 0.98439 | -0.77257 | 0.14585 | 0.070641
65 | 0.98449 | -0.76614 | 0 | 0
66 | 0.984 | -0.78948 | 0 | 0
67 | 0.98469 | -0.76041 | 0 | 0
68 | 0.9846 | -0.7655 | 0.11346 | 0.054953
69 | 0.98457 | -0.7657 | 0 | 0
70 | 0.98273 | -0.82543 | 0.15589 | 0.075503
71 | 0.98261 | -0.82466 | 0 | 0
72 | 0.9826 | -0.82452 | 0.14938 | 0.072346
73 | 0.98341 | -0.76903 | 0 | 0
74 | 0.98341 | -0.769 | 0.069352 | 0.033589
75 | 0.98338 | -0.7688 | 0 | 0
76 | 0.98337 | -0.7689 | 0.07948 | 0.038494
77 | 0.9901 | -0.55698 | 0.16252 | 0.078711
78 | 0.9901 | -0.55697 | 0 | 0
79 | 0.99012 | -0.55687 | 0 | 0
80 | 0.98554 | -0.75475 | 0.14827 | 0.071809
81 | 0.98554 | -0.75477 | 0 | 0
82 | 0.98552 | -0.75486 | 0.068635 | 0.033241
83 | 0.98555 | -0.75482 | 0.11195 | 0.05422
84 | 0.98556 | -0.75493 | 0.24052 | 0.11649
85 | 0.98557 | -0.75504 | 0 | 0
86 | 0.98399 | -0.78875 | 0.055527 | 0.026893
87 | 0.984 | -0.78884 | 0 | 0
88 | 0.98403 | -0.7885 | 0.085683 | 0.041498
89 | 0.98525 | -0.75638 | 0.14333 | 0.06942
90 | 0.98527 | -0.75657 | 0.096529 | 0.046751
91 | 0.98529 | -0.75677 | 0 | 0
92 | 0.98535 | -0.7564 | 0 | 0
93 | 0.98521 | -0.76153 | 0 | 0
94 | 0.98543 | -0.75143 | 0.085092 | 0.041212
95 | 0.9852 | -0.76137 | 0.14491 | 0.070185
96 | 0.98405 | -0.78908 | 0 | 0
97 | 0.98545 | -0.75128 | 0 | 0
98 | 0.9869 | -0.66264 | 0.10019 | 0.048526
99 | 0.99012 | -0.48402 | 0.081704 | 0.039571
100 | 0.99014 | -0.48383 | 0 | 0
101 | 0.98882 | -0.5652 | 0 | 0
102 | 0.99051 | -0.48113 | 0 | 0
103 | 0.98861 | -0.57831 | 0.05586 | 0.027054
104 | 0.99118 | -0.47599 | 0 | 0
105 | 0.99049 | -0.48129 | 0.096506 | 0.04674
106 | 0.99152 | -0.45358 | 0.091551 | 0.04434
107 | 0.98658 | -0.58176 | 0.091809 | 0.044465
108 | 0.98659 | -0.58169 | 0 | 0
109 | 0.98672 | -0.58275 | 0 | 0
110 | 0.98644 | -0.58277 | 0 | 0
111 | 0.98688 | -0.58402 | 0 | 0
112 | 0.98671 | -0.58278 | 0.13395 | 0.064873
113 | 0.98641 | -0.5825 | 0.13559 | 0.06567
114 | 0.98641 | -0.58252 | 0 | 0
115 | 0.98643 | -0.58284 | 0.064673 | 0.031323
116 | 0.98689 | -0.58404 | 0.15665 | 0.075867
117 | 0.98729 | -0.65872 | 0 | 0
118 | 0.98738 | -0.65909 | 0 | 0
119 | 0.98729 | -0.65871 | 0.08809 | 0.042664
120 | 0.99414 | -0.28605 | 0.15059 | 0.072935
121 | 0.99421 | -0.28554 | 0 | 0
122 | 0.98694 | -0.66239 | 0 | 0
123 | 0.98656 | -0.66634 | 0 | 0
124 | 0.98655 | -0.66625 | 0.059474 | 0.028804
125 | 0.98753 | -0.64894 | 0.077242 | 0.03741
126 | 0.98742 | -0.58799 | 0.077733 | 0.037648
127 | 0.99038 | -0.29219 | 0.078724 | 0.038128
128 | 0.9904 | -0.29227 | 0 | 0
129 | 0.9902 | -0.2943 | 0.079331 | 0.038422
130 | 0.99047 | -0.29269 | 0 | 0
131 | 0.99034 | -0.29266 | 0 | 0
132 | 0.99056 | -0.29185 | 0.1646 | 0.079717
133 | 0.99061 | -0.29221 | 0 | 0
134 | 0.9899 | -0.29309 | 0.082292 | 0.039856
135 | 0.9899 | -0.29312 | 0 | 0
136 | 0.99001 | -0.29352 | 0 | 0
137 | 0.98904 | -0.30444 | 0.060026 | 0.029072
138 | 0.99019 | -0.29429 | 0 | 0
139 | 0.99001 | -0.29356 | 0.10106 | 0.048946
140 | 0.98897 | -0.30428 | 0.058994 | 0.028572
141 | 0.98898 | -0.30439 | 0 | 0
142 | 0.98902 | -0.30441 | 0 | 0
143 | 0.98871 | -0.30252 | 0 | 0
144 | 0.98869 | -0.30232 | 0 | 0
145 | 0.98868 | -0.30219 | 0.15857 | 0.076797
146 | 0.98868 | -0.30237 | 0.070745 | 0.034263
147 | 0.99179 | -0.28522 | 0.13226 | 0.064056
148 | 0.99187 | -0.28585 | 0 | 0
149 | 0.99142 | -0.28822 | 0.15021 | 0.072748
150 | 0.99165 | -0.28609 | 0 | 0
151 | 0.99033 | -0.29273 | 0.1249 | 0.060493
152 | 0.9938 | -0.28272 | 0.15625 | 0.075676
153 | 0.99264 | -0.2919 | 0.10595 | 0.051316
154 | 0.99394 | -0.28388 | 0 | 0
155 | 0.99591 | -0.24054 | 0.13495 | 0.065359
156 | 0.99605 | -0.23965 | 0 | 0
157 | 0.99532 | -0.27703 | 0.098719 | 0.047812
158 | 0.99572 | -0.24221 | 0 | 0
159 | 1 | 0 | -14.9044 | -6.6536
160 | 0.99528 | -0.2773 | 0 | 0
161 | 0.99559 | -0.24284 | 0.11419 | 0.055304
162 | 0.99557 | -0.24298 | 0 | 0
163 | 0.99569 | -0.24199 | 0.14514 | 0.070296
164 | 0.99551 | -0.2425 | 0 | 0
165 | 0.9955 | -0.24257 | 0.12132 | 0.058756
166 | 0.99648 | -0.20126 | 0 | 0
167 | 0.99257 | -0.29135 | 0 | 0
168 | 0.99112 | -0.29086 | 0.14323 | 0.069367
169 | 0.99139 | -0.2884 | 0 | 0
170 | 0.99133 | -0.28783 | 0 | 0
171 | 0.99075 | -0.29309 | 0 | 0
172 | 0.99083 | -0.29356 | 0.14818 | 0.071769
173 | 0.99165 | -0.28606 | 0.13491 | 0.06534
174 | 0.99163 | -0.28619 | 0.12168 | 0.05893
175 | 0.99507 | -0.27865 | 0 | 0
176 | 0.99499 | -0.27919 | 0.11545 | 0.055913
177 | 0.99128 | -0.28734 | 0 | 0
178 | 0.99132 | -0.28787 | 0.14058 | 0.068088
179 | 0.99416 | -0.28559 | 0 | 0
180 | 0.99498 | -0.27933 | 0 | 0
181 | 0.99126 | -0.28746 | 0.1324 | 0.064123
182 | 0.99121 | -0.2878 | 0 | 0
183 | 0.99122 | -0.28768 | 0 | 0
184 | 0.99492 | -0.27888 | 0.1314 | 0.063638
185 | 0.99493 | -0.27898 | 0 | 0
186 | 0.99415 | -0.28551 | 0.38235 | 0.18518
187 | 0.99643 | -0.20104 | 0.11229 | 0.054387
188 | 0.99644 | -0.20095 | 0 | 0
189 | 0.99018 | -0.55656 | 0.12324 | 0.059688
190 | 0.9902 | -0.55644 | 0 | 0
191 | 0.99632 | -0.20201 | 0.067546 | 0.032714
192 | 0.98965 | -0.55921 | 0 | 0
193 | 0.98937 | -0.56059 | 0.078247 | 0.037897
194 | 0.98578 | -0.75378 | 2.481 | 1.2016
195 | 0.98907 | -0.56207 | 0 | 0
196 | 0.98578 | -0.75383 | 0 | 0
197 | 0.9912 | -0.28774 | 0.085528 | 0.041423
198 | 0.99122 | -0.28765 | 0.13438 | 0.065083
199 | 0.98717 | -0.58621 | 0.16242 | 0.078664
200 | 0.98718 | -0.58619 | 0 | 0
201 | 0.98693 | -0.58436 | 0 | 0
202 | 0.98739 | -0.58777 | 0 | 0
203 | 0.9874 | -0.58809 | 0.1372 | 0.066447
204 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13267 | -0.064255 | 0.13267 | 0.064166 | 2.6143e-06 | -8.9222e-05 | 0.0043229 | 0.0043217 | 0.0043229 | 0.98438 | -0.79015 | 0.9844 | -0.79002 | 2.0585
1 | 0.56559 | 0.2225 | -0.56544 | -0.23048 | 0.00014777 | -0.0079772 | 0.017823 | 0.01791 | 0.01791 | 0.9844 | -0.79002 | 0.98416 | -0.78868 | 8.1411
2 | -0.69826 | -0.28666 | 0.69837 | 0.28649 | 0.00011182 | -0.00017496 | 0.022135 | 0.022131 | 0.022135 | 0.9844 | -0.79002 | 0.9846 | -0.78426 | 6.3242
3 | 0.49579 | 0.19685 | -0.49578 | -0.19788 | 1.4675e-05 | -0.0010332 | 0.015647 | 0.015658 | 0.015658 | 0.98416 | -0.78868 | 0.98413 | -0.78853 | 7.1174
4 | 0.069645 | 0.033629 | -0.069645 | -0.03373 | 8.1051e-07 | -0.00010164 | 0.0022685 | 0.0022698 | 0.0022698 | 0.98416 | -0.78868 | 0.98414 | -0.78875 | 1.0809
5 | -0.69837 | -0.28649 | 0.69837 | 0.28592 | 4.0924e-06 | -0.00057252 | 0.022131 | 0.022125 | 0.022131 | 0.9846 | -0.78426 | 0.98461 | -0.78417 | 6.1136
6 | -0.90058 | -0.38332 | 0.90061 | 0.38326 | 3.203e-05 | -6.0185e-05 | 0.028682 | 0.02868 | 0.028682 | 0.9851 | -0.76576 | 0.98516 | -0.76185 | 4.4468
7 | 0.78974 | 0.32964 | -0.78945 | -0.33003 | 0.00028926 | -0.00039101 | 0.025078 | 0.025087 | 0.025087 | 0.9851 | -0.76576 | 0.98461 | -0.78417 | 6.1187
8 | -0.90061 | -0.38326 | 0.90066 | 0.37327 | 4.156e-05 | -0.0099883 | 0.02868 | 0.028567 | 0.02868 | 0.98516 | -0.76185 | 0.98521 | -0.76153 | 4.4953
9 | 0.35455 | 0.16704 | -0.35455 | -0.16707 | 5.7448e-06 | -2.4606e-05 | 0.011497 | 0.011497 | 0.011497 | 0.98413 | -0.78853 | 0.98411 | -0.78865 | 5.4747
10 | 0.14123 | 0.030839 | -0.14122 | -0.040566 | 1.0257e-05 | -0.0097271 | 0.0042402 | 0.0043101 | 0.0043101 | 0.98413 | -0.78853 | 0.98406 | -0.7887 | 1.9592
11 | 0.20812 | 0.096147 | -0.20811 | -0.096307 | 1.1671e-05 | -0.0001601 | 0.0067248 | 0.0067269 | 0.0067269 | 0.98411 | -0.78865 | 0.98405 | -0.78908 | 3.2033
12 | 0.085685 | 0.036117 | -0.085683 | -0.041498 | 2.3661e-06 | -0.005381 | 0.0027278 | 0.0027929 | 0.0027929 | 0.98406 | -0.7887 | 0.98403 | -0.7885 | 1.2695
13 | 0.05553 | 0.0044492 | -0.055527 | -0.023294 | 3.068e-06 | -0.018845 | 0.0016342 | 0.0017665 | 0.0017665 | 0.98406 | -0.7887 | 0.984 | -0.78884 | 0.80297
14 | -0.10158 | -0.049198 | 0.10158 | 0.046828 | 1.4883e-06 | -0.00237 | 0.0033118 | 0.0032821 | 0.0033118 | 0.98382 | -0.79041 | 0.98384 | -0.79053 | 1.5054
15 | -0.10158 | -0.046828 | 0.1016 | 0.045953 | 1.4632e-05 | -0.00087484 | 0.0032821 | 0.0032713 | 0.0032821 | 0.98384 | -0.79053 | 0.98399 | -0.78937 | 1.5629
16 | -0.20809 | -0.097531 | 0.20809 | 0.096453 | 2.8255e-06 | -0.0010777 | 0.0067421 | 0.0067288 | 0.0067421 | 0.98399 | -0.78937 | 0.984 | -0.78948 | 3.0646
17 | -0.11232 | -0.054399 | 0.11232 | 0.054274 | 2.5899e-06 | -0.00012441 | 0.0036567 | 0.0036551 | 0.0036567 | 0.98522 | -0.75719 | 0.98524 | -0.75704 | 1.7413
18 | 3.9437 | 1.705 | -3.9432 | -1.7111 | 0.00051194 | -0.0060834 | 0.12589 | 0.12596 | 0.12596 | 0.98524 | -0.75704 | 0.98511 | -0.75785 | 19.7432
19 | -4.056 | -1.7592 | 4.0567 | 1.7517 | 0.00067585 | -0.0075763 | 0.12954 | 0.12945 | 0.12954 | 0.98524 | -0.75704 | 0.98541 | -0.75599 | 20.3039
20 | 1.3371 | 0.59241 | -1.337 | -0.60765 | 0.00014329 | -0.015247 | 0.042856 | 0.04304 | 0.04304 | 0.98511 | -0.75785 | 0.985 | -0.75844 | 6.7461
21 | 2.6061 | 1.1187 | -2.6061 | -1.1199 | 4.3381e-05 | -0.0012147 | 0.083107 | 0.083121 | 0.083121 | 0.98511 | -0.75785 | 0.98509 | -0.75796 | 13.0284
22 | -4.0567 | -1.7517 | 4.057 | 1.7491 | 0.00023171 | -0.0026008 | 0.12945 | 0.12941 | 0.12945 | 0.98541 | -0.75599 | 0.98547 | -0.75563 | 20.2894
23 | 0.091725 | 0.042585 | -0.091724 | -0.044424 | 9.3838e-07 | -0.0018392 | 0.0029638 | 0.0029869 | 0.0029869 | 0.985 | -0.75844 | 0.98499 | -0.75835 | 1.3577
24 | 1.2453 | 0.56507 | -1.2446 | -0.56493 | 0.00064323 | 0.00014271 | 0.040077 | 0.04008 | 0.04008 | 0.985 | -0.75844 | 0.98446 | -0.76267 | 19.0856
25 | 2.4699 | 1.0539 | -2.4698 | -1.0558 | 5.8583e-05 | -0.0018331 | 0.078693 | 0.078714 | 0.078714 | 0.98509 | -0.75796 | 0.98507 | -0.75812 | 12.3377
26 | -4.2429 | -1.8391 | 4.2431 | 1.8371 | 0.000202 | -0.0020607 | 0.13546 | 0.13544 | 0.13546 | 0.98547 | -0.75563 | 0.98552 | -0.75533 | 21.2321
27 | 1.112 | 0.50072 | -1.112 | -0.50135 | 4.7992e-05 | -0.00063604 | 0.035762 | 0.035769 | 0.035769 | 0.98446 | -0.76267 | 0.98442 | -0.76236 | 16.2589
28 | 2.4698 | 1.0558 | -2.4689 | -1.0839 | 0.00090505 | -0.028179 | 0.078714 | 0.079049 | 0.079049 | 0.98507 | -0.75812 | 0.98469 | -0.76041 | 12.3901
29 | -4.2431 | -1.8371 | 4.2433 | 1.8351 | 0.00019586 | -0.001999 | 0.13544 | 0.13541 | 0.13544 | 0.98552 | -0.75533 | 0.98557 | -0.75504 | 21.2282
30 | 0.3419 | 0.16467 | -0.3419 | -0.16559 | 6.6196e-06 | -0.00092159 | 0.011134 | 0.011146 | 0.011146 | 0.98392 | -0.77508 | 0.9839 | -0.77491 | 5.0663
31 | -1.2688 | -0.59198 | 1.2689 | 0.58014 | 0.00010162 | -0.011841 | 0.041078 | 0.040932 | 0.041078 | 0.98392 | -0.77508 | 0.984 | -0.77469 | 6.4386
32 | 0.77249 | 0.35253 | -0.77247 | -0.35261 | 2.2567e-05 | -7.5593e-05 | 0.024913 | 0.024915 | 0.024915 | 0.98392 | -0.77508 | 0.98387 | -0.77817 | 3.8627
33 | -1.2689 | -0.58014 | 1.2691 | 0.56196 | 0.0001546 | -0.018182 | 0.040932 | 0.040712 | 0.040932 | 0.984 | -0.77469 | 0.98413 | -0.77404 | 6.4157
34 | 0.39571 | 0.17013 | -0.39561 | -0.17229 | 0.000104 | -0.0021542 | 0.012638 | 0.012666 | 0.012666 | 0.98387 | -0.77817 | 0.9834 | -0.80679 | 1.9638
35 | 0.8219 | 0.36964 | -0.82134 | -0.38348 | 0.00056927 | -0.013842 | 0.026435 | 0.026606 | 0.026606 | 0.98413 | -0.77404 | 0.98349 | -0.76873 | 12.0938
36 | -2.091 | -0.9316 | 2.0912 | 0.91987 | 0.00027159 | -0.011737 | 0.067147 | 0.067006 | 0.067147 | 0.98413 | -0.77404 | 0.98426 | -0.77329 | 10.5246
37 | 0.30545 | 0.12863 | -0.30529 | -0.13071 | 0.00016332 | -0.0020897 | 0.0097292 | 0.0097553 | 0.0097553 | 0.9834 | -0.80679 | 0.98273 | -0.82546 | 2.7872
38 | 0.1494 | 0.055619 | -0.14938 | -0.070566 | 1.9649e-05 | -0.014947 | 0.0046828 | 0.0048535 | 0.0048535 | 0.98273 | -0.82546 | 0.98261 | -0.82466 | 2.2061
39 | 0.15589 | 0.075096 | -0.15589 | -0.075503 | 6.1002e-07 | -0.00040722 | 0.005083 | 0.0050882 | 0.0050882 | 0.98273 | -0.82546 | 0.98273 | -0.82543 | 2.3128
40 | 0.21952 | 0.095585 | -0.21952 | -0.096494 | 2.6023e-06 | -0.00090929 | 0.0070278 | 0.0070385 | 0.0070385 | 0.98349 | -0.76873 | 0.98348 | -0.76865 | 3.1993
41 | 0.60181 | 0.2879 | -0.60178 | -0.28793 | 3.3055e-05 | -3.5159e-05 | 0.019582 | 0.019582 | 0.019582 | 0.98349 | -0.76873 | 0.98343 | -0.76911 | 9.325
42 | -2.2088 | -0.97679 | 2.209 | 0.97005 | 0.00017418 | -0.0067485 | 0.070835 | 0.070754 | 0.070835 | 0.98426 | -0.77329 | 0.98434 | -0.77282 | 11.1027
43 | 0.1176 | 0.056929 | -0.1176 | -0.056955 | 5.9648e-07 | -2.5992e-05 | 0.0038319 | 0.0038322 | 0.0038322 | 0.98426 | -0.77329 | 0.98426 | -0.77332 | 1.8249
44 | 0.14884 | 0.062264 | -0.14884 | -0.062458 | 6.8544e-06 | -0.00019367 | 0.0047358 | 0.0047381 | 0.0047381 | 0.98348 | -0.76865 | 0.98343 | -0.76912 | 2.2562
45 | 0.28215 | 0.13313 | -0.28215 | -0.1339 | 3.7389e-06 | -0.00076918 | 0.0091579 | 0.0091676 | 0.0091676 | 0.98343 | -0.76911 | 0.98342 | -0.769 | 4.1671
46 | -2.209 | -0.97005 | 2.2091 | 0.96636 | 9.4948e-05 | -0.0036858 | 0.070754 | 0.07071 | 0.070754 | 0.98434 | -0.77282 | 0.98439 | -0.77257 | 11.09
47 | 0.14884 | 0.062458 | -0.14884 | -0.064068 | 2.0989e-06 | -0.0016103 | 0.0047381 | 0.0047566 | 0.0047566 | 0.98343 | -0.76912 | 0.98341 | -0.76903 | 2.1621
48 | 0.12305 | 0.056846 | -0.12305 | -0.058107 | 1.1589e-06 | -0.0012608 | 0.0039789 | 0.0039946 | 0.0039946 | 0.98342 | -0.769 | 0.98341 | -0.76893 | 1.8157
49 | 0.12305 | 0.058107 | -0.12305 | -0.059595 | 1.3794e-06 | -0.0014878 | 0.0039946 | 0.0040134 | 0.0040134 | 0.98341 | -0.76893 | 0.9834 | -0.76883 | 1.8243
50 | -1.1117 | -0.50481 | 1.1118 | 0.50446 | 2.6273e-05 | -0.00034715 | 0.035812 | 0.035808 | 0.035812 | 0.9842 | -0.76061 | 0.98422 | -0.76079 | 16.2783
51 | 0.96782 | 0.43511 | -0.96769 | -0.43512 | 0.00013081 | -5.6919e-06 | 0.031124 | 0.031125 | 0.031125 | 0.9842 | -0.76061 | 0.98406 | -0.76175 | 14.8214
52 | -1.1118 | -0.50446 | 1.112 | 0.50135 | 0.00023517 | -0.0031118 | 0.035808 | 0.035769 | 0.035808 | 0.98422 | -0.76079 | 0.98442 | -0.76236 | 16.2763
53 | 0.96769 | 0.43512 | -0.96762 | -0.43628 | 6.5982e-05 | -0.0011594 | 0.031125 | 0.031139 | 0.031139 | 0.98406 | -0.76175 | 0.98399 | -0.76125 | 14.1542
54 | 0.96762 | 0.43628 | -0.96758 | -0.43688 | 3.4351e-05 | -0.00060311 | 0.031139 | 0.031147 | 0.031147 | 0.98399 | -0.76125 | 0.98396 | -0.76099 | 14.1575
55 | 0.80627 | 0.35875 | -0.80625 | -0.35925 | 1.9542e-05 | -0.00049889 | 0.02589 | 0.025896 | 0.025896 | 0.98396 | -0.76099 | 0.98394 | -0.76082 | 11.7711
56 | -0.24895 | -0.1141 | 0.24895 | 0.11308 | 3.7814e-06 | -0.0010144 | 0.0080352 | 0.0080228 | 0.0080352 | 0.98385 | -0.76129 | 0.98386 | -0.76141 | 3.6524
57 | 0.14031 | 0.061482 | -0.1403 | -0.061926 | 1.4145e-05 | -0.00044463 | 0.0044948 | 0.0045002 | 0.0045002 | 0.98385 | -0.76129 | 0.98374 | -0.7622 | 2.1429
58 | -0.24895 | -0.11308 | 0.24897 | 0.11291 | 1.7935e-05 | -0.00016955 | 0.0080228 | 0.0080206 | 0.0080228 | 0.98386 | -0.76141 | 0.98394 | -0.76082 | 3.8204
59 | 0.086806 | 0.036019 | -0.086793 | -0.037107 | 1.2909e-05 | -0.0010873 | 0.0027579 | 0.0027704 | 0.0027704 | 0.98374 | -0.7622 | 0.98359 | -0.76368 | 1.3192
60 | 0.55728 | 0.24634 | -0.5572 | -0.25049 | 7.7323e-05 | -0.0041546 | 0.017876 | 0.017926 | 0.017926 | 0.98394 | -0.76082 | 0.98381 | -0.75983 | 8.1481
61 | 0.28576 | 0.12136 | -0.28574 | -0.12569 | 2.0921e-05 | -0.0043334 | 0.0091098 | 0.0091603 | 0.0091603 | 0.98381 | -0.75983 | 0.98374 | -0.75935 | 4.1638
62 | 0.27144 | 0.12913 | -0.27144 | -0.1298 | 3.0313e-06 | -0.00067293 | 0.0088202 | 0.0088287 | 0.0088287 | 0.98381 | -0.75983 | 0.9838 | -0.75974 | 4.013
63 | 0.1292 | 0.060916 | -0.1292 | -0.060972 | 1.5568e-06 | -5.6482e-05 | 0.0041914 | 0.0041921 | 0.0041921 | 0.9838 | -0.75974 | 0.98379 | -0.75982 | 1.9962
64 | 0.1292 | 0.060972 | -0.1292 | -0.062202 | 1.254e-06 | -0.0012302 | 0.0041921 | 0.0042076 | 0.0042076 | 0.98379 | -0.75982 | 0.98378 | -0.75974 | 1.9126
65 | 0.15848 | 0.07671 | -0.15848 | -0.076754 | 1.8754e-06 | -4.4374e-05 | 0.0051667 | 0.0051672 | 0.0051672 | 0.98374 | -0.75935 | 0.98373 | -0.75943 | 2.4606
66 | 0.12726 | 0.048984 | -0.12726 | -0.05253 | 3.312e-06 | -0.0035453 | 0.0040015 | 0.00404 | 0.00404 | 0.98374 | -0.75935 | 0.98372 | -0.75922 | 1.8364
67 | 0.1292 | 0.062202 | -0.1292 | -0.062573 | 3.8008e-07 | -0.00037107 | 0.0042076 | 0.0042124 | 0.0042124 | 0.98378 | -0.75974 | 0.98377 | -0.75972 | 1.9147
68 | 0.12726 | 0.05253 | -0.12725 | -0.060944 | 8.131e-06 | -0.0084147 | 0.00404 | 0.0041406 | 0.0041406 | 0.98372 | -0.75922 | 0.98366 | -0.75876 | 1.8821
69 | 0.12725 | 0.060944 | -0.12725 | -0.061629 | 6.795e-07 | -0.00068422 | 0.0041406 | 0.0041493 | 0.0041493 | 0.98366 | -0.75876 | 0.98365 | -0.75872 | 1.886
70 | -0.086791 | -0.042035 | 0.086793 | 0.037107 | 2.2327e-06 | -0.0049282 | 0.0028303 | 0.0027704 | 0.0028303 | 0.98356 | -0.76349 | 0.98359 | -0.76368 | 1.2865
71 | -2.355 | -1.037 | 2.3551 | 1.0373 | 0.0001403 | 0.00028482 | 0.075459 | 0.075458 | 0.075459 | 0.98439 | -0.77257 | 0.98449 | -0.76614 | 11.6991
72 | -2.3551 | -1.0373 | 2.3553 | 1.0313 | 0.00017516 | -0.0059702 | 0.075458 | 0.075387 | 0.075458 | 0.98449 | -0.76614 | 0.98457 | -0.7657 | 11.8273
73 | -0.20809 | -0.096453 | 0.20811 | 0.096307 | 1.0664e-05 | -0.00014617 | 0.0067288 | 0.0067269 | 0.0067288 | 0.984 | -0.78948 | 0.98405 | -0.78908 | 3.2042
74 | 2.4689 | 1.0839 | -2.4688 | -1.0837 | 0.00011624 | 0.00024274 | 0.079049 | 0.079049 | 0.079049 | 0.98469 | -0.76041 | 0.9846 | -0.7655 | 12.2557
75 | 2.3554 | 1.0287 | -2.3553 | -1.0313 | 7.5402e-05 | -0.0025739 | 0.075356 | 0.075387 | 0.075387 | 0.9846 | -0.7655 | 0.98457 | -0.7657 | 11.8161
76 | 0.14938 | 0.070566 | -0.14938 | -0.072346 | 2.4395e-06 | -0.0017793 | 0.0048535 | 0.0048761 | 0.0048761 | 0.98261 | -0.82466 | 0.9826 | -0.82452 | 2.2164
77 | 0.069352 | 0.032703 | -0.069352 | -0.033589 | 2.6061e-07 | -0.00088531 | 0.0022508 | 0.002262 | 0.002262 | 0.98341 | -0.76903 | 0.98341 | -0.769 | 1.0282
78 | 0.079483 | 0.031365 | -0.079481 | -0.038387 | 2.6361e-06 | -0.0070224 | 0.0025083 | 0.002591 | 0.002591 | 0.98341 | -0.76903 | 0.98338 | -0.7688 | 1.1777
79 | 0.079481 | 0.038387 | -0.07948 | -0.038494 | 1.113e-06 | -0.00010667 | 0.002591 | 0.0025924 | 0.0025924 | 0.98338 | -0.7688 | 0.98337 | -0.7689 | 1.2345
80 | -0.16252 | -0.078711 | 0.16252 | 0.077354 | 1.882e-07 | -0.0013577 | 0.0052649 | 0.0052478 | 0.0052649 | 0.9901 | -0.55698 | 0.9901 | -0.55697 | 0.82522
81 | -0.16252 | -0.077354 | 0.16252 | 0.059507 | 2.3668e-06 | -0.017847 | 0.0052478 | 0.0050461 | 0.0052478 | 0.9901 | -0.55697 | 0.99012 | -0.55687 | 0.82253
82 | 7.3936 | 3.3529 | -7.3902 | -3.3629 | 0.0033424 | -0.0099978 | 0.23669 | 0.23684 | 0.23684 | 0.99012 | -0.55687 | 0.98965 | -0.55921 | 37.1218
83 | -7.5561 | -3.4124 | 7.5565 | 3.4111 | 0.00043702 | -0.001245 | 0.24173 | 0.24171 | 0.24173 | 0.99012 | -0.55687 | 0.99018 | -0.55656 | 37.8881
84 | -0.2169 | -0.10491 | 0.2169 | 0.10478 | 3.8297e-07 | -0.00013349 | 0.0070575 | 0.0070558 | 0.0070575 | 0.98554 | -0.75475 | 0.98554 | -0.75477 | 3.208
85 | 0.068636 | 0.033105 | -0.068635 | -0.033241 | 1.0485e-06 | -0.0001362 | 0.0022321 | 0.0022338 | 0.0022338 | 0.98554 | -0.75475 | 0.98552 | -0.75486 | 1.0637
86 | -0.2169 | -0.10478 | 0.21691 | 0.10432 | 1.33e-06 | -0.00046407 | 0.0070558 | 0.0070499 | 0.0070558 | 0.98554 | -0.75477 | 0.98555 | -0.75482 | 3.2072
87 | -0.32886 | -0.15854 | 0.32886 | 0.15789 | 4.2713e-06 | -0.00064812 | 0.010693 | 0.010685 | 0.010693 | 0.98555 | -0.75482 | 0.98556 | -0.75493 | 4.8606
88 | -0.56939 | -0.27438 | 0.56939 | 0.27403 | 6.8941e-06 | -0.00034748 | 0.018513 | 0.018509 | 0.018513 | 0.98556 | -0.75493 | 0.98557 | -0.75504 | 8.415
89 | -4.8127 | -2.1091 | 4.8136 | 2.1016 | 0.00096324 | -0.0074961 | 0.15391 | 0.15381 | 0.15391 | 0.98557 | -0.75504 | 0.98578 | -0.75383 | 24.1233
90 | -0.055527 | -0.026893 | 0.055527 | 0.023294 | 6.6413e-07 | -0.0035987 | 0.00181 | 0.0017665 | 0.00181 | 0.98399 | -0.78875 | 0.984 | -0.78884 | 0.82273
91 | -0.14333 | -0.06942 | 0.14334 | 0.066783 | 3.2853e-06 | -0.0026373 | 0.0046663 | 0.0046331 | 0.0046663 | 0.98525 | -0.75638 | 0.98527 | -0.75657 | 2.1211
92 | -0.23987 | -0.11353 | 0.23987 | 0.1118 | 6.0237e-06 | -0.0017329 | 0.0077754 | 0.0077538 | 0.0077754 | 0.98527 | -0.75657 | 0.98529 | -0.75677 | 3.5343
93 | -1.2855 | -0.55306 | 1.2856 | 0.54444 | 7.356e-05 | -0.0086181 | 0.041001 | 0.040901 | 0.041001 | 0.98529 | -0.75677 | 0.98535 | -0.7564 | 6.4265
94 | 1.0456 | 0.44126 | -1.0456 | -0.44129 | 4.5127e-05 | -3.205e-05 | 0.033251 | 0.033253 | 0.033253 | 0.98529 | -0.75677 | 0.98521 | -0.76153 | 5.1555
95 | -1.2856 | -0.54444 | 1.2856 | 0.54447 | 5.7992e-05 | 2.561e-05 | 0.040901 | 0.0409 | 0.040901 | 0.98535 | -0.7564 | 0.98543 | -0.75143 | 6.3413
96 | 0.14492 | 0.06802 | -0.14491 | -0.070185 | 2.7608e-06 | -0.0021648 | 0.0046907 | 0.004718 | 0.004718 | 0.98521 | -0.76153 | 0.9852 | -0.76137 | 2.1445
97 | -1.3707 | -0.58568 | 1.3707 | 0.58247 | 3.113e-05 | -0.003209 | 0.043666 | 0.043629 | 0.043666 | 0.98543 | -0.75143 | 0.98545 | -0.75128 | 6.8442
98 | -1.3707 | -0.58247 | 1.3719 | 0.58326 | 0.0011063 | 0.00078506 | 0.043629 | 0.043604 | 0.043629 | 0.98545 | -0.75128 | 0.9869 | -0.66264 | 6.7642
99 | -1.5315 | -0.65331 | 1.5316 | 0.64851 | 5.7732e-05 | -0.0047932 | 0.048704 | 0.048649 | 0.048704 | 0.9869 | -0.66264 | 0.98694 | -0.66239 | 7.6339
100 | 0.059493 | 0.021525 | -0.059474 | -0.025036 | 1.8856e-05 | -0.0035104 | 0.0018506 | 0.0018882 | 0.0018882 | 0.9869 | -0.66264 | 0.98656 | -0.66634 | 0.89913
101 | -2.8003 | -1.1587 | 2.8003 | 1.1569 | 7.0757e-05 | -0.0017673 | 0.088357 | 0.088336 | 0.088357 | 0.99012 | -0.48402 | 0.99014 | -0.48383 | 13.849
102 | 2.7186 | 1.1191 | -2.7166 | -1.1148 | 0.0019757 | 0.0042935 | 0.085714 | 0.085726 | 0.085726 | 0.99012 | -0.48402 | 0.98882 | -0.5652 | 13.2908
103 | -2.8003 | -1.1569 | 2.8013 | 1.1318 | 0.00099923 | -0.025056 | 0.088336 | 0.088054 | 0.088336 | 0.99014 | -0.48383 | 0.99051 | -0.48113 | 13.8458
104 | 2.7166 | 1.1148 | -2.7163 | -1.1141 | 0.0003188 | 0.00069307 | 0.085726 | 0.085728 | 0.085728 | 0.98882 | -0.5652 | 0.98861 | -0.57831 | 13.2911
105 | -2.8978 | -1.1784 | 2.8997 | 1.1351 | 0.001837 | -0.043319 | 0.091171 | 0.090692 | 0.091171 | 0.99051 | -0.48113 | 0.99118 | -0.47599 | 14.2901
106 | 0.096508 | 0.046581 | -0.096506 | -0.04674 | 2.3768e-06 | -0.00015859 | 0.0031231 | 0.0031251 | 0.0031251 | 0.99051 | -0.48113 | 0.99049 | -0.48129 | 1.4882
107 | 0.96163 | 0.42991 | -0.96054 | -0.42998 | 0.001088 | -7.05e-05 | 0.030758 | 0.030767 | 0.030767 | 0.98861 | -0.57831 | 0.98742 | -0.58799 | 14.651
108 | 1.6988 | 0.65713 | -1.6977 | -0.65572 | 0.001045 | 0.0014141 | 0.053186 | 0.053201 | 0.053201 | 0.98861 | -0.57831 | 0.98753 | -0.64894 | 8.2482
109 | -2.8997 | -1.1351 | 2.9003 | 1.1364 | 0.00056943 | 0.0012678 | 0.090692 | 0.090689 | 0.090692 | 0.99118 | -0.47599 | 0.99152 | -0.45358 | 14.0607
110 | -2.9918 | -1.1807 | 2.9962 | 1.1907 | 0.0044165 | 0.0099536 | 0.093642 | 0.093621 | 0.093642 | 0.99152 | -0.45358 | 0.99414 | -0.28605 | 14.5181
111 | -0.091809 | -0.044465 | 0.09181 | 0.044398 | 9.2858e-07 | -6.7413e-05 | 0.0029848 | 0.002984 | 0.0029848 | 0.98658 | -0.58176 | 0.98659 | -0.58169 | 1.4213
112 | -0.29211 | -0.1368 | 0.29215 | 0.1286 | 4.1539e-05 | -0.0081941 | 0.0094379 | 0.0093386 | 0.0094379 | 0.98659 | -0.58169 | 0.98672 | -0.58275 | 4.29
113 | 0.2003 | 0.0924 | -0.20027 | -0.092821 | 2.8078e-05 | -0.00042156 | 0.0064543 | 0.0064597 | 0.0064597 | 0.98659 | -0.58169 | 0.98644 | -0.58277 | 3.076
114 | -0.4261 | -0.19346 | 0.42617 | 0.18642 | 7.5506e-05 | -0.0070371 | 0.013691 | 0.013606 | 0.013691 | 0.98672 | -0.58275 | 0.98688 | -0.58402 | 6.223
115 | 0.13395 | 0.064853 | -0.13395 | -0.064873 | 5.8754e-07 | -1.985e-05 | 0.0043539 | 0.0043541 | 0.0043541 | 0.98672 | -0.58275 | 0.98671 | -0.58278 | 2.0734
116 | 0.064674 | 0.031235 | -0.064673 | -0.031323 | 6.009e-07 | -8.8262e-05 | 0.0021018 | 0.0021029 | 0.0021029 | 0.98644 | -0.58277 | 0.98643 | -0.58284 | 1.0014
117 | 0.1356 | 0.061587 | -0.13559 | -0.065496 | 4.3151e-06 | -0.003909 | 0.0043583 | 0.0044068 | 0.0044068 | 0.98644 | -0.58277 | 0.98641 | -0.58252 | 2.0031
118 | -0.42617 | -0.18642 | 0.42617 | 0.18628 | 1.4664e-06 | -0.00013755 | 0.013606 | 0.013605 | 0.013606 | 0.98688 | -0.58402 | 0.98689 | -0.58404 | 6.1848
119 | -0.13559 | -0.06567 | 0.13559 | 0.065496 | 1.9481e-07 | -0.00017441 | 0.004409 | 0.0044068 | 0.004409 | 0.98641 | -0.5825 | 0.98641 | -0.58252 | 2.0041
120 | -0.58282 | -0.26215 | 0.58284 | 0.26085 | 2.6112e-05 | -0.001295 | 0.018693 | 0.018678 | 0.018693 | 0.98689 | -0.58404 | 0.98693 | -0.58436 | 8.4969
121 | -0.08809 | -0.042504 | 0.088098 | 0.024537 | 7.8273e-06 | -0.017967 | 0.0028598 | 0.0026737 | 0.0028598 | 0.98729 | -0.65872 | 0.98738 | -0.65909 | 1.2999
122 | 0.08809 | 0.042504 | -0.08809 | -0.042664 | 7.5099e-08 | -0.00015993 | 0.0028598 | 0.0028618 | 0.0028618 | 0.98729 | -0.65872 | 0.98729 | -0.65871 | 1.3008
123 | -1.6203 | -0.61813 | 1.6205 | 0.61831 | 0.00014246 | 0.00017386 | 0.050703 | 0.050701 | 0.050703 | 0.98738 | -0.65909 | 0.98753 | -0.64894 | 7.861
124 | 1.5322 | 0.59359 | -1.5316 | -0.64851 | 0.00065197 | -0.054919 | 0.048042 | 0.048649 | 0.048649 | 0.98738 | -0.65909 | 0.98694 | -0.66239 | 7.6252
125 | -3.1468 | -1.2636 | 3.147 | 1.2596 | 0.00019876 | -0.0040098 | 0.098468 | 0.098423 | 0.098468 | 0.99414 | -0.28605 | 0.99421 | -0.28554 | 15.4338
126 | -3.147 | -1.2596 | 3.1493 | 1.2126 | 0.0023118 | -0.046954 | 0.098423 | 0.097911 | 0.098423 | 0.99421 | -0.28554 | 0.99498 | -0.27933 | 15.4268
127 | 0.059474 | 0.025036 | -0.059474 | -0.028804 | 7.9009e-07 | -0.0037688 | 0.0018882 | 0.0019336 | 0.0019336 | 0.98656 | -0.66634 | 0.98655 | -0.66625 | 0.87892
128 | 0.1372 | 0.066376 | -0.1372 | -0.066447 | 2.225e-06 | -7.1803e-05 | 0.0044558 | 0.0044567 | 0.0044567 | 0.98742 | -0.58799 | 0.9874 | -0.58809 | 2.1223
129 | 0.74561 | 0.32596 | -0.74559 | -0.32668 | 2.3669e-05 | -0.00072194 | 0.02379 | 0.023799 | 0.023799 | 0.98742 | -0.58799 | 0.98739 | -0.58777 | 10.8176
130 | -0.69037 | -0.27473 | 0.69038 | 0.2743 | 1.1512e-05 | -0.00042722 | 0.021658 | 0.021653 | 0.021658 | 0.99038 | -0.29219 | 0.9904 | -0.29227 | 9.8443
131 | 0.61165 | 0.2366 | -0.61154 | -0.23673 | 0.00010829 | -0.00012688 | 0.019116 | 0.019118 | 0.019118 | 0.99038 | -0.29219 | 0.9902 | -0.2943 | 9.1036
132 | -0.81529 | -0.33445 | 0.81535 | 0.33285 | 6.0988e-05 | -0.0016049 | 0.025685 | 0.025668 | 0.025685 | 0.9904 | -0.29227 | 0.99047 | -0.29269 | 11.6752
133 | 0.12491 | 0.06015 | -0.1249 | -0.060439 | 7.2824e-06 | -0.00028826 | 0.004041 | 0.0040447 | 0.0040447 | 0.9904 | -0.29227 | 0.99034 | -0.29266 | 1.926
134 | 0.53221 | 0.19831 | -0.53221 | -0.1984 | 1.3627e-06 | -8.6752e-05 | 0.016558 | 0.016559 | 0.016559 | 0.9902 | -0.2943 | 0.99019 | -0.29429 | 7.5266
135 | -0.81535 | -0.33285 | 0.81542 | 0.33283 | 6.3928e-05 | -2.3748e-05 | 0.025668 | 0.025667 | 0.025668 | 0.99047 | -0.29269 | 0.99056 | -0.29185 | 12.2226
136 | 0.1249 | 0.060439 | -0.1249 | -0.060493 | 1.384e-06 | -5.4717e-05 | 0.0040447 | 0.0040454 | 0.0040454 | 0.99034 | -0.29266 | 0.99033 | -0.29273 | 1.9264
137 | -0.98001 | -0.41254 | 0.98007 | 0.41149 | 5.8595e-05 | -0.0010539 | 0.030988 | 0.030976 | 0.030988 | 0.99056 | -0.29185 | 0.99061 | -0.29221 | 14.0853
138 | -0.98007 | -0.41149 | 0.98022 | 0.40887 | 0.00014518 | -0.0026154 | 0.030976 | 0.030946 | 0.030976 | 0.99061 | -0.29221 | 0.99075 | -0.29309 | 14.0798
139 | -0.082292 | -0.039856 | 0.082292 | 0.039106 | 3.0319e-07 | -0.00074991 | 0.0026664 | 0.002657 | 0.0026664 | 0.9899 | -0.29309 | 0.9899 | -0.29312 | 1.212
140 | -0.43099 | -0.16051 | 0.43104 | 0.15578 | 4.8533e-05 | -0.0047315 | 0.013412 | 0.013364 | 0.013412 | 0.9899 | -0.29312 | 0.99001 | -0.29352 | 6.0963
141 | 0.3487 | 0.1214 | -0.34842 | -0.12281 | 0.00028009 | -0.0014071 | 0.010768 | 0.010783 | 0.010783 | 0.9899 | -0.29312 | 0.98904 | -0.30444 | 5.1347
142 | -0.53211 | -0.20469 | 0.53221 | 0.1984 | 9.9312e-05 | -0.0062961 | 0.016624 | 0.016559 | 0.016624 | 0.99001 | -0.29352 | 0.99019 | -0.29429 | 7.5563
143 | 0.10106 | 0.048912 | -0.10106 | -0.048946 | 5.6364e-07 | -3.4178e-05 | 0.0032738 | 0.0032743 | 0.0032743 | 0.99001 | -0.29352 | 0.99001 | -0.29356 | 1.5592
144 | 0.2884 | 0.09374 | -0.28839 | -0.094949 | 5.4303e-06 | -0.0012095 | 0.008851 | 0.008862 | 0.008862 | 0.98904 | -0.30444 | 0.98902 | -0.30441 | 4.0282
145 | -0.058994 | -0.028572 | 0.058995 | 0.024409 | 8.4803e-07 | -0.0041629 | 0.0019134 | 0.0018636 | 0.0019134 | 0.98897 | -0.30428 | 0.98898 | -0.30439 | 0.8697
146 | -0.058995 | -0.024409 | 0.058998 | 0.012302 | 2.2512e-06 | -0.012108 | 0.0018636 | 0.0017591 | 0.0018636 | 0.98898 | -0.30439 | 0.98902 | -0.30441 | 0.84709
147 | 0.22939 | 0.082648 | -0.22932 | -0.10764 | 7.5148e-05 | -0.02499 | 0.0071168 | 0.0073963 | 0.0073963 | 0.98902 | -0.30441 | 0.98871 | -0.30252 | 3.362
148 | 0.22932 | 0.10764 | -0.22931 | -0.10939 | 5.5115e-06 | -0.0017545 | 0.0073963 | 0.0074182 | 0.0074182 | 0.98871 | -0.30252 | 0.98869 | -0.30232 | 3.3719
149 | 0.15857 | 0.075188 | -0.15857 | -0.076797 | 2.4271e-06 | -0.0016091 | 0.0051239 | 0.0051442 | 0.0051442 | 0.98869 | -0.30232 | 0.98868 | -0.30219 | 2.3383
150 | 0.070745 | 0.034204 | -0.070745 | -0.034263 | 4.7503e-07 | -5.8787e-05 | 0.0022944 | 0.0022951 | 0.0022951 | 0.98869 | -0.30232 | 0.98868 | -0.30237 | 1.0929
151 | -2.3051 | -1.0408 | 2.3053 | 1.0402 | 0.00019602 | -0.00057829 | 0.073616 | 0.073608 | 0.073616 | 0.99179 | -0.28522 | 0.99187 | -0.28585 | 33.4616
152 | 1.9162 | 0.85309 | -1.9156 | -0.85279 | 0.00066422 | 0.00029865 | 0.061052 | 0.061053 | 0.061053 | 0.99179 | -0.28522 | 0.99142 | -0.28822 | 29.073
153 | 0.25662 | 0.12365 | -0.25659 | -0.12395 | 3.342e-05 | -0.00029927 | 0.0082912 | 0.0082953 | 0.0082953 | 0.99179 | -0.28522 | 0.99165 | -0.28609 | 3.9501
154 | -2.3053 | -1.0402 | 2.307 | 1.0351 | 0.001736 | -0.0051317 | 0.073608 | 0.073541 | 0.073608 | 0.99187 | -0.28585 | 0.99257 | -0.29135 | 33.4582
155 | 1.2724 | 0.54869 | -1.272 | -0.54861 | 0.00035639 | 7.9092e-05 | 0.040346 | 0.040348 | 0.040348 | 0.99142 | -0.28822 | 0.99112 | -0.29086 | 19.2133
156 | 0.49297 | 0.23135 | -0.49296 | -0.23137 | 1.1503e-05 | -2.2925e-05 | 0.015856 | 0.015856 | 0.015856 | 0.99142 | -0.28822 | 0.99139 | -0.2884 | 7.5507
157 | 0.25659 | 0.12395 | -0.25659 | -0.12417 | 8.7438e-07 | -0.00022314 | 0.0082953 | 0.0082981 | 0.0082981 | 0.99165 | -0.28609 | 0.99165 | -0.28606 | 3.7719
158 | 2.4158 | 1.0872 | -2.4132 | -1.0859 | 0.0026362 | 0.001357 | 0.076953 | 0.076956 | 0.076956 | 0.9938 | -0.28272 | 0.99264 | -0.2919 | 36.6457
159 | -2.572 | -1.1629 | 2.5724 | 1.162 | 0.00040157 | -0.00093626 | 0.081994 | 0.081981 | 0.081994 | 0.9938 | -0.28272 | 0.99394 | -0.28388 | 37.2698
160 | 2.3072 | 1.0346 | -2.307 | -1.0351 | 0.00017565 | -0.00052024 | 0.073534 | 0.073541 | 0.073541 | 0.99264 | -0.2919 | 0.99257 | -0.29135 | 33.4275
161 | -2.5724 | -1.162 | 2.573 | 1.1606 | 0.00059726 | -0.0013937 | 0.081981 | 0.081962 | 0.081981 | 0.99394 | -0.28388 | 0.99416 | -0.28559 | 37.2641
162 | -6.5917 | -2.7798 | 6.5926 | 2.7763 | 0.00085157 | -0.0035161 | 0.20736 | 0.20732 | 0.20736 | 0.99591 | -0.24054 | 0.99605 | -0.23965 | 32.5019
163 | 6.4568 | 2.7144 | -6.4546 | -2.7089 | 0.0021316 | 0.0055336 | 0.20302 | 0.20302 | 0.20302 | 0.99591 | -0.24054 | 0.99532 | -0.27703 | 31.4766
164 | 0.38081 | 0.17228 | -0.38069 | -0.17274 | 0.00011837 | -0.00046162 | 0.012114 | 0.01212 | 0.01212 | 0.99605 | -0.23965 | 0.99572 | -0.24221 | 5.7714
165 | -6.9734 | -2.9486 | 6.9886 | 2.9883 | 0.01523 | 0.039735 | 0.21943 | 0.21941 | 0.21943 | 0.99605 | -0.23965 | 1 | 0 | 34.0196
166 | 6.3559 | 2.6611 | -6.3557 | -2.6622 | 0.0002411 | -0.0010801 | 0.19985 | 0.19986 | 0.19986 | 0.99532 | -0.27703 | 0.99528 | -0.2773 | 31.3262
167 | 0.38069 | 0.17274 | -0.38068 | -0.17409 | 1.1233e-05 | -0.0013508 | 0.01212 | 0.012136 | 0.012136 | 0.99572 | -0.24221 | 0.99569 | -0.24199 | 5.5165
168 | 7.9018 | 3.6548 | -7.8867 | -3.6152 | 0.015081 | 0.039632 | 0.25132 | 0.25133 | 0.25133 | 1 | 0 | 0.99648 | -0.20126 | 38.9665
169 | 6.3557 | 2.6622 | -6.3544 | -2.6677 | 0.0012329 | -0.0055192 | 0.19986 | 0.19993 | 0.19993 | 0.99528 | -0.2773 | 0.99507 | -0.27865 | 31.3371
170 | 0.12133 | 0.048746 | -0.12133 | -0.048817 | 1.5549e-06 | -7.0855e-05 | 0.0037913 | 0.003792 | 0.003792 | 0.99559 | -0.24284 | 0.99557 | -0.24298 | 1.8057
171 | -0.23552 | -0.10405 | 0.23554 | 0.1038 | 2.2492e-05 | -0.00025406 | 0.0074657 | 0.0074625 | 0.0074657 | 0.99559 | -0.24284 | 0.99569 | -0.24199 | 3.5551
172 | 0.12133 | 0.048817 | -0.12132 | -0.058703 | 8.2595e-06 | -0.0098858 | 0.003792 | 0.0039081 | 0.0039081 | 0.99557 | -0.24298 | 0.99551 | -0.2425 | 1.7764
173 | 0.12132 | 0.058703 | -0.12132 | -0.058756 | 1.2469e-06 | -5.3421e-05 | 0.0039081 | 0.0039088 | 0.0039088 | 0.99551 | -0.2425 | 0.9955 | -0.24257 | 1.8613
174 | 7.7744 | 3.5673 | -7.7732 | -3.5706 | 0.0011795 | -0.0032128 | 0.2478 | 0.24785 | 0.24785 | 0.99648 | -0.20126 | 0.99632 | -0.20201 | 38.8473
175 | 0.1123 | 0.047851 | -0.1123 | -0.05431 | 4.6468e-06 | -0.0064587 | 0.0035363 | 0.0036138 | 0.0036138 | 0.99648 | -0.20126 | 0.99644 | -0.20095 | 1.6426
176 | 1.1288 | 0.47925 | -1.1285 | -0.47921 | 0.00031056 | 3.4356e-05 | 0.035718 | 0.03572 | 0.03572 | 0.99112 | -0.29086 | 0.99083 | -0.29356 | 17.0093
177 | 0.49296 | 0.23137 | -0.49293 | -0.23375 | 3.4205e-05 | -0.0023767 | 0.015856 | 0.015886 | 0.015886 | 0.99139 | -0.2884 | 0.99133 | -0.28783 | 7.221
178 | 0.35234 | 0.16569 | -0.35232 | -0.16851 | 2.0742e-05 | -0.0028209 | 0.011338 | 0.011373 | 0.011373 | 0.99133 | -0.28783 | 0.99128 | -0.28734 | 5.1697
179 | 0.14059 | 0.068058 | -0.14058 | -0.068088 | 9.5809e-07 | -2.9893e-05 | 0.0045483 | 0.0045487 | 0.0045487 | 0.99133 | -0.28783 | 0.99132 | -0.28787 | 2.1661
180 | -0.98022 | -0.40887 | 0.9803 | 0.40744 | 7.9312e-05 | -0.0014313 | 0.030946 | 0.030929 | 0.030946 | 0.99075 | -0.29309 | 0.99083 | -0.29356 | 14.0662
181 | 0.12168 | 0.058828 | -0.12168 | -0.05893 | 2.4346e-06 | -0.00010207 | 0.0039344 | 0.0039357 | 0.0039357 | 0.99165 | -0.28606 | 0.99163 | -0.28619 | 1.8742
182 | 6.3544 | 2.6677 | -6.3539 | -2.6699 | 0.00048997 | -0.0021916 | 0.19993 | 0.19996 | 0.19996 | 0.99507 | -0.27865 | 0.99499 | -0.27919 | 31.3414
183 | 2.9577 | 1.3467 | -2.9554 | -1.3454 | 0.0023279 | 0.0012846 | 0.094287 | 0.094289 | 0.094289 | 0.99499 | -0.27919 | 0.99416 | -0.28559 | 44.8997
184 | 3.2808 | 1.2673 | -3.2807 | -1.2683 | 5.0552e-05 | -0.00094881 | 0.10204 | 0.10205 | 0.10205 | 0.99499 | -0.27919 | 0.99498 | -0.27933 | 15.9952
185 | 0.35232 | 0.16851 | -0.35231 | -0.16854 | 6.0533e-06 | -2.7018e-05 | 0.011373 | 0.011374 | 0.011374 | 0.99128 | -0.28734 | 0.99126 | -0.28746 | 5.416
186 | 0.38235 | 0.18479 | -0.38235 | -0.18518 | 3.3452e-06 | -0.00038774 | 0.012331 | 0.012336 | 0.012336 | 0.99416 | -0.28559 | 0.99415 | -0.28551 | 5.6072
187 | 0.1314 | 0.055639 | -0.1314 | -0.062003 | 6.2738e-06 | -0.0063645 | 0.0041401 | 0.0042156 | 0.0042156 | 0.99498 | -0.27933 | 0.99493 | -0.27898 | 1.9162
188 | 0.085532 | 0.03989 | -0.085528 | -0.040228 | 3.9117e-06 | -0.00033794 | 0.0027484 | 0.0027527 | 0.0027527 | 0.99126 | -0.28746 | 0.99121 | -0.2878 | 1.3108
189 | 0.13438 | 0.064523 | -0.13438 | -0.064673 | 4.361e-06 | -0.00014954 | 0.0043413 | 0.0043432 | 0.0043432 | 0.99126 | -0.28746 | 0.99122 | -0.28768 | 2.0682
190 | 0.085528 | 0.040228 | -0.085528 | -0.041423 | 5.183e-07 | -0.0011953 | 0.0027527 | 0.0027676 | 0.0027676 | 0.99121 | -0.2878 | 0.9912 | -0.28774 | 1.258
191 | 0.13438 | 0.064673 | -0.13438 | -0.065083 | 4.4051e-07 | -0.00040974 | 0.0043432 | 0.0043484 | 0.0043484 | 0.99122 | -0.28768 | 0.99122 | -0.28765 | 1.9765
192 | -0.1314 | -0.063638 | 0.1314 | 0.062003 | 1.6491e-06 | -0.0016344 | 0.004236 | 0.0042156 | 0.004236 | 0.99492 | -0.27888 | 0.99493 | -0.27898 | 1.9255
193 | -0.11229 | -0.054387 | 0.1123 | 0.05431 | 1.527e-06 | -7.6811e-05 | 0.0036148 | 0.0036138 | 0.0036148 | 0.99643 | -0.20104 | 0.99644 | -0.20095 | 1.7213
194 | -7.6798 | -3.4708 | 7.6799 | 3.4703 | 0.00018761 | -0.00051398 | 0.2457 | 0.24569 | 0.2457 | 0.99018 | -0.55656 | 0.9902 | -0.55644 | 38.5108
195 | -7.6799 | -3.4703 | 7.7057 | 3.5378 | 0.025726 | 0.06755 | 0.24569 | 0.24567 | 0.24569 | 0.9902 | -0.55644 | 0.99632 | -0.20201 | 38.0917
196 | 7.3902 | 3.3629 | -7.3882 | -3.3688 | 0.0019997 | -0.0059693 | 0.23684 | 0.23692 | 0.23692 | 0.98965 | -0.55921 | 0.98937 | -0.56059 | 37.1353
197 | 7.31 | 3.3309 | -7.3078 | -3.3375 | 0.0021323 | -0.0065194 | 0.23439 | 0.23448 | 0.23448 | 0.98937 | -0.56059 | 0.98907 | -0.56207 | 36.7524
198 | -7.2946 | -3.3029 | 7.3078 | 3.3375 | 0.013195 | 0.034575 | 0.23449 | 0.23448 | 0.23449 | 0.98578 | -0.75378 | 0.98907 | -0.56207 | 36.3553
199 | 4.8137 | 2.1013 | -4.8136 | -2.1016 | 3.9709e-05 | -0.00030931 | 0.15381 | 0.15381 | 0.15381 | 0.98578 | -0.75378 | 0.98578 | -0.75383 | 24.1085
200 | -0.16242 | -0.078664 | 0.16242 | 0.078653 | 4.8977e-07 | -1.1176e-05 | 0.0052773 | 0.0052772 | 0.0052773 | 0.98717 | -0.58621 | 0.98718 | -0.58619 | 2.513
201 | 0.583 | 0.2532 | -0.58284 | -0.26085 | 0.00015336 | -0.0076522 | 0.018587 | 0.018678 | 0.018678 | 0.98718 | -0.58619 | 0.98693 | -0.58436 | 8.4898
202 | -0.74542 | -0.33185 | 0.74559 | 0.32668 | 0.00017011 | -0.0051718 | 0.02386 | 0.023799 | 0.02386 | 0.98718 | -0.58619 | 0.98739 | -0.58777 | 10.8457

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 14.9767 | 6.6886

## res_load
| p_mw | q_mvar
0 | 0.13267 | 0.064255
1 | 0.11084 | 0.053685
2 | 0.091075 | 0.04411
3 | 0.069645 | 0.03373
4 | 0.14643 | 0.070919
5 | 0.10158 | 0.049198
6 | 0.10649 | 0.051578
7 | 0.11232 | 0.054399
8 | 0.13615 | 0.065941
9 | 0.18594 | 0.090054
10 | 0.091724 | 0.044424
11 | 0.13258 | 0.064209
12 | 0.15441 | 0.074786
13 | 0.3419 | 0.16559
14 | 0.37676 | 0.18247
15 | 0.090151 | 0.043662
16 | 0.070675 | 0.03423
17 | 0.31963 | 0.1548
18 | 0.1176 | 0.056955
19 | 0.1591 | 0.077054
20 | 0.12305 | 0.059595
21 | 0.14391 | 0.069698
22 | 0.16132 | 0.078128
23 | 0.10864 | 0.052616
24 | 0.053492 | 0.025907
25 | 0.14224 | 0.068889
26 | 0.1292 | 0.062573
27 | 0.15848 | 0.076754
28 | 0.086791 | 0.042035
29 | 0.12725 | 0.061629
30 | 0.14585 | 0.070641
31 | 0.11346 | 0.054953
32 | 0.15589 | 0.075503
33 | 0.14938 | 0.072346
34 | 0.069352 | 0.033589
35 | 0.07948 | 0.038494
36 | 0.16252 | 0.078711
37 | 0.14827 | 0.071809
38 | 0.068635 | 0.033241
39 | 0.11195 | 0.05422
40 | 0.24052 | 0.11649
41 | 0.055527 | 0.026893
42 | 0.085683 | 0.041498
43 | 0.14333 | 0.06942
44 | 0.096529 | 0.046751
45 | 0.085092 | 0.041212
46 | 0.14491 | 0.070185
47 | 0.10019 | 0.048526
48 | 0.081704 | 0.039571
49 | 0.05586 | 0.027054
50 | 0.096506 | 0.04674
51 | 0.091551 | 0.04434
52 | 0.091809 | 0.044465
53 | 0.13395 | 0.064873
54 | 0.13559 | 0.06567
55 | 0.064673 | 0.031323
56 | 0.15665 | 0.075867
57 | 0.08809 | 0.042664
58 | 0.15059 | 0.072935
59 | 0.059474 | 0.028804
60 | 0.077242 | 0.03741
61 | 0.077733 | 0.037648
62 | 0.078724 | 0.038128
63 | 0.079331 | 0.038422
64 | 0.1646 | 0.079717
65 | 0.082292 | 0.039856
66 | 0.060026 | 0.029072
67 | 0.10106 | 0.048946
68 | 0.058994 | 0.028572
69 | 0.15857 | 0.076797
70 | 0.070745 | 0.034263
71 | 0.13226 | 0.064056
72 | 0.15021 | 0.072748
73 | 0.1249 | 0.060493
74 | 0.15625 | 0.075676
75 | 0.10595 | 0.051316
76 | 0.13495 | 0.065359
77 | 0.098719 | 0.047812
78 | 0.072307 | 0.03502
79 | 0.11419 | 0.055304
80 | 0.14514 | 0.070296
81 | 0.12132 | 0.058756
82 | 0.14323 | 0.069367
83 | 0.14818 | 0.071769
84 | 0.13491 | 0.06534
85 | 0.12168 | 0.05893
86 | 0.11545 | 0.055913
87 | 0.14058 | 0.068088
88 | 0.1324 | 0.064123
89 | 0.1314 | 0.063638
90 | 0.38235 | 0.18518
91 | 0.11229 | 0.054387
92 | 0.12324 | 0.059688
93 | 0.067546 | 0.032714
94 | 0.078247 | 0.037897
95 | 2.481 | 1.2016
96 | 0.085528 | 0.041423
97 | 0.13438 | 0.065083
98 | 0.16242 | 0.078664
99 | 0.1372 | 0.066447

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1