## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_156_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_156_0_node_76 | 20 | n |  | TRUE
2 | bus_MV_156_0_node_244 | 20 | n |  | TRUE
3 | bus_MV_156_0_node_67 | 20 | n |  | TRUE
4 | bus_MV_156_0_node_75 | 20 | n |  | TRUE
5 | bus_MV_156_0_node_6 | 20 | n |  | TRUE
6 | bus_MV_156_0_node_1 | 20 | n |  | TRUE
7 | bus_MV_156_0_node_3 | 20 | n |  | TRUE
8 | bus_MV_156_0_node_2 | 20 | n |  | TRUE
9 | bus_MV_156_0_node_4 | 20 | n |  | TRUE
10 | bus_MV_156_0_node_5 | 20 | n |  | TRUE
11 | bus_MV_156_0_node_7 | 20 | n |  | TRUE
12 | bus_MV_156_0_node_133 | 20 | n |  | TRUE
13 | bus_MV_156_0_node_14 | 20 | n |  | TRUE
14 | bus_MV_156_0_node_132 | 20 | n |  | TRUE
15 | bus_MV_156_0_node_8 | 20 | n |  | TRUE
16 | bus_MV_156_0_node_9 | 20 | n |  | TRUE
17 | bus_MV_156_0_node_11 | 20 | n |  | TRUE
18 | bus_MV_156_0_node_12 | 20 | n |  | TRUE
19 | bus_MV_156_0_node_242 | 20 | n |  | TRUE
20 | bus_MV_156_0_node_241 | 20 | n |  | TRUE
21 | bus_MV_156_0_node_13 | 20 | n |  | TRUE
22 | bus_MV_156_0_node_245 | 20 | n |  | TRUE
23 | bus_MV_156_0_node_240 | 20 | n |  | TRUE
24 | bus_MV_156_0_node_15 | 20 | n |  | TRUE
25 | bus_MV_156_0_node_17 | 20 | n |  | TRUE
26 | bus_MV_156_0_node_21 | 20 | n |  | TRUE
27 | bus_MV_156_0_node_115 | 20 | n |  | TRUE
28 | bus_MV_156_0_node_16 | 20 | n |  | TRUE
29 | bus_MV_156_0_node_20 | 20 | n |  | TRUE
30 | bus_MV_156_0_node_19 | 20 | n |  | TRUE
31 | bus_MV_156_0_node_226 | 20 | n |  | TRUE
32 | bus_MV_156_0_node_225 | 20 | n |  | TRUE
33 | bus_MV_156_0_node_111 | 20 | n |  | TRUE
34 | bus_MV_156_0_node_23 | 20 | n |  | TRUE
35 | bus_MV_156_0_node_33 | 20 | n |  | TRUE
36 | bus_MV_156_0_node_227 | 20 | n |  | TRUE
37 | bus_MV_156_0_node_238 | 20 | n |  | TRUE
38 | bus_MV_156_0_node_120 | 20 | n |  | TRUE
39 | bus_MV_156_0_node_25 | 20 | n |  | TRUE
40 | bus_MV_156_0_node_127 | 20 | n |  | TRUE
41 | bus_MV_156_0_node_24 | 20 | n |  | TRUE
42 | bus_MV_156_0_node_112 | 20 | n |  | TRUE
43 | bus_MV_156_0_node_95 | 20 | n |  | TRUE
44 | bus_MV_156_0_node_22 | 20 | n |  | TRUE
45 | bus_MV_156_0_node_34 | 20 | n |  | TRUE
46 | bus_MV_156_0_node_26 | 20 | n |  | TRUE
47 | bus_MV_156_0_node_27 | 20 | n |  | TRUE
48 | bus_MV_156_0_node_128 | 20 | n |  | TRUE
49 | bus_MV_156_0_node_129 | 20 | n |  | TRUE
50 | bus_MV_156_0_node_28 | 20 | n |  | TRUE
51 | bus_MV_156_0_node_30 | 20 | n |  | TRUE
52 | bus_MV_156_0_node_32 | 20 | n |  | TRUE
53 | bus_MV_156_0_node_31 | 20 | n |  | TRUE
54 | bus_MV_156_0_node_35 | 20 | n |  | TRUE
55 | bus_MV_156_0_node_100 | 20 | n |  | TRUE
56 | bus_MV_156_0_node_113 | 20 | n |  | TRUE
57 | bus_MV_156_0_node_101 | 20 | n |  | TRUE
58 | bus_MV_156_0_node_104 | 20 | n |  | TRUE
59 | bus_MV_156_0_node_114 | 20 | n |  | TRUE
60 | bus_MV_156_0_node_36 | 20 | n |  | TRUE
61 | bus_MV_156_0_node_37 | 20 | n |  | TRUE
62 | bus_MV_156_0_node_38 | 20 | n |  | TRUE
63 | bus_MV_156_0_node_39 | 20 | n |  | TRUE
64 | bus_MV_156_0_node_40 | 20 | n |  | TRUE
65 | bus_MV_156_0_node_42 | 20 | n |  | TRUE
66 | bus_MV_156_0_node_103 | 20 | n |  | TRUE
67 | bus_MV_156_0_node_110 | 20 | n |  | TRUE
68 | bus_MV_156_0_node_41 | 20 | n |  | TRUE
69 | bus_MV_156_0_node_122 | 20 | n |  | TRUE
70 | bus_MV_156_0_node_215 | 20 | n |  | TRUE
71 | bus_MV_156_0_node_239 | 20 | n |  | TRUE
72 | bus_MV_156_0_node_118 | 20 | n |  | TRUE
73 | bus_MV_156_0_node_43 | 20 | n |  | TRUE
74 | bus_MV_156_0_node_44 | 20 | n |  | TRUE
75 | bus_MV_156_0_node_45 | 20 | n |  | TRUE
76 | bus_MV_156_0_node_46 | 20 | n |  | TRUE
77 | bus_MV_156_0_node_47 | 20 | n |  | TRUE
78 | bus_MV_156_0_node_243 | 20 | n |  | TRUE
79 | bus_MV_156_0_node_210 | 20 | n |  | TRUE
80 | bus_MV_156_0_node_102 | 20 | n |  | TRUE
81 | bus_MV_156_0_node_211 | 20 | n |  | TRUE
82 | bus_MV_156_0_node_48 | 20 | n |  | TRUE
83 | bus_MV_156_0_node_49 | 20 | n |  | TRUE
84 | bus_MV_156_0_node_50 | 20 | n |  | TRUE
85 | bus_MV_156_0_node_51 | 20 | n |  | TRUE
86 | bus_MV_156_0_node_58 | 20 | n |  | TRUE
87 | bus_MV_156_0_node_60 | 20 | n |  | TRUE
88 | bus_MV_156_0_node_59 | 20 | n |  | TRUE
89 | bus_MV_156_0_node_88 | 20 | n |  | TRUE
90 | bus_MV_156_0_node_208 | 20 | n |  | TRUE
91 | bus_MV_156_0_node_207 | 20 | n |  | TRUE
92 | bus_MV_156_0_node_206 | 20 | n |  | TRUE
93 | bus_MV_156_0_node_52 | 20 | n |  | TRUE
94 | bus_MV_156_0_node_53 | 20 | n |  | TRUE
95 | bus_MV_156_0_node_55 | 20 | n |  | TRUE
96 | bus_MV_156_0_node_97 | 20 | n |  | TRUE
97 | bus_MV_156_0_node_98 | 20 | n |  | TRUE
98 | bus_MV_156_0_node_96 | 20 | n |  | TRUE
99 | bus_MV_156_0_node_56 | 20 | n |  | TRUE
100 | bus_MV_156_0_node_57 | 20 | n |  | TRUE
101 | bus_MV_156_0_node_62 | 20 | n |  | TRUE
102 | bus_MV_156_0_node_65 | 20 | n |  | TRUE
103 | bus_MV_156_0_node_63 | 20 | n |  | TRUE
104 | bus_MV_156_0_node_61 | 20 | n |  | TRUE
105 | bus_MV_156_0_node_64 | 20 | n |  | TRUE
106 | bus_MV_156_0_node_80 | 20 | n |  | TRUE
107 | bus_MV_156_0_node_77 | 20 | n |  | TRUE
108 | bus_MV_156_0_node_78 | 20 | n |  | TRUE
109 | bus_MV_156_0_node_66 | 20 | n |  | TRUE
110 | bus_MV_156_0_node_209 | 20 | n |  | TRUE
111 | bus_MV_156_0_node_83 | 20 | n |  | TRUE
112 | bus_MV_156_0_node_81 | 20 | n |  | TRUE
113 | bus_MV_156_0_node_82 | 20 | n |  | TRUE
114 | bus_MV_156_0_node_236 | 20 | n |  | TRUE
115 | bus_MV_156_0_node_237 | 20 | n |  | TRUE
116 | bus_MV_156_0_node_68 | 20 | n |  | TRUE
117 | bus_MV_156_0_node_69 | 20 | n |  | TRUE
118 | bus_MV_156_0_node_70 | 20 | n |  | TRUE
119 | bus_MV_156_0_node_90 | 20 | n |  | TRUE
120 | bus_MV_156_0_node_89 | 20 | n |  | TRUE
121 | bus_MV_156_0_node_71 | 20 | n |  | TRUE
122 | bus_MV_156_0_node_72 | 20 | n |  | TRUE
123 | bus_MV_156_0_node_73 | 20 | n |  | TRUE
124 | bus_MV_156_0_node_125 | 20 | n |  | TRUE
125 | bus_MV_156_0_node_123 | 20 | n |  | TRUE
126 | bus_MV_156_0_node_74 | 20 | n |  | TRUE
127 | bus_MV_156_0_node_124 | 20 | n |  | TRUE
128 | bus_MV_156_0_node_79 | 20 | n |  | TRUE
129 | bus_MV_156_0_node_86 | 20 | n |  | TRUE
130 | bus_MV_156_0_node_87 | 20 | n |  | TRUE
131 | bus_MV_156_0_node_234 | 20 | n |  | TRUE
132 | bus_MV_156_0_node_213 | 20 | n |  | TRUE
133 | bus_MV_156_0_node_212 | 20 | n |  | TRUE
134 | bus_MV_156_0_node_91 | 20 | n |  | TRUE
135 | bus_MV_156_0_node_92 | 20 | n |  | TRUE
136 | bus_MV_156_0_node_93 | 20 | n |  | TRUE
137 | bus_MV_156_0_node_99 | 20 | n |  | TRUE
138 | bus_MV_156_0_node_224 | 20 | n |  | TRUE
139 | bus_MV_156_0_node_126 | 20 | n |  | TRUE
140 | bus_MV_156_0_node_130 | 20 | n |  | TRUE
141 | bus_MV_156_0_node_107 | 20 | n |  | TRUE
142 | bus_MV_156_0_node_214 | 20 | n |  | TRUE
143 | bus_MV_156_0_node_233 | 20 | n |  | TRUE
144 | bus_MV_156_0_node_131 | 20 | n |  | TRUE
145 | bus_MV_156_0_node_105 | 20 | n |  | TRUE
146 | bus_MV_156_0_node_106 | 20 | n |  | TRUE
147 | bus_MV_156_0_node_108 | 20 | n |  | TRUE
148 | bus_MV_156_0_node_109 | 20 | n |  | TRUE
149 | bus_MV_156_0_node_116 | 20 | n |  | TRUE
150 | bus_MV_156_0_node_117 | 20 | n |  | TRUE
151 | bus_MV_156_0_node_119 | 20 | n |  | TRUE
152 | bus_MV_156_0_node_144 | 20 | n |  | TRUE
153 | bus_MV_156_0_node_142 | 20 | n |  | TRUE
154 | bus_MV_156_0_node_139 | 20 | n |  | TRUE
155 | bus_MV_156_0_node_141 | 20 | n |  | TRUE
156 | bus_MV_156_0_node_216 | 20 | n |  | TRUE
157 | bus_MV_156_0_node_134 | 20 | n |  | TRUE
158 | bus_MV_156_0_node_135 | 20 | n |  | TRUE
159 | bus_MV_156_0_node_136 | 20 | n |  | TRUE
160 | bus_MV_156_0_node_137 | 20 | n |  | TRUE
161 | bus_MV_156_0_node_138 | 20 | n |  | TRUE
162 | bus_MV_156_0_node_151 | 20 | n |  | TRUE
163 | bus_MV_156_0_node_152 | 20 | n |  | TRUE
164 | bus_MV_156_0_node_143 | 20 | n |  | TRUE
165 | bus_MV_156_0_node_147 | 20 | n |  | TRUE
166 | bus_MV_156_0_node_149 | 20 | n |  | TRUE
167 | bus_MV_156_0_node_146 | 20 | n |  | TRUE
168 | bus_MV_156_0_node_140 | 20 | n |  | TRUE
169 | bus_MV_156_0_node_148 | 20 | n |  | TRUE
170 | bus_MV_156_0_node_145 | 20 | n |  | TRUE
171 | bus_MV_156_0_node_150 | 20 | n |  | TRUE
172 | bus_MV_156_0_node_153 | 20 | n |  | TRUE
173 | bus_MV_156_0_node_217 | 20 | n |  | TRUE
174 | bus_MV_156_0_node_235 | 20 | n |  | TRUE
175 | bus_HV_156_0_node_34 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_156_0_load_0 | 0 | 0.066705 | 0.032307 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_156_0_load_244 | 2 | 0.058987 | 0.028569 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_156_0_load_67 | 3 | 0.15033 | 0.072807 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_156_0_load_75 | 4 | 0.11218 | 0.054333 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_156_0_load_1 | 6 | 0.11401 | 0.055217 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_156_0_load_4 | 9 | 0.095749 | 0.046373 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_156_0_load_5 | 10 | 0.16958 | 0.082133 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_156_0_load_14 | 13 | 0.080435 | 0.038956 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_156_0_load_132 | 14 | 0.068685 | 0.033266 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_156_0_load_8 | 15 | 0.14028 | 0.067942 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_156_0_load_242 | 19 | 0.12691 | 0.061467 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_156_0_load_241 | 20 | 0.083497 | 0.04044 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_156_0_load_245 | 22 | 0.14514 | 0.070294 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_156_0_load_240 | 23 | 0.16175 | 0.078338 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_156_0_load_15 | 24 | 0.15511 | 0.075123 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_156_0_load_115 | 27 | 0.12692 | 0.06147 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_156_0_load_226 | 31 | 0.16418 | 0.079518 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_156_0_load_225 | 32 | 0.10527 | 0.050985 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_156_0_load_111 | 33 | 0.1024 | 0.049596 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_156_0_load_33 | 35 | 0.11475 | 0.055578 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_156_0_load_238 | 37 | 0.064815 | 0.031391 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_156_0_load_127 | 40 | 0.096227 | 0.046605 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_156_0_load_24 | 41 | 0.10936 | 0.052966 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_156_0_load_112 | 42 | 0.17036 | 0.08251 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_156_0_load_22 | 44 | 0.16321 | 0.079047 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_156_0_load_34 | 45 | 0.10295 | 0.04986 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_156_0_load_128 | 48 | 0.07841 | 0.037976 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_156_0_load_28 | 50 | 0.11544 | 0.055909 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_156_0_load_100 | 55 | 0.13242 | 0.064134 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_156_0_load_113 | 56 | 0.12111 | 0.058657 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_156_0_load_36 | 60 | 0.082713 | 0.04006 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_156_0_load_103 | 66 | 0.094557 | 0.045796 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_156_0_load_110 | 67 | 0.13699 | 0.066347 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_156_0_load_122 | 69 | 0.14272 | 0.06912 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_156_0_load_215 | 70 | 0.19932 | 0.096535 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_156_0_load_239 | 71 | 0.059594 | 0.028863 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_156_0_load_118 | 72 | 0.13181 | 0.063839 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_156_0_load_43 | 73 | 0.12891 | 0.062434 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_156_0_load_46 | 76 | 0.14192 | 0.068734 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_156_0_load_243 | 78 | 0.14813 | 0.071742 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_156_0_load_210 | 79 | 0.10433 | 0.050529 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_156_0_load_211 | 81 | 0.209 | 0.10122 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_156_0_load_48 | 82 | 0.10132 | 0.04907 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_156_0_load_58 | 86 | 0.13297 | 0.0644 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_156_0_load_88 | 89 | 0.093752 | 0.045406 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_156_0_load_207 | 91 | 0.11474 | 0.055569 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_156_0_load_206 | 92 | 0.084536 | 0.040943 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_156_0_load_52 | 93 | 0.059291 | 0.028716 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_156_0_load_96 | 98 | 0.1071 | 0.051872 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_156_0_load_56 | 99 | 0.13609 | 0.065911 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_156_0_load_57 | 100 | 0.15646 | 0.075776 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_156_0_load_61 | 104 | 0.11505 | 0.055721 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_156_0_load_77 | 107 | 0.10124 | 0.049035 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_156_0_load_209 | 110 | 0.092842 | 0.044966 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_156_0_load_83 | 111 | 0.12458 | 0.060336 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_156_0_load_82 | 113 | 0.12143 | 0.058809 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_156_0_load_236 | 114 | 0.15361 | 0.074397 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_156_0_load_237 | 115 | 0.087922 | 0.042583 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_156_0_load_90 | 119 | 0.1598 | 0.077396 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_156_0_load_89 | 120 | 0.12313 | 0.059636 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_156_0_load_71 | 121 | 0.12308 | 0.059612 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_156_0_load_73 | 123 | 0.30898 | 0.14964 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_156_0_load_125 | 124 | 0.2687 | 0.13014 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_156_0_load_123 | 125 | 0.12188 | 0.059028 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_156_0_load_86 | 129 | 0.082135 | 0.03978 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_156_0_load_234 | 131 | 0.097089 | 0.047023 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_156_0_load_212 | 133 | 0.12728 | 0.061644 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_156_0_load_91 | 134 | 0.085229 | 0.041278 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_156_0_load_92 | 135 | 1.0101 | 0.48919 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_156_0_load_224 | 138 | 0.11458 | 0.055494 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_156_0_load_214 | 142 | 1.7078 | 0.82713 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_156_0_load_233 | 143 | 0.091002 | 0.044074 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_156_0_load_105 | 145 | 0.16292 | 0.078907 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_156_0_load_109 | 148 | 0.14489 | 0.070174 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_156_0_load_116 | 149 | 0.32849 | 0.15909 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_156_0_load_119 | 151 | 0.15087 | 0.07307 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_156_0_load_144 | 152 | 0.10975 | 0.053152 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_156_0_load_139 | 154 | 0.058698 | 0.028429 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_156_0_load_216 | 156 | 2.9207 | 1.4146 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_156_0_load_136 | 159 | 0.14212 | 0.068831 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_156_0_load_151 | 162 | 0.14512 | 0.070283 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_156_0_load_140 | 168 | 0.092395 | 0.044749 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_156_0_load_148 | 169 | 0.1477 | 0.071535 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_156_0_load_145 | 170 | 0.16099 | 0.07797 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_156_0_load_150 | 171 | 0.16477 | 0.079802 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_156_0_load_217 | 173 | 0.08881 | 0.043013 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_156_0_load_235 | 174 | 0.10155 | 0.049182 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_156_0_line_0 |  | 0 | 1 | 2.9493 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
1 | MV_156_0_line_1 |  | 0 | 2 | 3.801 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
2 | MV_156_0_line_2 |  | 1 | 3 | 1.8708 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
3 | MV_156_0_line_3 |  | 1 | 4 | 0.064857 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_156_0_line_4 |  | 2 | 5 | 0.36005 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
5 | MV_156_0_line_5 |  | 3 | 116 | 0.041728 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_156_0_line_6 |  | 5 | 7 | 0.040312 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
7 | MV_156_0_line_7 |  | 6 | 7 | 0.075617 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
8 | MV_156_0_line_8 |  | 6 | 8 | 0.20405 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
9 | MV_156_0_line_9 |  | 8 | 9 | 0.043986 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
10 | MV_156_0_line_10 |  | 9 | 10 | 0.10488 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
11 | MV_156_0_line_11 |  | 10 | 11 | 0.10214 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
12 | MV_156_0_line_12 |  | 11 | 12 | 0.37207 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
13 | MV_156_0_line_13 |  | 11 | 13 | 0.79606 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_156_0_line_14 |  | 12 | 14 | 0.20265 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
15 | MV_156_0_line_15 |  | 13 | 22 | 0.28689 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_156_0_line_16 |  | 14 | 157 | 0.085544 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
17 | MV_156_0_line_17 |  | 15 | 16 | 0.1457 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_156_0_line_18 |  | 16 | 17 | 0.11695 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_156_0_line_19 |  | 16 | 18 | 0.16034 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_156_0_line_20 |  | 17 | 19 | 0.009255 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_156_0_line_21 |  | 18 | 20 | 0.018905 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_156_0_line_22 |  | 19 | 23 | 0.3707 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_156_0_line_23 |  | 20 | 21 | 0.22101 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_156_0_line_24 |  | 21 | 22 | 0.059536 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_156_0_line_25 |  | 24 | 25 | 0.055186 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_156_0_line_26 |  | 25 | 26 | 0.24019 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
27 | MV_156_0_line_27 |  | 25 | 27 | 0.10217 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
28 | MV_156_0_line_28 |  | 26 | 34 | 0.081945 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
29 | MV_156_0_line_29 |  | 26 | 35 | 0.040428 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
30 | MV_156_0_line_30 |  | 27 | 28 | 0.062121 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
31 | MV_156_0_line_31 |  | 28 | 29 | 0.091929 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
32 | MV_156_0_line_32 |  | 29 | 33 | 0.028249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_156_0_line_33 |  | 29 | 30 | 0.12071 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
34 | MV_156_0_line_34 |  | 30 | 31 | 0.074064 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_156_0_line_35 |  | 30 | 32 | 0.063716 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
36 | MV_156_0_line_36 |  | 32 | 36 | 0.04792 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
37 | MV_156_0_line_37 |  | 33 | 42 | 0.017615 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_156_0_line_38 |  | 33 | 43 | 0.026854 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_156_0_line_39 |  | 34 | 44 | 0.019705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_156_0_line_40 |  | 34 | 39 | 0.17291 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
41 | MV_156_0_line_41 |  | 35 | 45 | 0.18206 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
42 | MV_156_0_line_42 |  | 36 | 37 | 0.014746 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
43 | MV_156_0_line_43 |  | 37 | 38 | 0.11235 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
44 | MV_156_0_line_44 |  | 38 | 151 | 0.025704 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
45 | MV_156_0_line_45 |  | 39 | 40 | 0.084067 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_156_0_line_46 |  | 39 | 41 | 0.019328 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
47 | MV_156_0_line_47 |  | 41 | 46 | 0.035531 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
48 | MV_156_0_line_48 |  | 43 | 136 | 0.006705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_156_0_line_49 |  | 45 | 53 | 0.054292 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
50 | MV_156_0_line_50 |  | 46 | 47 | 0.10263 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
51 | MV_156_0_line_51 |  | 47 | 48 | 0.021167 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
52 | MV_156_0_line_52 |  | 48 | 49 | 0.036817 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
53 | MV_156_0_line_53 |  | 49 | 140 | 0.11957 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
54 | MV_156_0_line_54 |  | 50 | 51 | 0.064425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_156_0_line_55 |  | 51 | 52 | 0.27544 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_156_0_line_56 |  | 52 | 55 | 0.10084 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_156_0_line_57 |  | 53 | 54 | 0.042015 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
58 | MV_156_0_line_58 |  | 54 | 56 | 0.074553 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
59 | MV_156_0_line_59 |  | 55 | 57 | 0.050492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_156_0_line_60 |  | 55 | 58 | 0.30468 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_156_0_line_61 |  | 56 | 59 | 0.011261 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
62 | MV_156_0_line_62 |  | 57 | 80 | 0.45234 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_156_0_line_63 |  | 58 | 71 | 0.022868 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_156_0_line_64 |  | 58 | 63 | 0.13988 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_156_0_line_65 |  | 59 | 65 | 0.077063 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
66 | MV_156_0_line_66 |  | 60 | 61 | 0.021994 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_156_0_line_67 |  | 60 | 62 | 0.03425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_156_0_line_68 |  | 61 | 63 | 0.17385 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_156_0_line_69 |  | 62 | 64 | 0.34797 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_156_0_line_70 |  | 62 | 65 | 0.25294 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_156_0_line_71 |  | 63 | 66 | 0.04453 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_156_0_line_72 |  | 64 | 67 | 0.073367 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_156_0_line_73 |  | 65 | 70 | 0.019203 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_156_0_line_74 |  | 65 | 68 | 0.08729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_156_0_line_75 |  | 68 | 69 | 0.016195 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_156_0_line_76 |  | 70 | 72 | 0.010604 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_156_0_line_77 |  | 72 | 150 | 0.056199 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_156_0_line_78 |  | 73 | 74 | 0.083284 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
79 | MV_156_0_line_79 |  | 74 | 75 | 0.031302 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_156_0_line_80 |  | 75 | 76 | 0.11292 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_156_0_line_81 |  | 75 | 77 | 0.41707 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_156_0_line_82 |  | 75 | 78 | 0.41967 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_156_0_line_83 |  | 77 | 79 | 0.051444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_156_0_line_84 |  | 78 | 80 | 0.22558 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_156_0_line_85 |  | 79 | 81 | 0.025044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_156_0_line_86 |  | 81 | 133 | 0.024124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_156_0_line_87 |  | 82 | 83 | 0.078979 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
88 | MV_156_0_line_88 |  | 83 | 84 | 0.034322 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_156_0_line_89 |  | 83 | 85 | 0.21881 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_156_0_line_90 |  | 84 | 89 | 0.083372 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_156_0_line_91 |  | 85 | 90 | 0.054774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_156_0_line_92 |  | 85 | 91 | 0.045263 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_156_0_line_93 |  | 86 | 87 | 0.012904 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_156_0_line_94 |  | 86 | 88 | 0.029801 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_156_0_line_95 |  | 87 | 103 | 0.063838 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_156_0_line_96 |  | 88 | 104 | 0.0043742 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_156_0_line_97 |  | 90 | 92 | 0.021512 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_156_0_line_98 |  | 92 | 106 | 0.023655 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_156_0_line_99 |  | 93 | 94 | 0.1146 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_156_0_line_100 |  | 94 | 95 | 0.083594 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_156_0_line_101 |  | 95 | 98 | 0.066877 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_156_0_line_102 |  | 96 | 97 | 0.007444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_156_0_line_103 |  | 96 | 98 | 0.11969 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
104 | MV_156_0_line_104 |  | 97 | 131 | 0.080196 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_156_0_line_105 |  | 99 | 100 | 0.023339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_156_0_line_106 |  | 100 | 101 | 0.0631 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
107 | MV_156_0_line_107 |  | 101 | 102 | 0.081574 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_156_0_line_108 |  | 101 | 103 | 0.16279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_156_0_line_109 |  | 102 | 109 | 0.18608 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_156_0_line_110 |  | 102 | 110 | 0.12563 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_156_0_line_111 |  | 104 | 105 | 0.0079828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_156_0_line_112 |  | 105 | 106 | 0.024388 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_156_0_line_113 |  | 105 | 107 | 0.051547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_156_0_line_114 |  | 107 | 108 | 0.030937 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_156_0_line_115 |  | 108 | 128 | 0.3472 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_156_0_line_116 |  | 108 | 112 | 0.1141 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
117 | MV_156_0_line_117 |  | 109 | 111 | 0.031992 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_156_0_line_118 |  | 110 | 114 | 0.27892 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
119 | MV_156_0_line_119 |  | 111 | 115 | 0.29545 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
120 | MV_156_0_line_120 |  | 112 | 113 | 0.10039 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_156_0_line_121 |  | 113 | 132 | 0.011568 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_156_0_line_122 |  | 114 | 174 | 0.87557 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
123 | MV_156_0_line_123 |  | 116 | 117 | 0.37327 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_156_0_line_124 |  | 117 | 118 | 0.17618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_156_0_line_125 |  | 117 | 119 | 0.05857 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
126 | MV_156_0_line_126 |  | 118 | 120 | 0.054657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_156_0_line_127 |  | 121 | 122 | 0.063349 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
128 | MV_156_0_line_128 |  | 122 | 123 | 0.014506 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_156_0_line_129 |  | 123 | 126 | 0.030324 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_156_0_line_130 |  | 124 | 125 | 0.086127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_156_0_line_131 |  | 125 | 127 | 0.083331 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_156_0_line_132 |  | 125 | 126 | 0.14143 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
133 | MV_156_0_line_133 |  | 127 | 139 | 0.061789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_156_0_line_134 |  | 128 | 129 | 0.09204 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_156_0_line_135 |  | 129 | 130 | 0.11325 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_156_0_line_136 |  | 130 | 131 | 0.11971 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
137 | MV_156_0_line_137 |  | 132 | 133 | 0.031638 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_156_0_line_138 |  | 134 | 135 | 0.043824 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_156_0_line_139 |  | 134 | 136 | 0.06124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_156_0_line_140 |  | 137 | 138 | 0.049011 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_156_0_line_141 |  | 137 | 139 | 0.67194 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_156_0_line_142 |  | 137 | 140 | 0.32519 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_156_0_line_143 |  | 138 | 141 | 0.050253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_156_0_line_144 |  | 139 | 142 | 0.23354 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_156_0_line_145 |  | 140 | 143 | 0.07072 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_156_0_line_146 |  | 140 | 144 | 0.092291 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_156_0_line_147 |  | 141 | 146 | 0.23049 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_156_0_line_148 |  | 144 | 156 | 0.037761 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_156_0_line_149 |  | 145 | 146 | 0.07403 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
150 | MV_156_0_line_150 |  | 146 | 147 | 0.66484 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_156_0_line_151 |  | 147 | 148 | 0.083152 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_156_0_line_152 |  | 149 | 150 | 0.009123 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_156_0_line_153 |  | 151 | 152 | 0.79406 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
154 | MV_156_0_line_154 |  | 152 | 153 | 0.052937 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
155 | MV_156_0_line_155 |  | 153 | 154 | 1.0197 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
156 | MV_156_0_line_156 |  | 153 | 155 | 1.1001 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
157 | MV_156_0_line_157 |  | 155 | 164 | 0.34469 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
158 | MV_156_0_line_158 |  | 155 | 168 | 0.081062 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_156_0_line_159 |  | 157 | 158 | 0.14736 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
160 | MV_156_0_line_160 |  | 158 | 159 | 0.025426 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
161 | MV_156_0_line_161 |  | 159 | 160 | 0.020285 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
162 | MV_156_0_line_162 |  | 160 | 161 | 1.1233 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
163 | MV_156_0_line_163 |  | 161 | 162 | 0.043985 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
164 | MV_156_0_line_164 |  | 162 | 163 | 0.03474 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_156_0_line_165 |  | 162 | 164 | 0.18778 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
166 | MV_156_0_line_166 |  | 163 | 172 | 0.13818 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_156_0_line_167 |  | 165 | 166 | 0.34925 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
168 | MV_156_0_line_168 |  | 165 | 167 | 0.99431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_156_0_line_169 |  | 166 | 171 | 0.0071173 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_156_0_line_170 |  | 166 | 169 | 0.03774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
171 | MV_156_0_line_171 |  | 167 | 170 | 0.034824 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_156_0_line_172 |  | 171 | 172 | 0.083781 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_156_0_line_173 |  | 172 | 173 | 0.14319 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_156_0_trafo_34 | 25 MVA 110/20 kV | 175 | 45 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2719051.3522 | 1248032.4469
1 | 2721103.7554 | 1250150.5229
2 | 2722730.2462 | 1248987.9602
3 | 2720886.2097 | 1252008.6483
4 | 2721168.6106 | 1250146.8119
5 | 2723073.6505 | 1248879.7424
6 | 2723146.3093 | 1248946.8865
7 | 2723113.9364 | 1248878.5111
8 | 2723234.2984 | 1249130.9949
9 | 2723253.208 | 1249170.7332
10 | 2723298.2856 | 1249265.4325
11 | 2723342.1816 | 1249357.6553
12 | 2723300.6568 | 1249628.6019
13 | 2724085.5353 | 1249072.8237
14 | 2723270.8136 | 1249829.0423
15 | 2724537.954 | 1249014.4493
16 | 2724651.246 | 1249106.0649
17 | 2724730.3739 | 1249034.3563
18 | 2724587.7258 | 1249204.3032
19 | 2724737.8025 | 1249028.8078
20 | 2724576.2086 | 1249219.3185
21 | 2724374.8033 | 1249128.3222
22 | 2724350.5488 | 1249182.6936
23 | 2725052.5118 | 1249224.7072
24 | 2723030.7221 | 1252544.3852
25 | 2722982.7541 | 1252517.9887
26 | 2722823.5574 | 1252556.8422
27 | 2723014.0421 | 1252420.7317
28 | 2723073.8511 | 1252437.5217
29 | 2723107.4213 | 1252417.2015
30 | 2723134.5203 | 1252306.6021
31 | 2723108.255 | 1252237.3519
32 | 2723195.9804 | 1252289.7985
33 | 2723133.6304 | 1252427.7407
34 | 2722816.5263 | 1252616.3035
35 | 2722803.1907 | 1252529.185
36 | 2723233.3325 | 1252319.957
37 | 2723241.2243 | 1252307.4881
38 | 2723260.206 | 1252196.7537
39 | 2722972.7401 | 1252690.4302
40 | 2723049.7053 | 1252724.2465
41 | 2722965.229 | 1252708.2453
42 | 2723140.2021 | 1252411.3978
43 | 2723158.5458 | 1252437.7596
44 | 2722801.7094 | 1252629.341
45 | 2722806.8763 | 1252347.1594
46 | 2722950.8606 | 1252740.7531
47 | 2722895.6471 | 1252827.0712
48 | 2722883.139 | 1252844.1711
49 | 2722858.2139 | 1252871.0886
50 | 2722612.8106 | 1252479.1654
51 | 2722572.4772 | 1252428.8318
52 | 2722337.2684 | 1252419.974
53 | 2722844.3667 | 1252307.7914
54 | 2722874.8892 | 1252304.4547
55 | 2722270.0227 | 1252345.3881
56 | 2722933.1049 | 1252260.6244
57 | 2722223.256 | 1252364.0504
58 | 2722516.0227 | 1252165.6256
59 | 2722942.1088 | 1252253.8275
60 | 2722836.1413 | 1252155.9228
61 | 2722815.2638 | 1252148.8172
62 | 2722868.6532 | 1252166.9843
63 | 2722652.1449 | 1252171.7916
64 | 2723045.3154 | 1251995.88
65 | 2722998.872 | 1252303.215
66 | 2722621.342 | 1252203.9485
67 | 2722973.3811 | 1251981.452
68 | 2723056.2865 | 1252326.305
69 | 2723042.0091 | 1252334.0263
70 | 2722982.8179 | 1252313.7514
71 | 2722507.6837 | 1252144.3237
72 | 2722973.9526 | 1252319.5697
73 | 2721221.5501 | 1252337.3929
74 | 2721304.6492 | 1252342.9429
75 | 2721334.4506 | 1252333.1002
76 | 2721279.8432 | 1252235.7095
77 | 2721244.9575 | 1252447.3331
78 | 2721740.0146 | 1252225.2042
79 | 2721195.3416 | 1252433.7858
80 | 2721962.4743 | 1252187.8247
81 | 2721170.905 | 1252428.3255
82 | 2720807.8904 | 1252664.9699
83 | 2720878.0695 | 1252701.1991
84 | 2720895.8746 | 1252705.3549
85 | 2720796.0353 | 1252521.9942
86 | 2720860.7416 | 1252416.3342
87 | 2720865.6655 | 1252404.4022
88 | 2720862.0133 | 1252446.1079
89 | 2720968.8366 | 1252744.2443
90 | 2720816.6391 | 1252473.3837
91 | 2720779.3032 | 1252564.0003
92 | 2720837.9078 | 1252476.6094
93 | 2721368.1842 | 1253439.5224
94 | 2721313.9328 | 1253338.5796
95 | 2721318.8399 | 1253255.3082
96 | 2721340.9033 | 1253070.0558
97 | 2721341.8171 | 1253062.6682
98 | 2721326.8278 | 1253188.9145
99 | 2720762.5977 | 1252312.0101
100 | 2720747.5242 | 1252294.1543
101 | 2720798.2569 | 1252256.634
102 | 2720729.4846 | 1252223.6929
103 | 2720893.5124 | 1252368.5951
104 | 2720863.7864 | 1252450.1066
105 | 2720867.7312 | 1252457.0339
106 | 2720861.2956 | 1252480.1559
107 | 2720908.8386 | 1252487.8881
108 | 2720927.1142 | 1252512.649
109 | 2720741.486 | 1252087.9321
110 | 2720643.3924 | 1252210.9951
111 | 2720718.9553 | 1252065.1535
112 | 2721004.3194 | 1252428.6309
113 | 2721103.9664 | 1252424.4775
114 | 2720517.4007 | 1252459.8333
115 | 2720445.8168 | 1251952.5319
116 | 2720865.0163 | 1252044.6246
117 | 2721017.623 | 1252300.3702
118 | 2720916.2336 | 1252290.3026
119 | 2721075.1186 | 1252289.2018
120 | 2720961.933 | 1252319.9831
121 | 2723201.7523 | 1252972.5552
122 | 2723220.9059 | 1253032.9393
123 | 2723222.8484 | 1253047.3144
124 | 2723066.442 | 1253125.8453
125 | 2723136.1572 | 1253173.9441
126 | 2723236.5447 | 1253074.3228
127 | 2723161.8841 | 1253251.7799
128 | 2721136.4926 | 1252755.4795
129 | 2721214.011 | 1252805.4636
130 | 2721292.455 | 1252883.8922
131 | 2721357.9352 | 1252984.1084
132 | 2721115.4977 | 1252423.5537
133 | 2721147.0837 | 1252424.5961
134 | 2723221.6738 | 1252463.3499
135 | 2723207.8029 | 1252504.921
136 | 2723164.7819 | 1252440.2692
137 | 2722566.855 | 1253128.3321
138 | 2722542.9544 | 1253171.1525
139 | 2723147.2023 | 1253311.3264
140 | 2722767.0783 | 1252942.5947
141 | 2722517.8462 | 1253214.7154
142 | 2723189.8487 | 1253479.8861
143 | 2722715.8966 | 1252893.6363
144 | 2722826.3517 | 1252972.9607
145 | 2722714.8723 | 1253348.9877
146 | 2722672.0905 | 1253288.5715
147 | 2723011.8044 | 1253622.7507
148 | 2723026.8295 | 1253542.96
149 | 2722941.2171 | 1252360.9387
150 | 2722933.8357 | 1252355.5773
151 | 2723282.2894 | 1252184.7353
152 | 2724031.5224 | 1251921.7218
153 | 2724057.4931 | 1251967.8499
154 | 2725077.2273 | 1251965.3076
155 | 2724070.6506 | 1251052.7652
156 | 2722836.1643 | 1253008.2332
157 | 2723252.4973 | 1249912.5999
158 | 2723247.1656 | 1250057.7472
159 | 2723242.9885 | 1250082.8263
160 | 2723239.4764 | 1250102.8038
161 | 2723894.8445 | 1250664.129
162 | 2723937.9834 | 1250658.793
163 | 2723944.8271 | 1250625.4962
164 | 2723953.1702 | 1250845.9613
165 | 2724462.9551 | 1250613.3217
166 | 2724114.4678 | 1250590.2047
167 | 2725354.8761 | 1250462.0103
168 | 2724128.0383 | 1251109.2381
169 | 2724112.7574 | 1250627.857
170 | 2725337.8607 | 1250434.6156
171 | 2724107.3571 | 1250589.8999
172 | 2724023.6532 | 1250586.3114
173 | 2724085.0607 | 1250466.4205
174 | 2719641.9501 | 1252474.4474
175 | 2722806.8763 | 1252347.1594

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99045 | -0.39893 | 0.066705 | 0.032307
1 | 0.98938 | -0.46172 | 0 | 0
2 | 0.99198 | -0.30822 | 0.058987 | 0.028569
3 | 0.98884 | -0.49339 | 0.15033 | 0.072807
4 | 0.98937 | -0.46163 | 0.11218 | 0.054333
5 | 0.99214 | -0.29882 | 0 | 0
6 | 0.99217 | -0.29867 | 0.11401 | 0.055217
7 | 0.99215 | -0.29877 | 0 | 0
8 | 0.99227 | -0.29243 | 0 | 0
9 | 0.99228 | -0.29236 | 0.095749 | 0.046373
10 | 0.99231 | -0.29219 | 0.16958 | 0.082133
11 | 0.99235 | -0.292 | 0 | 0
12 | 0.99256 | -0.29082 | 0 | 0
13 | 0.99121 | -0.29983 | 0.080435 | 0.038956
14 | 0.9928 | -0.27669 | 0.068685 | 0.033266
15 | 0.99042 | -0.3037 | 0.14028 | 0.067942
16 | 0.99046 | -0.30344 | 0 | 0
17 | 0.99042 | -0.30305 | 0 | 0
18 | 0.99055 | -0.30423 | 0 | 0
19 | 0.99042 | -0.30302 | 0.12691 | 0.061467
20 | 0.99056 | -0.30432 | 0.083497 | 0.04044
21 | 0.99078 | -0.30277 | 0 | 0
22 | 0.99084 | -0.30235 | 0.14514 | 0.070294
23 | 0.9903 | -0.30376 | 0.16175 | 0.078338
24 | 0.99805 | -0.084512 | 0.15511 | 0.075123
25 | 0.99806 | -0.084613 | 0 | 0
26 | 0.99845 | -0.082038 | 0 | 0
27 | 0.99774 | -0.10429 | 0.12692 | 0.06147
28 | 0.99755 | -0.11597 | 0 | 0
29 | 0.9974 | -0.11691 | 0 | 0
30 | 0.99727 | -0.11794 | 0 | 0
31 | 0.99725 | -0.11809 | 0.16418 | 0.079518
32 | 0.99714 | -0.12621 | 0.10527 | 0.050985
33 | 0.99736 | -0.11645 | 0.1024 | 0.049596
34 | 0.99828 | -0.082753 | 0 | 0
35 | 0.9986 | -0.081245 | 0.11475 | 0.055578
36 | 0.99709 | -0.1266 | 0 | 0
37 | 0.99708 | -0.12672 | 0.064815 | 0.031391
38 | 0.99686 | -0.14059 | 0 | 0
39 | 0.99755 | -0.12389 | 0 | 0
40 | 0.99753 | -0.12399 | 0.096227 | 0.046605
41 | 0.99751 | -0.12406 | 0.10936 | 0.052966
42 | 0.99735 | -0.11642 | 0.17036 | 0.08251
43 | 0.9973 | -0.11682 | 0 | 0
44 | 0.99828 | -0.082715 | 0.16321 | 0.079047
45 | 1 | 0 | -16.1998 | -7.3172
46 | 0.99744 | -0.12435 | 0 | 0
47 | 0.99723 | -0.1252 | 0 | 0
48 | 0.99719 | -0.12537 | 0.07841 | 0.037976
49 | 0.99712 | -0.12567 | 0 | 0
50 | 0.99492 | 0.0043344 | 0.11544 | 0.055909
51 | 0.99493 | 0.0042476 | 0 | 0
52 | 0.99497 | 0.0039481 | 0 | 0
53 | 0.99992 | -0.00039166 | 0 | 0
54 | 0.99986 | -0.00069292 | 0 | 0
55 | 0.99498 | 0.0038673 | 0.13242 | 0.064134
56 | 0.99975 | -0.0012235 | 0.12111 | 0.058657
57 | 0.9948 | 0.0054027 | 0 | 0
58 | 0.99685 | 0.018122 | 0 | 0
59 | 0.99973 | -0.0013017 | 0 | 0
60 | 0.99826 | 0.0068069 | 0.082713 | 0.04006
61 | 0.99817 | 0.0075523 | 0 | 0
62 | 0.99841 | 0.0056138 | 0 | 0
63 | 0.99743 | 0.013475 | 0 | 0
64 | 0.99835 | 0.0060919 | 0 | 0
65 | 0.99955 | -0.0034107 | 0 | 0
66 | 0.99742 | 0.013424 | 0.094557 | 0.045796
67 | 0.99833 | 0.0059698 | 0.13699 | 0.066347
68 | 0.99954 | -0.0032694 | 0 | 0
69 | 0.99953 | -0.003242 | 0.14272 | 0.06912
70 | 0.99954 | -0.0032615 | 0.19932 | 0.096535
71 | 0.99685 | 0.018138 | 0.059594 | 0.028863
72 | 0.99953 | -0.0032042 | 0.13181 | 0.063839
73 | 0.98954 | -0.0070799 | 0.12891 | 0.062434
74 | 0.98956 | -0.006947 | 0 | 0
75 | 0.98957 | -0.0069954 | 0 | 0
76 | 0.98955 | -0.0068093 | 0.14192 | 0.068734
77 | 0.98823 | 0.0041719 | 0 | 0
78 | 0.99183 | 0.0098938 | 0.14813 | 0.071742
79 | 0.98807 | 0.0055697 | 0.10433 | 0.050529
80 | 0.9931 | 0.019357 | 0 | 0
81 | 0.98799 | 0.0062198 | 0.209 | 0.10122
82 | 0.98684 | 0.008733 | 0.10132 | 0.04907
83 | 0.98686 | 0.0088326 | 0 | 0
84 | 0.98685 | 0.0088669 | 0 | 0
85 | 0.98691 | 0.0083852 | 0 | 0
86 | 0.98689 | 0.0076823 | 0.13297 | 0.0644
87 | 0.98688 | 0.0078027 | 0 | 0
88 | 0.98695 | 0.0080934 | 0 | 0
89 | 0.98684 | 0.0089576 | 0.093752 | 0.045406
90 | 0.98693 | 0.0082112 | 0 | 0
91 | 0.98691 | 0.0084474 | 0.11474 | 0.055569
92 | 0.98694 | 0.0081441 | 0.084536 | 0.040943
93 | 0.98674 | 0.0075139 | 0.059291 | 0.028716
94 | 0.98676 | 0.0075989 | 0 | 0
95 | 0.98676 | 0.0075441 | 0 | 0
96 | 0.98681 | 0.0077937 | 0 | 0
97 | 0.98681 | 0.0077803 | 0 | 0
98 | 0.98677 | 0.0075078 | 0.1071 | 0.051872
99 | 0.98659 | 0.0097649 | 0.13609 | 0.065911
100 | 0.98659 | 0.0097263 | 0.15646 | 0.075776
101 | 0.98663 | 0.0099586 | 0 | 0
102 | 0.98657 | 0.010464 | 0 | 0
103 | 0.98681 | 0.008402 | 0 | 0
104 | 0.98695 | 0.0080455 | 0.11505 | 0.055721
105 | 0.98697 | 0.0079469 | 0 | 0
106 | 0.98695 | 0.0080466 | 0 | 0
107 | 0.98707 | 0.0071031 | 0.10124 | 0.049035
108 | 0.98713 | 0.0065603 | 0 | 0
109 | 0.98652 | 0.01091 | 0 | 0
110 | 0.98651 | 0.010978 | 0.092842 | 0.044966
111 | 0.98651 | 0.010993 | 0.12458 | 0.060336
112 | 0.98756 | 0.0097971 | 0 | 0
113 | 0.98781 | 0.0077329 | 0.12143 | 0.058809
114 | 0.98638 | 0.010066 | 0.15361 | 0.074397
115 | 0.98646 | 0.010666 | 0.087922 | 0.042583
116 | 0.98883 | -0.49329 | 0 | 0
117 | 0.9887 | -0.49224 | 0 | 0
118 | 0.98867 | -0.49201 | 0 | 0
119 | 0.98868 | -0.49235 | 0.1598 | 0.077396
120 | 0.98866 | -0.49193 | 0.12313 | 0.059636
121 | 0.99303 | -0.099089 | 0.12308 | 0.059612
122 | 0.99304 | -0.098994 | 0 | 0
123 | 0.99305 | -0.099015 | 0.30898 | 0.14964
124 | 0.99315 | -0.098134 | 0.2687 | 0.13014
125 | 0.99318 | -0.098409 | 0.12188 | 0.059028
126 | 0.99306 | -0.099172 | 0 | 0
127 | 0.99327 | -0.099217 | 0 | 0
128 | 0.98698 | 0.007739 | 0 | 0
129 | 0.98693 | 0.0080823 | 0.082135 | 0.03978
130 | 0.9869 | 0.0084082 | 0 | 0
131 | 0.98683 | 0.0079739 | 0.097089 | 0.047023
132 | 0.98784 | 0.0074789 | 0 | 0
133 | 0.98792 | 0.0067852 | 0.12728 | 0.061644
134 | 0.9972 | -0.11593 | 0.085229 | 0.041278
135 | 0.99715 | -0.1154 | 1.0101 | 0.48919
136 | 0.99729 | -0.11673 | 0 | 0
137 | 0.99551 | -0.11951 | 0 | 0
138 | 0.99548 | -0.11934 | 0.11458 | 0.055494
139 | 0.99334 | -0.09981 | 0 | 0
140 | 0.99673 | -0.12988 | 0 | 0
141 | 0.99546 | -0.11923 | 0 | 0
142 | 0.99282 | -0.095013 | 1.7078 | 0.82713
143 | 0.99673 | -0.12981 | 0.091002 | 0.044074
144 | 0.99639 | -0.12665 | 0 | 0
145 | 0.99535 | -0.11882 | 0.16292 | 0.078907
146 | 0.99537 | -0.11867 | 0 | 0
147 | 0.99525 | -0.11793 | 0 | 0
148 | 0.99524 | -0.11779 | 0.14489 | 0.070174
149 | 0.9995 | -0.0029505 | 0.32849 | 0.15909
150 | 0.99951 | -0.0029863 | 0 | 0
151 | 0.99684 | -0.14079 | 0.15087 | 0.07307
152 | 0.9954 | -0.23438 | 0.10975 | 0.053152
153 | 0.99531 | -0.24041 | 0 | 0
154 | 0.99519 | -0.24119 | 0.058698 | 0.028429
155 | 0.99434 | -0.24834 | 0 | 0
156 | 0.99625 | -0.12532 | 2.9207 | 1.4146
157 | 0.99285 | -0.27639 | 0 | 0
158 | 0.99294 | -0.27587 | 0 | 0
159 | 0.99296 | -0.27577 | 0.14212 | 0.068831
160 | 0.99297 | -0.2757 | 0 | 0
161 | 0.99369 | -0.27081 | 0 | 0
162 | 0.99372 | -0.27059 | 0.14512 | 0.070283
163 | 0.99369 | -0.27043 | 0 | 0
164 | 0.99404 | -0.25055 | 0 | 0
165 | 0.99344 | -0.27085 | 0 | 0
166 | 0.99354 | -0.26943 | 0 | 0
167 | 0.99324 | -0.26972 | 0 | 0
168 | 0.99433 | -0.24825 | 0.092395 | 0.044749
169 | 0.99354 | -0.26936 | 0.1477 | 0.071535
170 | 0.99323 | -0.26965 | 0.16099 | 0.07797
171 | 0.99355 | -0.26945 | 0.16477 | 0.079802
172 | 0.9936 | -0.26978 | 0 | 0
173 | 0.99358 | -0.26964 | 0.08881 | 0.043013
174 | 0.9862 | 0.0089226 | 0.10155 | 0.049182
175 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.54595 | 0.24221 | -0.54563 | -0.24535 | 0.00031994 | -0.0031347 | 0.017408 | 0.017455 | 0.017455 | 0.99045 | -0.39893 | 0.98938 | -0.46172 | 2.7063
1 | -0.61266 | -0.27452 | 0.61317 | 0.27075 | 0.00051791 | -0.0037695 | 0.019567 | 0.019506 | 0.019567 | 0.99045 | -0.39893 | 0.99198 | -0.30822 | 3.0337
2 | 0.43345 | 0.19253 | -0.43332 | -0.19471 | 0.00012818 | -0.0021854 | 0.013838 | 0.013868 | 0.013868 | 0.98938 | -0.46172 | 0.98884 | -0.49339 | 2.1501
3 | 0.11218 | 0.052818 | -0.11218 | -0.054333 | 1.1392e-06 | -0.0015155 | 0.0036179 | 0.0036369 | 0.0036369 | 0.98938 | -0.46172 | 0.98937 | -0.46163 | 1.6532
4 | -0.67216 | -0.29932 | 0.67222 | 0.29899 | 5.8917e-05 | -0.0003314 | 0.021412 | 0.021406 | 0.021412 | 0.99198 | -0.30822 | 0.99214 | -0.29882 | 3.3197
5 | 0.28299 | 0.12191 | -0.28299 | -0.12288 | 4.5132e-06 | -0.00097284 | 0.0089953 | 0.0090066 | 0.0090066 | 0.98884 | -0.49339 | 0.98883 | -0.49329 | 4.0939
6 | -0.67222 | -0.29899 | 0.67223 | 0.2965 | 5.7001e-06 | -0.00249 | 0.021406 | 0.021377 | 0.021406 | 0.99214 | -0.29882 | 0.99215 | -0.29877 | 3.3552
7 | 0.67224 | 0.29183 | -0.67223 | -0.2965 | 1.065e-05 | -0.0046709 | 0.021322 | 0.021377 | 0.021377 | 0.99217 | -0.29867 | 0.99215 | -0.29877 | 3.3506
8 | -0.78625 | -0.34704 | 0.78629 | 0.34689 | 4.5544e-05 | -0.00015522 | 0.025005 | 0.025002 | 0.025005 | 0.99217 | -0.29867 | 0.99227 | -0.29243 | 3.8768
9 | -0.78629 | -0.34689 | 0.7863 | 0.34417 | 8.4855e-06 | -0.0027164 | 0.025002 | 0.02497 | 0.025002 | 0.99227 | -0.29243 | 0.99228 | -0.29236 | 3.9188
10 | -0.88205 | -0.39054 | 0.88207 | 0.38407 | 2.5454e-05 | -0.0064744 | 0.028063 | 0.027987 | 0.028063 | 0.99228 | -0.29236 | 0.99231 | -0.29219 | 4.3986
11 | -1.0517 | -0.4662 | 1.0517 | 0.4599 | 3.5267e-05 | -0.0062995 | 0.033465 | 0.033391 | 0.033465 | 0.99231 | -0.29219 | 0.99235 | -0.292 | 5.2453
12 | -1.791 | -0.80874 | 1.7913 | 0.78593 | 0.0003739 | -0.022816 | 0.057165 | 0.056892 | 0.057165 | 0.99235 | -0.292 | 0.99256 | -0.29082 | 8.96
13 | 0.73927 | 0.34884 | -0.73846 | -0.34927 | 0.0008024 | -0.00043217 | 0.023779 | 0.023791 | 0.023791 | 0.99235 | -0.292 | 0.99121 | -0.29983 | 11.329
14 | -1.7913 | -0.78593 | 1.7916 | 0.78628 | 0.00023415 | 0.00035362 | 0.056892 | 0.056889 | 0.056892 | 0.99256 | -0.29082 | 0.9928 | -0.27669 | 8.8205
15 | 0.65803 | 0.31032 | -0.6578 | -0.31051 | 0.00022952 | -0.0001926 | 0.021188 | 0.021192 | 0.021192 | 0.99121 | -0.29983 | 0.99084 | -0.30235 | 10.0916
16 | -1.8603 | -0.81955 | 1.8603 | 0.8143 | 9.225e-05 | -0.0052461 | 0.059107 | 0.059045 | 0.059107 | 0.9928 | -0.27669 | 0.99285 | -0.27639 | 9.2644
17 | -0.14028 | -0.067942 | 0.14029 | 0.067774 | 5.3553e-06 | -0.00016727 | 0.0045431 | 0.0045409 | 0.0045431 | 0.99042 | -0.3037 | 0.99046 | -0.30344 | 2.1634
18 | 0.28869 | 0.13643 | -0.28868 | -0.13917 | 1.3572e-05 | -0.0027351 | 0.0093063 | 0.0093407 | 0.0093407 | 0.99046 | -0.30344 | 0.99042 | -0.30305 | 4.2458
19 | -0.42898 | -0.2042 | 0.42902 | 0.20046 | 4.0906e-05 | -0.0037439 | 0.013847 | 0.0138 | 0.013847 | 0.99046 | -0.30344 | 0.99055 | -0.30423 | 6.2941
20 | 0.28868 | 0.13917 | -0.28868 | -0.13938 | 1.0783e-06 | -0.00021644 | 0.0093407 | 0.0093435 | 0.0093435 | 0.99042 | -0.30305 | 0.99042 | -0.30302 | 4.247
21 | -0.42902 | -0.20046 | 0.42903 | 0.20002 | 4.8047e-06 | -0.00044147 | 0.0138 | 0.013795 | 0.0138 | 0.99055 | -0.30423 | 0.99056 | -0.30432 | 6.2729
22 | 0.16176 | 0.077915 | -0.16175 | -0.078338 | 1.8108e-05 | -0.00042271 | 0.0052333 | 0.0052388 | 0.0052388 | 0.99042 | -0.30302 | 0.9903 | -0.30376 | 2.4947
23 | -0.51252 | -0.24046 | 0.51263 | 0.24027 | 0.00010716 | -0.00019182 | 0.016498 | 0.016495 | 0.016498 | 0.99056 | -0.30432 | 0.99078 | -0.30277 | 7.8564
24 | -0.51263 | -0.24027 | 0.51266 | 0.24022 | 2.8861e-05 | -5.1697e-05 | 0.016495 | 0.016494 | 0.016495 | 0.99078 | -0.30277 | 0.99084 | -0.30235 | 7.8549
25 | -0.15511 | -0.075123 | 0.15511 | 0.073811 | 1.8247e-06 | -0.001312 | 0.0049849 | 0.0049684 | 0.0049849 | 0.99805 | -0.084512 | 0.99806 | -0.084613 | 2.2659
26 | -5.1178 | -2.1653 | 5.1197 | 2.1514 | 0.0019153 | -0.01396 | 0.16073 | 0.16056 | 0.16073 | 0.99806 | -0.084613 | 0.99845 | -0.082038 | 25.1928
27 | 4.9627 | 2.0915 | -4.9618 | -2.0893 | 0.00088497 | 0.0022391 | 0.15577 | 0.15577 | 0.15577 | 0.99806 | -0.084613 | 0.99774 | -0.10429 | 24.1501
28 | 6.4326 | 3.0297 | -6.4315 | -3.0342 | 0.0010704 | -0.0045292 | 0.20558 | 0.20564 | 0.20564 | 0.99845 | -0.082038 | 0.99828 | -0.082753 | 32.2319
29 | -11.5523 | -5.1811 | 11.554 | 5.1795 | 0.0016738 | -0.0015902 | 0.36606 | 0.36603 | 0.36606 | 0.99845 | -0.082038 | 0.9986 | -0.081245 | 57.3756
30 | 4.8349 | 2.0278 | -4.8344 | -2.0265 | 0.00051032 | 0.0012868 | 0.15169 | 0.15169 | 0.15169 | 0.99774 | -0.10429 | 0.99755 | -0.11597 | 23.5186
31 | 4.8344 | 2.0265 | -4.8337 | -2.0319 | 0.00065394 | -0.0053787 | 0.15169 | 0.15176 | 0.15176 | 0.99755 | -0.11597 | 0.9974 | -0.11691 | 23.7867
32 | 1.3684 | 0.65891 | -1.3683 | -0.65956 | 7.288e-05 | -0.00064932 | 0.043956 | 0.043965 | 0.043965 | 0.9974 | -0.11691 | 0.99736 | -0.11645 | 19.984
33 | 3.4654 | 1.373 | -3.465 | -1.3803 | 0.00043443 | -0.0072994 | 0.10788 | 0.10796 | 0.10796 | 0.9974 | -0.11691 | 0.99727 | -0.11794 | 16.9221
34 | 0.16419 | 0.079432 | -0.16418 | -0.079518 | 3.6791e-06 | -8.563e-05 | 0.0052796 | 0.0052807 | 0.0052807 | 0.99727 | -0.11794 | 0.99725 | -0.11809 | 2.5146
35 | 3.3008 | 1.3008 | -3.3005 | -1.3003 | 0.00023991 | 0.00055754 | 0.1027 | 0.1027 | 0.1027 | 0.99727 | -0.11794 | 0.99714 | -0.12621 | 15.9223
36 | 3.1953 | 1.2493 | -3.1951 | -1.2522 | 0.00014612 | -0.0029113 | 0.099322 | 0.099354 | 0.099354 | 0.99714 | -0.12621 | 0.99709 | -0.1266 | 15.5727
37 | 0.17036 | 0.082092 | -0.17036 | -0.08251 | 7.0521e-07 | -0.00041814 | 0.0054736 | 0.0054789 | 0.0054789 | 0.99736 | -0.11645 | 0.99735 | -0.11642 | 2.4904
38 | 1.0955 | 0.52788 | -1.0955 | -0.52787 | 5.9277e-05 | 5.2418e-06 | 0.035198 | 0.035198 | 0.035198 | 0.99736 | -0.11645 | 0.9973 | -0.11682 | 16.7611
39 | 0.16321 | 0.078578 | -0.16321 | -0.079047 | 7.2261e-07 | -0.00046864 | 0.0052382 | 0.0052441 | 0.0052441 | 0.99828 | -0.082753 | 0.99828 | -0.082715 | 2.3837
40 | 6.2683 | 2.9557 | -6.2658 | -2.9492 | 0.0024791 | 0.0064285 | 0.2004 | 0.2004 | 0.2004 | 0.99828 | -0.082753 | 0.99755 | -0.12389 | 31.0704
41 | -11.6687 | -5.2351 | 11.6776 | 5.2587 | 0.008884 | 0.023639 | 0.36971 | 0.36971 | 0.36971 | 0.9986 | -0.081245 | 1 | 0 | 57.3195
42 | 3.1951 | 1.2522 | -3.1951 | -1.2531 | 4.4983e-05 | -0.0008958 | 0.099354 | 0.099364 | 0.099364 | 0.99709 | -0.1266 | 0.99708 | -0.12672 | 15.5743
43 | 3.1302 | 1.2217 | -3.1299 | -1.2209 | 0.00037961 | 0.00086644 | 0.097285 | 0.097287 | 0.097287 | 0.99708 | -0.12672 | 0.99686 | -0.14059 | 15.0832
44 | 3.1299 | 1.2209 | -3.1298 | -1.2224 | 7.5187e-05 | -0.0015625 | 0.097287 | 0.097304 | 0.097304 | 0.99686 | -0.14059 | 0.99684 | -0.14079 | 15.2514
45 | 0.096228 | 0.046506 | -0.096227 | -0.046605 | 1.4334e-06 | -9.8968e-05 | 0.0030929 | 0.0030941 | 0.0030941 | 0.99755 | -0.12389 | 0.99753 | -0.12399 | 1.4734
46 | 6.1696 | 2.9027 | -6.1693 | -2.9038 | 0.00023253 | -0.0010775 | 0.19731 | 0.19733 | 0.19733 | 0.99755 | -0.12389 | 0.99751 | -0.12406 | 30.9289
47 | 6.06 | 2.8508 | -6.0596 | -2.8528 | 0.00041246 | -0.001989 | 0.19381 | 0.19384 | 0.19384 | 0.99751 | -0.12406 | 0.99744 | -0.12435 | 30.382
48 | 1.0955 | 0.52787 | -1.0955 | -0.52803 | 1.109e-05 | -0.00015593 | 0.035198 | 0.0352 | 0.0352 | 0.9973 | -0.11682 | 0.99729 | -0.11673 | 16.0002
49 | 4.5082 | 2.048 | -4.5078 | -2.0512 | 0.00034286 | -0.0032179 | 0.14294 | 0.14298 | 0.14298 | 1 | 0 | 0.99992 | -0.00039166 | 22.4106
50 | 6.0596 | 2.8528 | -6.0584 | -2.8586 | 0.0011921 | -0.005743 | 0.19384 | 0.19392 | 0.19392 | 0.99744 | -0.12435 | 0.99723 | -0.1252 | 30.3945
51 | 6.0584 | 2.8586 | -6.0581 | -2.8597 | 0.00024597 | -0.0011841 | 0.19392 | 0.19393 | 0.19393 | 0.99723 | -0.1252 | 0.99719 | -0.12537 | 30.397
52 | 5.9797 | 2.8218 | -5.9793 | -2.8238 | 0.00041687 | -0.0020654 | 0.19141 | 0.19144 | 0.19144 | 0.99719 | -0.12537 | 0.99712 | -0.12567 | 30.0062
53 | 5.9793 | 2.8238 | -5.9772 | -2.8264 | 0.0021172 | -0.0025384 | 0.19144 | 0.19149 | 0.19149 | 0.99712 | -0.12567 | 0.99673 | -0.12988 | 52.8978
54 | -0.11544 | -0.055909 | 0.11544 | 0.054387 | 1.1851e-06 | -0.0015223 | 0.0037216 | 0.0037025 | 0.0037216 | 0.99492 | 0.0043344 | 0.99493 | 0.0042476 | 1.6916
55 | -0.11544 | -0.054387 | 0.11544 | 0.047878 | 4.9347e-06 | -0.0065088 | 0.0037025 | 0.0036261 | 0.0037025 | 0.99493 | 0.0042476 | 0.99497 | 0.0039481 | 1.683
56 | -0.11544 | -0.047878 | 0.11545 | 0.045495 | 1.7572e-06 | -0.002383 | 0.0036261 | 0.0036001 | 0.0036261 | 0.99497 | 0.0039481 | 0.99498 | 0.0038673 | 1.6482
57 | 4.5078 | 2.0512 | -4.5076 | -2.0537 | 0.00026546 | -0.0024898 | 0.14298 | 0.14301 | 0.14301 | 0.99992 | -0.00039166 | 0.99986 | -0.00069292 | 22.4156
58 | 4.5076 | 2.0537 | -4.5071 | -2.0581 | 0.00047134 | -0.0044171 | 0.14301 | 0.14307 | 0.14307 | 0.99986 | -0.00069292 | 0.99975 | -0.0012235 | 22.4243
59 | 2.9456 | 1.3453 | -2.945 | -1.3464 | 0.00059509 | -0.0010167 | 0.093952 | 0.093967 | 0.093967 | 0.99498 | 0.0038673 | 0.9948 | 0.0054027 | 42.7122
60 | -3.1935 | -1.455 | 3.1991 | 1.4581 | 0.0056271 | 0.0031639 | 0.10182 | 0.10181 | 0.10182 | 0.99498 | 0.0038673 | 0.99685 | 0.018122 | 48.4834
61 | 4.386 | 1.9994 | -4.3859 | -2.0001 | 6.7411e-05 | -0.00066923 | 0.13918 | 0.13919 | 0.13919 | 0.99975 | -0.0012235 | 0.99973 | -0.0013017 | 21.8168
62 | 2.945 | 1.3464 | -2.9397 | -1.3554 | 0.0053394 | -0.009086 | 0.093967 | 0.094096 | 0.094096 | 0.9948 | 0.0054027 | 0.9931 | 0.019357 | 42.7709
63 | 0.059594 | 0.02832 | -0.059594 | -0.028863 | 1.1186e-07 | -0.00054253 | 0.0019107 | 0.0019175 | 0.0019175 | 0.99685 | 0.018122 | 0.99685 | 0.018138 | 0.8716
64 | -3.2587 | -1.4865 | 3.2607 | 1.4837 | 0.0020082 | -0.002725 | 0.10372 | 0.10368 | 0.10372 | 0.99685 | 0.018122 | 0.99743 | 0.013475 | 47.1461
65 | 4.3859 | 2.0001 | -4.3852 | -2.0022 | 0.0007213 | -0.0021177 | 0.13919 | 0.13922 | 0.13922 | 0.99973 | -0.0013017 | 0.99955 | -0.0034107 | 38.4594
66 | 3.3582 | 1.5257 | -3.3579 | -1.5261 | 0.00033408 | -0.00042416 | 0.10667 | 0.10667 | 0.10667 | 0.99826 | 0.0068069 | 0.99817 | 0.0075523 | 48.487
67 | -3.4409 | -1.5658 | 3.4415 | 1.5651 | 0.00054641 | -0.00065296 | 0.10932 | 0.10931 | 0.10932 | 0.99826 | 0.0068069 | 0.99841 | 0.0056138 | 49.6918
68 | 3.3579 | 1.5261 | -3.3552 | -1.5295 | 0.0026421 | -0.0033488 | 0.10667 | 0.10672 | 0.10672 | 0.99817 | 0.0075523 | 0.99743 | 0.013475 | 48.5095
69 | 0.137 | 0.057982 | -0.13699 | -0.066261 | 8.7876e-06 | -0.0082786 | 0.0043013 | 0.0044002 | 0.0044002 | 0.99841 | 0.0056138 | 0.99835 | 0.0060919 | 2.0001
70 | -3.5785 | -1.6231 | 3.5828 | 1.6184 | 0.0043558 | -0.0047348 | 0.11361 | 0.11354 | 0.11361 | 0.99841 | 0.0056138 | 0.99955 | -0.0034107 | 51.6418
71 | 0.094558 | 0.045744 | -0.094557 | -0.045796 | 7.3343e-07 | -5.2427e-05 | 0.0030401 | 0.0030408 | 0.0030408 | 0.99743 | 0.013475 | 0.99742 | 0.013424 | 1.448
72 | 0.13699 | 0.066261 | -0.13699 | -0.066347 | 2.5315e-06 | -8.571e-05 | 0.0044002 | 0.0044013 | 0.0044013 | 0.99835 | 0.0060919 | 0.99833 | 0.0059698 | 2.0958
73 | 0.65964 | 0.3172 | -0.65963 | -0.31766 | 1.1458e-05 | -0.00045467 | 0.021139 | 0.021145 | 0.021145 | 0.99955 | -0.0034107 | 0.99954 | -0.0032615 | 9.6112
74 | 0.14272 | 0.066652 | -0.14272 | -0.068734 | 2.4251e-06 | -0.0020815 | 0.0045491 | 0.0045749 | 0.0045749 | 0.99955 | -0.0034107 | 0.99954 | -0.0032694 | 2.0795
75 | 0.14272 | 0.068734 | -0.14272 | -0.06912 | 4.5298e-07 | -0.00038618 | 0.0045749 | 0.0045797 | 0.0045797 | 0.99954 | -0.0032694 | 0.99953 | -0.003242 | 2.0817
76 | 0.46031 | 0.22112 | -0.46031 | -0.22138 | 3.0799e-06 | -0.00025204 | 0.014748 | 0.014752 | 0.014752 | 0.99954 | -0.0032615 | 0.99953 | -0.0032042 | 6.7053
77 | 0.32849 | 0.15754 | -0.32849 | -0.15888 | 8.3193e-06 | -0.0013381 | 0.010522 | 0.010539 | 0.010539 | 0.99953 | -0.0032042 | 0.99951 | -0.0029863 | 4.7903
78 | -0.12891 | -0.062434 | 0.12891 | 0.062338 | 2.5901e-06 | -9.5737e-05 | 0.0041785 | 0.0041773 | 0.0041785 | 0.98954 | -0.0070799 | 0.98956 | -0.006947 | 1.9898
79 | -0.12891 | -0.062338 | 0.12891 | 0.061607 | 7.2756e-07 | -0.00073164 | 0.0041773 | 0.004168 | 0.0041773 | 0.98956 | -0.006947 | 0.98957 | -0.0069954 | 1.8988
80 | 0.14192 | 0.066095 | -0.14192 | -0.068734 | 3.1669e-06 | -0.0026391 | 0.004567 | 0.0046001 | 0.0046001 | 0.98957 | -0.0069954 | 0.98955 | -0.0068093 | 2.0909
81 | 2.5112 | 1.1508 | -2.5076 | -1.1595 | 0.0036208 | -0.0086643 | 0.080581 | 0.0807 | 0.0807 | 0.98957 | -0.0069954 | 0.98823 | 0.0041719 | 36.6819
82 | -2.782 | -1.2785 | 2.788 | 1.2817 | 0.0059645 | 0.0032442 | 0.089316 | 0.08931 | 0.089316 | 0.98957 | -0.0069954 | 0.99183 | 0.0098938 | 42.5313
83 | 2.5076 | 1.1595 | -2.5071 | -1.1605 | 0.00044735 | -0.0010667 | 0.0807 | 0.080715 | 0.080715 | 0.98823 | 0.0041719 | 0.98807 | 0.0055697 | 36.6886
84 | -2.9361 | -1.3535 | 2.9397 | 1.3554 | 0.0035587 | 0.0019638 | 0.094099 | 0.094096 | 0.094099 | 0.99183 | 0.0098938 | 0.9931 | 0.019357 | 44.8092
85 | 2.4028 | 1.11 | -2.4026 | -1.1105 | 0.00019994 | -0.0005244 | 0.077329 | 0.077336 | 0.077336 | 0.98807 | 0.0055697 | 0.98799 | 0.0062198 | 35.1527
86 | 2.1936 | 1.0093 | -2.1934 | -1.0098 | 0.00016032 | -0.00051463 | 0.070552 | 0.070559 | 0.070559 | 0.98799 | 0.0062198 | 0.98792 | 0.0067852 | 32.0722
87 | -0.10132 | -0.04907 | 0.10132 | 0.048979 | 1.5254e-06 | -9.0866e-05 | 0.0032931 | 0.0032919 | 0.0032931 | 0.98684 | 0.008733 | 0.98686 | 0.0088326 | 1.5681
88 | 0.093753 | 0.04267 | -0.093753 | -0.043468 | 4.1734e-07 | -0.00079794 | 0.0030132 | 0.0030229 | 0.0030229 | 0.98686 | 0.0088326 | 0.98685 | 0.0088669 | 1.374
89 | -0.19507 | -0.091649 | 0.19508 | 0.086565 | 1.1496e-05 | -0.0050848 | 0.0063047 | 0.0062428 | 0.0063047 | 0.98686 | 0.0088326 | 0.98691 | 0.0083852 | 2.8658
90 | 0.093753 | 0.043468 | -0.093752 | -0.045406 | 1.0252e-06 | -0.0019383 | 0.0030229 | 0.0030472 | 0.0030472 | 0.98685 | 0.0088669 | 0.98684 | 0.0089576 | 1.3851
91 | -0.30982 | -0.14108 | 0.30983 | 0.13981 | 7.2394e-06 | -0.0012717 | 0.0099577 | 0.0099423 | 0.0099577 | 0.98691 | 0.0083852 | 0.98693 | 0.0082112 | 4.5262
92 | 0.11474 | 0.054517 | -0.11474 | -0.055569 | 8.3725e-07 | -0.0010523 | 0.0037157 | 0.003729 | 0.003729 | 0.98691 | 0.0083852 | 0.98691 | 0.0084474 | 1.695
93 | 0.85343 | 0.39553 | -0.85342 | -0.39583 | 1.3043e-05 | -0.0002962 | 0.027514 | 0.027518 | 0.027518 | 0.98689 | 0.0076823 | 0.98688 | 0.0078027 | 12.5082
94 | -0.9864 | -0.45993 | 0.98645 | 0.45993 | 5.3812e-05 | -9.4583e-07 | 0.031835 | 0.031835 | 0.031835 | 0.98689 | 0.0076823 | 0.98695 | 0.0080934 | 15.1597
95 | 0.85342 | 0.39583 | -0.85335 | -0.39729 | 6.4578e-05 | -0.0014652 | 0.027518 | 0.027536 | 0.027536 | 0.98688 | 0.0078027 | 0.98681 | 0.008402 | 12.5165
96 | -0.98645 | -0.45993 | 0.98646 | 0.45983 | 5.9179e-06 | -9.9975e-05 | 0.031835 | 0.031834 | 0.031835 | 0.98695 | 0.0080934 | 0.98695 | 0.0080455 | 14.4704
97 | -0.30983 | -0.13981 | 0.30983 | 0.13931 | 2.8371e-06 | -0.00049945 | 0.0099423 | 0.0099363 | 0.0099423 | 0.98693 | 0.0082112 | 0.98694 | 0.0081441 | 4.5192
98 | -0.39437 | -0.18025 | 0.39437 | 0.1797 | 5.077e-06 | -0.00054864 | 0.012683 | 0.012676 | 0.012683 | 0.98694 | 0.0081441 | 0.98695 | 0.0080466 | 5.7649
99 | -0.059291 | -0.028716 | 0.059292 | 0.028583 | 7.5776e-07 | -0.00013273 | 0.0019273 | 0.0019256 | 0.0019273 | 0.98674 | 0.0075139 | 0.98676 | 0.0075989 | 0.91777
100 | -0.059292 | -0.028583 | 0.059292 | 0.02664 | 4.0859e-07 | -0.0019433 | 0.0019256 | 0.0019016 | 0.0019256 | 0.98676 | 0.0075989 | 0.98676 | 0.0075441 | 0.87528
101 | -0.059292 | -0.02664 | 0.059292 | 0.025085 | 3.1973e-07 | -0.0015547 | 0.0019016 | 0.0018834 | 0.0019016 | 0.98676 | 0.0075441 | 0.98677 | 0.0075078 | 0.86437
102 | -0.1664 | -0.076822 | 0.1664 | 0.076649 | 2.8554e-07 | -0.00017299 | 0.0053615 | 0.0053594 | 0.0053615 | 0.98681 | 0.0077937 | 0.98681 | 0.0077803 | 2.4371
103 | 0.1664 | 0.076822 | -0.16639 | -0.076957 | 6.132e-06 | -0.00013529 | 0.0053615 | 0.0053632 | 0.0053632 | 0.98681 | 0.0077937 | 0.98677 | 0.0075078 | 2.5539
104 | -0.1664 | -0.076649 | 0.16641 | 0.076558 | 4.1033e-06 | -9.0662e-05 | 0.0053594 | 0.0053583 | 0.0053594 | 0.98681 | 0.0077803 | 0.98683 | 0.0079739 | 2.5521
105 | -0.13609 | -0.065911 | 0.13609 | 0.065368 | 6.0896e-07 | -0.00054222 | 0.0044244 | 0.0044175 | 0.0044244 | 0.98659 | 0.0097649 | 0.98659 | 0.0097263 | 2.0111
106 | -0.29255 | -0.14114 | 0.29256 | 0.14108 | 1.0154e-05 | -6.6965e-05 | 0.009504 | 0.0095031 | 0.009504 | 0.98659 | 0.0097263 | 0.98663 | 0.0099586 | 4.5257
107 | 0.56063 | 0.25995 | -0.56059 | -0.26184 | 3.5648e-05 | -0.0018853 | 0.018081 | 0.018104 | 0.018104 | 0.98663 | 0.0099586 | 0.98657 | 0.010464 | 8.2292
108 | -0.85319 | -0.40103 | 0.85335 | 0.39729 | 0.00016507 | -0.0037353 | 0.027583 | 0.027536 | 0.027583 | 0.98663 | 0.0099586 | 0.98681 | 0.008402 | 12.5378
109 | 0.21252 | 0.097515 | -0.21251 | -0.10184 | 1.1719e-05 | -0.0043207 | 0.0068418 | 0.0068955 | 0.0068955 | 0.98657 | 0.010464 | 0.98652 | 0.01091 | 3.1343
110 | 0.34807 | 0.16432 | -0.34805 | -0.16724 | 2.1344e-05 | -0.002913 | 0.011263 | 0.011299 | 0.011299 | 0.98657 | 0.010464 | 0.98651 | 0.010978 | 5.1361
111 | -1.1015 | -0.51555 | 1.1015 | 0.51537 | 1.3484e-05 | -0.00018166 | 0.035572 | 0.03557 | 0.035572 | 0.98695 | 0.0080455 | 0.98697 | 0.0079469 | 16.1692
112 | 0.39438 | 0.17914 | -0.39437 | -0.1797 | 5.2287e-06 | -0.00056565 | 0.012669 | 0.012676 | 0.012676 | 0.98697 | 0.0079469 | 0.98695 | 0.0080466 | 5.7619
113 | -1.4959 | -0.69451 | 1.4961 | 0.69336 | 0.00016008 | -0.0011515 | 0.048239 | 0.048224 | 0.048239 | 0.98697 | 0.0079469 | 0.98707 | 0.0071031 | 21.9267
114 | -1.5973 | -0.74239 | 1.5974 | 0.74171 | 0.00010958 | -0.00068721 | 0.051513 | 0.051505 | 0.051513 | 0.98707 | 0.0071031 | 0.98713 | 0.0065603 | 23.4152
115 | 0.34573 | 0.15041 | -0.34567 | -0.15846 | 5.6836e-05 | -0.0080596 | 0.011026 | 0.011122 | 0.011122 | 0.98713 | 0.0065603 | 0.98698 | 0.007739 | 5.0555
116 | -1.9431 | -0.89211 | 1.9439 | 0.89248 | 0.00079482 | 0.00036506 | 0.062528 | 0.062526 | 0.062528 | 0.98713 | 0.0065603 | 0.98756 | 0.0097971 | 29.7751
117 | 0.21251 | 0.10184 | -0.21251 | -0.10258 | 2.0335e-06 | -0.00074278 | 0.0068955 | 0.006905 | 0.006905 | 0.98652 | 0.01091 | 0.98651 | 0.010993 | 3.1386
118 | 0.25521 | 0.12227 | -0.25518 | -0.12257 | 3.4093e-05 | -0.00030265 | 0.0082808 | 0.0082849 | 0.0082849 | 0.98651 | 0.010978 | 0.98638 | 0.010066 | 3.9452
119 | 0.087927 | 0.042242 | -0.087922 | -0.042583 | 4.2956e-06 | -0.00034055 | 0.0028545 | 0.0028588 | 0.0028588 | 0.98651 | 0.010993 | 0.98646 | 0.010666 | 1.3613
120 | -1.9439 | -0.89248 | 1.9445 | 0.89029 | 0.00052373 | -0.002183 | 0.062526 | 0.062498 | 0.062526 | 0.98756 | 0.0097971 | 0.98781 | 0.0077329 | 28.4209
121 | -2.0659 | -0.9491 | 2.066 | 0.94885 | 6.8168e-05 | -0.0002493 | 0.066439 | 0.066436 | 0.066439 | 0.98781 | 0.0077329 | 0.98784 | 0.0074789 | 30.1998
122 | 0.10157 | 0.048176 | -0.10155 | -0.049182 | 1.695e-05 | -0.0010062 | 0.0032899 | 0.0033027 | 0.0033027 | 0.98638 | 0.010066 | 0.9862 | 0.0089226 | 1.5727
123 | 0.28299 | 0.12288 | -0.28294 | -0.13158 | 4.0885e-05 | -0.0087008 | 0.0090066 | 0.0091109 | 0.0091109 | 0.98883 | -0.49329 | 0.9887 | -0.49224 | 4.1413
124 | 0.12314 | 0.05425 | -0.12314 | -0.058361 | 3.6761e-06 | -0.0041108 | 0.0039288 | 0.0039787 | 0.0039787 | 0.9887 | -0.49224 | 0.98867 | -0.49201 | 1.8085
125 | 0.15981 | 0.07733 | -0.1598 | -0.077396 | 2.8044e-06 | -6.6592e-05 | 0.0051835 | 0.0051844 | 0.0051844 | 0.9887 | -0.49224 | 0.98868 | -0.49235 | 2.4688
126 | 0.12314 | 0.058361 | -0.12313 | -0.059636 | 1.1597e-06 | -0.0012752 | 0.0039787 | 0.0039948 | 0.0039948 | 0.98867 | -0.49201 | 0.98866 | -0.49193 | 1.8158
127 | -0.12308 | -0.059612 | 0.12309 | 0.059539 | 1.7835e-06 | -7.346e-05 | 0.0039756 | 0.0039747 | 0.0039756 | 0.99303 | -0.099089 | 0.99304 | -0.098994 | 1.8932
128 | -0.12309 | -0.059539 | 0.12309 | 0.059197 | 3.0559e-07 | -0.00034145 | 0.0039747 | 0.0039704 | 0.0039747 | 0.99304 | -0.098994 | 0.99305 | -0.099015 | 1.8067
129 | -0.43206 | -0.20884 | 0.43207 | 0.20813 | 7.8732e-06 | -0.00071167 | 0.01395 | 0.013941 | 0.01395 | 0.99305 | -0.099015 | 0.99306 | -0.099172 | 6.341
130 | -0.2687 | -0.13014 | 0.26871 | 0.12811 | 8.6335e-06 | -0.0020258 | 0.0086781 | 0.0086526 | 0.0086781 | 0.99315 | -0.098134 | 0.99318 | -0.098409 | 3.9446
131 | -0.82271 | -0.39514 | 0.82279 | 0.3932 | 7.8213e-05 | -0.0019396 | 0.026528 | 0.026503 | 0.026528 | 0.99318 | -0.098409 | 0.99327 | -0.099217 | 12.058
132 | 0.43212 | 0.20799 | -0.43207 | -0.20813 | 4.8967e-05 | -0.00013585 | 0.013939 | 0.013941 | 0.013941 | 0.99318 | -0.098409 | 0.99306 | -0.099172 | 6.6387
133 | -0.82279 | -0.3932 | 0.82284 | 0.39176 | 5.7901e-05 | -0.0014384 | 0.026503 | 0.026485 | 0.026503 | 0.99327 | -0.099217 | 0.99334 | -0.09981 | 12.0468
134 | 0.34567 | 0.15846 | -0.34566 | -0.1606 | 1.5235e-05 | -0.0021361 | 0.011122 | 0.011148 | 0.011148 | 0.98698 | 0.007739 | 0.98693 | 0.0080823 | 5.0674
135 | 0.26352 | 0.12082 | -0.26351 | -0.12345 | 1.0912e-05 | -0.0026304 | 0.0084794 | 0.0085118 | 0.0085118 | 0.98693 | 0.0080823 | 0.9869 | 0.0084082 | 3.869
136 | 0.26351 | 0.12345 | -0.26349 | -0.12358 | 1.5456e-05 | -0.0001295 | 0.0085118 | 0.0085136 | 0.0085136 | 0.9869 | 0.0084082 | 0.98683 | 0.0079739 | 4.0541
137 | -2.066 | -0.94885 | 2.0661 | 0.94817 | 0.0001864 | -0.0006819 | 0.066436 | 0.066427 | 0.066436 | 0.98784 | 0.0074789 | 0.98792 | 0.0067852 | 30.1983
138 | 1.0101 | 0.48817 | -1.0101 | -0.48919 | 6.1735e-05 | -0.0010221 | 0.032477 | 0.03249 | 0.03249 | 0.9972 | -0.11593 | 0.99715 | -0.1154 | 14.7684
139 | -1.0954 | -0.52945 | 1.0955 | 0.52803 | 0.00010135 | -0.0014241 | 0.035219 | 0.0352 | 0.035219 | 0.9972 | -0.11593 | 0.99729 | -0.11673 | 16.0085
140 | 0.42247 | 0.17902 | -0.42245 | -0.18017 | 1.1594e-05 | -0.0011562 | 0.013305 | 0.013318 | 0.013318 | 0.99551 | -0.11951 | 0.99548 | -0.11934 | 6.0537
141 | 2.5376 | 1.1996 | -2.5316 | -1.2137 | 0.0059569 | -0.014098 | 0.081391 | 0.081589 | 0.081589 | 0.99551 | -0.11951 | 0.99334 | -0.09981 | 37.0861
142 | -2.96 | -1.3786 | 2.9639 | 1.372 | 0.0038884 | -0.0065509 | 0.094687 | 0.094593 | 0.094687 | 0.99551 | -0.11951 | 0.99673 | -0.12988 | 43.0395
143 | 0.30787 | 0.12468 | -0.30787 | -0.12587 | 6.2327e-06 | -0.0011872 | 0.0096322 | 0.0096452 | 0.0096452 | 0.99548 | -0.11934 | 0.99546 | -0.11923 | 4.3842
144 | 1.7088 | 0.82192 | -1.7078 | -0.82713 | 0.00094792 | -0.005218 | 0.055105 | 0.055174 | 0.055174 | 0.99334 | -0.09981 | 0.99282 | -0.095013 | 25.0792
145 | 0.091003 | 0.042397 | -0.091002 | -0.044074 | 8.0388e-07 | -0.0016773 | 0.0029076 | 0.0029285 | 0.0029285 | 0.99673 | -0.12988 | 0.99673 | -0.12981 | 1.3311
146 | 2.9223 | 1.4119 | -2.9212 | -1.4138 | 0.0010889 | -0.0018654 | 0.093996 | 0.094023 | 0.094023 | 0.99673 | -0.12988 | 0.99639 | -0.12665 | 42.738
147 | 0.30787 | 0.12587 | -0.30784 | -0.13131 | 2.8805e-05 | -0.0054444 | 0.0096452 | 0.0097061 | 0.0097061 | 0.99546 | -0.11923 | 0.99537 | -0.11867 | 4.4119
148 | 2.9212 | 1.4138 | -2.9207 | -1.4146 | 0.0004457 | -0.00076274 | 0.094023 | 0.094035 | 0.094035 | 0.99639 | -0.12665 | 0.99625 | -0.12532 | 42.7431
149 | -0.16292 | -0.078907 | 0.16293 | 0.078822 | 3.6349e-06 | -8.5283e-05 | 0.0052501 | 0.005249 | 0.0052501 | 0.99535 | -0.11882 | 0.99537 | -0.11867 | 2.5001
150 | 0.14491 | 0.052489 | -0.14489 | -0.068208 | 1.8396e-05 | -0.01572 | 0.0044699 | 0.0046451 | 0.0046451 | 0.99537 | -0.11867 | 0.99525 | -0.11793 | 2.1114
151 | 0.14489 | 0.068208 | -0.14489 | -0.070174 | 2.4078e-06 | -0.0019658 | 0.0046451 | 0.0046696 | 0.0046696 | 0.99525 | -0.11793 | 0.99524 | -0.11779 | 2.1226
152 | -0.32849 | -0.15909 | 0.32849 | 0.15888 | 1.353e-06 | -0.00021721 | 0.010541 | 0.010539 | 0.010541 | 0.9995 | -0.0029505 | 0.99951 | -0.0029863 | 4.7915
153 | 2.9789 | 1.1493 | -2.9765 | -1.1439 | 0.002424 | 0.0054291 | 0.092465 | 0.092476 | 0.092476 | 0.99684 | -0.14079 | 0.9954 | -0.23438 | 14.3374
154 | 2.8667 | 1.0908 | -2.8666 | -1.0904 | 0.00014954 | 0.00032962 | 0.088953 | 0.088954 | 0.088954 | 0.9954 | -0.23438 | 0.99531 | -0.24041 | 13.7913
155 | 0.058704 | 0.027227 | -0.058698 | -0.028429 | 6.4507e-06 | -0.0012018 | 0.0018768 | 0.0018918 | 0.0018918 | 0.99531 | -0.24041 | 0.99519 | -0.24119 | 0.90087
156 | 2.8079 | 1.0632 | -2.8053 | -1.1302 | 0.0025989 | -0.066943 | 0.087082 | 0.087804 | 0.087804 | 0.99531 | -0.24041 | 0.99434 | -0.24834 | 13.7624
157 | 2.7129 | 1.0873 | -2.7121 | -1.1083 | 0.00076894 | -0.020974 | 0.084851 | 0.085084 | 0.085084 | 0.99434 | -0.24834 | 0.99404 | -0.25055 | 13.3361
158 | 0.092396 | 0.042836 | -0.092395 | -0.044749 | 9.5361e-07 | -0.0019133 | 0.0029567 | 0.0029805 | 0.0029805 | 0.99434 | -0.24834 | 0.99433 | -0.24825 | 1.3548
159 | -1.8603 | -0.8143 | 1.8605 | 0.80526 | 0.00015846 | -0.0090384 | 0.059045 | 0.058939 | 0.059045 | 0.99285 | -0.27639 | 0.99294 | -0.27587 | 9.2547
160 | -1.8605 | -0.80526 | 1.8605 | 0.8037 | 2.7284e-05 | -0.0015597 | 0.058939 | 0.058921 | 0.058939 | 0.99294 | -0.27587 | 0.99296 | -0.27577 | 9.2381
161 | -2.0026 | -0.87253 | 2.0027 | 0.87129 | 2.5275e-05 | -0.0012424 | 0.063508 | 0.063493 | 0.063508 | 0.99296 | -0.27577 | 0.99297 | -0.2757 | 9.9542
162 | -2.0027 | -0.87129 | 2.0041 | 0.80243 | 0.0013819 | -0.068864 | 0.063493 | 0.062713 | 0.063493 | 0.99297 | -0.2757 | 0.99369 | -0.27081 | 9.9519
163 | -2.0041 | -0.80243 | 2.0041 | 0.79973 | 5.3428e-05 | -0.0026989 | 0.062713 | 0.062683 | 0.062713 | 0.99369 | -0.27081 | 0.99372 | -0.27059 | 9.8296
164 | 0.56242 | 0.23723 | -0.56241 | -0.23805 | 1.4591e-05 | -0.00081472 | 0.017732 | 0.017742 | 0.017742 | 0.99372 | -0.27059 | 0.99369 | -0.27043 | 8.0644
165 | -2.7116 | -1.1072 | 2.7121 | 1.1083 | 0.00048533 | 0.0010487 | 0.085087 | 0.085084 | 0.085087 | 0.99372 | -0.27059 | 0.99404 | -0.25055 | 13.1918
166 | 0.56241 | 0.23805 | -0.56235 | -0.24129 | 5.8184e-05 | -0.00324 | 0.017742 | 0.017779 | 0.017779 | 0.99369 | -0.27043 | 0.9936 | -0.26978 | 8.0812
167 | -0.16102 | -0.053736 | 0.16104 | 0.053334 | 1.5129e-05 | -0.00040205 | 0.0049327 | 0.0049289 | 0.0049327 | 0.99344 | -0.27085 | 0.99354 | -0.26943 | 2.3489
168 | 0.16102 | 0.053736 | -0.16099 | -0.077151 | 3.3863e-05 | -0.023415 | 0.0049327 | 0.0051886 | 0.0051886 | 0.99344 | -0.27085 | 0.99324 | -0.26972 | 2.3584
169 | -0.30874 | -0.12398 | 0.30874 | 0.12381 | 8.8771e-07 | -0.00016748 | 0.0096668 | 0.0096649 | 0.0096668 | 0.99354 | -0.26943 | 0.99355 | -0.26945 | 4.394
170 | 0.1477 | 0.070646 | -0.1477 | -0.071535 | 1.1429e-06 | -0.00088914 | 0.0047571 | 0.0047683 | 0.0047683 | 0.99354 | -0.26943 | 0.99354 | -0.26936 | 2.1674
171 | 0.16099 | 0.077151 | -0.16099 | -0.07797 | 1.2541e-06 | -0.00081988 | 0.0051886 | 0.0051989 | 0.0051989 | 0.99324 | -0.26972 | 0.99323 | -0.26965 | 2.3631
172 | -0.47351 | -0.20361 | 0.47354 | 0.20165 | 2.5047e-05 | -0.0019673 | 0.014976 | 0.014953 | 0.014976 | 0.99355 | -0.26945 | 0.9936 | -0.26978 | 6.8073
173 | 0.088812 | 0.039638 | -0.08881 | -0.043013 | 1.5483e-06 | -0.0033746 | 0.0028256 | 0.002867 | 0.002867 | 0.9936 | -0.26978 | 0.99358 | -0.26964 | 1.3032

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 16.3027 | 7.367

## res_load
| p_mw | q_mvar
0 | 0.066705 | 0.032307
1 | 0.058987 | 0.028569
2 | 0.15033 | 0.072807
3 | 0.11218 | 0.054333
4 | 0.11401 | 0.055217
5 | 0.095749 | 0.046373
6 | 0.16958 | 0.082133
7 | 0.080435 | 0.038956
8 | 0.068685 | 0.033266
9 | 0.14028 | 0.067942
10 | 0.12691 | 0.061467
11 | 0.083497 | 0.04044
12 | 0.14514 | 0.070294
13 | 0.16175 | 0.078338
14 | 0.15511 | 0.075123
15 | 0.12692 | 0.06147
16 | 0.16418 | 0.079518
17 | 0.10527 | 0.050985
18 | 0.1024 | 0.049596
19 | 0.11475 | 0.055578
20 | 0.064815 | 0.031391
21 | 0.096227 | 0.046605
22 | 0.10936 | 0.052966
23 | 0.17036 | 0.08251
24 | 0.16321 | 0.079047
25 | 0.10295 | 0.04986
26 | 0.07841 | 0.037976
27 | 0.11544 | 0.055909
28 | 0.13242 | 0.064134
29 | 0.12111 | 0.058657
30 | 0.082713 | 0.04006
31 | 0.094557 | 0.045796
32 | 0.13699 | 0.066347
33 | 0.14272 | 0.06912
34 | 0.19932 | 0.096535
35 | 0.059594 | 0.028863
36 | 0.13181 | 0.063839
37 | 0.12891 | 0.062434
38 | 0.14192 | 0.068734
39 | 0.14813 | 0.071742
40 | 0.10433 | 0.050529
41 | 0.209 | 0.10122
42 | 0.10132 | 0.04907
43 | 0.13297 | 0.0644
44 | 0.093752 | 0.045406
45 | 0.11474 | 0.055569
46 | 0.084536 | 0.040943
47 | 0.059291 | 0.028716
48 | 0.1071 | 0.051872
49 | 0.13609 | 0.065911
50 | 0.15646 | 0.075776
51 | 0.11505 | 0.055721
52 | 0.10124 | 0.049035
53 | 0.092842 | 0.044966
54 | 0.12458 | 0.060336
55 | 0.12143 | 0.058809
56 | 0.15361 | 0.074397
57 | 0.087922 | 0.042583
58 | 0.1598 | 0.077396
59 | 0.12313 | 0.059636
60 | 0.12308 | 0.059612
61 | 0.30898 | 0.14964
62 | 0.2687 | 0.13014
63 | 0.12188 | 0.059028
64 | 0.082135 | 0.03978
65 | 0.097089 | 0.047023
66 | 0.12728 | 0.061644
67 | 0.085229 | 0.041278
68 | 1.0101 | 0.48919
69 | 0.11458 | 0.055494
70 | 1.7078 | 0.82713
71 | 0.091002 | 0.044074
72 | 0.16292 | 0.078907
73 | 0.14489 | 0.070174
74 | 0.32849 | 0.15909
75 | 0.15087 | 0.07307
76 | 0.10975 | 0.053152
77 | 0.058698 | 0.028429
78 | 2.9207 | 1.4146
79 | 0.14212 | 0.068831
80 | 0.14512 | 0.070283
81 | 0.092395 | 0.044749
82 | 0.1477 | 0.071535
83 | 0.16099 | 0.07797
84 | 0.16477 | 0.079802
85 | 0.08881 | 0.043013
86 | 0.10155 | 0.049182

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1