## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_159_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_159_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_159_0_node_1 | 20 | n |  | TRUE
3 | bus_MV_159_0_node_4 | 20 | n |  | TRUE
4 | bus_MV_159_0_node_3 | 20 | n |  | TRUE
5 | bus_MV_159_0_node_65 | 20 | n |  | TRUE
6 | bus_MV_159_0_node_8 | 20 | n |  | TRUE
7 | bus_MV_159_0_node_18 | 20 | n |  | TRUE
8 | bus_MV_159_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_159_0_node_6 | 20 | n |  | TRUE
10 | bus_MV_159_0_node_7 | 20 | n |  | TRUE
11 | bus_MV_159_0_node_9 | 20 | n |  | TRUE
12 | bus_MV_159_0_node_17 | 20 | n |  | TRUE
13 | bus_MV_159_0_node_10 | 20 | n |  | TRUE
14 | bus_MV_159_0_node_11 | 20 | n |  | TRUE
15 | bus_MV_159_0_node_14 | 20 | n |  | TRUE
16 | bus_MV_159_0_node_15 | 20 | n |  | TRUE
17 | bus_MV_159_0_node_12 | 20 | n |  | TRUE
18 | bus_MV_159_0_node_21 | 20 | n |  | TRUE
19 | bus_MV_159_0_node_23 | 20 | n |  | TRUE
20 | bus_MV_159_0_node_50 | 20 | n |  | TRUE
21 | bus_MV_159_0_node_16 | 20 | n |  | TRUE
22 | bus_MV_159_0_node_13 | 20 | n |  | TRUE
23 | bus_MV_159_0_node_19 | 20 | n |  | TRUE
24 | bus_MV_159_0_node_33 | 20 | n |  | TRUE
25 | bus_MV_159_0_node_51 | 20 | n |  | TRUE
26 | bus_MV_159_0_node_36 | 20 | n |  | TRUE
27 | bus_MV_159_0_node_37 | 20 | n |  | TRUE
28 | bus_MV_159_0_node_38 | 20 | n |  | TRUE
29 | bus_MV_159_0_node_57 | 20 | n |  | TRUE
30 | bus_MV_159_0_node_39 | 20 | n |  | TRUE
31 | bus_MV_159_0_node_41 | 20 | n |  | TRUE
32 | bus_MV_159_0_node_40 | 20 | n |  | TRUE
33 | bus_MV_159_0_node_44 | 20 | n |  | TRUE
34 | bus_MV_159_0_node_43 | 20 | n |  | TRUE
35 | bus_MV_159_0_node_46 | 20 | n |  | TRUE
36 | bus_MV_159_0_node_58 | 20 | n |  | TRUE
37 | bus_MV_159_0_node_42 | 20 | n |  | TRUE
38 | bus_MV_159_0_node_64 | 20 | n |  | TRUE
39 | bus_MV_159_0_node_45 | 20 | n |  | TRUE
40 | bus_MV_159_0_node_66 | 20 | n |  | TRUE
41 | bus_MV_159_0_node_63 | 20 | n |  | TRUE
42 | bus_MV_159_0_node_20 | 20 | n |  | TRUE
43 | bus_MV_159_0_node_22 | 20 | n |  | TRUE
44 | bus_MV_159_0_node_24 | 20 | n |  | TRUE
45 | bus_MV_159_0_node_25 | 20 | n |  | TRUE
46 | bus_MV_159_0_node_34 | 20 | n |  | TRUE
47 | bus_MV_159_0_node_29 | 20 | n |  | TRUE
48 | bus_MV_159_0_node_32 | 20 | n |  | TRUE
49 | bus_MV_159_0_node_28 | 20 | n |  | TRUE
50 | bus_MV_159_0_node_26 | 20 | n |  | TRUE
51 | bus_MV_159_0_node_27 | 20 | n |  | TRUE
52 | bus_MV_159_0_node_52 | 20 | n |  | TRUE
53 | bus_MV_159_0_node_53 | 20 | n |  | TRUE
54 | bus_MV_159_0_node_55 | 20 | n |  | TRUE
55 | bus_MV_159_0_node_54 | 20 | n |  | TRUE
56 | bus_MV_159_0_node_56 | 20 | n |  | TRUE
57 | bus_MV_159_0_node_60 | 20 | n |  | TRUE
58 | bus_MV_159_0_node_62 | 20 | n |  | TRUE
59 | bus_MV_159_0_node_59 | 20 | n |  | TRUE
60 | bus_MV_159_0_node_61 | 20 | n |  | TRUE
61 | bus_MV_159_0_node_49 | 20 | n |  | TRUE
62 | bus_HV_159_0_node_66 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_159_0_load_0 | 0 | 0.16135 | 0.078147 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_159_0_load_65 | 5 | 0.24228 | 0.11734 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_159_0_load_8 | 6 | 0.15715 | 0.07611 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_159_0_load_5 | 8 | 0.16403 | 0.079444 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_159_0_load_17 | 12 | 0.068262 | 0.033061 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_159_0_load_10 | 13 | 0.12465 | 0.060369 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_159_0_load_50 | 20 | 0.075749 | 0.036687 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_159_0_load_16 | 21 | 0.14819 | 0.071773 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_159_0_load_13 | 22 | 0.14905 | 0.072186 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_159_0_load_19 | 23 | 0.1622 | 0.078558 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_159_0_load_33 | 24 | 0.14904 | 0.072184 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_159_0_load_51 | 25 | 0.12785 | 0.061922 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_159_0_load_36 | 26 | 0.13163 | 0.063752 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_159_0_load_57 | 29 | 0.092979 | 0.045032 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_159_0_load_44 | 33 | 0.14562 | 0.070525 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_159_0_load_43 | 34 | 0.12056 | 0.058391 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_159_0_load_58 | 36 | 0.15338 | 0.074286 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_159_0_load_42 | 37 | 0.077314 | 0.037445 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_159_0_load_45 | 39 | 0.13325 | 0.064537 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_159_0_load_66 | 40 | 0.067593 | 0.032737 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_159_0_load_63 | 41 | 0.11971 | 0.05798 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_159_0_load_24 | 44 | 0.1288 | 0.062383 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_159_0_load_34 | 46 | 0.097732 | 0.047334 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_159_0_load_28 | 49 | 0.15525 | 0.07519 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_159_0_load_27 | 51 | 0.073524 | 0.03561 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_159_0_load_52 | 52 | 0.15735 | 0.076209 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_159_0_load_56 | 56 | 0.16206 | 0.078492 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_159_0_load_62 | 58 | 0.1423 | 0.068917 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_159_0_load_61 | 60 | 0.11142 | 0.053963 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_159_0_load_49 | 61 | 0.15171 | 0.073475 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 40 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_159_0_line_0 |  | 0 | 1 | 0.093037 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_159_0_line_1 |  | 0 | 2 | 0.1194 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_159_0_line_2 |  | 1 | 3 | 0.13477 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_159_0_line_3 |  | 2 | 4 | 0.081672 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_159_0_line_4 |  | 3 | 6 | 0.023602 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_159_0_line_5 |  | 4 | 5 | 0.015274 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_159_0_line_6 |  | 5 | 7 | 1.6569 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_159_0_line_7 |  | 6 | 10 | 0.056218 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_159_0_line_8 |  | 7 | 12 | 0.053409 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_159_0_line_9 |  | 8 | 9 | 0.063297 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_159_0_line_10 |  | 9 | 10 | 0.018104 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_159_0_line_11 |  | 10 | 11 | 0.10871 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_159_0_line_12 |  | 11 | 13 | 0.016942 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_159_0_line_13 |  | 13 | 14 | 0.062492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_159_0_line_14 |  | 14 | 15 | 0.24984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_159_0_line_15 |  | 14 | 16 | 0.21853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_159_0_line_16 |  | 14 | 17 | 0.096878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_159_0_line_17 |  | 15 | 18 | 0.59396 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_159_0_line_18 |  | 15 | 19 | 0.19925 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_159_0_line_19 |  | 15 | 20 | 0.00668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_159_0_line_20 |  | 16 | 21 | 0.025632 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_159_0_line_21 |  | 17 | 22 | 0.035933 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_159_0_line_22 |  | 18 | 23 | 0.089356 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_159_0_line_23 |  | 19 | 24 | 0.06203 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_159_0_line_24 |  | 19 | 25 | 0.10395 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_159_0_line_25 |  | 23 | 42 | 0.027158 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_159_0_line_26 |  | 24 | 46 | 0.19431 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_159_0_line_27 |  | 24 | 47 | 0.11007 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_159_0_line_28 |  | 24 | 48 | 0.62528 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_159_0_line_29 |  | 26 | 27 | 0.044063 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_159_0_line_30 |  | 26 | 28 | 0.068532 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_159_0_line_31 |  | 26 | 29 | 0.31294 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_159_0_line_32 |  | 27 | 30 | 0.21393 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_159_0_line_33 |  | 28 | 31 | 0.093957 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_159_0_line_34 |  | 30 | 32 | 0.10336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_159_0_line_35 |  | 30 | 33 | 0.024198 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_159_0_line_36 |  | 31 | 35 | 0.63559 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_159_0_line_37 |  | 31 | 36 | 0.055381 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_159_0_line_38 |  | 32 | 34 | 0.071731 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_159_0_line_39 |  | 33 | 38 | 2.3772 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_159_0_line_40 |  | 34 | 37 | 0.0088408 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_159_0_line_41 |  | 35 | 39 | 0.015425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_159_0_line_42 |  | 38 | 41 | 0.049074 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_159_0_line_43 |  | 39 | 40 | 2.2067 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_159_0_line_44 |  | 40 | 51 | 2.9204 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_159_0_line_45 |  | 40 | 52 | 7.2804 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_159_0_line_46 |  | 42 | 43 | 0.068917 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_159_0_line_47 |  | 43 | 44 | 0.044401 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_159_0_line_48 |  | 44 | 45 | 0.14089 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_159_0_line_49 |  | 45 | 50 | 0.03042 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_159_0_line_50 |  | 47 | 49 | 0.076055 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_159_0_line_51 |  | 48 | 61 | 0.0314 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_159_0_line_52 |  | 50 | 51 | 0.024613 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_159_0_line_53 |  | 52 | 53 | 0.039414 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_159_0_line_54 |  | 53 | 54 | 0.13887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_159_0_line_55 |  | 54 | 57 | 0.13585 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_159_0_line_56 |  | 54 | 58 | 0.037365 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_159_0_line_57 |  | 54 | 55 | 0.1345 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_159_0_line_58 |  | 55 | 56 | 0.009953 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_159_0_line_59 |  | 57 | 59 | 0.13025 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_159_0_line_60 |  | 59 | 60 | 0.030004 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_159_0_trafo_66 | 25 MVA 110/20 kV | 62 | 40 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2778455.0669 | 1144680.6518
1 | 2778540.3437 | 1144718.421
2 | 2778447.9915 | 1144561.4661
3 | 2778643.6387 | 1144632.1108
4 | 2778470.8218 | 1144526.4537
5 | 2778486.054 | 1144528.0725
6 | 2778659.1471 | 1144614.287
7 | 2778848.1062 | 1142911.2384
8 | 2778622.0193 | 1144560.0357
9 | 2778679.915 | 1144564.8343
10 | 2778696.3442 | 1144572.5058
11 | 2778757.0814 | 1144652.3122
12 | 2778799.6499 | 1142894.4981
13 | 2778761.0221 | 1144668.7886
14 | 2778777.8309 | 1144728.9755
15 | 2778831.0984 | 1144955.4633
16 | 2778721.0971 | 1144716.7275
17 | 2778858.5385 | 1144704.779
18 | 2778349.9705 | 1144881.4839
19 | 2778822.5585 | 1145112.1324
20 | 2778833.3959 | 1144961.7372
21 | 2778696.8949 | 1144725.363
22 | 2778862.1848 | 1144730.3885
23 | 2778282.1255 | 1144939.6985
24 | 2778838.4516 | 1145172.0144
25 | 2778921.0397 | 1145078.8554
26 | 2773544.9318 | 1141508.9153
27 | 2773544.9609 | 1141464.8656
28 | 2773546.3778 | 1141577.3627
29 | 2773857.8588 | 1141505.7298
30 | 2773519.3522 | 1141283.4779
31 | 2773515.2471 | 1141664.6235
32 | 2773568.6378 | 1141227.1113
33 | 2773497.6732 | 1141292.8924
34 | 2773636.1263 | 1141202.8072
35 | 2773960.6741 | 1142118.02
36 | 2773478.4515 | 1141706.0139
37 | 2773633.9217 | 1141194.2457
38 | 2771364.9178 | 1140242.9021
39 | 2773971.6061 | 1142128.9338
40 | 2775386.4304 | 1143822.4303
41 | 2771339.6744 | 1140200.7816
42 | 2778261.5007 | 1144957.4275
43 | 2778207.8806 | 1145000.8942
44 | 2778174.174 | 1145029.8918
45 | 2778049.4245 | 1145095.3683
46 | 2778957.1544 | 1145325.8547
47 | 2778737.2247 | 1145215.2316
48 | 2778824.1289 | 1145797.133
49 | 2778681.4171 | 1145165.4211
50 | 2778030.441 | 1145119.0075
51 | 2778007.0473 | 1145111.2989
52 | 2769904.9534 | 1148613.8643
53 | 2769880.6103 | 1148644.9056
54 | 2769882.1864 | 1148767.1911
55 | 2769827.2618 | 1148858.7242
56 | 2769822.6311 | 1148849.9082
57 | 2770009.9437 | 1148813.3781
58 | 2769904.4936 | 1148737.2156
59 | 2769960.5986 | 1148929.3222
60 | 2769985.9961 | 1148945.2969
61 | 2778823.9816 | 1145828.5243
62 | 2775386.4304 | 1143822.4303

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98307 | -0.079805 | 0.16135 | 0.078147
1 | 0.98312 | -0.080308 | 0 | 0
2 | 0.983 | -0.080326 | 0 | 0
3 | 0.98321 | -0.081013 | 0 | 0
4 | 0.98296 | -0.080035 | 0 | 0
5 | 0.98296 | -0.07998 | 0.24228 | 0.11734
6 | 0.98322 | -0.081134 | 0.15715 | 0.07611
7 | 0.98274 | -0.081714 | 0 | 0
8 | 0.98325 | -0.081367 | 0.16403 | 0.079444
9 | 0.98326 | -0.081492 | 0 | 0
10 | 0.98327 | -0.081527 | 0 | 0
11 | 0.98338 | -0.082481 | 0 | 0
12 | 0.98273 | -0.081671 | 0.068262 | 0.033061
13 | 0.98339 | -0.082628 | 0.12465 | 0.060369
14 | 0.98347 | -0.083263 | 0 | 0
15 | 0.98386 | -0.086516 | 0 | 0
16 | 0.98343 | -0.082907 | 0 | 0
17 | 0.98345 | -0.083097 | 0 | 0
18 | 0.98536 | -0.099019 | 0 | 0
19 | 0.98368 | -0.084934 | 0 | 0
20 | 0.98386 | -0.086509 | 0.075749 | 0.036687
21 | 0.98342 | -0.082861 | 0.14819 | 0.071773
22 | 0.98344 | -0.083032 | 0.14905 | 0.072186
23 | 0.98559 | -0.10085 | 0.1622 | 0.078558
24 | 0.98364 | -0.084527 | 0.14904 | 0.072184
25 | 0.98366 | -0.0851 | 0.12785 | 0.061922
26 | 0.99467 | -0.036068 | 0.13163 | 0.063752
27 | 0.99464 | -0.035858 | 0 | 0
28 | 0.99473 | -0.036574 | 0 | 0
29 | 0.99461 | -0.036429 | 0.092979 | 0.045032
30 | 0.99452 | -0.034794 | 0 | 0
31 | 0.99481 | -0.037256 | 0 | 0
32 | 0.99449 | -0.034557 | 0 | 0
33 | 0.99451 | -0.034723 | 0.14562 | 0.070525
34 | 0.99446 | -0.034732 | 0.12056 | 0.058391
35 | 0.99584 | -0.029748 | 0 | 0
36 | 0.9948 | -0.03736 | 0.15338 | 0.074286
37 | 0.99446 | -0.034724 | 0.077314 | 0.037445
38 | 0.99396 | -0.038726 | 0 | 0
39 | 0.99586 | -0.029887 | 0.13325 | 0.064537
40 | 1 | 0 | -3.9447 | -1.8107
41 | 0.99395 | -0.038656 | 0.11971 | 0.05798
42 | 0.98567 | -0.10146 | 0 | 0
43 | 0.98585 | -0.103 | 0 | 0
44 | 0.98598 | -0.10398 | 0.1288 | 0.062383
45 | 0.98659 | -0.099231 | 0 | 0
46 | 0.9836 | -0.084766 | 0.097732 | 0.047334
47 | 0.98361 | -0.084758 | 0 | 0
48 | 0.98345 | -0.085771 | 0 | 0
49 | 0.98359 | -0.084616 | 0.15525 | 0.07519
50 | 0.98668 | -0.099953 | 0 | 0
51 | 0.98675 | -0.10054 | 0.073524 | 0.03561
52 | 0.99196 | -0.060303 | 0.15735 | 0.076209
53 | 0.99194 | -0.06013 | 0 | 0
54 | 0.99187 | -0.059503 | 0 | 0
55 | 0.99184 | -0.059254 | 0 | 0
56 | 0.99184 | -0.059234 | 0.16206 | 0.078492
57 | 0.99184 | -0.059726 | 0 | 0
58 | 0.99186 | -0.059568 | 0.1423 | 0.068917
59 | 0.99182 | -0.059563 | 0 | 0
60 | 0.99181 | -0.059604 | 0.11142 | 0.053963
61 | 0.98345 | -0.085713 | 0.15171 | 0.073475
62 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.47194 | -0.22306 | 0.47197 | 0.22092 | 2.9132e-05 | -0.0021383 | 0.015328 | 0.015302 | 0.015328 | 0.98307 | -0.079805 | 0.98312 | -0.080308 | 6.9675
1 | 0.31059 | 0.14491 | -0.31057 | -0.14504 | 2.1551e-05 | -0.00012424 | 0.010064 | 0.010066 | 0.010066 | 0.98307 | -0.079805 | 0.983 | -0.080326 | 4.7933
2 | -0.47197 | -0.22092 | 0.47202 | 0.21782 | 4.2021e-05 | -0.003098 | 0.015302 | 0.015263 | 0.015302 | 0.98312 | -0.080308 | 0.98321 | -0.081013 | 6.9553
3 | 0.31057 | 0.14504 | -0.31056 | -0.14692 | 1.1073e-05 | -0.0018809 | 0.010066 | 0.01009 | 0.01009 | 0.983 | -0.080326 | 0.98296 | -0.080035 | 4.5862
4 | -0.47202 | -0.21782 | 0.47202 | 0.21728 | 7.3371e-06 | -0.00054259 | 0.015263 | 0.015256 | 0.015263 | 0.98321 | -0.081013 | 0.98322 | -0.081134 | 6.9378
5 | 0.31056 | 0.14692 | -0.31056 | -0.14727 | 2.0767e-06 | -0.00035174 | 0.01009 | 0.010094 | 0.010094 | 0.98296 | -0.080035 | 0.98296 | -0.07998 | 4.5882
6 | 0.068276 | 0.029927 | -0.068262 | -0.031829 | 1.4297e-05 | -0.0019018 | 0.0021893 | 0.0022124 | 0.0022124 | 0.98296 | -0.07998 | 0.98274 | -0.081714 | 1.0535
7 | -0.62917 | -0.29339 | 0.6292 | 0.2921 | 3.1154e-05 | -0.0012884 | 0.020382 | 0.020366 | 0.020382 | 0.98322 | -0.081134 | 0.98327 | -0.081527 | 9.2647
8 | 0.068262 | 0.031829 | -0.068262 | -0.033061 | 3.5144e-07 | -0.0012314 | 0.0022124 | 0.002228 | 0.002228 | 0.98274 | -0.081714 | 0.98273 | -0.081671 | 1.0127
9 | -0.16403 | -0.079444 | 0.16403 | 0.077984 | 2.4111e-06 | -0.0014604 | 0.005351 | 0.0053324 | 0.005351 | 0.98325 | -0.081367 | 0.98326 | -0.081492 | 2.4323
10 | -0.16403 | -0.077984 | 0.16403 | 0.077566 | 6.8656e-07 | -0.0004177 | 0.0053324 | 0.0053271 | 0.0053324 | 0.98326 | -0.081492 | 0.98327 | -0.081527 | 2.4238
11 | -0.79324 | -0.36967 | 0.79333 | 0.36719 | 9.5691e-05 | -0.0024814 | 0.025693 | 0.025662 | 0.025693 | 0.98327 | -0.081527 | 0.98338 | -0.082481 | 11.6787
12 | -0.79333 | -0.36719 | 0.79335 | 0.3668 | 1.4892e-05 | -0.00038676 | 0.025662 | 0.025657 | 0.025662 | 0.98338 | -0.082481 | 0.98339 | -0.082628 | 11.6646
13 | -0.91799 | -0.42717 | 0.91807 | 0.42575 | 7.3656e-05 | -0.0014212 | 0.029722 | 0.029704 | 0.029722 | 0.98339 | -0.082628 | 0.98347 | -0.083263 | 13.5101
14 | -1.2153 | -0.561 | 1.2158 | 0.55539 | 0.00051396 | -0.0056194 | 0.03929 | 0.03922 | 0.03929 | 0.98347 | -0.083263 | 0.98386 | -0.086516 | 17.8592
15 | 0.1482 | 0.066137 | -0.14819 | -0.071182 | 6.7057e-06 | -0.0050444 | 0.0047636 | 0.0048259 | 0.0048259 | 0.98347 | -0.083263 | 0.98343 | -0.082907 | 2.1936
16 | 0.14905 | 0.06912 | -0.14905 | -0.071356 | 3.0253e-06 | -0.0022363 | 0.0048225 | 0.0048505 | 0.0048505 | 0.98347 | -0.083263 | 0.98345 | -0.083097 | 2.2048
17 | -1.9734 | -0.91238 | 1.9766 | 0.89959 | 0.003218 | -0.012794 | 0.06379 | 0.063622 | 0.06379 | 0.98386 | -0.086516 | 0.98536 | -0.099019 | 28.9954
18 | 0.68178 | 0.32046 | -0.68165 | -0.32503 | 0.0001303 | -0.0045655 | 0.022104 | 0.022162 | 0.022162 | 0.98386 | -0.086516 | 0.98368 | -0.084934 | 10.0735
19 | 0.075749 | 0.036533 | -0.075749 | -0.036687 | 5.4356e-08 | -0.00015437 | 0.0024676 | 0.0024695 | 0.0024695 | 0.98386 | -0.086516 | 0.98386 | -0.086509 | 1.1225
20 | 0.14819 | 0.071182 | -0.14819 | -0.071773 | 7.9817e-07 | -0.00059164 | 0.0048259 | 0.0048334 | 0.0048334 | 0.98343 | -0.082907 | 0.98342 | -0.082861 | 2.197
21 | 0.14905 | 0.071356 | -0.14905 | -0.072186 | 1.1311e-06 | -0.00082944 | 0.0048505 | 0.0048611 | 0.0048611 | 0.98345 | -0.083097 | 0.98344 | -0.083032 | 2.2096
22 | -1.9766 | -0.89959 | 1.9771 | 0.89766 | 0.00048266 | -0.0019288 | 0.063622 | 0.063597 | 0.063622 | 0.98536 | -0.099019 | 0.98559 | -0.10085 | 28.919
23 | 0.5538 | 0.26323 | -0.55377 | -0.26465 | 2.684e-05 | -0.0014251 | 0.017994 | 0.018012 | 0.018012 | 0.98368 | -0.084934 | 0.98364 | -0.084527 | 8.1874
24 | 0.12786 | 0.061804 | -0.12785 | -0.061922 | 3.2179e-06 | -0.00011806 | 0.0041675 | 0.004169 | 0.004169 | 0.98368 | -0.084934 | 0.98366 | -0.0851 | 1.9852
25 | -2.1393 | -0.97622 | 2.1394 | 0.97564 | 0.00017196 | -0.00057891 | 0.068874 | 0.068866 | 0.068874 | 0.98559 | -0.10085 | 0.98567 | -0.10146 | 31.3063
26 | 0.097735 | 0.047111 | -0.097732 | -0.047334 | 3.5133e-06 | -0.00022223 | 0.0031841 | 0.003187 | 0.003187 | 0.98364 | -0.084527 | 0.9836 | -0.084766 | 1.5176
27 | 0.15526 | 0.07331 | -0.15525 | -0.073434 | 4.9806e-06 | -0.00012401 | 0.0050388 | 0.0050404 | 0.0050404 | 0.98364 | -0.084527 | 0.98361 | -0.084758 | 2.4002
28 | 0.15174 | 0.072045 | -0.15171 | -0.07275 | 2.7122e-05 | -0.00070511 | 0.0049295 | 0.0049387 | 0.0049387 | 0.98364 | -0.084527 | 0.98345 | -0.085771 | 2.3517
29 | 0.46336 | 0.21105 | -0.46334 | -0.21208 | 1.2855e-05 | -0.001037 | 0.014777 | 0.014789 | 0.014789 | 0.99467 | -0.036068 | 0.99464 | -0.035858 | 6.7225
30 | -0.68797 | -0.31946 | 0.68802 | 0.31786 | 4.4299e-05 | -0.0016058 | 0.022014 | 0.021994 | 0.022014 | 0.99467 | -0.036068 | 0.99473 | -0.036574 | 10.0064
31 | 0.092984 | 0.044665 | -0.092979 | -0.045032 | 5.0052e-06 | -0.00036646 | 0.0029938 | 0.0029985 | 0.0029985 | 0.99467 | -0.036068 | 0.99461 | -0.036429 | 1.4278
32 | 0.46334 | 0.21208 | -0.46328 | -0.21712 | 6.2728e-05 | -0.0050341 | 0.014789 | 0.014851 | 0.014851 | 0.99464 | -0.035858 | 0.99452 | -0.034794 | 6.7505
33 | -0.68802 | -0.31786 | 0.68808 | 0.31566 | 6.0604e-05 | -0.002202 | 0.021994 | 0.021967 | 0.021994 | 0.99473 | -0.036574 | 0.99481 | -0.037256 | 9.9975
34 | 0.19789 | 0.093106 | -0.19788 | -0.095545 | 5.587e-06 | -0.0024391 | 0.006348 | 0.0063785 | 0.0063785 | 0.99452 | -0.034794 | 0.99449 | -0.034557 | 2.8993
35 | 0.2654 | 0.12401 | -0.26539 | -0.12458 | 2.3376e-06 | -0.00057073 | 0.0085031 | 0.0085101 | 0.0085101 | 0.99452 | -0.034794 | 0.99451 | -0.034723 | 3.8682
36 | -0.84146 | -0.38988 | 0.84228 | 0.38964 | 0.00081984 | -0.00023817 | 0.026911 | 0.026902 | 0.026911 | 0.99481 | -0.037256 | 0.99584 | -0.029748 | 12.8149
37 | 0.15338 | 0.074222 | -0.15338 | -0.074286 | 2.4129e-06 | -6.3918e-05 | 0.0049446 | 0.0049454 | 0.0049454 | 0.99481 | -0.037256 | 0.9948 | -0.03736 | 2.355
38 | 0.19788 | 0.095545 | -0.19788 | -0.095627 | 5.2006e-06 | -8.1433e-05 | 0.0063785 | 0.0063795 | 0.0063795 | 0.99449 | -0.034557 | 0.99446 | -0.034732 | 3.0379
39 | 0.11978 | 0.054056 | -0.11971 | -0.056823 | 6.2174e-05 | -0.0027664 | 0.0038144 | 0.0038486 | 0.0038486 | 0.99451 | -0.034723 | 0.99396 | -0.038726 | 1.8327
40 | 0.077314 | 0.037236 | -0.077314 | -0.037445 | 7.3308e-08 | -0.00020873 | 0.002491 | 0.0024936 | 0.0024936 | 0.99446 | -0.034732 | 0.99446 | -0.034724 | 1.1335
41 | -0.84228 | -0.38964 | 0.8423 | 0.38928 | 1.4901e-05 | -0.00036082 | 0.026902 | 0.026898 | 0.026902 | 0.99584 | -0.029748 | 0.99586 | -0.029887 | 12.2282
42 | 0.11971 | 0.056823 | -0.11971 | -0.05798 | 9.7405e-07 | -0.0011573 | 0.0038486 | 0.0038632 | 0.0038632 | 0.99396 | -0.038726 | 0.99395 | -0.038656 | 1.756
43 | -0.97555 | -0.45382 | 0.97937 | 0.45359 | 0.0038207 | -0.00023037 | 0.031189 | 0.031157 | 0.031189 | 0.99586 | -0.029887 | 1 | 0 | 14.8519
44 | 2.3738 | 1.0858 | -2.3442 | -1.0707 | 0.029562 | 0.015076 | 0.075353 | 0.075395 | 0.075395 | 1 | 0 | 0.98675 | -0.10054 | 35.9024
45 | 0.57755 | 0.26083 | -0.57319 | -0.26672 | 0.0043659 | -0.0058872 | 0.018294 | 0.018398 | 0.018398 | 1 | 0 | 0.99196 | -0.060303 | 8.761
46 | -2.1394 | -0.97564 | 2.1399 | 0.97417 | 0.00043621 | -0.0014695 | 0.068866 | 0.068847 | 0.068866 | 0.98567 | -0.10146 | 0.98585 | -0.103 | 31.3028
47 | -2.1399 | -0.97417 | 2.1402 | 0.97322 | 0.00028091 | -0.00094714 | 0.068847 | 0.068834 | 0.068847 | 0.98585 | -0.103 | 0.98598 | -0.10398 | 31.294
48 | -2.269 | -1.0356 | 2.2703 | 1.0363 | 0.0013385 | 0.00067479 | 0.073023 | 0.073021 | 0.073023 | 0.98598 | -0.10398 | 0.98659 | -0.099231 | 34.773
49 | -2.2703 | -1.0363 | 2.2705 | 1.0356 | 0.00021651 | -0.00064281 | 0.073021 | 0.073013 | 0.073021 | 0.98659 | -0.099231 | 0.98668 | -0.099953 | 33.1915
50 | 0.15525 | 0.073434 | -0.15525 | -0.07519 | 2.5909e-06 | -0.001756 | 0.0050404 | 0.0050627 | 0.0050627 | 0.98361 | -0.084758 | 0.98359 | -0.084616 | 2.3012
51 | 0.15171 | 0.07275 | -0.15171 | -0.073475 | 1.0243e-06 | -0.0007248 | 0.0049387 | 0.0049479 | 0.0049479 | 0.98345 | -0.085771 | 0.98345 | -0.085713 | 2.2491
52 | -2.2705 | -1.0356 | 2.2707 | 1.0351 | 0.00017515 | -0.0005202 | 0.073013 | 0.073006 | 0.073013 | 0.98668 | -0.099953 | 0.98675 | -0.10054 | 33.1876
53 | 0.41584 | 0.19051 | -0.41583 | -0.19143 | 9.3308e-06 | -0.0009232 | 0.013311 | 0.013322 | 0.013322 | 0.99196 | -0.060303 | 0.99194 | -0.06013 | 6.0556
54 | 0.41583 | 0.19143 | -0.41579 | -0.19469 | 3.3003e-05 | -0.0032525 | 0.013322 | 0.013362 | 0.013362 | 0.99194 | -0.06013 | 0.99187 | -0.059503 | 6.0737
55 | 0.11143 | 0.050712 | -0.11142 | -0.05087 | 3.0744e-06 | -0.00015762 | 0.003563 | 0.003565 | 0.003565 | 0.99187 | -0.059503 | 0.99184 | -0.059726 | 1.6976
56 | 0.1423 | 0.068874 | -0.1423 | -0.068917 | 1.4095e-06 | -4.3001e-05 | 0.0046011 | 0.0046016 | 0.0046016 | 0.99187 | -0.059503 | 0.99186 | -0.059568 | 2.1913
57 | 0.16207 | 0.0751 | -0.16207 | -0.078258 | 4.8892e-06 | -0.0031577 | 0.0051987 | 0.005238 | 0.005238 | 0.99187 | -0.059503 | 0.99184 | -0.059254 | 2.3809
58 | 0.16207 | 0.078258 | -0.16206 | -0.078492 | 3.6477e-07 | -0.00023367 | 0.005238 | 0.005241 | 0.005241 | 0.99184 | -0.059254 | 0.99184 | -0.059234 | 2.3823
59 | 0.11142 | 0.05087 | -0.11142 | -0.053928 | 2.2331e-06 | -0.0030586 | 0.003565 | 0.0036028 | 0.0036028 | 0.99184 | -0.059726 | 0.99182 | -0.059563 | 1.6377
60 | 0.11142 | 0.053928 | -0.11142 | -0.053963 | 6.9399e-07 | -3.48e-05 | 0.0036028 | 0.0036033 | 0.0036033 | 0.99182 | -0.059563 | 0.99181 | -0.059604 | 1.7159

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 4.0123 | 1.8435

## res_load
| p_mw | q_mvar
0 | 0.16135 | 0.078147
1 | 0.24228 | 0.11734
2 | 0.15715 | 0.07611
3 | 0.16403 | 0.079444
4 | 0.068262 | 0.033061
5 | 0.12465 | 0.060369
6 | 0.075749 | 0.036687
7 | 0.14819 | 0.071773
8 | 0.14905 | 0.072186
9 | 0.1622 | 0.078558
10 | 0.14904 | 0.072184
11 | 0.12785 | 0.061922
12 | 0.13163 | 0.063752
13 | 0.092979 | 0.045032
14 | 0.14562 | 0.070525
15 | 0.12056 | 0.058391
16 | 0.15338 | 0.074286
17 | 0.077314 | 0.037445
18 | 0.13325 | 0.064537
19 | 0.067593 | 0.032737
20 | 0.11971 | 0.05798
21 | 0.1288 | 0.062383
22 | 0.097732 | 0.047334
23 | 0.15525 | 0.07519
24 | 0.073524 | 0.03561
25 | 0.15735 | 0.076209
26 | 0.16206 | 0.078492
27 | 0.1423 | 0.068917
28 | 0.11142 | 0.053963
29 | 0.15171 | 0.073475

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1