## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_164_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_164_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_164_0_node_27 | 20 | n |  | TRUE
3 | bus_MV_164_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_164_0_node_35 | 20 | n |  | TRUE
5 | bus_MV_164_0_node_25 | 20 | n |  | TRUE
6 | bus_MV_164_0_node_2 | 20 | n |  | TRUE
7 | bus_MV_164_0_node_24 | 20 | n |  | TRUE
8 | bus_MV_164_0_node_4 | 20 | n |  | TRUE
9 | bus_MV_164_0_node_5 | 20 | n |  | TRUE
10 | bus_MV_164_0_node_7 | 20 | n |  | TRUE
11 | bus_MV_164_0_node_8 | 20 | n |  | TRUE
12 | bus_MV_164_0_node_19 | 20 | n |  | TRUE
13 | bus_MV_164_0_node_20 | 20 | n |  | TRUE
14 | bus_MV_164_0_node_13 | 20 | n |  | TRUE
15 | bus_MV_164_0_node_6 | 20 | n |  | TRUE
16 | bus_MV_164_0_node_37 | 20 | n |  | TRUE
17 | bus_MV_164_0_node_36 | 20 | n |  | TRUE
18 | bus_MV_164_0_node_10 | 20 | n |  | TRUE
19 | bus_MV_164_0_node_9 | 20 | n |  | TRUE
20 | bus_MV_164_0_node_15 | 20 | n |  | TRUE
21 | bus_MV_164_0_node_23 | 20 | n |  | TRUE
22 | bus_MV_164_0_node_11 | 20 | n |  | TRUE
23 | bus_MV_164_0_node_12 | 20 | n |  | TRUE
24 | bus_MV_164_0_node_14 | 20 | n |  | TRUE
25 | bus_MV_164_0_node_17 | 20 | n |  | TRUE
26 | bus_MV_164_0_node_18 | 20 | n |  | TRUE
27 | bus_MV_164_0_node_16 | 20 | n |  | TRUE
28 | bus_MV_164_0_node_21 | 20 | n |  | TRUE
29 | bus_MV_164_0_node_22 | 20 | n |  | TRUE
30 | bus_MV_164_0_node_34 | 20 | n |  | TRUE
31 | bus_MV_164_0_node_33 | 20 | n |  | TRUE
32 | bus_MV_164_0_node_28 | 20 | n |  | TRUE
33 | bus_MV_164_0_node_29 | 20 | n |  | TRUE
34 | bus_MV_164_0_node_30 | 20 | n |  | TRUE
35 | bus_MV_164_0_node_31 | 20 | n |  | TRUE
36 | bus_MV_164_0_node_32 | 20 | n |  | TRUE
37 | bus_HV_164_0_node_19 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_164_0_load_0 | 0 | 0.066395 | 0.032157 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_164_0_load_35 | 4 | 0.093041 | 0.045062 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_164_0_load_2 | 6 | 0.088651 | 0.042935 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_164_0_load_24 | 7 | 0.1508 | 0.073035 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_164_0_load_4 | 8 | 0.069649 | 0.033732 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_164_0_load_19 | 12 | 0.1056 | 0.051145 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_164_0_load_20 | 13 | 0.066942 | 0.032421 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_164_0_load_37 | 16 | 0.11657 | 0.056458 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_164_0_load_36 | 17 | 0.12309 | 0.059617 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_164_0_load_9 | 19 | 0.1192 | 0.057731 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_164_0_load_15 | 20 | 0.12035 | 0.058287 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_164_0_load_23 | 21 | 0.16229 | 0.078602 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_164_0_load_11 | 22 | 0.15463 | 0.07489 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_164_0_load_16 | 27 | 0.069045 | 0.03344 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_164_0_load_34 | 30 | 0.093752 | 0.045406 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_164_0_load_28 | 32 | 0.15863 | 0.076829 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_164_0_load_30 | 34 | 0.14582 | 0.070624 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_164_0_load_32 | 36 | 0.12163 | 0.05891 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_164_0_line_0 |  | 0 | 1 | 0.12842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_164_0_line_1 |  | 0 | 2 | 12.1848 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_164_0_line_2 |  | 1 | 3 | 3.2409 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_164_0_line_3 |  | 2 | 4 | 0.008459 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_164_0_line_4 |  | 2 | 5 | 0.15737 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_164_0_line_5 |  | 3 | 6 | 0.39825 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_164_0_line_6 |  | 4 | 14 | 1.2596 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_164_0_line_7 |  | 5 | 7 | 0.015512 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_164_0_line_8 |  | 8 | 9 | 0.049867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_164_0_line_9 |  | 9 | 10 | 0.23464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_164_0_line_10 |  | 9 | 11 | 0.048689 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_164_0_line_11 |  | 10 | 17 | 0.029551 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_164_0_line_12 |  | 10 | 15 | 0.2896 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_164_0_line_13 |  | 11 | 18 | 1.3467 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_164_0_line_14 |  | 11 | 19 | 0.064383 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_164_0_line_15 |  | 12 | 13 | 2.0738 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_164_0_line_16 |  | 12 | 14 | 0.059806 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_164_0_line_17 |  | 13 | 28 | 0.1206 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_164_0_line_18 |  | 14 | 23 | 0.99366 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_164_0_line_19 |  | 15 | 16 | 0.18087 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_164_0_line_20 |  | 18 | 20 | 0.11649 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_164_0_line_21 |  | 20 | 21 | 1.1687 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_164_0_line_22 |  | 21 | 29 | 0.048324 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_164_0_line_23 |  | 22 | 23 | 0.003069 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_164_0_line_24 |  | 23 | 24 | 0.84185 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_164_0_line_25 |  | 24 | 27 | 0.15898 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_164_0_line_26 |  | 25 | 26 | 1.1001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_164_0_line_27 |  | 25 | 27 | 0.60037 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_164_0_line_28 |  | 26 | 30 | 0.10924 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_164_0_line_29 |  | 28 | 29 | 1.1876 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_164_0_line_30 |  | 30 | 31 | 0.070373 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_164_0_line_31 |  | 31 | 35 | 0.32 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_164_0_line_32 |  | 32 | 33 | 0.024949 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_164_0_line_33 |  | 32 | 34 | 0.097788 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_164_0_line_34 |  | 33 | 35 | 0.063394 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_164_0_line_35 |  | 35 | 36 | 0.099934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_164_0_trafo_19 | 25 MVA 110/20 kV | 37 | 12 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2762195.1589 | 1146639.3884
1 | 2762082.2841 | 1146697.2133
2 | 2761818.5678 | 1134460.3906
3 | 2759558.2516 | 1148730.1377
4 | 2761826.482 | 1134457.3444
5 | 2761690.5644 | 1134453.5358
6 | 2759269.7718 | 1148938.1932
7 | 2761692.6396 | 1134438.1673
8 | 2767913.6431 | 1135538.3037
9 | 2767864.1371 | 1135541.553
10 | 2768051.2112 | 1135622.5912
11 | 2767839.5421 | 1135506.8951
12 | 2763085.6417 | 1134180.421
13 | 2765072.8173 | 1134773.6451
14 | 2763044.6564 | 1134136.8669
15 | 2767913.1533 | 1135729.7453
16 | 2767741.6173 | 1135787.0962
17 | 2768070.5572 | 1135643.8145
18 | 2766795.0961 | 1135300.4785
19 | 2767776.3295 | 1135494.6782
20 | 2766688.9672 | 1135264.0179
21 | 2765655.499 | 1134718.4011
22 | 2762894.7621 | 1133702.7236
23 | 2762894.8449 | 1133699.6566
24 | 2762316.9466 | 1133871.3508
25 | 2761612.1164 | 1133610.7066
26 | 2760582.0958 | 1133515.29
27 | 2762157.9036 | 1133860.8274
28 | 2765133.6279 | 1134669.4955
29 | 2765617.336 | 1134688.6961
30 | 2760476.6388 | 1133544.4796
31 | 2760412.9783 | 1133574.8147
32 | 2760018.6883 | 1133530.1904
33 | 2760041.9647 | 1133539.2477
34 | 2759924.2977 | 1133504.637
35 | 2760101.588 | 1133559.7219
36 | 2760052.5343 | 1133626.0778
37 | 2763085.6417 | 1134180.421

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99553 | -0.058832 | 0.066395 | 0.032157
1 | 0.99552 | -0.058816 | 0 | 0
2 | 0.99894 | -0.011387 | 0 | 0
3 | 0.99499 | -0.065475 | 0 | 0
4 | 0.99894 | -0.011399 | 0.093041 | 0.045062
5 | 0.99891 | -0.011125 | 0 | 0
6 | 0.99495 | -0.065169 | 0.088651 | 0.042935
7 | 0.99891 | -0.011097 | 0.1508 | 0.073035
8 | 0.99377 | -0.039663 | 0.069649 | 0.033732
9 | 0.99377 | -0.039703 | 0 | 0
10 | 0.9937 | -0.03918 | 0 | 0
11 | 0.99379 | -0.039838 | 0 | 0
12 | 1 | 0 | -1.9416 | -0.73167
13 | 0.99702 | -0.034435 | 0.066942 | 0.032421
14 | 0.99987 | -0.0014772 | 0 | 0
15 | 0.99366 | -0.038839 | 0 | 0
16 | 0.99362 | -0.039099 | 0.11657 | 0.056458
17 | 0.9937 | -0.039137 | 0.12309 | 0.059617
18 | 0.99451 | -0.043958 | 0 | 0
19 | 0.99378 | -0.039748 | 0.1192 | 0.057731
20 | 0.99458 | -0.044185 | 0.12035 | 0.058287
21 | 0.99577 | -0.031093 | 0.16229 | 0.078602
22 | 0.99896 | 0.0023734 | 0.15463 | 0.07489
23 | 0.99896 | 0.0023678 | 0 | 0
24 | 0.99834 | 0.0052492 | 0 | 0
25 | 0.99764 | -8.2175e-05 | 0 | 0
26 | 0.99692 | 0.0047183 | 0 | 0
27 | 0.99822 | 0.0059148 | 0.069045 | 0.03344
28 | 0.99686 | -0.036333 | 0 | 0
29 | 0.99581 | -0.031341 | 0 | 0
30 | 0.99685 | 0.0052959 | 0.093752 | 0.045406
31 | 0.99681 | 0.0055982 | 0 | 0
32 | 0.99661 | 0.0073857 | 0.15863 | 0.076829
33 | 0.99661 | 0.0072948 | 0 | 0
34 | 0.99658 | 0.0072117 | 0.14582 | 0.070624
35 | 0.99664 | 0.0070683 | 0 | 0
36 | 0.99662 | 0.0072071 | 0.12163 | 0.05891
37 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.088699 | 0.02668 | -0.088698 | -0.029718 | 1.2487e-06 | -0.0030384 | 0.0026858 | 0.0027125 | 0.0027125 | 0.99553 | -0.058832 | 0.99552 | -0.058816 | 1.233
1 | -0.15509 | -0.058836 | 0.15558 | 0.044676 | 0.00048775 | -0.014161 | 0.00481 | 0.0046777 | 0.00481 | 0.99553 | -0.058832 | 0.99894 | -0.011387 | 2.2905
2 | 0.088698 | 0.029718 | -0.088655 | -0.033523 | 4.3058e-05 | -0.0038054 | 0.0027125 | 0.0027499 | 0.0027499 | 0.99552 | -0.058816 | 0.99499 | -0.065475 | 1.3095
3 | -0.30638 | -0.11359 | 0.30639 | 0.11339 | 1.0067e-06 | -0.00020124 | 0.0094429 | 0.0094409 | 0.0094429 | 0.99894 | -0.011387 | 0.99894 | -0.011399 | 4.2922
4 | 0.1508 | 0.068917 | -0.1508 | -0.072665 | 4.8692e-06 | -0.0037478 | 0.0047914 | 0.0048375 | 0.0048375 | 0.99894 | -0.011387 | 0.99891 | -0.011125 | 2.1989
5 | 0.088655 | 0.033523 | -0.088651 | -0.042935 | 4.1715e-06 | -0.0094121 | 0.0027499 | 0.0028579 | 0.0028579 | 0.99499 | -0.065475 | 0.99495 | -0.065169 | 1.299
6 | -0.39943 | -0.15845 | 0.39977 | 0.15717 | 0.00034562 | -0.0012855 | 0.012418 | 0.012402 | 0.012418 | 0.99894 | -0.011399 | 0.99987 | -0.0014772 | 5.9132
7 | 0.1508 | 0.072665 | -0.1508 | -0.073035 | 4.8507e-07 | -0.00036941 | 0.0048375 | 0.0048421 | 0.0048421 | 0.99891 | -0.011125 | 0.99891 | -0.011097 | 2.201
8 | -0.069649 | -0.033732 | 0.069649 | 0.032557 | 3.3422e-07 | -0.0011757 | 0.002248 | 0.0022333 | 0.002248 | 0.99377 | -0.039663 | 0.99377 | -0.039703 | 1.0218
9 | 0.23969 | 0.10282 | -0.23967 | -0.10834 | 1.8133e-05 | -0.005527 | 0.0075762 | 0.007641 | 0.007641 | 0.99377 | -0.039703 | 0.9937 | -0.03918 | 3.4732
10 | -0.30934 | -0.13537 | 0.30935 | 0.13423 | 6.2452e-06 | -0.0011462 | 0.0098087 | 0.0097953 | 0.0098087 | 0.99377 | -0.039703 | 0.99379 | -0.039838 | 4.4585
11 | 0.12309 | 0.058921 | -0.12309 | -0.059617 | 6.2143e-07 | -0.00069651 | 0.0039645 | 0.0039733 | 0.0039733 | 0.9937 | -0.03918 | 0.9937 | -0.039137 | 1.806
12 | 0.11658 | 0.049421 | -0.11657 | -0.056247 | 5.3452e-06 | -0.0068257 | 0.0036785 | 0.0037603 | 0.0037603 | 0.9937 | -0.03918 | 0.99366 | -0.038839 | 1.7092
13 | -0.42855 | -0.19044 | 0.42887 | 0.15876 | 0.00032482 | -0.031682 | 0.013622 | 0.013274 | 0.013622 | 0.99379 | -0.039838 | 0.99451 | -0.043958 | 6.1919
14 | 0.1192 | 0.056213 | -0.1192 | -0.057731 | 1.2659e-06 | -0.0015178 | 0.0038282 | 0.0038472 | 0.0038472 | 0.99379 | -0.039838 | 0.99378 | -0.039748 | 1.7487
15 | 0.78216 | 0.29408 | -0.78001 | -0.2952 | 0.0021523 | -0.0011203 | 0.024122 | 0.024147 | 0.024147 | 1 | 0 | 0.99702 | -0.034435 | 11.4987
16 | 1.1454 | 0.42709 | -1.1453 | -0.42708 | 0.0001327 | 1.1728e-05 | 0.035289 | 0.035289 | 0.035289 | 1 | 0 | 0.99987 | -0.0014772 | 16.8044
17 | 0.71307 | 0.26277 | -0.71296 | -0.26285 | 0.00010404 | -7.7932e-05 | 0.022003 | 0.022005 | 0.022005 | 0.99702 | -0.034435 | 0.99686 | -0.036333 | 10.4784
18 | 0.74549 | 0.26991 | -0.74479 | -0.2934 | 0.0007023 | -0.023489 | 0.02289 | 0.023132 | 0.023132 | 0.99987 | -0.0014772 | 0.99896 | 0.0023678 | 10.5147
19 | 0.11657 | 0.056247 | -0.11657 | -0.056458 | 4.56e-06 | -0.00021033 | 0.0037603 | 0.003763 | 0.003763 | 0.99366 | -0.038839 | 0.99362 | -0.039099 | 1.7919
20 | -0.42887 | -0.15876 | 0.4289 | 0.15601 | 2.7346e-05 | -0.002743 | 0.013274 | 0.013247 | 0.013274 | 0.99451 | -0.043958 | 0.99458 | -0.044185 | 6.0338
21 | -0.54925 | -0.2143 | 0.54986 | 0.2133 | 0.00060922 | -0.0010001 | 0.017112 | 0.017098 | 0.017112 | 0.99458 | -0.044185 | 0.99577 | -0.031093 | 8.1488
22 | -0.71215 | -0.2919 | 0.71218 | 0.29077 | 3.2099e-05 | -0.0011346 | 0.022312 | 0.0223 | 0.022312 | 0.99577 | -0.031093 | 0.99581 | -0.031341 | 10.142
23 | -0.15463 | -0.07489 | 0.15463 | 0.074817 | 1.0098e-07 | -7.3093e-05 | 0.0049649 | 0.004964 | 0.0049649 | 0.99896 | 0.0023734 | 0.99896 | 0.0023678 | 2.2568
24 | 0.59016 | 0.21858 | -0.58978 | -0.23852 | 0.00037592 | -0.019934 | 0.018186 | 0.018396 | 0.018396 | 0.99896 | 0.0023678 | 0.99834 | 0.0052492 | 8.3617
25 | 0.58978 | 0.23852 | -0.58971 | -0.24228 | 7.1983e-05 | -0.0037615 | 0.018396 | 0.018437 | 0.018437 | 0.99834 | 0.0052492 | 0.99822 | 0.0059148 | 8.3804
26 | 0.52038 | 0.20937 | -0.51999 | -0.23538 | 0.00039385 | -0.026008 | 0.016231 | 0.016528 | 0.016528 | 0.99764 | -8.2175e-05 | 0.99692 | 0.0047183 | 7.5127
27 | -0.52038 | -0.20937 | 0.52067 | 0.20884 | 0.00028166 | -0.00053734 | 0.016231 | 0.016223 | 0.016231 | 0.99764 | -8.2175e-05 | 0.99822 | 0.0059148 | 7.7289
28 | 0.51999 | 0.23538 | -0.51995 | -0.23796 | 3.9914e-05 | -0.0025802 | 0.016528 | 0.016559 | 0.016559 | 0.99692 | 0.0047183 | 0.99685 | 0.0052959 | 7.5269
29 | 0.71296 | 0.26285 | -0.71218 | -0.29077 | 0.00077777 | -0.027917 | 0.022005 | 0.0223 | 0.0223 | 0.99686 | -0.036333 | 0.99581 | -0.031341 | 10.1363
30 | 0.4262 | 0.19256 | -0.42618 | -0.19422 | 1.7258e-05 | -0.0016645 | 0.013543 | 0.013563 | 0.013563 | 0.99685 | 0.0052959 | 0.99681 | 0.0055982 | 6.1652
31 | 0.42618 | 0.19422 | -0.4261 | -0.20179 | 7.9123e-05 | -0.007567 | 0.013563 | 0.013656 | 0.013656 | 0.99681 | 0.0055982 | 0.99664 | 0.0070683 | 6.2073
32 | -0.30446 | -0.14734 | 0.30446 | 0.14675 | 3.1946e-06 | -0.00059071 | 0.0097972 | 0.0097898 | 0.0097972 | 0.99661 | 0.0073857 | 0.99661 | 0.0072948 | 4.4533
33 | 0.14582 | 0.07051 | -0.14582 | -0.070624 | 3.8364e-06 | -0.00011354 | 0.0046918 | 0.0046932 | 0.0046932 | 0.99661 | 0.0073857 | 0.99658 | 0.0072117 | 2.2349
34 | -0.30446 | -0.14675 | 0.30447 | 0.14525 | 8.0954e-06 | -0.001501 | 0.0097898 | 0.0097709 | 0.0097898 | 0.99661 | 0.0072948 | 0.99664 | 0.0070683 | 4.4499
35 | 0.12164 | 0.05654 | -0.12163 | -0.05891 | 2.0289e-06 | -0.0023694 | 0.0038852 | 0.0039146 | 0.0039146 | 0.99664 | 0.0070683 | 0.99662 | 0.0072071 | 1.7794

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 2.0472 | 0.78281

## res_load
| p_mw | q_mvar
0 | 0.066395 | 0.032157
1 | 0.093041 | 0.045062
2 | 0.088651 | 0.042935
3 | 0.1508 | 0.073035
4 | 0.069649 | 0.033732
5 | 0.1056 | 0.051145
6 | 0.066942 | 0.032421
7 | 0.11657 | 0.056458
8 | 0.12309 | 0.059617
9 | 0.1192 | 0.057731
10 | 0.12035 | 0.058287
11 | 0.16229 | 0.078602
12 | 0.15463 | 0.07489
13 | 0.069045 | 0.03344
14 | 0.093752 | 0.045406
15 | 0.15863 | 0.076829
16 | 0.14582 | 0.070624
17 | 0.12163 | 0.05891

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1