## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_175_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_175_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_175_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_175_0_node_2 | 20 | n |  | TRUE
4 | bus_MV_175_0_node_31 | 20 | n |  | TRUE
5 | bus_MV_175_0_node_28 | 20 | n |  | TRUE
6 | bus_MV_175_0_node_27 | 20 | n |  | TRUE
7 | bus_MV_175_0_node_40 | 20 | n |  | TRUE
8 | bus_MV_175_0_node_39 | 20 | n |  | TRUE
9 | bus_MV_175_0_node_4 | 20 | n |  | TRUE
10 | bus_MV_175_0_node_5 | 20 | n |  | TRUE
11 | bus_MV_175_0_node_45 | 20 | n |  | TRUE
12 | bus_MV_175_0_node_6 | 20 | n |  | TRUE
13 | bus_MV_175_0_node_44 | 20 | n |  | TRUE
14 | bus_MV_175_0_node_48 | 20 | n |  | TRUE
15 | bus_MV_175_0_node_37 | 20 | n |  | TRUE
16 | bus_MV_175_0_node_38 | 20 | n |  | TRUE
17 | bus_MV_175_0_node_7 | 20 | n |  | TRUE
18 | bus_MV_175_0_node_8 | 20 | n |  | TRUE
19 | bus_MV_175_0_node_9 | 20 | n |  | TRUE
20 | bus_MV_175_0_node_10 | 20 | n |  | TRUE
21 | bus_MV_175_0_node_11 | 20 | n |  | TRUE
22 | bus_MV_175_0_node_49 | 20 | n |  | TRUE
23 | bus_MV_175_0_node_36 | 20 | n |  | TRUE
24 | bus_MV_175_0_node_12 | 20 | n |  | TRUE
25 | bus_MV_175_0_node_14 | 20 | n |  | TRUE
26 | bus_MV_175_0_node_13 | 20 | n |  | TRUE
27 | bus_MV_175_0_node_17 | 20 | n |  | TRUE
28 | bus_MV_175_0_node_15 | 20 | n |  | TRUE
29 | bus_MV_175_0_node_16 | 20 | n |  | TRUE
30 | bus_MV_175_0_node_42 | 20 | n |  | TRUE
31 | bus_MV_175_0_node_43 | 20 | n |  | TRUE
32 | bus_MV_175_0_node_18 | 20 | n |  | TRUE
33 | bus_MV_175_0_node_19 | 20 | n |  | TRUE
34 | bus_MV_175_0_node_35 | 20 | n |  | TRUE
35 | bus_MV_175_0_node_24 | 20 | n |  | TRUE
36 | bus_MV_175_0_node_26 | 20 | n |  | TRUE
37 | bus_MV_175_0_node_25 | 20 | n |  | TRUE
38 | bus_MV_175_0_node_23 | 20 | n |  | TRUE
39 | bus_MV_175_0_node_20 | 20 | n |  | TRUE
40 | bus_MV_175_0_node_21 | 20 | n |  | TRUE
41 | bus_MV_175_0_node_22 | 20 | n |  | TRUE
42 | bus_MV_175_0_node_41 | 20 | n |  | TRUE
43 | bus_MV_175_0_node_29 | 20 | n |  | TRUE
44 | bus_MV_175_0_node_30 | 20 | n |  | TRUE
45 | bus_MV_175_0_node_32 | 20 | n |  | TRUE
46 | bus_MV_175_0_node_33 | 20 | n |  | TRUE
47 | bus_MV_175_0_node_34 | 20 | n |  | TRUE
48 | bus_MV_175_0_node_47 | 20 | n |  | TRUE
49 | bus_HV_175_0_node_32 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_175_0_load_0 | 0 | 0.16135 | 0.078147 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_175_0_load_3 | 2 | 0.13351 | 0.064662 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_175_0_load_27 | 6 | 0.1275 | 0.06175 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_175_0_load_40 | 7 | 0.15923 | 0.077119 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_175_0_load_4 | 9 | 0.099835 | 0.048352 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_175_0_load_44 | 13 | 0.12077 | 0.05849 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_175_0_load_37 | 15 | 0.14142 | 0.068493 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_175_0_load_7 | 17 | 0.12739 | 0.061699 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_175_0_load_49 | 22 | 0.058663 | 0.028412 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_175_0_load_36 | 23 | 0.064709 | 0.03134 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_175_0_load_12 | 24 | 0.070169 | 0.033984 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_175_0_load_43 | 31 | 0.10129 | 0.049057 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_175_0_load_19 | 33 | 0.14505 | 0.070251 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_175_0_load_35 | 34 | 0.12935 | 0.062646 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_175_0_load_26 | 36 | 0.15111 | 0.073184 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_175_0_load_25 | 37 | 0.1225 | 0.059331 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_175_0_load_23 | 38 | 0.11728 | 0.0568 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_175_0_load_20 | 39 | 0.14044 | 0.068019 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_175_0_load_41 | 42 | 0.092928 | 0.045007 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_175_0_load_29 | 43 | 0.34043 | 0.16488 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_175_0_load_34 | 47 | 0.1132 | 0.054827 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_175_0_load_47 | 48 | 0.059263 | 0.028702 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_175_0_line_0 |  | 0 | 1 | 0.018407 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_175_0_line_1 |  | 0 | 2 | 0.045624 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_175_0_line_2 |  | 1 | 3 | 0.16545 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_175_0_line_3 |  | 2 | 4 | 0.003479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_175_0_line_4 |  | 3 | 7 | 0.032079 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_175_0_line_5 |  | 4 | 5 | 0.06262 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_175_0_line_6 |  | 5 | 6 | 0.18394 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_175_0_line_7 |  | 6 | 43 | 0.015022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_175_0_line_8 |  | 6 | 44 | 0.16413 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_175_0_line_9 |  | 7 | 8 | 0.035542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_175_0_line_10 |  | 8 | 16 | 0.64717 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_175_0_line_11 |  | 9 | 10 | 0.08134 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_175_0_line_12 |  | 9 | 11 | 2.5043 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_175_0_line_13 |  | 10 | 12 | 0.64903 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_175_0_line_14 |  | 11 | 13 | 0.067172 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_175_0_line_15 |  | 12 | 15 | 0.08159 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_175_0_line_16 |  | 13 | 14 | 1.5905 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_175_0_line_17 |  | 14 | 48 | 0.14993 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_175_0_line_18 |  | 14 | 22 | 1.9889 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_175_0_line_19 |  | 15 | 16 | 0.14542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_175_0_line_20 |  | 17 | 18 | 0.085464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_175_0_line_21 |  | 17 | 19 | 0.10794 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_175_0_line_22 |  | 18 | 20 | 0.76222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_175_0_line_23 |  | 19 | 21 | 0.5412 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_175_0_line_24 |  | 20 | 22 | 0.072214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_175_0_line_25 |  | 21 | 23 | 0.22504 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_175_0_line_26 |  | 24 | 25 | 0.006081 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_175_0_line_27 |  | 24 | 26 | 0.051325 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_175_0_line_28 |  | 25 | 27 | 0.34969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_175_0_line_29 |  | 26 | 28 | 0.15789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_175_0_line_30 |  | 26 | 29 | 0.21891 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_175_0_line_31 |  | 27 | 34 | 0.019183 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_175_0_line_32 |  | 27 | 30 | 1.6588 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_175_0_line_33 |  | 28 | 32 | 0.287 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_175_0_line_34 |  | 29 | 33 | 0.095973 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_175_0_line_35 |  | 30 | 31 | 0.083703 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_175_0_line_36 |  | 31 | 46 | 0.12417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_175_0_line_37 |  | 32 | 35 | 0.24311 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_175_0_line_38 |  | 32 | 36 | 0.083939 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_175_0_line_39 |  | 32 | 37 | 0.12014 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_175_0_line_40 |  | 35 | 38 | 0.04796 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_175_0_line_41 |  | 38 | 39 | 0.22568 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_175_0_line_42 |  | 39 | 40 | 0.009292 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_175_0_line_43 |  | 40 | 41 | 0.24232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_175_0_line_44 |  | 41 | 42 | 0.073118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_175_0_line_45 |  | 44 | 45 | 0.10533 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_175_0_line_46 |  | 44 | 46 | 0.29723 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_175_0_line_47 |  | 45 | 47 | 0.093667 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_175_0_trafo_32 | 25 MVA 110/20 kV | 49 | 45 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2828678.0836 | 1165466.4781
1 | 2828661.4825 | 1165474.145
2 | 2828709.6947 | 1165499.3757
3 | 2828566.0883 | 1165401.6193
4 | 2828712.2818 | 1165501.7103
5 | 2828756.6619 | 1165546.0077
6 | 2828859.5133 | 1165698.5084
7 | 2828537.3745 | 1165413.4534
8 | 2828506.3406 | 1165418.558
9 | 2827056.274 | 1165490.1504
10 | 2827137.7849 | 1165487.381
11 | 2824612.3797 | 1166037.0948
12 | 2827663.906 | 1165288.6371
13 | 2824575.3382 | 1166093.1778
14 | 2824339.102 | 1167666.0601
15 | 2827742.0645 | 1165311.0792
16 | 2827887.4053 | 1165304.8889
17 | 2821754.2223 | 1168051.3961
18 | 2821836.6391 | 1168028.9777
19 | 2821653.0679 | 1168085.4493
20 | 2822326.855 | 1168028.3675
21 | 2821220.9662 | 1168390.1197
22 | 2822389.0943 | 1168057.5043
23 | 2821031.4137 | 1168268.815
24 | 2830267.3344 | 1167732.5983
25 | 2830273.0842 | 1167730.5716
26 | 2830241.2043 | 1167776.7737
27 | 2830372.8185 | 1167450.5608
28 | 2830232.8197 | 1167932.8549
29 | 2830423.2881 | 1167655.2572
30 | 2829325.5856 | 1166164.0633
31 | 2829291.8625 | 1166087.4617
32 | 2830278.7599 | 1168182.0868
33 | 2830387.3659 | 1167566.2602
34 | 2830389.7758 | 1167454.115
35 | 2830370.8334 | 1168359.0209
36 | 2830262.267 | 1168264.3892
37 | 2830198.0318 | 1168093.1078
38 | 2830388.2329 | 1168403.7093
39 | 2830373.4898 | 1168628.9094
40 | 2830382.4328 | 1168631.522
41 | 2830604.3262 | 1168724.0452
42 | 2830645.3706 | 1168663.4791
43 | 2828848.8608 | 1165709.1003
44 | 2828975.5159 | 1165814.3745
45 | 2828893.5441 | 1165836.525
46 | 2829212.2149 | 1165994.1336
47 | 2828839.2007 | 1165760.8876
48 | 2824362.4539 | 1167786.9086
49 | 2828893.5441 | 1165836.525

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99876 | 4.7764e-05 | 0.16135 | 0.078147
1 | 0.99874 | 0.00012184 | 0 | 0
2 | 0.99884 | 0.00096224 | 0.13351 | 0.064662
3 | 0.99857 | 0.00081095 | 0 | 0
4 | 0.99884 | 0.000936 | 0 | 0
5 | 0.99893 | 0.00046698 | 0 | 0
6 | 0.99932 | 0.0044761 | 0.1275 | 0.06175
7 | 0.99853 | 0.0009494 | 0.15923 | 0.077119
8 | 0.9985 | 0.0010367 | 0 | 0
9 | 0.99731 | 0.0056083 | 0.099835 | 0.048352
10 | 0.99736 | 0.0053503 | 0 | 0
11 | 0.99532 | -0.017845 | 0 | 0
12 | 0.99779 | 0.0036532 | 0 | 0
13 | 0.99528 | -0.017693 | 0.12077 | 0.05849
14 | 0.99439 | -0.029738 | 0 | 0
15 | 0.99784 | 0.0034854 | 0.14142 | 0.068493
16 | 0.99796 | 0.0029643 | 0 | 0
17 | 0.99327 | -0.041844 | 0.12739 | 0.061699
18 | 0.99329 | -0.041951 | 0 | 0
19 | 0.99326 | -0.041859 | 0 | 0
20 | 0.99347 | -0.04242 | 0 | 0
21 | 0.99322 | -0.041666 | 0 | 0
22 | 0.99349 | -0.042418 | 0.058663 | 0.028412
23 | 0.99319 | -0.041847 | 0.064709 | 0.03134
24 | 0.99553 | -0.014341 | 0.070169 | 0.033984
25 | 0.99553 | -0.014393 | 0 | 0
26 | 0.99545 | -0.014938 | 0 | 0
27 | 0.9959 | -0.017254 | 0 | 0
28 | 0.99533 | -0.013988 | 0 | 0
29 | 0.99539 | -0.015329 | 0 | 0
30 | 0.99897 | 0.0073838 | 0 | 0
31 | 0.99908 | 0.006609 | 0.10129 | 0.049057
32 | 0.9951 | -0.012165 | 0 | 0
33 | 0.99536 | -0.0155 | 0.14505 | 0.070251
34 | 0.9959 | -0.017225 | 0.12935 | 0.062646
35 | 0.99499 | -0.011322 | 0 | 0
36 | 0.99507 | -0.01232 | 0.15111 | 0.073184
37 | 0.99507 | -0.012345 | 0.1225 | 0.059331
38 | 0.99497 | -0.011145 | 0.11728 | 0.0568
39 | 0.99487 | -0.011939 | 0.14044 | 0.068019
40 | 0.99487 | -0.011933 | 0 | 0
41 | 0.99484 | -0.011733 | 0 | 0
42 | 0.99483 | -0.011654 | 0.092928 | 0.045007
43 | 0.99931 | 0.0045372 | 0.34043 | 0.16488
44 | 0.99965 | 0.0023615 | 0 | 0
45 | 1 | 0 | -2.8001 | -1.2063
46 | 0.99925 | 0.0053288 | 0 | 0
47 | 0.99999 | 0.00012018 | 0.1132 | 0.054827
48 | 0.99438 | -0.029648 | 0.059263 | 0.028702
49 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.83357 | 0.31002 | -0.83355 | -0.31045 | 1.624e-05 | -0.00043357 | 0.025705 | 0.02571 | 0.02571 | 0.99876 | 4.7764e-05 | 0.99874 | 0.00012184 | 11.6863
1 | -0.99492 | -0.38816 | 0.995 | 0.38816 | 7.7451e-05 | -5.822e-06 | 0.030868 | 0.030867 | 0.030868 | 0.99876 | 4.7764e-05 | 0.99884 | 0.00096224 | 14.6989
2 | 0.83355 | 0.31045 | -0.83341 | -0.31435 | 0.00014623 | -0.0038963 | 0.02571 | 0.02575 | 0.02575 | 0.99874 | 0.00012184 | 0.99857 | 0.00081095 | 11.7044
3 | -1.1285 | -0.45282 | 1.1285 | 0.45274 | 5.7358e-06 | -8.1171e-05 | 0.035143 | 0.035142 | 0.035143 | 0.99884 | 0.00096224 | 0.99884 | 0.000936 | 15.974
4 | 0.83341 | 0.31435 | -0.83338 | -0.3151 | 2.8404e-05 | -0.00075528 | 0.02575 | 0.025758 | 0.025758 | 0.99857 | 0.00081095 | 0.99853 | 0.0009494 | 11.708
5 | -1.1285 | -0.45274 | 1.1286 | 0.45128 | 0.00010319 | -0.0014612 | 0.035142 | 0.035126 | 0.035142 | 0.99884 | 0.000936 | 0.99893 | 0.00046698 | 15.9736
6 | -1.1286 | -0.45128 | 1.129 | 0.45131 | 0.00040433 | 3.4055e-05 | 0.035126 | 0.035123 | 0.035126 | 0.99893 | 0.00046698 | 0.99932 | 0.0044761 | 16.7266
7 | 0.34043 | 0.16452 | -0.34043 | -0.16488 | 2.3935e-06 | -0.00035747 | 0.010922 | 0.010927 | 0.010927 | 0.99932 | 0.0044761 | 0.99931 | 0.0045372 | 4.9668
8 | -1.597 | -0.67758 | 1.5975 | 0.67383 | 0.00054975 | -0.0037516 | 0.050112 | 0.050068 | 0.050112 | 0.99932 | 0.0044761 | 0.99965 | 0.0023615 | 22.7783
9 | 0.67415 | 0.23798 | -0.67413 | -0.23882 | 2.0277e-05 | -0.00084008 | 0.020668 | 0.020676 | 0.020676 | 0.99853 | 0.0009494 | 0.9985 | 0.0010367 | 9.3984
10 | 0.67413 | 0.23882 | -0.67375 | -0.25411 | 0.00037206 | -0.015287 | 0.020676 | 0.020829 | 0.020829 | 0.9985 | 0.0010367 | 0.99796 | 0.0029643 | 9.4679
11 | -0.53196 | -0.20826 | 0.53199 | 0.20633 | 2.9655e-05 | -0.0019229 | 0.016536 | 0.016515 | 0.016536 | 0.99731 | 0.0056083 | 0.99736 | 0.0053503 | 7.5162
12 | 0.43212 | 0.1599 | -0.43133 | -0.16237 | 0.00079545 | -0.0024695 | 0.013337 | 0.013367 | 0.013367 | 0.99731 | 0.0056083 | 0.99532 | -0.017845 | 6.3652
13 | -0.53199 | -0.20633 | 0.53222 | 0.19098 | 0.00023407 | -0.015352 | 0.016515 | 0.016359 | 0.016515 | 0.99736 | 0.0053503 | 0.99779 | 0.0036532 | 7.507
14 | 0.43133 | 0.16237 | -0.43131 | -0.16396 | 1.6042e-05 | -0.001584 | 0.013367 | 0.013383 | 0.013383 | 0.99532 | -0.017845 | 0.99528 | -0.017693 | 6.0833
15 | -0.53222 | -0.19098 | 0.53225 | 0.18905 | 2.9117e-05 | -0.0019309 | 0.016359 | 0.01634 | 0.016359 | 0.99779 | 0.0036532 | 0.99784 | 0.0034854 | 7.436
16 | 0.31054 | 0.10547 | -0.31029 | -0.10719 | 0.0002569 | -0.0017183 | 0.0095124 | 0.00953 | 0.00953 | 0.99528 | -0.017693 | 0.99439 | -0.029738 | 4.5381
17 | 0.059264 | 0.025163 | -0.059263 | -0.028702 | 7.1481e-07 | -0.0035394 | 0.0018691 | 0.0019116 | 0.0019116 | 0.99439 | -0.029738 | 0.99438 | -0.029648 | 0.86891
18 | 0.25102 | 0.082022 | -0.25081 | -0.084237 | 0.00020885 | -0.0022149 | 0.0076664 | 0.0076879 | 0.0076879 | 0.99439 | -0.029738 | 0.99349 | -0.042418 | 3.6609
19 | -0.67367 | -0.25754 | 0.67375 | 0.25411 | 8.4371e-05 | -0.0034325 | 0.020865 | 0.020829 | 0.020865 | 0.99784 | 0.0034854 | 0.99796 | 0.0029643 | 9.484
20 | -0.19211 | -0.077486 | 0.19211 | 0.075474 | 4.1203e-06 | -0.002012 | 0.0060203 | 0.0059987 | 0.0060203 | 0.99327 | -0.041844 | 0.99329 | -0.041951 | 2.7365
21 | 0.064715 | 0.015787 | -0.064714 | -0.01833 | 5.4519e-07 | -0.0025426 | 0.001936 | 0.0019548 | 0.0019548 | 0.99327 | -0.041844 | 0.99326 | -0.041859 | 0.88854
22 | -0.19211 | -0.075474 | 0.19215 | 0.057526 | 3.552e-05 | -0.017948 | 0.0059987 | 0.0058281 | 0.0059987 | 0.99329 | -0.041951 | 0.99347 | -0.04242 | 2.7267
23 | 0.064714 | 0.01833 | -0.064711 | -0.031076 | 2.9282e-06 | -0.012747 | 0.0019548 | 0.0020864 | 0.0020864 | 0.99326 | -0.041859 | 0.99322 | -0.041666 | 0.94838
24 | -0.19215 | -0.057526 | 0.19215 | 0.055826 | 3.2667e-06 | -0.0017008 | 0.0058281 | 0.0058141 | 0.0058281 | 0.99347 | -0.04242 | 0.99349 | -0.042418 | 2.6491
25 | 0.064711 | 0.031076 | -0.064709 | -0.03134 | 1.7483e-06 | -0.00026393 | 0.0020864 | 0.0020898 | 0.0020898 | 0.99322 | -0.041666 | 0.99319 | -0.041847 | 0.99514
26 | -0.83986 | -0.3807 | 0.83986 | 0.38056 | 5.8038e-06 | -0.00014217 | 0.026739 | 0.026737 | 0.026739 | 0.99553 | -0.014341 | 0.99553 | -0.014393 | 12.154
27 | 0.76969 | 0.34672 | -0.76963 | -0.34675 | 5.4797e-05 | -2.6397e-05 | 0.024479 | 0.02448 | 0.02448 | 0.99553 | -0.014341 | 0.99545 | -0.014938 | 11.6569
28 | -0.83986 | -0.38056 | 0.8402 | 0.37238 | 0.00033249 | -0.0081792 | 0.026737 | 0.026639 | 0.026737 | 0.99553 | -0.014393 | 0.9959 | -0.017254 | 12.1532
29 | 0.62457 | 0.27686 | -0.62449 | -0.28057 | 8.292e-05 | -0.0037105 | 0.019812 | 0.019856 | 0.019856 | 0.99545 | -0.014938 | 0.99533 | -0.013988 | 9.0255
30 | 0.14506 | 0.069886 | -0.14505 | -0.07014 | 8.5101e-06 | -0.00025361 | 0.0046695 | 0.0046727 | 0.0046727 | 0.99545 | -0.014938 | 0.99539 | -0.015329 | 2.2251
31 | 0.12935 | 0.062192 | -0.12935 | -0.062646 | 4.4385e-07 | -0.00045414 | 0.0041602 | 0.0041659 | 0.0041659 | 0.9959 | -0.017254 | 0.9959 | -0.017225 | 1.8936
32 | -0.96955 | -0.43457 | 0.97235 | 0.43436 | 0.0028012 | -0.00021565 | 0.030797 | 0.030774 | 0.030797 | 0.9959 | -0.017254 | 0.99897 | 0.0073838 | 14.6654
33 | 0.62449 | 0.28057 | -0.62434 | -0.28731 | 0.00015168 | -0.0067421 | 0.019856 | 0.019938 | 0.019938 | 0.99533 | -0.013988 | 0.9951 | -0.012165 | 9.0625
34 | 0.14505 | 0.07014 | -0.14505 | -0.070251 | 3.7347e-06 | -0.00011118 | 0.0046727 | 0.0046742 | 0.0046742 | 0.99539 | -0.015329 | 0.99536 | -0.0155 | 2.2258
35 | -0.97235 | -0.43436 | 0.97245 | 0.4324 | 0.00010575 | -0.0019632 | 0.030774 | 0.030751 | 0.030774 | 0.99897 | 0.0073838 | 0.99908 | 0.006609 | 13.9882
36 | -1.0737 | -0.48145 | 1.0739 | 0.47855 | 0.00019145 | -0.002903 | 0.034001 | 0.033966 | 0.034001 | 0.99908 | 0.006609 | 0.99925 | 0.0053288 | 15.455
37 | 0.35072 | 0.15503 | -0.35068 | -0.16077 | 4.0408e-05 | -0.0057352 | 0.011124 | 0.011193 | 0.011193 | 0.9951 | -0.012165 | 0.99499 | -0.011322 | 5.0875
38 | 0.15111 | 0.073087 | -0.15111 | -0.073184 | 3.5471e-06 | -9.7002e-05 | 0.0048695 | 0.0048707 | 0.0048707 | 0.9951 | -0.012165 | 0.99507 | -0.01232 | 2.3194
39 | 0.12251 | 0.059191 | -0.1225 | -0.059331 | 3.3362e-06 | -0.00013993 | 0.0039469 | 0.0039487 | 0.0039487 | 0.9951 | -0.012165 | 0.99507 | -0.012345 | 1.8803
40 | 0.35068 | 0.16077 | -0.35067 | -0.1619 | 8.0306e-06 | -0.0011312 | 0.011193 | 0.011206 | 0.011206 | 0.99499 | -0.011322 | 0.99497 | -0.011145 | 5.0938
41 | 0.2334 | 0.1051 | -0.23337 | -0.10535 | 2.2187e-05 | -0.00025279 | 0.0074265 | 0.0074297 | 0.0074297 | 0.99497 | -0.011145 | 0.99487 | -0.011939 | 3.538
42 | 0.092932 | 0.037335 | -0.092932 | -0.037554 | 1.0486e-07 | -0.00021955 | 0.002906 | 0.0029084 | 0.0029084 | 0.99487 | -0.011939 | 0.99487 | -0.011933 | 1.322
43 | 0.092932 | 0.037554 | -0.092929 | -0.04328 | 2.7972e-06 | -0.0057255 | 0.0029084 | 0.0029746 | 0.0029746 | 0.99487 | -0.011933 | 0.99484 | -0.011733 | 1.3521
44 | 0.092929 | 0.04328 | -0.092928 | -0.045007 | 8.6994e-07 | -0.0017275 | 0.0029746 | 0.0029962 | 0.0029962 | 0.99484 | -0.011733 | 0.99483 | -0.011654 | 1.3619
45 | -2.6719 | -1.1454 | 2.6729 | 1.1432 | 0.00099064 | -0.0022201 | 0.083949 | 0.083921 | 0.083949 | 0.99965 | 0.0023615 | 1 | 0 | 38.1588
46 | 1.0744 | 0.4716 | -1.0739 | -0.47855 | 0.00045667 | -0.0069534 | 0.033883 | 0.033966 | 0.033966 | 0.99965 | 0.0023615 | 0.99925 | 0.0053288 | 15.4391
47 | 0.11321 | 0.052591 | -0.1132 | -0.054827 | 1.636e-06 | -0.0022359 | 0.0036034 | 0.0036311 | 0.0036311 | 1 | 0 | 0.99999 | 0.00012018 | 1.6505

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 2.8001 | 1.2063

## res_load
| p_mw | q_mvar
0 | 0.16135 | 0.078147
1 | 0.13351 | 0.064662
2 | 0.1275 | 0.06175
3 | 0.15923 | 0.077119
4 | 0.099835 | 0.048352
5 | 0.12077 | 0.05849
6 | 0.14142 | 0.068493
7 | 0.12739 | 0.061699
8 | 0.058663 | 0.028412
9 | 0.064709 | 0.03134
10 | 0.070169 | 0.033984
11 | 0.10129 | 0.049057
12 | 0.14505 | 0.070251
13 | 0.12935 | 0.062646
14 | 0.15111 | 0.073184
15 | 0.1225 | 0.059331
16 | 0.11728 | 0.0568
17 | 0.14044 | 0.068019
18 | 0.092928 | 0.045007
19 | 0.34043 | 0.16488
20 | 0.1132 | 0.054827
21 | 0.059263 | 0.028702

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1