## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_176_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_176_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_176_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_176_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_176_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_176_0_node_5 | 20 | n |  | TRUE
6 | bus_MV_176_0_node_6 | 20 | n |  | TRUE
7 | bus_MV_176_0_node_7 | 20 | n |  | TRUE
8 | bus_MV_176_0_node_8 | 20 | n |  | TRUE
9 | bus_MV_176_0_node_87 | 20 | n |  | TRUE
10 | bus_MV_176_0_node_9 | 20 | n |  | TRUE
11 | bus_MV_176_0_node_10 | 20 | n |  | TRUE
12 | bus_MV_176_0_node_83 | 20 | n |  | TRUE
13 | bus_MV_176_0_node_12 | 20 | n |  | TRUE
14 | bus_MV_176_0_node_14 | 20 | n |  | TRUE
15 | bus_MV_176_0_node_15 | 20 | n |  | TRUE
16 | bus_MV_176_0_node_17 | 20 | n |  | TRUE
17 | bus_MV_176_0_node_18 | 20 | n |  | TRUE
18 | bus_MV_176_0_node_219 | 20 | n |  | TRUE
19 | bus_MV_176_0_node_218 | 20 | n |  | TRUE
20 | bus_MV_176_0_node_31 | 20 | n |  | TRUE
21 | bus_MV_176_0_node_19 | 20 | n |  | TRUE
22 | bus_MV_176_0_node_20 | 20 | n |  | TRUE
23 | bus_MV_176_0_node_21 | 20 | n |  | TRUE
24 | bus_MV_176_0_node_22 | 20 | n |  | TRUE
25 | bus_MV_176_0_node_23 | 20 | n |  | TRUE
26 | bus_MV_176_0_node_225 | 20 | n |  | TRUE
27 | bus_MV_176_0_node_226 | 20 | n |  | TRUE
28 | bus_MV_176_0_node_25 | 20 | n |  | TRUE
29 | bus_MV_176_0_node_26 | 20 | n |  | TRUE
30 | bus_MV_176_0_node_28 | 20 | n |  | TRUE
31 | bus_MV_176_0_node_30 | 20 | n |  | TRUE
32 | bus_MV_176_0_node_27 | 20 | n |  | TRUE
33 | bus_MV_176_0_node_29 | 20 | n |  | TRUE
34 | bus_MV_176_0_node_221 | 20 | n |  | TRUE
35 | bus_MV_176_0_node_33 | 20 | n |  | TRUE
36 | bus_MV_176_0_node_32 | 20 | n |  | TRUE
37 | bus_MV_176_0_node_34 | 20 | n |  | TRUE
38 | bus_MV_176_0_node_236 | 20 | n |  | TRUE
39 | bus_MV_176_0_node_35 | 20 | n |  | TRUE
40 | bus_MV_176_0_node_36 | 20 | n |  | TRUE
41 | bus_MV_176_0_node_37 | 20 | n |  | TRUE
42 | bus_MV_176_0_node_38 | 20 | n |  | TRUE
43 | bus_MV_176_0_node_39 | 20 | n |  | TRUE
44 | bus_MV_176_0_node_44 | 20 | n |  | TRUE
45 | bus_MV_176_0_node_41 | 20 | n |  | TRUE
46 | bus_MV_176_0_node_57 | 20 | n |  | TRUE
47 | bus_MV_176_0_node_40 | 20 | n |  | TRUE
48 | bus_MV_176_0_node_42 | 20 | n |  | TRUE
49 | bus_MV_176_0_node_48 | 20 | n |  | TRUE
50 | bus_MV_176_0_node_47 | 20 | n |  | TRUE
51 | bus_MV_176_0_node_45 | 20 | n |  | TRUE
52 | bus_MV_176_0_node_46 | 20 | n |  | TRUE
53 | bus_MV_176_0_node_56 | 20 | n |  | TRUE
54 | bus_MV_176_0_node_49 | 20 | n |  | TRUE
55 | bus_MV_176_0_node_52 | 20 | n |  | TRUE
56 | bus_MV_176_0_node_50 | 20 | n |  | TRUE
57 | bus_MV_176_0_node_59 | 20 | n |  | TRUE
58 | bus_MV_176_0_node_51 | 20 | n |  | TRUE
59 | bus_MV_176_0_node_53 | 20 | n |  | TRUE
60 | bus_MV_176_0_node_54 | 20 | n |  | TRUE
61 | bus_MV_176_0_node_55 | 20 | n |  | TRUE
62 | bus_MV_176_0_node_76 | 20 | n |  | TRUE
63 | bus_MV_176_0_node_58 | 20 | n |  | TRUE
64 | bus_MV_176_0_node_60 | 20 | n |  | TRUE
65 | bus_MV_176_0_node_227 | 20 | n |  | TRUE
66 | bus_MV_176_0_node_61 | 20 | n |  | TRUE
67 | bus_MV_176_0_node_62 | 20 | n |  | TRUE
68 | bus_MV_176_0_node_63 | 20 | n |  | TRUE
69 | bus_MV_176_0_node_64 | 20 | n |  | TRUE
70 | bus_MV_176_0_node_65 | 20 | n |  | TRUE
71 | bus_MV_176_0_node_66 | 20 | n |  | TRUE
72 | bus_MV_176_0_node_67 | 20 | n |  | TRUE
73 | bus_MV_176_0_node_222 | 20 | n |  | TRUE
74 | bus_MV_176_0_node_69 | 20 | n |  | TRUE
75 | bus_MV_176_0_node_77 | 20 | n |  | TRUE
76 | bus_MV_176_0_node_68 | 20 | n |  | TRUE
77 | bus_MV_176_0_node_70 | 20 | n |  | TRUE
78 | bus_MV_176_0_node_71 | 20 | n |  | TRUE
79 | bus_MV_176_0_node_72 | 20 | n |  | TRUE
80 | bus_MV_176_0_node_78 | 20 | n |  | TRUE
81 | bus_MV_176_0_node_73 | 20 | n |  | TRUE
82 | bus_MV_176_0_node_74 | 20 | n |  | TRUE
83 | bus_MV_176_0_node_75 | 20 | n |  | TRUE
84 | bus_MV_176_0_node_239 | 20 | n |  | TRUE
85 | bus_MV_176_0_node_79 | 20 | n |  | TRUE
86 | bus_MV_176_0_node_80 | 20 | n |  | TRUE
87 | bus_MV_176_0_node_81 | 20 | n |  | TRUE
88 | bus_MV_176_0_node_82 | 20 | n |  | TRUE
89 | bus_MV_176_0_node_230 | 20 | n |  | TRUE
90 | bus_MV_176_0_node_229 | 20 | n |  | TRUE
91 | bus_MV_176_0_node_88 | 20 | n |  | TRUE
92 | bus_MV_176_0_node_84 | 20 | n |  | TRUE
93 | bus_MV_176_0_node_90 | 20 | n |  | TRUE
94 | bus_MV_176_0_node_85 | 20 | n |  | TRUE
95 | bus_MV_176_0_node_86 | 20 | n |  | TRUE
96 | bus_MV_176_0_node_89 | 20 | n |  | TRUE
97 | bus_MV_176_0_node_232 | 20 | n |  | TRUE
98 | bus_MV_176_0_node_217 | 20 | n |  | TRUE
99 | bus_MV_176_0_node_220 | 20 | n |  | TRUE
100 | bus_MV_176_0_node_228 | 20 | n |  | TRUE
101 | bus_MV_176_0_node_231 | 20 | n |  | TRUE
102 | bus_HV_176_0_node_81 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_176_0_load_0 | 0 | 0.15436 | 0.074759 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_176_0_load_6 | 6 | 0.15986 | 0.077426 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_176_0_load_7 | 7 | 0.080128 | 0.038808 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_176_0_load_8 | 8 | 0.087989 | 0.042615 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_176_0_load_87 | 9 | 0.064084 | 0.031037 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_176_0_load_83 | 12 | 0.13129 | 0.063586 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_176_0_load_12 | 13 | 0.13412 | 0.064956 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_176_0_load_219 | 18 | 0.18329 | 0.088773 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_176_0_load_31 | 20 | 0.14845 | 0.071895 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_176_0_load_19 | 21 | 0.1366 | 0.066158 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_176_0_load_23 | 25 | 0.13541 | 0.065583 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_176_0_load_225 | 26 | 0.078141 | 0.037845 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_176_0_load_30 | 31 | 0.064949 | 0.031456 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_176_0_load_27 | 32 | 0.051007 | 0.024704 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_176_0_load_221 | 34 | 0.14942 | 0.072368 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_176_0_load_32 | 36 | 0.06374 | 0.030871 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_176_0_load_236 | 38 | 0.14387 | 0.069682 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_176_0_load_35 | 39 | 0.10884 | 0.052711 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_176_0_load_38 | 42 | 0.11654 | 0.056443 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_176_0_load_57 | 46 | 0.090045 | 0.043611 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_176_0_load_40 | 47 | 0.15485 | 0.074999 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_176_0_load_48 | 49 | 0.15503 | 0.075086 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_176_0_load_56 | 53 | 0.12405 | 0.060081 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_176_0_load_49 | 54 | 0.118 | 0.057149 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_176_0_load_52 | 55 | 0.14298 | 0.06925 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_176_0_load_53 | 59 | 0.11839 | 0.057339 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_176_0_load_76 | 62 | 0.078648 | 0.038091 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_176_0_load_58 | 63 | 0.10628 | 0.051475 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_176_0_load_227 | 65 | 0.11988 | 0.058058 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_176_0_load_61 | 66 | 0.15663 | 0.075859 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_176_0_load_64 | 69 | 0.16379 | 0.079329 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_176_0_load_65 | 70 | 0.095113 | 0.046065 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_176_0_load_67 | 72 | 0.12433 | 0.060217 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_176_0_load_222 | 73 | 0.1367 | 0.066207 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_176_0_load_77 | 75 | 0.14576 | 0.070595 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_176_0_load_68 | 76 | 0.1611 | 0.078023 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_176_0_load_70 | 77 | 0.16093 | 0.077941 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_176_0_load_78 | 80 | 0.075072 | 0.036359 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_176_0_load_239 | 84 | 0.12678 | 0.061404 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_176_0_load_79 | 85 | 0.09147 | 0.044301 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_176_0_load_80 | 86 | 0.15059 | 0.072933 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_176_0_load_229 | 90 | 0.13218 | 0.064018 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_176_0_load_88 | 91 | 0.1147 | 0.055552 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_176_0_load_84 | 92 | 0.15726 | 0.076164 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_176_0_load_85 | 94 | 0.077609 | 0.037588 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_176_0_load_232 | 97 | 0.096489 | 0.046732 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_176_0_load_217 | 98 | 0.080156 | 0.038821 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_176_0_load_220 | 99 | 0.14996 | 0.072627 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_176_0_load_228 | 100 | 0.12395 | 0.060033 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_176_0_load_231 | 101 | 0.11067 | 0.053599 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 87 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_176_0_line_0 |  | 0 | 1 | 0.039225 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_176_0_line_1 |  | 0 | 2 | 0.03959 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_176_0_line_2 |  | 1 | 3 | 0.24471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_176_0_line_3 |  | 2 | 4 | 0.24197 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_176_0_line_4 |  | 3 | 5 | 1.2445 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
5 | MV_176_0_line_5 |  | 3 | 6 | 0.043391 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
6 | MV_176_0_line_6 |  | 4 | 7 | 0.10003 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_176_0_line_7 |  | 5 | 8 | 0.004007 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
8 | MV_176_0_line_8 |  | 6 | 9 | 1.2916 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
9 | MV_176_0_line_9 |  | 8 | 10 | 0.26259 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
10 | MV_176_0_line_10 |  | 9 | 17 | 1.5711 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
11 | MV_176_0_line_11 |  | 9 | 94 | 1.024 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_176_0_line_12 |  | 10 | 11 | 1.3357 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
13 | MV_176_0_line_13 |  | 11 | 12 | 0.068453 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
14 | MV_176_0_line_14 |  | 12 | 83 | 0.020367 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
15 | MV_176_0_line_15 |  | 13 | 14 | 0.057304 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_176_0_line_16 |  | 13 | 15 | 0.065757 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_176_0_line_17 |  | 14 | 16 | 0.083704 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_176_0_line_18 |  | 15 | 17 | 0.21802 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_176_0_line_19 |  | 16 | 18 | 0.036935 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_176_0_line_20 |  | 16 | 19 | 0.03744 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_176_0_line_21 |  | 17 | 20 | 0.054564 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_176_0_line_22 |  | 18 | 99 | 0.087244 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_176_0_line_23 |  | 19 | 98 | 0.019168 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_176_0_line_24 |  | 21 | 22 | 0.11538 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_176_0_line_25 |  | 22 | 23 | 0.40073 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_176_0_line_26 |  | 22 | 24 | 1.1608 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_176_0_line_27 |  | 23 | 25 | 0.047735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_176_0_line_28 |  | 24 | 26 | 0.089279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_176_0_line_29 |  | 24 | 27 | 1.2384 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_176_0_line_30 |  | 27 | 100 | 0.018396 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_176_0_line_31 |  | 27 | 33 | 0.9663 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_176_0_line_32 |  | 28 | 29 | 1.2365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_176_0_line_33 |  | 28 | 30 | 0.21087 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_176_0_line_34 |  | 29 | 31 | 0.025485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_176_0_line_35 |  | 30 | 33 | 0.22796 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_176_0_line_36 |  | 30 | 32 | 0.12443 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_176_0_line_37 |  | 33 | 34 | 0.14189 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_176_0_line_38 |  | 33 | 35 | 0.34679 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_176_0_line_39 |  | 34 | 99 | 0.1576 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_176_0_line_40 |  | 35 | 37 | 0.14386 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_176_0_line_41 |  | 35 | 36 | 0.029832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_176_0_line_42 |  | 37 | 38 | 0.04537 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_176_0_line_43 |  | 39 | 40 | 0.060647 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_176_0_line_44 |  | 40 | 41 | 0.14704 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_176_0_line_45 |  | 41 | 42 | 0.088636 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_176_0_line_46 |  | 41 | 43 | 0.18266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_176_0_line_47 |  | 42 | 44 | 0.06752 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_176_0_line_48 |  | 43 | 45 | 0.30101 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_176_0_line_49 |  | 43 | 46 | 0.062982 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_176_0_line_50 |  | 44 | 50 | 0.091289 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_176_0_line_51 |  | 45 | 48 | 0.088453 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_176_0_line_52 |  | 45 | 47 | 0.072685 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_176_0_line_53 |  | 48 | 49 | 0.059495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_176_0_line_54 |  | 50 | 55 | 0.082075 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_176_0_line_55 |  | 50 | 51 | 0.10147 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_176_0_line_56 |  | 51 | 52 | 0.1257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_176_0_line_57 |  | 51 | 53 | 0.006431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_176_0_line_58 |  | 52 | 54 | 0.081515 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_176_0_line_59 |  | 54 | 56 | 0.056189 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_176_0_line_60 |  | 54 | 57 | 0.98735 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_176_0_line_61 |  | 56 | 58 | 0.043934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_176_0_line_62 |  | 57 | 64 | 0.28793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_176_0_line_63 |  | 57 | 63 | 0.16526 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_176_0_line_64 |  | 58 | 59 | 0.083675 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_176_0_line_65 |  | 59 | 60 | 0.10169 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_176_0_line_66 |  | 60 | 61 | 1.1975 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_176_0_line_67 |  | 61 | 62 | 0.1555 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_176_0_line_68 |  | 62 | 76 | 0.4672 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
69 | MV_176_0_line_69 |  | 64 | 65 | 0.004554 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_176_0_line_70 |  | 66 | 67 | 0.037777 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_176_0_line_71 |  | 67 | 68 | 0.021404 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_176_0_line_72 |  | 68 | 69 | 0.042499 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_176_0_line_73 |  | 68 | 70 | 0.042507 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_176_0_line_74 |  | 68 | 71 | 0.13648 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_176_0_line_75 |  | 69 | 72 | 0.10162 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_176_0_line_76 |  | 70 | 73 | 0.10434 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
77 | MV_176_0_line_77 |  | 71 | 74 | 0.03231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_176_0_line_78 |  | 71 | 75 | 0.029764 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_176_0_line_79 |  | 73 | 81 | 0.017833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_176_0_line_80 |  | 74 | 76 | 0.044744 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_176_0_line_81 |  | 77 | 78 | 0.010079 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_176_0_line_82 |  | 77 | 79 | 0.11253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_176_0_line_83 |  | 77 | 80 | 0.15404 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
84 | MV_176_0_line_84 |  | 78 | 81 | 0.34887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_176_0_line_85 |  | 78 | 82 | 0.17345 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_176_0_line_86 |  | 79 | 83 | 0.29267 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_176_0_line_87 |  | 81 | 84 | 0.082351 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
88 | MV_176_0_line_88 |  | 82 | 85 | 0.043177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_176_0_line_89 |  | 83 | 86 | 0.69891 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
90 | MV_176_0_line_90 |  | 86 | 87 | 0.047464 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
91 | MV_176_0_line_91 |  | 88 | 89 | 0.40953 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_176_0_line_92 |  | 88 | 90 | 0.20636 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
93 | MV_176_0_line_93 |  | 88 | 91 | 0.22491 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
94 | MV_176_0_line_94 |  | 89 | 101 | 0.028333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_176_0_line_95 |  | 91 | 96 | 0.0838 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_176_0_line_96 |  | 92 | 93 | 5.6024 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
97 | MV_176_0_line_97 |  | 93 | 97 | 0.012163 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_176_0_line_98 |  | 94 | 95 | 0.093719 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_176_0_line_99 |  | 95 | 96 | 1.2194 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_176_0_line_100 |  | 97 | 101 | 0.065794 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_176_0_trafo_81 | 25 MVA 110/20 kV | 102 | 87 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2775427.0089 | 1198563.8594
1 | 2775411.3281 | 1198599.8228
2 | 2775397.9326 | 1198541.0956
3 | 2775584.6568 | 1198633.3427
4 | 2775163.7318 | 1198579.8001
5 | 2776294.1399 | 1198481.1294
6 | 2775600.2399 | 1198673.8393
7 | 2775070.1973 | 1198615.2501
8 | 2776298.158 | 1198481.0701
9 | 2775364.4394 | 1199943.7728
10 | 2776371.2361 | 1198644.75
11 | 2777391.7132 | 1198502.2465
12 | 2777383.1041 | 1198551.2524
13 | 2773546.4918 | 1200056.7676
14 | 2773578.7046 | 1200104.2149
15 | 2773609.4728 | 1200037.2779
16 | 2773513.0536 | 1200156.3585
17 | 2773793.2972 | 1199946.3997
18 | 2773483.8156 | 1200178.9005
19 | 2773526.4889 | 1200190.5923
20 | 2773738.8527 | 1199950.0093
21 | 2772725.2759 | 1201185.0984
22 | 2772833.536 | 1201225.8561
23 | 2772603.3546 | 1201066.3963
24 | 2773158.4645 | 1201635.3083
25 | 2772555.6917 | 1201061.9045
26 | 2773132.3712 | 1201720.5893
27 | 2773573.9771 | 1201333.4297
28 | 2772873.9819 | 1200286.0756
29 | 2772442.7509 | 1200698.7774
30 | 2772996.803 | 1200457.4813
31 | 2772465.9432 | 1200709.2232
32 | 2772911.1584 | 1200547.9335
33 | 2773200.1733 | 1200442.3567
34 | 2773305.072 | 1200346.5282
35 | 2773174.113 | 1200096.5499
36 | 2773145.6556 | 1200087.3834
37 | 2773263.3238 | 1200061.3127
38 | 2773258.6902 | 1200016.191
39 | 2780865.4674 | 1198244.1523
40 | 2780804.8291 | 1198243.1174
41 | 2780663.5565 | 1198284.7772
42 | 2780576.2299 | 1198292.736
43 | 2780729.2201 | 1198138.3394
44 | 2780511.5848 | 1198311.0688
45 | 2780870.1612 | 1197953.6966
46 | 2780674.3831 | 1198169.3138
47 | 2780921.6682 | 1197902.9826
48 | 2780821.7791 | 1197903.9732
49 | 2780772.0486 | 1197936.631
50 | 2780430.842 | 1198353.6626
51 | 2780349.1248 | 1198293.5158
52 | 2780249.0868 | 1198330.747
53 | 2780343.0393 | 1198295.6454
54 | 2780168.2666 | 1198341.366
55 | 2780398.188 | 1198428.9626
56 | 2780125.2893 | 1198374.6928
57 | 2779751.6751 | 1197446.2052
58 | 2780154.0556 | 1198407.97
59 | 2780087.8699 | 1198459.2933
60 | 2780010.0559 | 1198525.0036
61 | 2778851.6197 | 1198563.4097
62 | 2778788.4349 | 1198618.3069
63 | 2779603.5573 | 1197519.4933
64 | 2779847.0863 | 1197245.4882
65 | 2779844.5552 | 1197241.6973
66 | 2778178.5076 | 1198542.3809
67 | 2778146.4219 | 1198562.322
68 | 2778142.7134 | 1198583.1762
69 | 2778136.3783 | 1198624.639
70 | 2778100.889 | 1198589.5659
71 | 2778254.7437 | 1198540.3068
72 | 2778099.2273 | 1198685.6583
73 | 2778002.0862 | 1198623.1156
74 | 2778280.5406 | 1198557.1924
75 | 2778271.4014 | 1198515.8685
76 | 2778324.2788 | 1198565.1045
77 | 2777684.6276 | 1198565.2721
78 | 2777687.6723 | 1198555.6644
79 | 2777589.3669 | 1198557.4565
80 | 2777742.4072 | 1198708.0616
81 | 2777985.8147 | 1198615.7129
82 | 2777599.3482 | 1198482.9473
83 | 2777388.4017 | 1198569.6136
84 | 2777959.0298 | 1198537.8399
85 | 2777557.7225 | 1198471.0995
86 | 2777186.3693 | 1199238.6829
87 | 2777154.9534 | 1199271.9953
88 | 2777333.5708 | 1199840.9438
89 | 2777612.074 | 1200080.1453
90 | 2777128.0405 | 1199822.5099
91 | 2777297.4543 | 1200062.9327
92 | 2780690.6481 | 1204801.6701
93 | 2777569.616 | 1200149.1955
94 | 2776076.535 | 1200679.6509
95 | 2776155.7524 | 1200646.0193
96 | 2777258.0686 | 1200124.6024
97 | 2777567.5955 | 1200137.2016
98 | 2773511.8812 | 1200203.0023
99 | 2773419.431 | 1200237.7747
100 | 2773574.5473 | 1201351.8083
101 | 2777625.1394 | 1200105.3025
102 | 2777154.9534 | 1199271.9953

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99063 | -0.19577 | 0.15436 | 0.074759
1 | 0.99064 | -0.19587 | 0 | 0
2 | 0.99062 | -0.19575 | 0 | 0
3 | 0.99071 | -0.1964 | 0 | 0
4 | 0.9906 | -0.19556 | 0 | 0
5 | 0.99256 | -0.17106 | 0 | 0
6 | 0.99058 | -0.19999 | 0.15986 | 0.077426
7 | 0.99058 | -0.19566 | 0.080128 | 0.038808
8 | 0.99257 | -0.17097 | 0.087989 | 0.042615
9 | 0.98702 | -0.30094 | 0.064084 | 0.031037
10 | 0.99297 | -0.16535 | 0 | 0
11 | 0.99499 | -0.13597 | 0 | 0
12 | 0.9951 | -0.13443 | 0.13129 | 0.063586
13 | 0.98355 | -0.38464 | 0.13412 | 0.064956
14 | 0.98345 | -0.38415 | 0 | 0
15 | 0.98367 | -0.3853 | 0 | 0
16 | 0.9833 | -0.38343 | 0 | 0
17 | 0.98408 | -0.38745 | 0 | 0
18 | 0.98325 | -0.38314 | 0.18329 | 0.088773
19 | 0.9833 | -0.38339 | 0 | 0
20 | 0.98407 | -0.38755 | 0.14845 | 0.071895
21 | 0.98094 | -0.39327 | 0.1366 | 0.066158
22 | 0.98096 | -0.39345 | 0 | 0
23 | 0.98089 | -0.39293 | 0 | 0
24 | 0.98136 | -0.39536 | 0 | 0
25 | 0.98088 | -0.39285 | 0.13541 | 0.065583
26 | 0.98135 | -0.39528 | 0.078141 | 0.037845
27 | 0.9819 | -0.39616 | 0 | 0
28 | 0.98269 | -0.38526 | 0 | 0
29 | 0.98259 | -0.38548 | 0 | 0
30 | 0.98271 | -0.38455 | 0 | 0
31 | 0.98259 | -0.38546 | 0.064949 | 0.031456
32 | 0.9827 | -0.38448 | 0.051007 | 0.024704
33 | 0.98274 | -0.38435 | 0 | 0
34 | 0.98288 | -0.38467 | 0.14942 | 0.072368
35 | 0.9826 | -0.38541 | 0 | 0
36 | 0.9826 | -0.38539 | 0.06374 | 0.030871
37 | 0.98257 | -0.38518 | 0 | 0
38 | 0.98256 | -0.3851 | 0.14387 | 0.069682
39 | 0.98666 | -0.10322 | 0.10884 | 0.052711
40 | 0.98668 | -0.10313 | 0 | 0
41 | 0.9867 | -0.10331 | 0 | 0
42 | 0.98675 | -0.10374 | 0.11654 | 0.056443
43 | 0.9866 | -0.1026 | 0 | 0
44 | 0.98681 | -0.10415 | 0 | 0
45 | 0.98648 | -0.10163 | 0 | 0
46 | 0.9866 | -0.10254 | 0.090045 | 0.043611
47 | 0.98647 | -0.10149 | 0.15485 | 0.074999
48 | 0.98647 | -0.10147 | 0 | 0
49 | 0.98645 | -0.10136 | 0.15503 | 0.075086
50 | 0.98688 | -0.1047 | 0 | 0
51 | 0.98703 | -0.10349 | 0 | 0
52 | 0.98717 | -0.10463 | 0 | 0
53 | 0.98703 | -0.10348 | 0.12405 | 0.060081
54 | 0.98731 | -0.10351 | 0.118 | 0.057149
55 | 0.98686 | -0.10484 | 0.14298 | 0.06925
56 | 0.9874 | -0.10422 | 0 | 0
57 | 0.98688 | -0.10693 | 0 | 0
58 | 0.98747 | -0.10477 | 0 | 0
59 | 0.9876 | -0.10581 | 0.11839 | 0.057339
60 | 0.98778 | -0.10721 | 0 | 0
61 | 0.98985 | -0.12245 | 0 | 0
62 | 0.99012 | -0.12426 | 0.078648 | 0.038091
63 | 0.98685 | -0.10715 | 0.10628 | 0.051475
64 | 0.98684 | -0.10657 | 0 | 0
65 | 0.98684 | -0.10656 | 0.11988 | 0.058058
66 | 0.99184 | -0.11615 | 0.15663 | 0.075859
67 | 0.99185 | -0.11608 | 0 | 0
68 | 0.99185 | -0.11612 | 0 | 0
69 | 0.99184 | -0.11598 | 0.16379 | 0.079329
70 | 0.99197 | -0.11701 | 0.095113 | 0.046065
71 | 0.99155 | -0.11394 | 0 | 0
72 | 0.99182 | -0.11583 | 0.12433 | 0.060217
73 | 0.99243 | -0.11328 | 0.1367 | 0.066207
74 | 0.99149 | -0.11348 | 0 | 0
75 | 0.99155 | -0.11389 | 0.14576 | 0.070595
76 | 0.9914 | -0.11284 | 0.1611 | 0.078023
77 | 0.99365 | -0.12265 | 0.16093 | 0.077941
78 | 0.99362 | -0.1224 | 0 | 0
79 | 0.99406 | -0.12582 | 0 | 0
80 | 0.99363 | -0.1228 | 0.075072 | 0.036359
81 | 0.99248 | -0.1137 | 0 | 0
82 | 0.9936 | -0.12224 | 0 | 0
83 | 0.99513 | -0.13396 | 0 | 0
84 | 0.99246 | -0.11383 | 0.12678 | 0.061404
85 | 0.99359 | -0.12219 | 0.09147 | 0.044301
86 | 0.99985 | -0.0020173 | 0.15059 | 0.072933
87 | 1 | 0 | -6.1124 | -2.5988
88 | 0.98386 | -0.32383 | 0 | 0
89 | 0.98366 | -0.3223 | 0 | 0
90 | 0.9838 | -0.32417 | 0.13218 | 0.064018
91 | 0.98407 | -0.3221 | 0.1147 | 0.055552
92 | 0.98189 | -0.33508 | 0.15726 | 0.076164
93 | 0.98361 | -0.32247 | 0 | 0
94 | 0.98565 | -0.3118 | 0.077609 | 0.037588
95 | 0.98558 | -0.31122 | 0 | 0
96 | 0.98414 | -0.32263 | 0 | 0
97 | 0.98362 | -0.32243 | 0.096489 | 0.046732
98 | 0.9833 | -0.38338 | 0.080156 | 0.038821
99 | 0.98307 | -0.38527 | 0.14996 | 0.072627
100 | 0.9819 | -0.39613 | 0.12395 | 0.060033
101 | 0.98365 | -0.32219 | 0.11067 | 0.053599
102 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.23449 | -0.10685 | 0.23449 | 0.10594 | 2.9484e-06 | -0.0009182 | 0.0075092 | 0.0074981 | 0.0075092 | 0.99063 | -0.19577 | 0.99064 | -0.19587 | 3.4133
1 | 0.080131 | 0.032095 | -0.080131 | -0.033022 | 3.3576e-07 | -0.00092751 | 0.0025154 | 0.0025256 | 0.0025256 | 0.99063 | -0.19577 | 0.99062 | -0.19575 | 1.148
2 | -0.23449 | -0.10594 | 0.23451 | 0.10021 | 1.8201e-05 | -0.0057289 | 0.0074981 | 0.0074309 | 0.0074981 | 0.99064 | -0.19587 | 0.99071 | -0.1964 | 3.4082
3 | 0.080131 | 0.033022 | -0.080129 | -0.038691 | 2.114e-06 | -0.0056687 | 0.0025256 | 0.002593 | 0.002593 | 0.99062 | -0.19575 | 0.9906 | -0.19556 | 1.1787
4 | -2.8063 | -1.192 | 2.811 | 1.1534 | 0.004719 | -0.038554 | 0.08884 | 0.08837 | 0.08884 | 0.99071 | -0.1964 | 0.99256 | -0.17106 | 24.5416
5 | 2.5718 | 1.0917 | -2.5715 | -1.0915 | 0.000264 | 0.00024845 | 0.08141 | 0.08141 | 0.08141 | 0.99071 | -0.1964 | 0.99058 | -0.19999 | 23.2601
6 | 0.080129 | 0.038691 | -0.080128 | -0.038808 | 1.199e-06 | -0.00011642 | 0.002593 | 0.0025945 | 0.0025945 | 0.9906 | -0.19556 | 0.99058 | -0.19566 | 1.2355
7 | -2.811 | -1.1534 | 2.811 | 1.1533 | 1.5114e-05 | -0.00012444 | 0.08837 | 0.088368 | 0.08837 | 0.99256 | -0.17106 | 0.99257 | -0.17097 | 24.4115
8 | 2.4116 | 1.0141 | -2.4048 | -1.0078 | 0.0068938 | 0.0062981 | 0.076241 | 0.076259 | 0.076259 | 0.99058 | -0.19999 | 0.98702 | -0.30094 | 21.7882
9 | -2.899 | -1.1959 | 2.9001 | 1.1878 | 0.0010539 | -0.0081127 | 0.091206 | 0.091108 | 0.091206 | 0.99257 | -0.17097 | 0.99297 | -0.16535 | 25.1951
10 | 1.6495 | 0.66559 | -1.6456 | -0.66304 | 0.0039049 | 0.0025486 | 0.052022 | 0.052043 | 0.052043 | 0.98702 | -0.30094 | 0.98408 | -0.38745 | 14.8694
11 | 0.6912 | 0.31115 | -0.6903 | -0.31178 | 0.00089728 | -0.00062726 | 0.022169 | 0.022184 | 0.022184 | 0.98702 | -0.30094 | 0.98565 | -0.3118 | 10.5637
12 | -2.9001 | -1.1878 | 2.9054 | 1.1464 | 0.0053261 | -0.041402 | 0.091108 | 0.090618 | 0.091108 | 0.99297 | -0.16535 | 0.99499 | -0.13597 | 25.168
13 | -2.9054 | -1.1464 | 2.9057 | 1.1442 | 0.00027142 | -0.0021279 | 0.090618 | 0.090593 | 0.090618 | 0.99499 | -0.13597 | 0.9951 | -0.13443 | 25.0325
14 | -3.0369 | -1.2078 | 3.037 | 1.2072 | 8.8425e-05 | -0.00062764 | 0.094813 | 0.094806 | 0.094813 | 0.9951 | -0.13443 | 0.99513 | -0.13396 | 26.1915
15 | 1.3622 | 0.53256 | -1.362 | -0.53384 | 0.00014102 | -0.0012816 | 0.042927 | 0.042941 | 0.042941 | 0.98355 | -0.38464 | 0.98345 | -0.38415 | 19.5186
16 | -1.4963 | -0.59751 | 1.4965 | 0.59605 | 0.00019624 | -0.0014608 | 0.047288 | 0.047272 | 0.047288 | 0.98355 | -0.38464 | 0.98367 | -0.3853 | 21.4947
17 | 1.362 | 0.53384 | -1.3618 | -0.53571 | 0.00020615 | -0.0018715 | 0.042941 | 0.042962 | 0.042962 | 0.98345 | -0.38415 | 0.9833 | -0.38343 | 19.5281
18 | -1.4965 | -0.59605 | 1.4971 | 0.5912 | 0.00064965 | -0.0048462 | 0.047272 | 0.047217 | 0.047272 | 0.98367 | -0.3853 | 0.98408 | -0.38745 | 21.4872
19 | 1.2817 | 0.49819 | -1.2816 | -0.49902 | 8.0374e-05 | -0.00082878 | 0.040369 | 0.040378 | 0.040378 | 0.9833 | -0.38343 | 0.98325 | -0.38314 | 18.3537
20 | 0.080157 | 0.037515 | -0.080156 | -0.038379 | 3.3882e-07 | -0.00086422 | 0.0025982 | 0.002609 | 0.002609 | 0.9833 | -0.38343 | 0.9833 | -0.38339 | 1.1859
21 | 0.14845 | 0.071834 | -0.14845 | -0.071895 | 2.2755e-06 | -6.1656e-05 | 0.0048377 | 0.0048385 | 0.0048385 | 0.98408 | -0.38745 | 0.98407 | -0.38755 | 2.304
22 | 1.0983 | 0.41025 | -1.0981 | -0.41023 | 0.00018418 | 1.4688e-05 | 0.034421 | 0.034422 | 0.034422 | 0.98325 | -0.38314 | 0.98307 | -0.38527 | 16.3915
23 | 0.080156 | 0.038379 | -0.080156 | -0.038821 | 1.7456e-07 | -0.00044244 | 0.002609 | 0.0026147 | 0.0026147 | 0.9833 | -0.38339 | 0.9833 | -0.38338 | 1.1885
24 | -0.1366 | -0.066158 | 0.1366 | 0.063508 | 3.0498e-06 | -0.00265 | 0.0044666 | 0.0044331 | 0.0044666 | 0.98094 | -0.39327 | 0.98096 | -0.39345 | 2.0303
25 | 0.13542 | 0.055284 | -0.13541 | -0.064487 | 1.0158e-05 | -0.0092034 | 0.0043045 | 0.004414 | 0.004414 | 0.98096 | -0.39345 | 0.98089 | -0.39293 | 2.0064
26 | -0.27203 | -0.11879 | 0.27214 | 0.092145 | 0.00011423 | -0.026647 | 0.0087351 | 0.0084517 | 0.0087351 | 0.98096 | -0.39345 | 0.98136 | -0.39536 | 3.9705
27 | 0.13541 | 0.064487 | -0.13541 | -0.065583 | 1.2455e-06 | -0.0010962 | 0.004414 | 0.004428 | 0.004428 | 0.98089 | -0.39293 | 0.98088 | -0.39285 | 2.0127
28 | 0.078141 | 0.035793 | -0.078141 | -0.037845 | 7.6954e-07 | -0.0020527 | 0.0025282 | 0.002554 | 0.002554 | 0.98136 | -0.39536 | 0.98135 | -0.39528 | 1.1609
29 | -0.35028 | -0.12794 | 0.35048 | 0.099504 | 0.00019401 | -0.028433 | 0.01097 | 0.010711 | 0.01097 | 0.98136 | -0.39536 | 0.9819 | -0.39616 | 4.9862
30 | 0.12395 | 0.05961 | -0.12395 | -0.060033 | 4.021e-07 | -0.00042335 | 0.0040437 | 0.0040491 | 0.0040491 | 0.9819 | -0.39616 | 0.9819 | -0.39613 | 1.8405
31 | -0.47443 | -0.15911 | 0.4748 | 0.15823 | 0.00037236 | -0.00087991 | 0.014712 | 0.014701 | 0.014712 | 0.9819 | -0.39616 | 0.98274 | -0.38435 | 7.0055
32 | 0.064955 | 0.0023643 | -0.064949 | -0.030869 | 6.4036e-06 | -0.028504 | 0.0019094 | 0.0021127 | 0.0021127 | 0.98269 | -0.38526 | 0.98259 | -0.38548 | 0.96031
33 | -0.064955 | -0.0023643 | 0.064957 | 0.0021221 | 1.3696e-06 | -0.00024224 | 0.0019094 | 0.0019092 | 0.0019094 | 0.98269 | -0.38526 | 0.98271 | -0.38455 | 0.90924
34 | 0.064949 | 0.030869 | -0.064949 | -0.031456 | 1.5239e-07 | -0.00058743 | 0.0021127 | 0.0021202 | 0.0021202 | 0.98259 | -0.38548 | 0.98259 | -0.38546 | 0.9637
35 | -0.11596 | -0.023957 | 0.11597 | 0.018702 | 3.6509e-06 | -0.0052552 | 0.0034784 | 0.0034505 | 0.0034784 | 0.98271 | -0.38455 | 0.98274 | -0.38435 | 1.5811
36 | 0.051007 | 0.021835 | -0.051007 | -0.024704 | 4.5055e-07 | -0.0028688 | 0.0016299 | 0.0016649 | 0.0016649 | 0.98271 | -0.38455 | 0.9827 | -0.38448 | 0.75675
37 | -0.79842 | -0.27206 | 0.79853 | 0.26882 | 0.00011614 | -0.0032378 | 0.024777 | 0.024747 | 0.024777 | 0.98274 | -0.38435 | 0.98288 | -0.38467 | 11.2624
38 | 0.20765 | 0.095122 | -0.20762 | -0.095504 | 2.7832e-05 | -0.00038234 | 0.0067091 | 0.006714 | 0.006714 | 0.98274 | -0.38435 | 0.9826 | -0.38541 | 3.1972
39 | -0.94796 | -0.34119 | 0.94814 | 0.33761 | 0.000184 | -0.0035813 | 0.02959 | 0.029554 | 0.02959 | 0.98288 | -0.38467 | 0.98307 | -0.38527 | 13.4501
40 | 0.14388 | 0.065321 | -0.14388 | -0.068636 | 4.1753e-06 | -0.0033151 | 0.0046422 | 0.0046834 | 0.0046834 | 0.9826 | -0.38541 | 0.98257 | -0.38518 | 2.1288
41 | 0.063741 | 0.030183 | -0.06374 | -0.030871 | 1.7169e-07 | -0.00068765 | 0.002072 | 0.0020807 | 0.0020807 | 0.9826 | -0.38541 | 0.9826 | -0.38539 | 0.94577
42 | 0.14388 | 0.068636 | -0.14387 | -0.069682 | 1.3323e-06 | -0.0010454 | 0.0046834 | 0.0046967 | 0.0046967 | 0.98257 | -0.38518 | 0.98256 | -0.3851 | 2.1349
43 | -0.10884 | -0.052711 | 0.10884 | 0.052642 | 1.3523e-06 | -6.9636e-05 | 0.0035381 | 0.0035372 | 0.0035381 | 0.98666 | -0.10322 | 0.98668 | -0.10313 | 1.6848
44 | -0.10884 | -0.052642 | 0.10884 | 0.049224 | 2.4263e-06 | -0.0034171 | 0.0035372 | 0.0034948 | 0.0035372 | 0.98668 | -0.10313 | 0.9867 | -0.10331 | 1.6078
45 | -0.50886 | -0.22512 | 0.50889 | 0.22307 | 3.1312e-05 | -0.0020512 | 0.016279 | 0.016255 | 0.016279 | 0.9867 | -0.10331 | 0.98675 | -0.10374 | 7.3997
46 | 0.40002 | 0.17589 | -0.39998 | -0.18013 | 4.0013e-05 | -0.0042336 | 0.012785 | 0.012835 | 0.012835 | 0.9867 | -0.10331 | 0.9866 | -0.1026 | 5.8342
47 | -0.62543 | -0.27951 | 0.62547 | 0.27795 | 3.617e-05 | -0.001559 | 0.020041 | 0.020022 | 0.020041 | 0.98675 | -0.10374 | 0.98681 | -0.10415 | 9.1096
48 | 0.30993 | 0.13798 | -0.30989 | -0.14496 | 3.9934e-05 | -0.0069831 | 0.0099266 | 0.010012 | 0.010012 | 0.9866 | -0.1026 | 0.98648 | -0.10163 | 4.5507
49 | 0.090046 | 0.042147 | -0.090045 | -0.043611 | 7.1601e-07 | -0.0014635 | 0.002909 | 0.0029274 | 0.0029274 | 0.9866 | -0.1026 | 0.9866 | -0.10254 | 1.3307
50 | -0.62547 | -0.27795 | 0.62552 | 0.27584 | 4.8796e-05 | -0.0021082 | 0.020022 | 0.019997 | 0.020022 | 0.98681 | -0.10415 | 0.98688 | -0.1047 | 9.1011
51 | 0.15504 | 0.07165 | -0.15504 | -0.073705 | 2.9647e-06 | -0.0020543 | 0.004998 | 0.0050235 | 0.0050235 | 0.98648 | -0.10163 | 0.98647 | -0.10147 | 2.2834
52 | 0.15486 | 0.073311 | -0.15485 | -0.074999 | 2.4495e-06 | -0.0016881 | 0.0050137 | 0.005035 | 0.005035 | 0.98648 | -0.10163 | 0.98647 | -0.10149 | 2.2887
53 | 0.15504 | 0.073705 | -0.15503 | -0.075086 | 2.0113e-06 | -0.0013817 | 0.0050235 | 0.005041 | 0.005041 | 0.98647 | -0.10147 | 0.98645 | -0.10136 | 2.2914
54 | 0.14299 | 0.069156 | -0.14298 | -0.06925 | 3.1574e-06 | -9.3448e-05 | 0.004646 | 0.0046472 | 0.0046472 | 0.98688 | -0.1047 | 0.98686 | -0.10484 | 2.213
55 | -0.7685 | -0.345 | 0.76861 | 0.34495 | 0.00010976 | -4.9241e-05 | 0.024641 | 0.02464 | 0.024641 | 0.98688 | -0.1047 | 0.98703 | -0.10349 | 11.7338
56 | -0.89266 | -0.40488 | 0.8928 | 0.402 | 0.00013774 | -0.0028834 | 0.028667 | 0.028632 | 0.028667 | 0.98703 | -0.10349 | 0.98717 | -0.10463 | 13.0307
57 | 0.12405 | 0.059931 | -0.12405 | -0.060081 | 1.3945e-07 | -0.00014955 | 0.0040293 | 0.0040312 | 0.0040312 | 0.98703 | -0.10349 | 0.98703 | -0.10348 | 1.8324
58 | -0.8928 | -0.402 | 0.89292 | 0.40198 | 0.00011906 | -2.0271e-05 | 0.028632 | 0.028631 | 0.028632 | 0.98717 | -0.10463 | 0.98731 | -0.10351 | 13.6344
59 | -1.2372 | -0.56058 | 1.2373 | 0.5593 | 0.00011826 | -0.0012728 | 0.039713 | 0.039697 | 0.039713 | 0.98731 | -0.10351 | 0.9874 | -0.10422 | 18.0514
60 | 0.22626 | 0.10145 | -0.22617 | -0.10254 | 9.2644e-05 | -0.0010905 | 0.0072501 | 0.0072639 | 0.0072639 | 0.98731 | -0.10351 | 0.98688 | -0.10693 | 3.459
61 | -1.2373 | -0.5593 | 1.2374 | 0.55831 | 9.24e-05 | -0.00099538 | 0.039697 | 0.039685 | 0.039697 | 0.9874 | -0.10422 | 0.98747 | -0.10477 | 18.0443
62 | 0.11988 | 0.051259 | -0.11988 | -0.057953 | 5.7075e-06 | -0.0066936 | 0.0038138 | 0.0038949 | 0.0038949 | 0.98688 | -0.10693 | 0.98684 | -0.10657 | 1.7704
63 | 0.10629 | 0.051285 | -0.10628 | -0.051475 | 3.5111e-06 | -0.00018994 | 0.003452 | 0.0034544 | 0.0034544 | 0.98688 | -0.10693 | 0.98685 | -0.10715 | 1.645
64 | -1.2374 | -0.55831 | 1.2376 | 0.55641 | 0.00017582 | -0.0018962 | 0.039685 | 0.039662 | 0.039685 | 0.98747 | -0.10477 | 0.9876 | -0.10581 | 18.0387
65 | -1.356 | -0.61375 | 1.3562 | 0.61146 | 0.00025679 | -0.0022925 | 0.043505 | 0.043477 | 0.043505 | 0.9876 | -0.10581 | 0.98778 | -0.10721 | 19.7752
66 | -1.3562 | -0.61146 | 1.3592 | 0.58439 | 0.0029989 | -0.027067 | 0.043477 | 0.043148 | 0.043477 | 0.98778 | -0.10721 | 0.98985 | -0.12245 | 19.7622
67 | -1.3592 | -0.58439 | 1.3596 | 0.58087 | 0.0003861 | -0.0035241 | 0.043148 | 0.043106 | 0.043148 | 0.98985 | -0.12245 | 0.99012 | -0.12426 | 19.6127
68 | -1.4382 | -0.61896 | 1.44 | 0.6195 | 0.0017345 | 0.00053897 | 0.045651 | 0.045645 | 0.045651 | 0.99012 | -0.12426 | 0.9914 | -0.11284 | 21.7387
69 | 0.11988 | 0.057953 | -0.11988 | -0.058058 | 9.2282e-08 | -0.00010586 | 0.0038949 | 0.0038963 | 0.0038963 | 0.98684 | -0.10657 | 0.98684 | -0.10656 | 1.771
70 | -0.15663 | -0.075859 | 0.15663 | 0.075816 | 1.7267e-06 | -4.3285e-05 | 0.0050652 | 0.0050646 | 0.0050652 | 0.99184 | -0.11615 | 0.99185 | -0.11608 | 2.412
71 | -0.15663 | -0.075816 | 0.15663 | 0.075313 | 7.3203e-07 | -0.00050253 | 0.0050646 | 0.0050583 | 0.0050646 | 0.99185 | -0.11608 | 0.99185 | -0.11612 | 2.3021
72 | 0.28813 | 0.13616 | -0.28813 | -0.13716 | 4.8876e-06 | -0.00099678 | 0.0092752 | 0.0092877 | 0.0092877 | 0.99185 | -0.11612 | 0.99184 | -0.11598 | 4.2217
73 | -2.1924 | -0.97413 | 2.1927 | 0.97321 | 0.00027662 | -0.0009165 | 0.069825 | 0.069813 | 0.069825 | 0.99185 | -0.11612 | 0.99197 | -0.11701 | 31.7385
74 | 1.7477 | 0.76265 | -1.7471 | -0.76569 | 0.00056156 | -0.0030383 | 0.055497 | 0.055535 | 0.055535 | 0.99185 | -0.11612 | 0.99155 | -0.11394 | 25.243
75 | 0.12433 | 0.057831 | -0.12433 | -0.060217 | 2.1769e-06 | -0.0023861 | 0.003991 | 0.0040208 | 0.0040208 | 0.99184 | -0.11598 | 0.99182 | -0.11583 | 1.8277
76 | -2.2878 | -1.0193 | 2.2888 | 1.0198 | 0.00098762 | 0.00049598 | 0.072887 | 0.072885 | 0.072887 | 0.99197 | -0.11701 | 0.99243 | -0.11328 | 34.708
77 | 1.6013 | 0.69579 | -1.6012 | -0.69652 | 0.00011147 | -0.00072534 | 0.050831 | 0.05084 | 0.05084 | 0.99155 | -0.11394 | 0.99149 | -0.11348 | 23.1091
78 | 0.14576 | 0.069897 | -0.14576 | -0.070595 | 8.8175e-07 | -0.00069843 | 0.0047063 | 0.0047151 | 0.0047151 | 0.99155 | -0.11394 | 0.99155 | -0.11389 | 2.1432
79 | -2.4255 | -1.086 | 2.4256 | 1.0856 | 0.00014225 | -0.00037719 | 0.077301 | 0.077296 | 0.077301 | 0.99243 | -0.11328 | 0.99248 | -0.1137 | 35.1369
80 | 1.6012 | 0.69652 | -1.6011 | -0.69752 | 0.00015443 | -0.0010043 | 0.05084 | 0.050852 | 0.050852 | 0.99149 | -0.11348 | 0.9914 | -0.11284 | 23.1147
81 | 2.6471 | 1.1786 | -2.647 | -1.1788 | 9.5355e-05 | -0.00020931 | 0.084181 | 0.084184 | 0.084184 | 0.99365 | -0.12265 | 0.99362 | -0.1224 | 38.2655
82 | -2.8831 | -1.2927 | 2.8843 | 1.2904 | 0.0012654 | -0.0022785 | 0.091794 | 0.091762 | 0.091794 | 0.99365 | -0.12265 | 0.99406 | -0.12582 | 41.7244
83 | 0.075073 | 0.036178 | -0.075072 | -0.036359 | 1.6102e-06 | -0.00018055 | 0.0024211 | 0.0024234 | 0.0024234 | 0.99365 | -0.12265 | 0.99363 | -0.1228 | 1.154
84 | 2.5555 | 1.1396 | -2.5524 | -1.1469 | 0.0030816 | -0.0073002 | 0.081293 | 0.081391 | 0.081391 | 0.99362 | -0.1224 | 0.99248 | -0.1137 | 36.9958
85 | 0.091473 | 0.039195 | -0.091471 | -0.043283 | 1.9678e-06 | -0.004088 | 0.0028912 | 0.0029401 | 0.0029401 | 0.99362 | -0.1224 | 0.9936 | -0.12224 | 1.3364
86 | -2.8843 | -1.2904 | 2.8876 | 1.2845 | 0.003287 | -0.0059375 | 0.091762 | 0.09168 | 0.091762 | 0.99406 | -0.12582 | 0.99513 | -0.13396 | 41.7101
87 | 0.12679 | 0.061308 | -0.12678 | -0.061404 | 2.4626e-06 | -9.5294e-05 | 0.0040962 | 0.0040974 | 0.0040974 | 0.99248 | -0.1137 | 0.99246 | -0.11383 | 1.9512
88 | 0.091471 | 0.043283 | -0.09147 | -0.044301 | 5.0041e-07 | -0.0010176 | 0.0029401 | 0.0029528 | 0.0029528 | 0.9936 | -0.12224 | 0.99359 | -0.12219 | 1.3422
89 | -5.9247 | -2.4917 | 5.947 | 2.5163 | 0.022303 | 0.024636 | 0.18645 | 0.18644 | 0.18645 | 0.99513 | -0.13396 | 0.99985 | -0.0020173 | 53.271
90 | -6.0976 | -2.5893 | 6.0984 | 2.5883 | 0.00083856 | -0.0010187 | 0.19126 | 0.19124 | 0.19126 | 0.99985 | -0.0020173 | 1 | 0 | 52.8352
91 | 0.36477 | 0.16002 | -0.36469 | -0.16946 | 7.5401e-05 | -0.0094405 | 0.011687 | 0.011802 | 0.011802 | 0.98386 | -0.32383 | 0.98366 | -0.3223 | 5.3643
92 | 0.13219 | 0.063784 | -0.13218 | -0.064018 | 6.8234e-06 | -0.00023417 | 0.0043065 | 0.0043095 | 0.0043095 | 0.98386 | -0.32383 | 0.9838 | -0.32417 | 2.0521
93 | -0.49695 | -0.2238 | 0.49706 | 0.22361 | 0.00010246 | -0.00019578 | 0.015992 | 0.015989 | 0.015992 | 0.98386 | -0.32383 | 0.98407 | -0.3221 | 7.6151
94 | 0.36469 | 0.16946 | -0.36468 | -0.17011 | 5.2717e-06 | -0.00065299 | 0.011802 | 0.01181 | 0.01181 | 0.98366 | -0.3223 | 0.98365 | -0.32219 | 5.368
95 | -0.61176 | -0.27916 | 0.6118 | 0.27724 | 4.3479e-05 | -0.0019248 | 0.019726 | 0.019702 | 0.019726 | 0.98407 | -0.3221 | 0.98414 | -0.32263 | 8.9663
96 | -0.15726 | -0.076164 | 0.15752 | 0.069867 | 0.00025927 | -0.006297 | 0.0051371 | 0.0050573 | 0.0051371 | 0.98189 | -0.33508 | 0.98361 | -0.32247 | 2.4462
97 | -0.15752 | -0.069867 | 0.15752 | 0.069854 | 5.5423e-07 | -1.3701e-05 | 0.0050573 | 0.0050571 | 0.0050573 | 0.98361 | -0.32247 | 0.98362 | -0.32243 | 2.4082
98 | 0.61269 | 0.27419 | -0.61264 | -0.27635 | 4.8419e-05 | -0.0021594 | 0.019659 | 0.019685 | 0.019685 | 0.98565 | -0.3118 | 0.98558 | -0.31122 | 8.9479
99 | 0.61264 | 0.27635 | -0.6118 | -0.27724 | 0.00084265 | -0.00088419 | 0.019685 | 0.019702 | 0.019702 | 0.98558 | -0.31122 | 0.98414 | -0.32263 | 9.3821
100 | -0.25401 | -0.11659 | 0.25402 | 0.11651 | 7.886e-06 | -7.1056e-05 | 0.0082024 | 0.0082015 | 0.0082024 | 0.98362 | -0.32243 | 0.98365 | -0.32219 | 3.9059

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 6.1124 | 2.5988

## res_load
| p_mw | q_mvar
0 | 0.15436 | 0.074759
1 | 0.15986 | 0.077426
2 | 0.080128 | 0.038808
3 | 0.087989 | 0.042615
4 | 0.064084 | 0.031037
5 | 0.13129 | 0.063586
6 | 0.13412 | 0.064956
7 | 0.18329 | 0.088773
8 | 0.14845 | 0.071895
9 | 0.1366 | 0.066158
10 | 0.13541 | 0.065583
11 | 0.078141 | 0.037845
12 | 0.064949 | 0.031456
13 | 0.051007 | 0.024704
14 | 0.14942 | 0.072368
15 | 0.06374 | 0.030871
16 | 0.14387 | 0.069682
17 | 0.10884 | 0.052711
18 | 0.11654 | 0.056443
19 | 0.090045 | 0.043611
20 | 0.15485 | 0.074999
21 | 0.15503 | 0.075086
22 | 0.12405 | 0.060081
23 | 0.118 | 0.057149
24 | 0.14298 | 0.06925
25 | 0.11839 | 0.057339
26 | 0.078648 | 0.038091
27 | 0.10628 | 0.051475
28 | 0.11988 | 0.058058
29 | 0.15663 | 0.075859
30 | 0.16379 | 0.079329
31 | 0.095113 | 0.046065
32 | 0.12433 | 0.060217
33 | 0.1367 | 0.066207
34 | 0.14576 | 0.070595
35 | 0.1611 | 0.078023
36 | 0.16093 | 0.077941
37 | 0.075072 | 0.036359
38 | 0.12678 | 0.061404
39 | 0.09147 | 0.044301
40 | 0.15059 | 0.072933
41 | 0.13218 | 0.064018
42 | 0.1147 | 0.055552
43 | 0.15726 | 0.076164
44 | 0.077609 | 0.037588
45 | 0.096489 | 0.046732
46 | 0.080156 | 0.038821
47 | 0.14996 | 0.072627
48 | 0.12395 | 0.060033
49 | 0.11067 | 0.053599

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1