## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_190_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_190_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_190_0_node_173 | 20 | n |  | TRUE
3 | bus_MV_190_0_node_5 | 20 | n |  | TRUE
4 | bus_MV_190_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_190_0_node_3 | 20 | n |  | TRUE
6 | bus_MV_190_0_node_6 | 20 | n |  | TRUE
7 | bus_MV_190_0_node_13 | 20 | n |  | TRUE
8 | bus_MV_190_0_node_261 | 20 | n |  | TRUE
9 | bus_MV_190_0_node_207 | 20 | n |  | TRUE
10 | bus_MV_190_0_node_228 | 20 | n |  | TRUE
11 | bus_MV_190_0_node_260 | 20 | n |  | TRUE
12 | bus_MV_190_0_node_191 | 20 | n |  | TRUE
13 | bus_MV_190_0_node_196 | 20 | n |  | TRUE
14 | bus_MV_190_0_node_226 | 20 | n |  | TRUE
15 | bus_MV_190_0_node_249 | 20 | n |  | TRUE
16 | bus_MV_190_0_node_170 | 20 | n |  | TRUE
17 | bus_MV_190_0_node_206 | 20 | n |  | TRUE
18 | bus_MV_190_0_node_227 | 20 | n |  | TRUE
19 | bus_MV_190_0_node_14 | 20 | n |  | TRUE
20 | bus_MV_190_0_node_25 | 20 | n |  | TRUE
21 | bus_MV_190_0_node_253 | 20 | n |  | TRUE
22 | bus_MV_190_0_node_208 | 20 | n |  | TRUE
23 | bus_MV_190_0_node_229 | 20 | n |  | TRUE
24 | bus_MV_190_0_node_234 | 20 | n |  | TRUE
25 | bus_MV_190_0_node_7 | 20 | n |  | TRUE
26 | bus_MV_190_0_node_8 | 20 | n |  | TRUE
27 | bus_MV_190_0_node_10 | 20 | n |  | TRUE
28 | bus_MV_190_0_node_9 | 20 | n |  | TRUE
29 | bus_MV_190_0_node_35 | 20 | n |  | TRUE
30 | bus_MV_190_0_node_29 | 20 | n |  | TRUE
31 | bus_MV_190_0_node_11 | 20 | n |  | TRUE
32 | bus_MV_190_0_node_12 | 20 | n |  | TRUE
33 | bus_MV_190_0_node_209 | 20 | n |  | TRUE
34 | bus_MV_190_0_node_133 | 20 | n |  | TRUE
35 | bus_MV_190_0_node_16 | 20 | n |  | TRUE
36 | bus_MV_190_0_node_18 | 20 | n |  | TRUE
37 | bus_MV_190_0_node_32 | 20 | n |  | TRUE
38 | bus_MV_190_0_node_38 | 20 | n |  | TRUE
39 | bus_MV_190_0_node_26 | 20 | n |  | TRUE
40 | bus_MV_190_0_node_27 | 20 | n |  | TRUE
41 | bus_MV_190_0_node_28 | 20 | n |  | TRUE
42 | bus_MV_190_0_node_34 | 20 | n |  | TRUE
43 | bus_MV_190_0_node_210 | 20 | n |  | TRUE
44 | bus_MV_190_0_node_19 | 20 | n |  | TRUE
45 | bus_MV_190_0_node_255 | 20 | n |  | TRUE
46 | bus_MV_190_0_node_20 | 20 | n |  | TRUE
47 | bus_MV_190_0_node_256 | 20 | n |  | TRUE
48 | bus_MV_190_0_node_21 | 20 | n |  | TRUE
49 | bus_MV_190_0_node_22 | 20 | n |  | TRUE
50 | bus_MV_190_0_node_17 | 20 | n |  | TRUE
51 | bus_MV_190_0_node_24 | 20 | n |  | TRUE
52 | bus_MV_190_0_node_23 | 20 | n |  | TRUE
53 | bus_MV_190_0_node_31 | 20 | n |  | TRUE
54 | bus_MV_190_0_node_30 | 20 | n |  | TRUE
55 | bus_MV_190_0_node_36 | 20 | n |  | TRUE
56 | bus_MV_190_0_node_15 | 20 | n |  | TRUE
57 | bus_MV_190_0_node_33 | 20 | n |  | TRUE
58 | bus_MV_190_0_node_37 | 20 | n |  | TRUE
59 | bus_MV_190_0_node_232 | 20 | n |  | TRUE
60 | bus_MV_190_0_node_254 | 20 | n |  | TRUE
61 | bus_MV_190_0_node_39 | 20 | n |  | TRUE
62 | bus_MV_190_0_node_233 | 20 | n |  | TRUE
63 | bus_MV_190_0_node_167 | 20 | n |  | TRUE
64 | bus_MV_190_0_node_168 | 20 | n |  | TRUE
65 | bus_MV_190_0_node_102 | 20 | n |  | TRUE
66 | bus_MV_190_0_node_103 | 20 | n |  | TRUE
67 | bus_MV_190_0_node_105 | 20 | n |  | TRUE
68 | bus_MV_190_0_node_111 | 20 | n |  | TRUE
69 | bus_MV_190_0_node_218 | 20 | n |  | TRUE
70 | bus_MV_190_0_node_109 | 20 | n |  | TRUE
71 | bus_MV_190_0_node_242 | 20 | n |  | TRUE
72 | bus_MV_190_0_node_112 | 20 | n |  | TRUE
73 | bus_MV_190_0_node_113 | 20 | n |  | TRUE
74 | bus_MV_190_0_node_230 | 20 | n |  | TRUE
75 | bus_MV_190_0_node_217 | 20 | n |  | TRUE
76 | bus_MV_190_0_node_219 | 20 | n |  | TRUE
77 | bus_MV_190_0_node_107 | 20 | n |  | TRUE
78 | bus_MV_190_0_node_106 | 20 | n |  | TRUE
79 | bus_MV_190_0_node_108 | 20 | n |  | TRUE
80 | bus_MV_190_0_node_110 | 20 | n |  | TRUE
81 | bus_MV_190_0_node_148 | 20 | n |  | TRUE
82 | bus_MV_190_0_node_149 | 20 | n |  | TRUE
83 | bus_MV_190_0_node_150 | 20 | n |  | TRUE
84 | bus_MV_190_0_node_152 | 20 | n |  | TRUE
85 | bus_MV_190_0_node_153 | 20 | n |  | TRUE
86 | bus_MV_190_0_node_120 | 20 | n |  | TRUE
87 | bus_MV_190_0_node_236 | 20 | n |  | TRUE
88 | bus_MV_190_0_node_143 | 20 | n |  | TRUE
89 | bus_MV_190_0_node_257 | 20 | n |  | TRUE
90 | bus_MV_190_0_node_144 | 20 | n |  | TRUE
91 | bus_MV_190_0_node_145 | 20 | n |  | TRUE
92 | bus_MV_190_0_node_142 | 20 | n |  | TRUE
93 | bus_MV_190_0_node_114 | 20 | n |  | TRUE
94 | bus_MV_190_0_node_115 | 20 | n |  | TRUE
95 | bus_MV_190_0_node_116 | 20 | n |  | TRUE
96 | bus_MV_190_0_node_117 | 20 | n |  | TRUE
97 | bus_MV_190_0_node_118 | 20 | n |  | TRUE
98 | bus_MV_190_0_node_239 | 20 | n |  | TRUE
99 | bus_MV_190_0_node_156 | 20 | n |  | TRUE
100 | bus_MV_190_0_node_231 | 20 | n |  | TRUE
101 | bus_MV_190_0_node_157 | 20 | n |  | TRUE
102 | bus_MV_190_0_node_161 | 20 | n |  | TRUE
103 | bus_MV_190_0_node_121 | 20 | n |  | TRUE
104 | bus_MV_190_0_node_122 | 20 | n |  | TRUE
105 | bus_MV_190_0_node_125 | 20 | n |  | TRUE
106 | bus_MV_190_0_node_159 | 20 | n |  | TRUE
107 | bus_MV_190_0_node_160 | 20 | n |  | TRUE
108 | bus_MV_190_0_node_158 | 20 | n |  | TRUE
109 | bus_MV_190_0_node_124 | 20 | n |  | TRUE
110 | bus_MV_190_0_node_128 | 20 | n |  | TRUE
111 | bus_MV_190_0_node_127 | 20 | n |  | TRUE
112 | bus_MV_190_0_node_146 | 20 | n |  | TRUE
113 | bus_MV_190_0_node_147 | 20 | n |  | TRUE
114 | bus_MV_190_0_node_129 | 20 | n |  | TRUE
115 | bus_MV_190_0_node_130 | 20 | n |  | TRUE
116 | bus_MV_190_0_node_132 | 20 | n |  | TRUE
117 | bus_MV_190_0_node_131 | 20 | n |  | TRUE
118 | bus_MV_190_0_node_251 | 20 | n |  | TRUE
119 | bus_MV_190_0_node_165 | 20 | n |  | TRUE
120 | bus_MV_190_0_node_134 | 20 | n |  | TRUE
121 | bus_MV_190_0_node_136 | 20 | n |  | TRUE
122 | bus_MV_190_0_node_137 | 20 | n |  | TRUE
123 | bus_MV_190_0_node_139 | 20 | n |  | TRUE
124 | bus_MV_190_0_node_135 | 20 | n |  | TRUE
125 | bus_MV_190_0_node_138 | 20 | n |  | TRUE
126 | bus_MV_190_0_node_140 | 20 | n |  | TRUE
127 | bus_MV_190_0_node_141 | 20 | n |  | TRUE
128 | bus_MV_190_0_node_244 | 20 | n |  | TRUE
129 | bus_MV_190_0_node_162 | 20 | n |  | TRUE
130 | bus_MV_190_0_node_220 | 20 | n |  | TRUE
131 | bus_MV_190_0_node_154 | 20 | n |  | TRUE
132 | bus_MV_190_0_node_155 | 20 | n |  | TRUE
133 | bus_MV_190_0_node_237 | 20 | n |  | TRUE
134 | bus_MV_190_0_node_222 | 20 | n |  | TRUE
135 | bus_MV_190_0_node_221 | 20 | n |  | TRUE
136 | bus_MV_190_0_node_151 | 20 | n |  | TRUE
137 | bus_MV_190_0_node_166 | 20 | n |  | TRUE
138 | bus_MV_190_0_node_238 | 20 | n |  | TRUE
139 | bus_MV_190_0_node_164 | 20 | n |  | TRUE
140 | bus_MV_190_0_node_190 | 20 | n |  | TRUE
141 | bus_MV_190_0_node_187 | 20 | n |  | TRUE
142 | bus_MV_190_0_node_163 | 20 | n |  | TRUE
143 | bus_MV_190_0_node_240 | 20 | n |  | TRUE
144 | bus_MV_190_0_node_169 | 20 | n |  | TRUE
145 | bus_MV_190_0_node_171 | 20 | n |  | TRUE
146 | bus_MV_190_0_node_172 | 20 | n |  | TRUE
147 | bus_MV_190_0_node_241 | 20 | n |  | TRUE
148 | bus_MV_190_0_node_174 | 20 | n |  | TRUE
149 | bus_MV_190_0_node_175 | 20 | n |  | TRUE
150 | bus_MV_190_0_node_176 | 20 | n |  | TRUE
151 | bus_MV_190_0_node_252 | 20 | n |  | TRUE
152 | bus_MV_190_0_node_178 | 20 | n |  | TRUE
153 | bus_MV_190_0_node_177 | 20 | n |  | TRUE
154 | bus_MV_190_0_node_179 | 20 | n |  | TRUE
155 | bus_MV_190_0_node_248 | 20 | n |  | TRUE
156 | bus_MV_190_0_node_180 | 20 | n |  | TRUE
157 | bus_MV_190_0_node_182 | 20 | n |  | TRUE
158 | bus_MV_190_0_node_184 | 20 | n |  | TRUE
159 | bus_MV_190_0_node_235 | 20 | n |  | TRUE
160 | bus_MV_190_0_node_186 | 20 | n |  | TRUE
161 | bus_MV_190_0_node_225 | 20 | n |  | TRUE
162 | bus_MV_190_0_node_197 | 20 | n |  | TRUE
163 | bus_MV_190_0_node_195 | 20 | n |  | TRUE
164 | bus_MV_190_0_node_192 | 20 | n |  | TRUE
165 | bus_MV_190_0_node_193 | 20 | n |  | TRUE
166 | bus_MV_190_0_node_194 | 20 | n |  | TRUE
167 | bus_MV_190_0_node_211 | 20 | n |  | TRUE
168 | bus_MV_190_0_node_223 | 20 | n |  | TRUE
169 | bus_MV_190_0_node_224 | 20 | n |  | TRUE
170 | bus_HV_190_0_node_164 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_190_0_load_0 | 0 | 0.054544 | 0.026417 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_190_0_load_173 | 2 | 0.070708 | 0.034246 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_190_0_load_6 | 6 | 0.10503 | 0.050866 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_190_0_load_13 | 7 | 0.10395 | 0.050346 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_190_0_load_261 | 8 | 0.095024 | 0.046022 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_190_0_load_228 | 10 | 0.050104 | 0.024266 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_190_0_load_191 | 12 | 0.052545 | 0.025449 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_190_0_load_226 | 14 | 0.29247 | 0.14165 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_190_0_load_249 | 15 | 0.056878 | 0.027547 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_190_0_load_206 | 17 | 0.083737 | 0.040556 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_190_0_load_253 | 21 | 0.087711 | 0.04248 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_190_0_load_208 | 22 | 0.099963 | 0.048414 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_190_0_load_234 | 24 | 0.050158 | 0.024292 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_190_0_load_7 | 25 | 0.14196 | 0.068756 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_190_0_load_35 | 29 | 0.11684 | 0.056587 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_190_0_load_209 | 33 | 0.11116 | 0.053838 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_190_0_load_133 | 34 | 0.056989 | 0.027601 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_190_0_load_16 | 35 | 0.067365 | 0.032626 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_190_0_load_38 | 38 | 0.14779 | 0.071578 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_190_0_load_26 | 39 | 0.087759 | 0.042504 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_190_0_load_34 | 42 | 0.13909 | 0.067362 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_190_0_load_255 | 45 | 0.10235 | 0.04957 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_190_0_load_256 | 47 | 0.10096 | 0.048898 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_190_0_load_17 | 50 | 0.13818 | 0.066922 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_190_0_load_23 | 52 | 0.14827 | 0.071809 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_190_0_load_30 | 54 | 0.11719 | 0.056759 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_190_0_load_36 | 55 | 0.084505 | 0.040928 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_190_0_load_33 | 57 | 0.15607 | 0.075589 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_190_0_load_37 | 58 | 0.058805 | 0.028481 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_190_0_load_254 | 60 | 0.11639 | 0.056371 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_190_0_load_39 | 61 | 0.089156 | 0.04318 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_190_0_load_233 | 62 | 0.06338 | 0.030697 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_190_0_load_167 | 63 | 0.098162 | 0.047542 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_190_0_load_168 | 64 | 0.0646 | 0.031287 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_190_0_load_102 | 65 | 0.15018 | 0.072738 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_190_0_load_111 | 68 | 0.15027 | 0.072781 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_190_0_load_242 | 71 | 0.071993 | 0.034868 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_190_0_load_230 | 74 | 0.12214 | 0.059156 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_190_0_load_217 | 75 | 0.15596 | 0.075535 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_190_0_load_219 | 76 | 0.082839 | 0.040121 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_190_0_load_106 | 78 | 0.15633 | 0.075715 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_190_0_load_149 | 82 | 0.10355 | 0.050154 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_190_0_load_150 | 83 | 0.13278 | 0.064308 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_190_0_load_120 | 86 | 0.14726 | 0.071323 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_190_0_load_236 | 87 | 0.16017 | 0.077572 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_190_0_load_257 | 89 | 0.12197 | 0.059071 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_190_0_load_142 | 92 | 0.12544 | 0.060754 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_190_0_load_114 | 93 | 0.092583 | 0.04484 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_190_0_load_239 | 98 | 0.16207 | 0.078496 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_190_0_load_231 | 100 | 0.122 | 0.059087 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_190_0_load_121 | 103 | 0.11415 | 0.055287 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_190_0_load_158 | 108 | 0.13374 | 0.064772 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_190_0_load_128 | 110 | 0.13944 | 0.067533 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_190_0_load_127 | 111 | 0.083165 | 0.040279 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_190_0_load_146 | 112 | 0.09078 | 0.043967 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_190_0_load_129 | 114 | 0.080844 | 0.039155 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_190_0_load_251 | 118 | 0.084119 | 0.040741 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_190_0_load_134 | 120 | 0.1619 | 0.078414 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_190_0_load_137 | 122 | 0.098878 | 0.047889 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_190_0_load_140 | 126 | 0.1326 | 0.064223 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_190_0_load_244 | 128 | 0.10576 | 0.051222 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_190_0_load_162 | 129 | 0.16324 | 0.079061 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_190_0_load_220 | 130 | 0.072206 | 0.034971 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_190_0_load_154 | 131 | 0.087033 | 0.042152 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_190_0_load_237 | 133 | 0.097376 | 0.047161 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_190_0_load_222 | 134 | 0.15083 | 0.073049 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_190_0_load_221 | 135 | 0.11536 | 0.055874 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_190_0_load_151 | 136 | 0.14314 | 0.069326 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_190_0_load_190 | 140 | 0.074387 | 0.036027 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_190_0_load_187 | 141 | 0.12106 | 0.058634 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_190_0_load_163 | 142 | 0.12461 | 0.060351 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_190_0_load_240 | 143 | 0.067918 | 0.032894 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_190_0_load_241 | 147 | 0.13824 | 0.066952 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_190_0_load_174 | 148 | 0.077452 | 0.037512 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_190_0_load_252 | 151 | 0.12654 | 0.061288 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_190_0_load_177 | 153 | 0.14339 | 0.069445 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_190_0_load_248 | 155 | 0.11342 | 0.05493 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_190_0_load_180 | 156 | 0.13523 | 0.065493 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_190_0_load_235 | 159 | 0.1622 | 0.078556 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_190_0_load_225 | 161 | 0.090914 | 0.044032 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_190_0_load_195 | 163 | 0.14115 | 0.068361 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_190_0_load_192 | 164 | 0.060352 | 0.02923 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_190_0_load_211 | 167 | 0.1308 | 0.06335 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_190_0_load_224 | 169 | 0.18109 | 0.087704 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 139 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_190_0_line_0 |  | 0 | 1 | 0.13047 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
1 | MV_190_0_line_1 |  | 0 | 2 | 0.71561 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
2 | MV_190_0_line_2 |  | 1 | 3 | 0.87425 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
3 | MV_190_0_line_3 |  | 2 | 4 | 0.059445 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
4 | MV_190_0_line_4 |  | 3 | 9 | 1.2691 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
5 | MV_190_0_line_5 |  | 3 | 10 | 0.023827 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_190_0_line_6 |  | 4 | 5 | 0.38779 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
7 | MV_190_0_line_7 |  | 5 | 8 | 0.010578 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
8 | MV_190_0_line_8 |  | 6 | 7 | 0.71156 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_190_0_line_9 |  | 7 | 19 | 0.069808 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_190_0_line_10 |  | 8 | 11 | 0.1371 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
11 | MV_190_0_line_11 |  | 9 | 17 | 0.046694 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
12 | MV_190_0_line_12 |  | 10 | 18 | 0.011207 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_190_0_line_13 |  | 11 | 12 | 1.0143 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
14 | MV_190_0_line_14 |  | 12 | 13 | 0.81487 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
15 | MV_190_0_line_15 |  | 13 | 162 | 0.63711 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
16 | MV_190_0_line_16 |  | 13 | 163 | 0.045438 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_190_0_line_17 |  | 14 | 15 | 0.42064 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
18 | MV_190_0_line_18 |  | 14 | 16 | 0.02039 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
19 | MV_190_0_line_19 |  | 15 | 162 | 0.025761 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
20 | MV_190_0_line_20 |  | 16 | 145 | 0.3557 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
21 | MV_190_0_line_21 |  | 16 | 146 | 1.2663 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
22 | MV_190_0_line_22 |  | 16 | 144 | 0.35177 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
23 | MV_190_0_line_23 |  | 17 | 22 | 0.23265 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
24 | MV_190_0_line_24 |  | 18 | 23 | 1.2158 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_190_0_line_25 |  | 19 | 56 | 0.26693 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_190_0_line_26 |  | 19 | 20 | 0.19763 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_190_0_line_27 |  | 20 | 21 | 0.079938 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_190_0_line_28 |  | 23 | 24 | 0.05091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_190_0_line_29 |  | 25 | 26 | 0.073908 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_190_0_line_30 |  | 26 | 27 | 0.68931 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_190_0_line_31 |  | 27 | 31 | 0.39421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_190_0_line_32 |  | 27 | 32 | 0.21519 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_190_0_line_33 |  | 27 | 33 | 0.024708 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_190_0_line_34 |  | 27 | 34 | 1.0445 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_190_0_line_35 |  | 28 | 29 | 0.12327 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_190_0_line_36 |  | 28 | 30 | 0.75578 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_190_0_line_37 |  | 30 | 42 | 0.018015 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_190_0_line_38 |  | 30 | 40 | 0.77964 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_190_0_line_39 |  | 31 | 35 | 0.02247 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_190_0_line_40 |  | 32 | 36 | 0.88092 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_190_0_line_41 |  | 32 | 37 | 1.2361 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_190_0_line_42 |  | 32 | 38 | 0.029581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_190_0_line_43 |  | 33 | 43 | 0.012739 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_190_0_line_44 |  | 34 | 117 | 0.039446 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_190_0_line_45 |  | 36 | 49 | 0.74389 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_190_0_line_46 |  | 36 | 50 | 0.060923 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_190_0_line_47 |  | 36 | 44 | 0.4923 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_190_0_line_48 |  | 36 | 46 | 0.75852 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_190_0_line_49 |  | 37 | 55 | 0.064006 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_190_0_line_50 |  | 37 | 53 | 0.27244 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_190_0_line_51 |  | 39 | 40 | 0.011324 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_190_0_line_52 |  | 40 | 41 | 0.41 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_190_0_line_53 |  | 41 | 61 | 0.062758 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_190_0_line_54 |  | 43 | 167 | 0.016938 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_190_0_line_55 |  | 44 | 45 | 0.004016 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_190_0_line_56 |  | 46 | 47 | 0.10866 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_190_0_line_57 |  | 46 | 48 | 0.66933 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_190_0_line_58 |  | 48 | 58 | 0.092111 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_190_0_line_59 |  | 49 | 51 | 0.13585 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_190_0_line_60 |  | 49 | 52 | 0.004343 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_190_0_line_61 |  | 51 | 60 | 0.080062 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_190_0_line_62 |  | 51 | 57 | 0.040601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_190_0_line_63 |  | 53 | 54 | 0.076881 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_190_0_line_64 |  | 54 | 61 | 0.95727 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_190_0_line_65 |  | 56 | 57 | 0.1041 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_190_0_line_66 |  | 58 | 59 | 2.7987 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_190_0_line_67 |  | 59 | 62 | 0.021928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_190_0_line_68 |  | 63 | 64 | 1.3493 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
69 | MV_190_0_line_69 |  | 64 | 144 | 0.040781 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
70 | MV_190_0_line_70 |  | 65 | 66 | 0.056119 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_190_0_line_71 |  | 66 | 67 | 0.5511 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_190_0_line_72 |  | 66 | 68 | 0.14702 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_190_0_line_73 |  | 67 | 69 | 0.16685 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_190_0_line_74 |  | 67 | 70 | 0.13891 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
75 | MV_190_0_line_75 |  | 67 | 71 | 0.16374 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
76 | MV_190_0_line_76 |  | 68 | 72 | 0.090035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_190_0_line_77 |  | 69 | 75 | 0.042433 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_190_0_line_78 |  | 70 | 76 | 0.04474 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
79 | MV_190_0_line_79 |  | 70 | 77 | 0.058677 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
80 | MV_190_0_line_80 |  | 72 | 73 | 0.095607 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_190_0_line_81 |  | 73 | 74 | 0.028098 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_190_0_line_82 |  | 76 | 85 | 0.053062 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
83 | MV_190_0_line_83 |  | 77 | 78 | 0.075801 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
84 | MV_190_0_line_84 |  | 78 | 79 | 0.09039 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
85 | MV_190_0_line_85 |  | 79 | 80 | 0.62696 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
86 | MV_190_0_line_86 |  | 79 | 81 | 0.38756 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
87 | MV_190_0_line_87 |  | 80 | 87 | 0.009817 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_190_0_line_88 |  | 80 | 88 | 0.14583 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
89 | MV_190_0_line_89 |  | 81 | 89 | 0.036232 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
90 | MV_190_0_line_90 |  | 82 | 83 | 0.000961 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_190_0_line_91 |  | 83 | 84 | 0.069305 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_190_0_line_92 |  | 84 | 85 | 0.087554 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
93 | MV_190_0_line_93 |  | 84 | 86 | 0.051623 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
94 | MV_190_0_line_94 |  | 85 | 136 | 0.053853 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_190_0_line_95 |  | 86 | 97 | 0.035479 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
96 | MV_190_0_line_96 |  | 88 | 90 | 0.2274 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
97 | MV_190_0_line_97 |  | 88 | 91 | 0.29505 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
98 | MV_190_0_line_98 |  | 88 | 92 | 0.090118 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
99 | MV_190_0_line_99 |  | 90 | 108 | 0.013928 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
100 | MV_190_0_line_100 |  | 91 | 133 | 0.080797 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_190_0_line_101 |  | 91 | 134 | 0.035606 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
102 | MV_190_0_line_102 |  | 92 | 113 | 0.49939 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
103 | MV_190_0_line_103 |  | 93 | 94 | 0.0064142 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
104 | MV_190_0_line_104 |  | 93 | 95 | 0.0544 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
105 | MV_190_0_line_105 |  | 94 | 96 | 0.044644 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
106 | MV_190_0_line_106 |  | 95 | 97 | 0.055542 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
107 | MV_190_0_line_107 |  | 96 | 98 | 0.034299 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
108 | MV_190_0_line_108 |  | 98 | 101 | 0.013271 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
109 | MV_190_0_line_109 |  | 99 | 100 | 0.030016 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
110 | MV_190_0_line_110 |  | 99 | 101 | 0.070091 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
111 | MV_190_0_line_111 |  | 100 | 137 | 0.084995 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
112 | MV_190_0_line_112 |  | 101 | 102 | 0.10169 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
113 | MV_190_0_line_113 |  | 102 | 126 | 0.042013 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
114 | MV_190_0_line_114 |  | 103 | 104 | 0.011225 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_190_0_line_115 |  | 104 | 105 | 0.61717 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
116 | MV_190_0_line_116 |  | 105 | 112 | 0.0469 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
117 | MV_190_0_line_117 |  | 105 | 109 | 0.35775 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
118 | MV_190_0_line_118 |  | 106 | 107 | 0.058673 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
119 | MV_190_0_line_119 |  | 106 | 108 | 0.047358 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
120 | MV_190_0_line_120 |  | 107 | 140 | 0.16405 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
121 | MV_190_0_line_121 |  | 109 | 110 | 0.20107 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
122 | MV_190_0_line_122 |  | 109 | 111 | 0.054453 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
123 | MV_190_0_line_123 |  | 112 | 113 | 0.072617 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
124 | MV_190_0_line_124 |  | 114 | 115 | 0.092118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_190_0_line_125 |  | 115 | 116 | 0.043618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_190_0_line_126 |  | 116 | 118 | 0.22924 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_190_0_line_127 |  | 116 | 117 | 0.03866 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_190_0_line_128 |  | 118 | 119 | 0.25733 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_190_0_line_129 |  | 119 | 139 | 0.1369 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_190_0_line_130 |  | 120 | 121 | 0.007774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_190_0_line_131 |  | 120 | 122 | 0.073887 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
132 | MV_190_0_line_132 |  | 121 | 123 | 0.2722 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_190_0_line_133 |  | 122 | 124 | 0.02273 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
134 | MV_190_0_line_134 |  | 123 | 128 | 0.027976 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_190_0_line_135 |  | 124 | 125 | 0.034642 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
136 | MV_190_0_line_136 |  | 125 | 126 | 0.094291 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
137 | MV_190_0_line_137 |  | 125 | 127 | 0.1439 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_190_0_line_138 |  | 126 | 129 | 0.080187 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_190_0_line_139 |  | 127 | 130 | 0.027565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_190_0_line_140 |  | 131 | 132 | 0.05894 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
141 | MV_190_0_line_141 |  | 132 | 137 | 0.11431 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
142 | MV_190_0_line_142 |  | 134 | 135 | 0.037377 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
143 | MV_190_0_line_143 |  | 135 | 161 | 0.028213 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
144 | MV_190_0_line_144 |  | 135 | 160 | 0.074702 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
145 | MV_190_0_line_145 |  | 137 | 138 | 0.22648 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
146 | MV_190_0_line_146 |  | 137 | 139 | 0.15544 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
147 | MV_190_0_line_147 |  | 138 | 143 | 0.068086 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
148 | MV_190_0_line_148 |  | 139 | 142 | 0.036604 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
149 | MV_190_0_line_149 |  | 140 | 141 | 0.32354 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
150 | MV_190_0_line_150 |  | 145 | 147 | 0.13836 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
151 | MV_190_0_line_151 |  | 146 | 148 | 0.081138 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
152 | MV_190_0_line_152 |  | 148 | 149 | 0.02757 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
153 | MV_190_0_line_153 |  | 149 | 150 | 0.4024 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
154 | MV_190_0_line_154 |  | 150 | 151 | 0.024329 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
155 | MV_190_0_line_155 |  | 150 | 152 | 0.28958 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
156 | MV_190_0_line_156 |  | 152 | 153 | 0.029391 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
157 | MV_190_0_line_157 |  | 153 | 154 | 0.15333 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
158 | MV_190_0_line_158 |  | 154 | 155 | 0.069929 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
159 | MV_190_0_line_159 |  | 155 | 156 | 0.17275 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
160 | MV_190_0_line_160 |  | 156 | 157 | 0.032259 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
161 | MV_190_0_line_161 |  | 157 | 158 | 0.091811 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
162 | MV_190_0_line_162 |  | 158 | 159 | 0.035207 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_190_0_line_163 |  | 158 | 160 | 0.23216 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
164 | MV_190_0_line_164 |  | 161 | 168 | 0.015597 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_190_0_line_165 |  | 163 | 166 | 0.022035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_190_0_line_166 |  | 164 | 165 | 0.030181 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_190_0_line_167 |  | 165 | 166 | 0.95327 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_190_0_line_168 |  | 168 | 169 | 0.023209 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_190_0_trafo_164 | 25 MVA 110/20 kV | 170 | 139 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2567551.5546 | 1124392.4441
1 | 2567647.8744 | 1124316.3442
2 | 2567223.3821 | 1125028.3707
3 | 2568284.6408 | 1124025.5953
4 | 2567214.7581 | 1125086.8247
5 | 2566985.9157 | 1125376.1402
6 | 2569838.9714 | 1124565.0388
7 | 2570544.1244 | 1124660.2796
8 | 2566982.193 | 1125386.0433
9 | 2568442.6405 | 1123370.783
10 | 2568307.0844 | 1124018.3738
11 | 2566941.4081 | 1125515.0537
12 | 2567387.3014 | 1126426.0503
13 | 2568124.1412 | 1126774.0187
14 | 2568395.9487 | 1127668.9711
15 | 2568300.1376 | 1127259.3897
16 | 2568405.1112 | 1127687.1862
17 | 2568479.1389 | 1123341.6588
18 | 2568314.2074 | 1124027.0407
19 | 2570613.5096 | 1124661.3639
20 | 2570592.2279 | 1124857.8435
21 | 2570629.501 | 1124900.9501
22 | 2568566.1053 | 1123125.8713
23 | 2568350.5016 | 1124618.38
24 | 2568392.6859 | 1124645.0166
25 | 2572134.9086 | 1126030.2914
26 | 2572071.4853 | 1126068.2371
27 | 2571623.428 | 1125773.7157
28 | 2572642.2007 | 1126363.6119
29 | 2572544.3205 | 1126438.5497
30 | 2573361.6405 | 1126595.1384
31 | 2571352.4654 | 1125561.3354
32 | 2571780.3584 | 1125794.9342
33 | 2571647.2678 | 1125780.1798
34 | 2570913.0212 | 1126539.4823
35 | 2571347.0588 | 1125539.528
36 | 2571470.8799 | 1125149.491
37 | 2572548.7835 | 1125795.8207
38 | 2571810.023 | 1125794.662
39 | 2573696.3742 | 1126542.0978
40 | 2573687.2513 | 1126535.3898
41 | 2573722.8585 | 1126384.2039
42 | 2573377.8358 | 1126587.3519
43 | 2571659.7226 | 1125780.326
44 | 2571604.8499 | 1125453.9993
45 | 2571608.0218 | 1125456.4745
46 | 2571957.1752 | 1125472.1263
47 | 2571980.9305 | 1125548.3428
48 | 2572568.7184 | 1125522.2717
49 | 2571081.8418 | 1124830.707
50 | 2571432.1375 | 1125196.5089
51 | 2570973.6769 | 1124794.4863
52 | 2571085.9045 | 1124829.1423
53 | 2572724.7188 | 1125945.33
54 | 2572801.2919 | 1125947.4629
55 | 2572485.2482 | 1125803.5697
56 | 2570872.3783 | 1124700.6389
57 | 2570959.7681 | 1124757.2013
58 | 2572658.88 | 1125507.8772
59 | 2573559.2644 | 1122857.9884
60 | 2570989.087 | 1124873.0514
61 | 2573668.4823 | 1126352.87
62 | 2573545.971 | 1122840.5492
63 | 2567278.977 | 1128911.3166
64 | 2568271.3965 | 1127997.1879
65 | 2571105.1423 | 1127227.0791
66 | 2571086.1027 | 1127174.2885
67 | 2570685.7159 | 1127465.645
68 | 2571046.5744 | 1127032.6808
69 | 2570571.324 | 1127399.5805
70 | 2570605.9197 | 1127579.3458
71 | 2570776.9049 | 1127601.6368
72 | 2570967.2198 | 1127015.9587
73 | 2570907.1302 | 1126995.3603
74 | 2570892.036 | 1127018.0444
75 | 2570548.4493 | 1127363.841
76 | 2570568.4507 | 1127555.282
77 | 2570581.5546 | 1127632.7246
78 | 2570541.0773 | 1127696.832
79 | 2570509.2515 | 1127780.9962
80 | 2570148.3843 | 1127880.4219
81 | 2570857.6251 | 1127950.809
82 | 2570402.8363 | 1127565.4991
83 | 2570403.4413 | 1127564.7513
84 | 2570441.1726 | 1127508.0157
85 | 2570524.6039 | 1127534.5649
86 | 2570415.0275 | 1127463.8219
87 | 2570140.1596 | 1127875.0266
88 | 2570171.0791 | 1128024.4703
89 | 2570890.7619 | 1127963.344
90 | 2570103.2457 | 1128194.8357
91 | 2569893.2652 | 1127928.5145
92 | 2570254.6037 | 1128058.6302
93 | 2570450.8249 | 1127340.4062
94 | 2570455.0287 | 1127335.5617
95 | 2570414.7293 | 1127381.1043
96 | 2570484.6697 | 1127302.1221
97 | 2570403.1369 | 1127433.743
98 | 2570481.9671 | 1127267.9294
99 | 2570510.287 | 1127199.0676
100 | 2570508.3146 | 1127169.1845
101 | 2570473.7711 | 1127257.4754
102 | 2570381.9537 | 1127276.7131
103 | 2570900.1763 | 1128816.5681
104 | 2570890.6795 | 1128810.5443
105 | 2570673.3913 | 1128481.1445
106 | 2570122.0483 | 1128253.1272
107 | 2570064.7542 | 1128266.0956
108 | 2570106.664 | 1128208.3366
109 | 2570852.8397 | 1128570.1407
110 | 2571052.2553 | 1128595.9037
111 | 2570801.348 | 1128587.8543
112 | 2570626.4065 | 1128481.5291
113 | 2570606.1818 | 1128413.2825
114 | 2570976.4312 | 1126682.1368
115 | 2570908.4293 | 1126627.5373
116 | 2570878.8276 | 1126598.499
117 | 2570912.1018 | 1126578.9175
118 | 2570675.7994 | 1126688.1611
119 | 2570518.5297 | 1126809.5107
120 | 2570224.9012 | 1127334.7934
121 | 2570218.9279 | 1127329.7982
122 | 2570298.6683 | 1127330.583
123 | 2570013.4985 | 1127461.1598
124 | 2570296.6604 | 1127353.1931
125 | 2570305.5326 | 1127386.6772
126 | 2570353.5957 | 1127307.7124
127 | 2570281.7652 | 1127492.1358
128 | 2569994.9863 | 1127482.0178
129 | 2570377.7699 | 1127367.7124
130 | 2570291.8055 | 1127466.4639
131 | 2570358.2617 | 1127156.6141
132 | 2570417.2003 | 1127156.1577
133 | 2569912.447 | 1128006.6244
134 | 2569864.7576 | 1127911.5373
135 | 2569827.6483 | 1127916.0065
136 | 2570502.3602 | 1127583.6093
137 | 2570506.034 | 1127084.22
138 | 2570645.5445 | 1126906.4727
139 | 2570476.1896 | 1126934.8137
140 | 2569910.8833 | 1128322.979
141 | 2569598.5218 | 1128238.6484
142 | 2570512.7906 | 1126934.3344
143 | 2570675.6177 | 1126967.5568
144 | 2568298.3031 | 1127966.7867
145 | 2568597.107 | 1127739.2315
146 | 2568858.4363 | 1127889.7847
147 | 2568560.815 | 1127623.7295
148 | 2568898.8446 | 1127820.4748
149 | 2568916.1325 | 1127799.2084
150 | 2569229.1697 | 1127834.4759
151 | 2569251.9655 | 1127842.9749
152 | 2569235.9977 | 1127544.9741
153 | 2569206.6866 | 1127541.8555
154 | 2569313.5034 | 1127650.6875
155 | 2569381.8381 | 1127665.5364
156 | 2569502.3091 | 1127789.3433
157 | 2569529.8626 | 1127806.2457
158 | 2569556.8241 | 1127863.1046
159 | 2569530.2638 | 1127885.5945
160 | 2569753.5277 | 1127924.5008
161 | 2569828.5888 | 1127944.2042
162 | 2568323.8097 | 1127249.2268
163 | 2568168.4025 | 1126763.2018
164 | 2568340.0307 | 1126288.3494
165 | 2568320.1355 | 1126265.6092
166 | 2568187.1382 | 1126751.875
167 | 2571676.473 | 1125777.5015
168 | 2569813.019 | 1127945.124
169 | 2569813.4742 | 1127968.3222
170 | 2570476.1896 | 1126934.8137

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99126 | -0.29052 | 0.054544 | 0.026417
1 | 0.99125 | -0.29107 | 0 | 0
2 | 0.99144 | -0.2795 | 0.070708 | 0.034246
3 | 0.99116 | -0.29449 | 0 | 0
4 | 0.99144 | -0.27919 | 0 | 0
5 | 0.9915 | -0.27708 | 0 | 0
6 | 0.98997 | -0.024309 | 0.10503 | 0.050866
7 | 0.99012 | -0.023362 | 0.10395 | 0.050346
8 | 0.9915 | -0.27702 | 0.095024 | 0.046022
9 | 0.99107 | -0.29687 | 0 | 0
10 | 0.99116 | -0.29451 | 0.050104 | 0.024266
11 | 0.99153 | -0.27615 | 0 | 0
12 | 0.99192 | -0.25412 | 0.052545 | 0.025449
13 | 0.99229 | -0.23497 | 0 | 0
14 | 0.99276 | -0.21419 | 0.29247 | 0.14165
15 | 0.99248 | -0.2284 | 0.056878 | 0.027547
16 | 0.99277 | -0.21395 | 0 | 0
17 | 0.99107 | -0.29694 | 0.083737 | 0.040556
18 | 0.99116 | -0.29452 | 0 | 0
19 | 0.99014 | -0.023533 | 0 | 0
20 | 0.9901 | -0.02378 | 0 | 0
21 | 0.99009 | -0.0237 | 0.087711 | 0.04248
22 | 0.99104 | -0.29772 | 0.099963 | 0.048414
23 | 0.99109 | -0.295 | 0 | 0
24 | 0.99108 | -0.29497 | 0.050158 | 0.024292
25 | 0.99279 | -0.039345 | 0.14196 | 0.068756
26 | 0.99281 | -0.039216 | 0 | 0
27 | 0.99294 | -0.040039 | 0 | 0
28 | 0.98975 | -0.036724 | 0 | 0
29 | 0.98972 | -0.036902 | 0.11684 | 0.056587
30 | 0.98992 | -0.035596 | 0 | 0
31 | 0.9929 | -0.039848 | 0 | 0
32 | 0.99241 | -0.037386 | 0 | 0
33 | 0.99293 | -0.039968 | 0.11116 | 0.053838
34 | 0.99766 | 0.009575 | 0.056989 | 0.027601
35 | 0.9929 | -0.03983 | 0.067365 | 0.032626
36 | 0.9911 | -0.030251 | 0 | 0
37 | 0.99142 | -0.032106 | 0 | 0
38 | 0.9924 | -0.037334 | 0.14779 | 0.071578
39 | 0.99018 | -0.037508 | 0.087759 | 0.042504
40 | 0.99018 | -0.037496 | 0 | 0
41 | 0.99036 | -0.038562 | 0 | 0
42 | 0.98992 | -0.035566 | 0.13909 | 0.067362
43 | 0.99293 | -0.039948 | 0 | 0
44 | 0.99104 | -0.029825 | 0 | 0
45 | 0.99104 | -0.02982 | 0.10235 | 0.04957
46 | 0.99089 | -0.029817 | 0 | 0
47 | 0.99088 | -0.029693 | 0.10096 | 0.048898
48 | 0.99079 | -0.02942 | 0 | 0
49 | 0.99042 | -0.024904 | 0 | 0
50 | 0.99108 | -0.030355 | 0.13818 | 0.066922
51 | 0.99032 | -0.024081 | 0 | 0
52 | 0.99042 | -0.024896 | 0.14827 | 0.071809
53 | 0.99123 | -0.030907 | 0 | 0
54 | 0.99118 | -0.030548 | 0.11719 | 0.056759
55 | 0.99141 | -0.032173 | 0.084505 | 0.040928
56 | 0.99024 | -0.024366 | 0 | 0
57 | 0.9903 | -0.023887 | 0.15607 | 0.075589
58 | 0.99077 | -0.029312 | 0.058805 | 0.028481
59 | 0.99043 | -0.032018 | 0 | 0
60 | 0.9903 | -0.024196 | 0.11639 | 0.056371
61 | 0.9904 | -0.038136 | 0.089156 | 0.04318
62 | 0.99043 | -0.032002 | 0.06338 | 0.030697
63 | 0.99261 | -0.21895 | 0.098162 | 0.047542
64 | 0.99275 | -0.2145 | 0.0646 | 0.031287
65 | 0.997 | -0.07492 | 0.15018 | 0.072738
66 | 0.99701 | -0.074817 | 0 | 0
67 | 0.99731 | -0.077201 | 0 | 0
68 | 0.99693 | -0.075369 | 0.15027 | 0.072781
69 | 0.99727 | -0.07692 | 0 | 0
70 | 0.9974 | -0.074109 | 0 | 0
71 | 0.9973 | -0.07759 | 0.071993 | 0.034868
72 | 0.99692 | -0.07526 | 0 | 0
73 | 0.99691 | -0.075131 | 0 | 0
74 | 0.9969 | -0.07509 | 0.12214 | 0.059156
75 | 0.99727 | -0.076842 | 0.15596 | 0.075535
76 | 0.99748 | -0.072131 | 0.082839 | 0.040121
77 | 0.9973 | -0.076386 | 0 | 0
78 | 0.99717 | -0.079326 | 0.15633 | 0.075715
79 | 0.99702 | -0.082719 | 0 | 0
80 | 0.99602 | -0.10553 | 0 | 0
81 | 0.99697 | -0.084298 | 0 | 0
82 | 0.99798 | -0.053773 | 0.10355 | 0.050154
83 | 0.99798 | -0.053774 | 0.13278 | 0.064308
84 | 0.998 | -0.053967 | 0 | 0
85 | 0.99759 | -0.06975 | 0 | 0
86 | 0.99812 | -0.051501 | 0.14726 | 0.071323
87 | 0.99602 | -0.10551 | 0.16017 | 0.077572
88 | 0.99552 | -0.12526 | 0 | 0
89 | 0.99697 | -0.084324 | 0.12197 | 0.059071
90 | 0.99549 | -0.12587 | 0 | 0
91 | 0.99518 | -0.13329 | 0 | 0
92 | 0.9955 | -0.1257 | 0.12544 | 0.060754
93 | 0.99844 | -0.044386 | 0.092583 | 0.04484
94 | 0.99846 | -0.044067 | 0 | 0
95 | 0.99832 | -0.047049 | 0 | 0
96 | 0.99856 | -0.041849 | 0 | 0
97 | 0.9982 | -0.049766 | 0 | 0
98 | 0.99874 | -0.035125 | 0.16207 | 0.078496
99 | 0.99896 | -0.030462 | 0 | 0
100 | 0.99904 | -0.028754 | 0.122 | 0.059087
101 | 0.99877 | -0.03445 | 0 | 0
102 | 0.99874 | -0.035054 | 0 | 0
103 | 0.99524 | -0.13432 | 0.11415 | 0.055287
104 | 0.99524 | -0.13434 | 0 | 0
105 | 0.99528 | -0.13379 | 0 | 0
106 | 0.99548 | -0.12598 | 0 | 0
107 | 0.99548 | -0.12607 | 0 | 0
108 | 0.99549 | -0.1259 | 0.13374 | 0.064772
109 | 0.99523 | -0.13429 | 0 | 0
110 | 0.99518 | -0.13463 | 0.13944 | 0.067533
111 | 0.99522 | -0.13434 | 0.083165 | 0.040279
112 | 0.99528 | -0.13366 | 0.09078 | 0.043967
113 | 0.9953 | -0.13342 | 0 | 0
114 | 0.99795 | 0.010948 | 0.080844 | 0.039155
115 | 0.99796 | 0.010865 | 0 | 0
116 | 0.99796 | 0.010831 | 0 | 0
117 | 0.99784 | 0.011469 | 0 | 0
118 | 0.9987 | 0.0069207 | 0.084119 | 0.040741
119 | 0.99955 | 0.0023744 | 0 | 0
120 | 0.99865 | -0.037086 | 0.1619 | 0.078414
121 | 0.99865 | -0.03708 | 0 | 0
122 | 0.99867 | -0.036489 | 0.098878 | 0.047889
123 | 0.99861 | -0.036803 | 0 | 0
124 | 0.99868 | -0.036438 | 0 | 0
125 | 0.99869 | -0.03636 | 0 | 0
126 | 0.99871 | -0.036095 | 0.1326 | 0.064223
127 | 0.99867 | -0.036257 | 0 | 0
128 | 0.99861 | -0.036768 | 0.10576 | 0.051222
129 | 0.99869 | -0.035943 | 0.16324 | 0.079061
130 | 0.99867 | -0.036234 | 0.072206 | 0.034971
131 | 0.99954 | -0.0095401 | 0.087033 | 0.042152
132 | 0.99955 | -0.0094779 | 0 | 0
133 | 0.99517 | -0.1332 | 0.097376 | 0.047161
134 | 0.99514 | -0.13422 | 0.15083 | 0.073049
135 | 0.99506 | -0.1378 | 0.11536 | 0.055874
136 | 0.99758 | -0.069843 | 0.14314 | 0.069326
137 | 0.99956 | -0.0091893 | 0 | 0
138 | 0.99956 | -0.0093235 | 0 | 0
139 | 1 | 0 | -9.4699 | -3.8713
140 | 0.99545 | -0.12713 | 0.074387 | 0.036027
141 | 0.99541 | -0.12843 | 0.12106 | 0.058634
142 | 0.99999 | -5.5185e-05 | 0.12461 | 0.060351
143 | 0.99955 | -0.0094754 | 0.067918 | 0.032894
144 | 0.99275 | -0.21445 | 0 | 0
145 | 0.99275 | -0.21431 | 0 | 0
146 | 0.99348 | -0.19462 | 0 | 0
147 | 0.99274 | -0.21443 | 0.13824 | 0.066952
148 | 0.99352 | -0.19335 | 0.077452 | 0.037512
149 | 0.99354 | -0.1929 | 0 | 0
150 | 0.99377 | -0.18627 | 0 | 0
151 | 0.99377 | -0.18638 | 0.12654 | 0.061288
152 | 0.99417 | -0.16783 | 0 | 0
153 | 0.99419 | -0.16732 | 0.14339 | 0.069445
154 | 0.9943 | -0.16445 | 0 | 0
155 | 0.9944 | -0.15965 | 0.11342 | 0.05493
156 | 0.99469 | -0.14715 | 0.13523 | 0.065493
157 | 0.99471 | -0.14648 | 0 | 0
158 | 0.99479 | -0.14458 | 0 | 0
159 | 0.99478 | -0.14451 | 0.1622 | 0.078556
160 | 0.99499 | -0.13945 | 0 | 0
161 | 0.99505 | -0.13805 | 0.090914 | 0.044032
162 | 0.99247 | -0.22922 | 0 | 0
163 | 0.99228 | -0.23493 | 0.14115 | 0.068361
164 | 0.9922 | -0.23497 | 0.060352 | 0.02923
165 | 0.9922 | -0.23499 | 0 | 0
166 | 0.99227 | -0.23495 | 0 | 0
167 | 0.99293 | -0.039921 | 0.1308 | 0.06335
168 | 0.99504 | -0.13802 | 0 | 0
169 | 0.99504 | -0.13797 | 0.18109 | 0.087704
170 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.28401 | 0.019655 | -0.28401 | -0.024549 | 3.2865e-06 | -0.0048945 | 0.0082907 | 0.0083017 | 0.0083017 | 0.99126 | -0.29052 | 0.99125 | -0.29107 | 1.9719
1 | -0.33855 | -0.046072 | 0.3386 | 0.045234 | 5.0484e-05 | -0.00083719 | 0.0099502 | 0.0099466 | 0.0099502 | 0.99126 | -0.29052 | 0.99144 | -0.2795 | 2.4269
2 | 0.28401 | 0.024549 | -0.28398 | -0.057342 | 2.2344e-05 | -0.032793 | 0.0083017 | 0.0084379 | 0.0084379 | 0.99125 | -0.29107 | 0.99116 | -0.29449 | 2.0043
3 | -0.40931 | -0.07948 | 0.40931 | 0.077251 | 3.2035e-06 | -0.0022293 | 0.01214 | 0.012128 | 0.01214 | 0.99144 | -0.2795 | 0.99144 | -0.27919 | 2.8837
4 | 0.18372 | 0.039314 | -0.1837 | -0.086925 | 1.4869e-05 | -0.047611 | 0.0054719 | 0.0059196 | 0.0059196 | 0.99116 | -0.29449 | 0.99107 | -0.29687 | 1.4061
5 | 0.10027 | 0.018028 | -0.10027 | -0.018586 | 2.803e-07 | -0.0005588 | 0.002967 | 0.00297 | 0.00297 | 0.99116 | -0.29449 | 0.99116 | -0.29451 | 1.35
6 | -0.40931 | -0.077251 | 0.40933 | 0.062707 | 2.0748e-05 | -0.014544 | 0.012128 | 0.012057 | 0.012128 | 0.99144 | -0.27919 | 0.9915 | -0.27708 | 2.8808
7 | -0.40933 | -0.062707 | 0.40934 | 0.06231 | 5.6272e-07 | -0.00039674 | 0.012057 | 0.012055 | 0.012057 | 0.9915 | -0.27708 | 0.9915 | -0.27702 | 2.8638
8 | -0.10503 | -0.050866 | 0.10504 | 0.050043 | 1.4634e-05 | -0.00082347 | 0.0034028 | 0.0033923 | 0.0034028 | 0.98997 | -0.024309 | 0.99012 | -0.023362 | 1.6204
9 | -0.20899 | -0.10039 | 0.209 | 0.098756 | 4.2455e-06 | -0.0016327 | 0.0067598 | 0.0067393 | 0.0067598 | 0.99012 | -0.023362 | 0.99014 | -0.023533 | 3.0726
10 | -0.50436 | -0.10833 | 0.50437 | 0.10319 | 1.1296e-05 | -0.0051387 | 0.015019 | 0.014989 | 0.015019 | 0.9915 | -0.27702 | 0.99153 | -0.27615 | 3.5675
11 | 0.1837 | 0.086925 | -0.1837 | -0.088677 | 6.0109e-07 | -0.0017515 | 0.0059196 | 0.0059416 | 0.0059416 | 0.99107 | -0.29687 | 0.99107 | -0.29694 | 1.4113
12 | 0.050161 | -0.0056799 | -0.050161 | 0.0054171 | 3.2334e-08 | -0.00026286 | 0.0014703 | 0.0014694 | 0.0014703 | 0.99116 | -0.29451 | 0.99116 | -0.29452 | 0.66831
13 | -0.50437 | -0.10319 | 0.50453 | 0.10214 | 0.00016234 | -0.0010561 | 0.014989 | 0.014981 | 0.014989 | 0.99153 | -0.27615 | 0.99192 | -0.25412 | 3.6557
14 | -0.55708 | -0.12759 | 0.55724 | 0.12678 | 0.00016061 | -0.00080559 | 0.016632 | 0.016625 | 0.016632 | 0.99192 | -0.25412 | 0.99229 | -0.23497 | 4.0566
15 | -0.75874 | -0.19967 | 0.75887 | 0.17581 | 0.00012057 | -0.023858 | 0.022825 | 0.022657 | 0.022825 | 0.99229 | -0.23497 | 0.99247 | -0.22922 | 5.4216
16 | 0.20151 | 0.072888 | -0.2015 | -0.073956 | 2.3614e-06 | -0.0010675 | 0.0062339 | 0.0062446 | 0.0062446 | 0.99229 | -0.23497 | 0.99228 | -0.23493 | 2.8384
17 | 0.81593 | 0.20306 | -0.81575 | -0.20334 | 0.00017926 | -0.00027691 | 0.024449 | 0.024453 | 0.024453 | 0.99276 | -0.21419 | 0.99248 | -0.2284 | 5.9642
18 | -1.1084 | -0.34471 | 1.1084 | 0.34395 | 8.5e-06 | -0.0007599 | 0.033753 | 0.033746 | 0.033753 | 0.99276 | -0.21419 | 0.99277 | -0.21395 | 8.0172
19 | 0.75887 | 0.17579 | -0.75887 | -0.17581 | 9.4266e-06 | -1.9196e-05 | 0.022657 | 0.022657 | 0.022657 | 0.99248 | -0.2284 | 0.99247 | -0.22922 | 5.5262
20 | 0.13824 | 0.050251 | -0.13824 | -0.062276 | 3.236e-06 | -0.012024 | 0.0042771 | 0.0044089 | 0.0044089 | 0.99277 | -0.21395 | 0.99275 | -0.21431 | 1.2179
21 | -1.4094 | -0.45655 | 1.4103 | 0.40962 | 0.00085183 | -0.046931 | 0.043079 | 0.042672 | 0.043079 | 0.99277 | -0.21395 | 0.99348 | -0.19462 | 10.2326
22 | 0.16278 | 0.062346 | -0.16277 | -0.075587 | 3.402e-06 | -0.013241 | 0.0050684 | 0.0052186 | 0.0052186 | 0.99277 | -0.21395 | 0.99275 | -0.21445 | 1.2396
23 | 0.099965 | 0.048121 | -0.099963 | -0.048414 | 1.7338e-06 | -0.00029326 | 0.0032316 | 0.0032353 | 0.0032353 | 0.99107 | -0.29694 | 0.99104 | -0.29772 | 0.7891
24 | 0.050161 | -0.0054171 | -0.050158 | -0.023099 | 3.5721e-06 | -0.028516 | 0.0014694 | 0.0016084 | 0.0016084 | 0.99116 | -0.29452 | 0.99109 | -0.295 | 0.7311
25 | -0.29671 | -0.13914 | 0.29674 | 0.1329 | 3.227e-05 | -0.0062392 | 0.0095545 | 0.0094786 | 0.0095545 | 0.99014 | -0.023533 | 0.99024 | -0.024366 | 4.3429
26 | 0.087714 | 0.04038 | -0.087712 | -0.04061 | 2.7936e-06 | -0.00022954 | 0.0028153 | 0.0028181 | 0.0028181 | 0.99014 | -0.023533 | 0.9901 | -0.02378 | 1.342
27 | 0.087712 | 0.04061 | -0.087711 | -0.04248 | 8.545e-07 | -0.0018707 | 0.0028181 | 0.0028415 | 0.0028415 | 0.9901 | -0.02378 | 0.99009 | -0.0237 | 1.2916
28 | 0.050158 | 0.023099 | -0.050158 | -0.024292 | 1.7744e-07 | -0.0011939 | 0.0016084 | 0.0016233 | 0.0016233 | 0.99109 | -0.295 | 0.99108 | -0.29497 | 0.73785
29 | -0.14196 | -0.068756 | 0.14197 | 0.068671 | 2.7694e-06 | -8.5232e-05 | 0.0045865 | 0.0045854 | 0.0045865 | 0.99279 | -0.039345 | 0.99281 | -0.039216 | 2.1841
30 | -0.14197 | -0.068671 | 0.14198 | 0.052452 | 1.8533e-05 | -0.016219 | 0.0045854 | 0.0044006 | 0.0045854 | 0.99281 | -0.039216 | 0.99294 | -0.040039 | 2.0843
31 | 0.067367 | 0.022819 | -0.067365 | -0.032097 | 2.3541e-06 | -0.0092787 | 0.0020679 | 0.0021695 | 0.0021695 | 0.99294 | -0.040039 | 0.9929 | -0.039848 | 0.98614
32 | 1.9682 | 0.77183 | -1.9671 | -0.77657 | 0.0010862 | -0.0047406 | 0.061463 | 0.061517 | 0.061517 | 0.99294 | -0.040039 | 0.99241 | -0.037386 | 27.9621
33 | 0.24196 | 0.11591 | -0.24196 | -0.11649 | 2.0087e-06 | -0.00058102 | 0.0078 | 0.0078074 | 0.0078074 | 0.99294 | -0.040039 | 0.99293 | -0.039968 | 3.5488
34 | -2.4195 | -0.96301 | 2.4301 | 0.96845 | 0.010665 | 0.0054451 | 0.075708 | 0.075695 | 0.075708 | 0.99294 | -0.040039 | 0.99766 | 0.009575 | 36.0515
35 | 0.11684 | 0.056445 | -0.11684 | -0.056587 | 3.1475e-06 | -0.00014219 | 0.0037846 | 0.0037865 | 0.0037865 | 0.98975 | -0.036724 | 0.98972 | -0.036902 | 1.8031
36 | -0.11684 | -0.056445 | 0.11686 | 0.055573 | 1.9231e-05 | -0.00087196 | 0.0037846 | 0.0037735 | 0.0037846 | 0.98975 | -0.036724 | 0.98992 | -0.035596 | 1.8022
37 | 0.13909 | 0.066941 | -0.13909 | -0.067362 | 4.8786e-07 | -0.00042136 | 0.0045012 | 0.0045066 | 0.0045066 | 0.98992 | -0.035596 | 0.98992 | -0.035566 | 2.0484
38 | -0.25595 | -0.12251 | 0.25601 | 0.10429 | 6.9361e-05 | -0.018226 | 0.0082747 | 0.0080593 | 0.0082747 | 0.98992 | -0.035596 | 0.99018 | -0.037496 | 3.7612
39 | 0.067365 | 0.032097 | -0.067365 | -0.032626 | 1.4162e-07 | -0.00052887 | 0.0021695 | 0.0021762 | 0.0021762 | 0.9929 | -0.039848 | 0.9929 | -0.03983 | 0.98917
40 | 1.1835 | 0.46568 | -1.1819 | -0.48589 | 0.0016192 | -0.020207 | 0.036994 | 0.037219 | 0.037219 | 0.99241 | -0.037386 | 0.9911 | -0.030251 | 16.9178
41 | 0.63582 | 0.24001 | -0.63517 | -0.26885 | 0.00065492 | -0.028843 | 0.019769 | 0.020083 | 0.020083 | 0.99241 | -0.037386 | 0.99142 | -0.032106 | 9.1285
42 | 0.14779 | 0.070882 | -0.14779 | -0.071578 | 8.9937e-07 | -0.00069532 | 0.0047678 | 0.0047766 | 0.0047766 | 0.99241 | -0.037386 | 0.9924 | -0.037334 | 2.1712
43 | 0.1308 | 0.062651 | -0.1308 | -0.062951 | 3.0263e-07 | -0.00029978 | 0.0042165 | 0.0042203 | 0.0042203 | 0.99293 | -0.039968 | 0.99293 | -0.039948 | 1.9183
44 | -2.4871 | -0.99605 | 2.4876 | 0.99627 | 0.00042237 | 0.00021768 | 0.077523 | 0.077522 | 0.077523 | 0.99766 | 0.009575 | 0.99784 | 0.011469 | 36.9155
45 | 0.71809 | 0.31497 | -0.71756 | -0.33225 | 0.00052271 | -0.017279 | 0.022839 | 0.023048 | 0.023048 | 0.9911 | -0.030251 | 0.99042 | -0.024904 | 10.4763
46 | 0.13818 | 0.066852 | -0.13818 | -0.066922 | 2.1703e-06 | -7.0081e-05 | 0.004471 | 0.0044719 | 0.0044719 | 0.9911 | -0.030251 | 0.99108 | -0.030355 | 2.1295
47 | 0.10236 | 0.037932 | -0.10235 | -0.049476 | 6.9064e-06 | -0.011543 | 0.0031794 | 0.0033113 | 0.0033113 | 0.9911 | -0.030251 | 0.99104 | -0.029825 | 1.5052
48 | 0.22323 | 0.066133 | -0.22318 | -0.083905 | 4.7646e-05 | -0.017772 | 0.0067813 | 0.0069463 | 0.0069463 | 0.9911 | -0.030251 | 0.99089 | -0.029817 | 3.1574
49 | 0.084506 | 0.040853 | -0.084505 | -0.040928 | 8.5211e-07 | -7.4571e-05 | 0.002733 | 0.002734 | 0.002734 | 0.99142 | -0.032106 | 0.99141 | -0.032173 | 1.3019
50 | 0.55066 | 0.228 | -0.55055 | -0.23436 | 0.00010998 | -0.0063598 | 0.017354 | 0.017426 | 0.017426 | 0.99142 | -0.032106 | 0.99123 | -0.030907 | 7.9208
51 | -0.087759 | -0.042504 | 0.087759 | 0.042491 | 1.6304e-07 | -1.3152e-05 | 0.0028428 | 0.0028426 | 0.0028428 | 0.99018 | -0.037508 | 0.99018 | -0.037496 | 1.3537
52 | -0.34377 | -0.14678 | 0.34384 | 0.1372 | 6.4358e-05 | -0.0095805 | 0.010898 | 0.010791 | 0.010898 | 0.99018 | -0.037496 | 0.99036 | -0.038562 | 4.9535
53 | -0.34384 | -0.1372 | 0.34385 | 0.13713 | 1.3019e-05 | -6.5331e-05 | 0.010791 | 0.01079 | 0.010791 | 0.99036 | -0.038562 | 0.9904 | -0.038136 | 5.1385
54 | 0.1308 | 0.062951 | -0.1308 | -0.06335 | 4.0321e-07 | -0.00039859 | 0.0042203 | 0.0042253 | 0.0042253 | 0.99293 | -0.039948 | 0.99293 | -0.039921 | 1.9206
55 | 0.10235 | 0.049476 | -0.10235 | -0.04957 | 5.8795e-08 | -9.4158e-05 | 0.0033113 | 0.0033125 | 0.0033125 | 0.99104 | -0.029825 | 0.99104 | -0.02982 | 1.5057
56 | 0.10096 | 0.046351 | -0.10096 | -0.048898 | 1.5343e-06 | -0.0025469 | 0.0032365 | 0.0032681 | 0.0032681 | 0.99089 | -0.029817 | 0.99088 | -0.029693 | 1.4855
57 | 0.12222 | 0.037554 | -0.12221 | -0.05324 | 1.2892e-05 | -0.015686 | 0.0037249 | 0.0038839 | 0.0038839 | 0.99089 | -0.029817 | 0.99079 | -0.02942 | 1.7654
58 | 0.12221 | 0.05324 | -0.12221 | -0.055398 | 1.867e-06 | -0.0021583 | 0.0038839 | 0.0039094 | 0.0039094 | 0.99079 | -0.02942 | 0.99077 | -0.029312 | 1.777
59 | 0.5693 | 0.26054 | -0.56924 | -0.26371 | 6.0522e-05 | -0.0031635 | 0.018248 | 0.018287 | 0.018287 | 0.99042 | -0.024904 | 0.99032 | -0.024081 | 8.3123
60 | 0.14827 | 0.071707 | -0.14827 | -0.071809 | 1.3362e-07 | -0.00010168 | 0.0048004 | 0.0048017 | 0.0048017 | 0.99042 | -0.024904 | 0.99042 | -0.024896 | 2.1826
61 | 0.11639 | 0.056279 | -0.11639 | -0.056371 | 2.0266e-06 | -9.2466e-05 | 0.0037687 | 0.0037698 | 0.0037698 | 0.99032 | -0.024081 | 0.9903 | -0.024196 | 1.7952
62 | 0.45284 | 0.20743 | -0.45283 | -0.20837 | 1.1435e-05 | -0.0009473 | 0.014519 | 0.014531 | 0.014531 | 0.99032 | -0.024081 | 0.9903 | -0.023887 | 6.6048
63 | 0.55055 | 0.23436 | -0.55052 | -0.23615 | 3.1203e-05 | -0.0017942 | 0.017426 | 0.017446 | 0.017446 | 0.99123 | -0.030907 | 0.99118 | -0.030548 | 7.9302
64 | 0.43333 | 0.17939 | -0.43301 | -0.18031 | 0.0003185 | -0.00092234 | 0.013659 | 0.013672 | 0.013672 | 0.99118 | -0.030548 | 0.9904 | -0.038136 | 6.5103
65 | -0.29674 | -0.1329 | 0.29676 | 0.13279 | 1.6661e-05 | -0.00011143 | 0.0094786 | 0.0094771 | 0.0094786 | 0.99024 | -0.024366 | 0.9903 | -0.023887 | 4.5136
66 | 0.063401 | 0.026917 | -0.063381 | -0.030183 | 2.0468e-05 | -0.0032658 | 0.0020069 | 0.0020461 | 0.0020461 | 0.99077 | -0.029312 | 0.99043 | -0.032018 | 0.97433
67 | 0.063381 | 0.030183 | -0.06338 | -0.030697 | 1.2294e-07 | -0.00051355 | 0.0020461 | 0.0020526 | 0.0020526 | 0.99043 | -0.032018 | 0.99043 | -0.032002 | 0.93299
68 | -0.098162 | -0.047542 | 0.098172 | 0.045835 | 9.6108e-06 | -0.001707 | 0.003172 | 0.0031505 | 0.003172 | 0.99261 | -0.21895 | 0.99275 | -0.2145 | 0.77366
69 | -0.16277 | -0.077122 | 0.16277 | 0.075587 | 4.0797e-07 | -0.001535 | 0.0052375 | 0.0052186 | 0.0052375 | 0.99275 | -0.2145 | 0.99275 | -0.21445 | 1.2441
70 | -0.15018 | -0.072738 | 0.15019 | 0.072673 | 2.3338e-06 | -6.5133e-05 | 0.0048317 | 0.0048308 | 0.0048317 | 0.997 | -0.07492 | 0.99701 | -0.074817 | 2.3008
71 | -0.42263 | -0.19938 | 0.42276 | 0.18633 | 0.0001331 | -0.013044 | 0.01353 | 0.013373 | 0.01353 | 0.99701 | -0.074817 | 0.99731 | -0.077201 | 6.15
72 | 0.27244 | 0.1267 | -0.27242 | -0.12687 | 1.983e-05 | -0.00016203 | 0.0086996 | 0.0087017 | 0.0087017 | 0.99701 | -0.074817 | 0.99693 | -0.075369 | 4.1437
73 | 0.15597 | 0.070567 | -0.15596 | -0.074527 | 5.5219e-06 | -0.0039605 | 0.0049551 | 0.0050035 | 0.0050035 | 0.99731 | -0.077201 | 0.99727 | -0.07692 | 2.2743
74 | -0.65072 | -0.29156 | 0.65076 | 0.29144 | 4.2175e-05 | -0.00011778 | 0.02064 | 0.020638 | 0.02064 | 0.99731 | -0.077201 | 0.9974 | -0.074109 | 5.0341
75 | 0.071994 | 0.034658 | -0.071993 | -0.034868 | 6.25e-07 | -0.00020988 | 0.0023128 | 0.0023154 | 0.0023154 | 0.99731 | -0.077201 | 0.9973 | -0.07759 | 0.56474
76 | 0.12215 | 0.054086 | -0.12214 | -0.056221 | 1.8102e-06 | -0.002136 | 0.0038681 | 0.0038936 | 0.0038936 | 0.99693 | -0.075369 | 0.99692 | -0.07526 | 1.7698
77 | 0.15596 | 0.074527 | -0.15596 | -0.075535 | 1.4217e-06 | -0.0010072 | 0.0050035 | 0.0050161 | 0.0050161 | 0.99727 | -0.07692 | 0.99727 | -0.076842 | 2.2801
78 | -4.7849 | -1.8762 | 4.7852 | 1.8749 | 0.0003623 | -0.0013678 | 0.14875 | 0.14874 | 0.14875 | 0.9974 | -0.074109 | 0.99748 | -0.072131 | 35.3336
79 | 4.1341 | 1.5848 | -4.1338 | -1.5867 | 0.00035271 | -0.0019059 | 0.12814 | 0.12817 | 0.12817 | 0.9974 | -0.074109 | 0.9973 | -0.076386 | 30.4435
80 | 0.12214 | 0.056221 | -0.12214 | -0.05849 | 1.9488e-06 | -0.0022681 | 0.0038936 | 0.0039215 | 0.0039215 | 0.99692 | -0.07526 | 0.99691 | -0.075131 | 1.7825
81 | 0.12214 | 0.05849 | -0.12214 | -0.059156 | 5.7808e-07 | -0.00066655 | 0.0039215 | 0.0039299 | 0.0039299 | 0.99691 | -0.075131 | 0.9969 | -0.07509 | 1.7863
82 | -4.8681 | -1.915 | 4.8685 | 1.9134 | 0.00044506 | -0.0016085 | 0.15139 | 0.15137 | 0.15139 | 0.99748 | -0.072131 | 0.99759 | -0.06975 | 35.9602
83 | 4.1338 | 1.5867 | -4.1333 | -1.5892 | 0.00045584 | -0.0024612 | 0.12817 | 0.1282 | 0.1282 | 0.9973 | -0.076386 | 0.99717 | -0.079326 | 30.4506
84 | 3.977 | 1.5135 | -3.9765 | -1.5164 | 0.00050217 | -0.002972 | 0.12319 | 0.12322 | 0.12322 | 0.99717 | -0.079326 | 0.99702 | -0.082719 | 29.2689
85 | 3.8545 | 1.4591 | -3.8512 | -1.4799 | 0.0032743 | -0.020779 | 0.11933 | 0.11958 | 0.11958 | 0.99702 | -0.082719 | 0.99602 | -0.10553 | 28.403
86 | 0.12197 | 0.057343 | -0.12197 | -0.057836 | 4.2134e-06 | -0.00049252 | 0.0039023 | 0.0039085 | 0.0039085 | 0.99702 | -0.082719 | 0.99697 | -0.084298 | 0.95329
87 | 0.16017 | 0.07734 | -0.16017 | -0.077572 | 3.4847e-07 | -0.00023243 | 0.005155 | 0.0051579 | 0.0051579 | 0.99602 | -0.10553 | 0.99602 | -0.10551 | 2.3445
88 | 3.6911 | 1.4025 | -3.6897 | -1.4007 | 0.0013613 | 0.0017838 | 0.11444 | 0.11444 | 0.11444 | 0.99602 | -0.10553 | 0.99552 | -0.12526 | 27.9127
89 | 0.12197 | 0.057836 | -0.12197 | -0.059071 | 2.6839e-07 | -0.0012353 | 0.0039085 | 0.003924 | 0.003924 | 0.99697 | -0.084298 | 0.99697 | -0.084324 | 1.084
90 | -0.10355 | -0.050154 | 0.10355 | 0.050131 | 1.414e-08 | -2.2848e-05 | 0.0033282 | 0.0033279 | 0.0033282 | 0.99798 | -0.053773 | 0.99798 | -0.053774 | 1.5128
91 | -0.23633 | -0.11444 | 0.23634 | 0.11279 | 5.3231e-06 | -0.0016465 | 0.0075954 | 0.0075748 | 0.0075954 | 0.99798 | -0.053774 | 0.998 | -0.053967 | 3.4525
92 | 5.0132 | 1.9847 | -5.0117 | -1.9826 | 0.001518 | 0.0020849 | 0.15596 | 0.15596 | 0.15596 | 0.998 | -0.053967 | 0.99759 | -0.06975 | 38.039
93 | -5.2495 | -2.0975 | 5.25 | 2.096 | 0.00050512 | -0.0015007 | 0.16352 | 0.1635 | 0.16352 | 0.998 | -0.053967 | 0.99812 | -0.051501 | 38.84
94 | 0.14314 | 0.069263 | -0.14314 | -0.069326 | 2.032e-06 | -6.2707e-05 | 0.0046016 | 0.0046024 | 0.0046024 | 0.99759 | -0.06975 | 0.99758 | -0.069843 | 2.1916
95 | -5.3973 | -2.1673 | 5.3977 | 2.1663 | 0.00036741 | -0.0010131 | 0.16822 | 0.1682 | 0.16822 | 0.99812 | -0.051501 | 0.9982 | -0.049766 | 39.9563
96 | 0.32921 | 0.14568 | -0.3292 | -0.15428 | 9.1589e-06 | -0.0086009 | 0.010439 | 0.010543 | 0.010543 | 0.99552 | -0.12526 | 0.99549 | -0.12587 | 2.5042
97 | 2.8074 | 1.0289 | -2.8066 | -1.0393 | 0.00081283 | -0.010421 | 0.086703 | 0.086815 | 0.086815 | 0.99552 | -0.12526 | 0.99518 | -0.13329 | 20.6211
98 | 0.55308 | 0.22613 | -0.55307 | -0.22953 | 9.9234e-06 | -0.0034027 | 0.017327 | 0.017364 | 0.017364 | 0.99552 | -0.12526 | 0.9955 | -0.1257 | 4.1245
99 | 0.3292 | 0.15428 | -0.3292 | -0.15481 | 5.6693e-07 | -0.00052676 | 0.010543 | 0.010549 | 0.010549 | 0.99549 | -0.12587 | 0.99549 | -0.1259 | 2.5057
100 | 0.097377 | 0.045251 | -0.097376 | -0.047161 | 1.0544e-06 | -0.0019102 | 0.0031147 | 0.0031385 | 0.0031385 | 0.99518 | -0.13329 | 0.99517 | -0.1332 | 1.4266
101 | 2.7092 | 0.9941 | -2.7091 | -0.99536 | 9.1335e-05 | -0.0012632 | 0.083711 | 0.083724 | 0.083724 | 0.99518 | -0.13329 | 0.99514 | -0.13422 | 19.887
102 | 0.42763 | 0.16878 | -0.42757 | -0.16933 | 6.3295e-05 | -0.0005488 | 0.013331 | 0.013338 | 0.013338 | 0.9955 | -0.1257 | 0.9953 | -0.13342 | 3.2532
103 | -5.4914 | -2.208 | 5.4915 | 2.2079 | 6.8744e-05 | -0.00018116 | 0.17112 | 0.17112 | 0.17112 | 0.99844 | -0.044386 | 0.99846 | -0.044067 | 40.6469
104 | 5.3988 | 2.1632 | -5.3982 | -2.1647 | 0.00056307 | -0.0015545 | 0.16816 | 0.16818 | 0.16818 | 0.99844 | -0.044386 | 0.99832 | -0.047049 | 39.9475
105 | -5.4915 | -2.2079 | 5.4919 | 2.2066 | 0.00047841 | -0.0012612 | 0.17112 | 0.1711 | 0.17112 | 0.99846 | -0.044067 | 0.99856 | -0.041849 | 40.6463
106 | 5.3982 | 2.1647 | -5.3977 | -2.1663 | 0.00057505 | -0.0015865 | 0.16818 | 0.1682 | 0.1682 | 0.99832 | -0.047049 | 0.9982 | -0.049766 | 39.9529
107 | -5.4919 | -2.2066 | 5.4926 | 2.2076 | 0.00071576 | 0.00099201 | 0.1711 | 0.1711 | 0.1711 | 0.99856 | -0.041849 | 0.99874 | -0.035125 | 41.7323
108 | -5.6547 | -2.2861 | 5.6549 | 2.2857 | 0.00015096 | -0.00036713 | 0.1763 | 0.17629 | 0.1763 | 0.99874 | -0.035125 | 0.99877 | -0.03445 | 41.8754
109 | -6.3905 | -2.6173 | 6.391 | 2.6165 | 0.00043747 | -0.00074276 | 0.19956 | 0.19955 | 0.19956 | 0.99896 | -0.030462 | 0.99904 | -0.028754 | 47.4013
110 | 6.3905 | 2.6173 | -6.3895 | -2.619 | 0.0010218 | -0.0017335 | 0.19956 | 0.19959 | 0.19959 | 0.99896 | -0.030462 | 0.99877 | -0.03445 | 47.4082
111 | -6.513 | -2.6756 | 6.5155 | 2.6791 | 0.0025079 | 0.003521 | 0.20346 | 0.20346 | 0.20346 | 0.99904 | -0.028754 | 0.99956 | -0.0091893 | 49.6235
112 | 0.73466 | 0.3333 | -0.73464 | -0.33716 | 2.0276e-05 | -0.0038566 | 0.023317 | 0.023363 | 0.023363 | 0.99877 | -0.03445 | 0.99874 | -0.035054 | 5.5495
113 | 0.73464 | 0.33716 | -0.73462 | -0.33719 | 1.6347e-05 | -3.0573e-05 | 0.023363 | 0.023364 | 0.023364 | 0.99874 | -0.035054 | 0.99871 | -0.036095 | 5.6986
114 | -0.11415 | -0.055287 | 0.11415 | 0.055022 | 2.0265e-07 | -0.0002654 | 0.003679 | 0.0036756 | 0.003679 | 0.99524 | -0.13432 | 0.99524 | -0.13434 | 1.6723
115 | -0.11415 | -0.055022 | 0.11416 | 0.034052 | 3.7655e-06 | -0.02097 | 0.0036756 | 0.0034553 | 0.0036756 | 0.99524 | -0.13434 | 0.99528 | -0.13379 | 1.0154
116 | -0.33678 | -0.12942 | 0.33678 | 0.12782 | 2.4767e-06 | -0.001592 | 0.010464 | 0.010448 | 0.010464 | 0.99528 | -0.13379 | 0.99528 | -0.13366 | 2.8907
117 | 0.22262 | 0.095364 | -0.22261 | -0.10751 | 8.7001e-06 | -0.01215 | 0.0070245 | 0.0071707 | 0.0071707 | 0.99528 | -0.13379 | 0.99523 | -0.13429 | 1.9808
118 | 0.19546 | 0.091827 | -0.19546 | -0.094048 | 8.4588e-07 | -0.0022204 | 0.0062624 | 0.00629 | 0.00629 | 0.99548 | -0.12598 | 0.99548 | -0.12607 | 1.4941
119 | -0.19546 | -0.091827 | 0.19546 | 0.090035 | 6.7736e-07 | -0.0017922 | 0.0062624 | 0.0062405 | 0.0062624 | 0.99548 | -0.12598 | 0.99549 | -0.1259 | 1.4875
120 | 0.19546 | 0.094048 | -0.19545 | -0.094251 | 4.6284e-06 | -0.00020371 | 0.00629 | 0.0062927 | 0.0062927 | 0.99548 | -0.12607 | 0.99545 | -0.12713 | 1.5348
121 | 0.13945 | 0.0673 | -0.13944 | -0.067533 | 7.231e-06 | -0.00023322 | 0.0044912 | 0.0044942 | 0.0044942 | 0.99523 | -0.13429 | 0.99518 | -0.13463 | 2.1401
122 | 0.083166 | 0.040215 | -0.083165 | -0.040279 | 6.9678e-07 | -6.3951e-05 | 0.0026795 | 0.0026803 | 0.0026803 | 0.99523 | -0.13429 | 0.99522 | -0.13434 | 1.2763
123 | -0.42756 | -0.17179 | 0.42757 | 0.16933 | 6.2522e-06 | -0.0024633 | 0.013365 | 0.013338 | 0.013365 | 0.99528 | -0.13366 | 0.9953 | -0.13342 | 3.6919
124 | -0.080844 | -0.039155 | 0.080845 | 0.036964 | 8.2161e-07 | -0.0021902 | 0.0025984 | 0.0025714 | 0.0025984 | 0.99795 | 0.010948 | 0.99796 | 0.010865 | 1.1811
125 | -0.080845 | -0.036964 | 0.080845 | 0.035927 | 3.8317e-07 | -0.0010371 | 0.0025714 | 0.0025591 | 0.0025714 | 0.99796 | 0.010865 | 0.99796 | 0.010831 | 1.1688
126 | -2.5687 | -1.0314 | 2.5707 | 1.0265 | 0.0019606 | -0.0048735 | 0.08007 | 0.080011 | 0.08007 | 0.99796 | 0.010831 | 0.9987 | 0.0069207 | 36.3953
127 | 2.4879 | 0.99544 | -2.4876 | -0.99627 | 0.00031012 | -0.00082718 | 0.077512 | 0.077522 | 0.077522 | 0.99796 | 0.010831 | 0.99784 | 0.011469 | 35.2373
128 | -2.6548 | -1.0672 | 2.6571 | 1.0618 | 0.002348 | -0.0054367 | 0.082706 | 0.08264 | 0.082706 | 0.9987 | 0.0069207 | 0.99955 | 0.0023744 | 37.5936
129 | -2.6571 | -1.0618 | 2.6584 | 1.0589 | 0.0012476 | -0.0028971 | 0.08264 | 0.082605 | 0.08264 | 0.99955 | 0.0023744 | 1 | 0 | 37.5637
130 | 0.10577 | 0.043891 | -0.10577 | -0.044076 | 1.1379e-07 | -0.00018508 | 0.0033101 | 0.0033122 | 0.0033122 | 0.99865 | -0.037086 | 0.99865 | -0.03708 | 1.5055
131 | -0.26767 | -0.12231 | 0.26767 | 0.12222 | 4.9079e-06 | -8.6988e-05 | 0.0085069 | 0.0085057 | 0.0085069 | 0.99865 | -0.037086 | 0.99867 | -0.036489 | 2.4305
132 | 0.10577 | 0.044076 | -0.10576 | -0.050556 | 4.0764e-06 | -0.00648 | 0.0033122 | 0.0033887 | 0.0033887 | 0.99865 | -0.03708 | 0.99861 | -0.036803 | 1.5403
133 | -0.36655 | -0.17011 | 0.36655 | 0.16933 | 1.4967e-06 | -0.00077662 | 0.011681 | 0.011671 | 0.011681 | 0.99867 | -0.036489 | 0.99868 | -0.036438 | 3.2268
134 | 0.10576 | 0.050556 | -0.10576 | -0.051222 | 4.2992e-07 | -0.00066598 | 0.0033887 | 0.003397 | 0.003397 | 0.99861 | -0.036803 | 0.99861 | -0.036768 | 1.5441
135 | -0.36655 | -0.16933 | 0.36656 | 0.16815 | 2.2765e-06 | -0.0011837 | 0.011671 | 0.011657 | 0.011671 | 0.99868 | -0.036438 | 0.99869 | -0.03636 | 3.2241
136 | -0.43876 | -0.19903 | 0.43877 | 0.19581 | 8.8086e-06 | -0.0032199 | 0.013927 | 0.013888 | 0.013927 | 0.99869 | -0.03636 | 0.99871 | -0.036095 | 3.8471
137 | 0.072207 | 0.030888 | -0.072206 | -0.034315 | 1.0075e-06 | -0.0034263 | 0.0022701 | 0.0023109 | 0.0023109 | 0.99869 | -0.03636 | 0.99867 | -0.036257 | 1.0504
138 | 0.16324 | 0.077153 | -0.16324 | -0.079061 | 2.9291e-06 | -0.0019087 | 0.005219 | 0.0052428 | 0.0052428 | 0.99871 | -0.036095 | 0.99869 | -0.035943 | 2.3831
139 | 0.072206 | 0.034315 | -0.072206 | -0.034971 | 1.9722e-07 | -0.00065635 | 0.0023109 | 0.0023191 | 0.0023191 | 0.99867 | -0.036257 | 0.99867 | -0.036234 | 1.0541
140 | -0.087033 | -0.042152 | 0.087034 | 0.042082 | 8.1887e-07 | -6.9787e-05 | 0.0027929 | 0.002792 | 0.0027929 | 0.99954 | -0.0095401 | 0.99955 | -0.0094779 | 1.3299
141 | -0.087034 | -0.042082 | 0.087035 | 0.04194 | 8.1746e-07 | -0.00014258 | 0.002792 | 0.0027902 | 0.002792 | 0.99955 | -0.0094779 | 0.99956 | -0.0091893 | 0.79771
142 | 2.5583 | 0.92231 | -2.5581 | -0.92212 | 0.00016581 | 0.00019215 | 0.078888 | 0.078888 | 0.078888 | 0.99514 | -0.13422 | 0.99506 | -0.1378 | 19.2411
143 | 0.272 | 0.13079 | -0.272 | -0.13082 | 1.5419e-06 | -3.3925e-05 | 0.0087559 | 0.0087563 | 0.0087563 | 0.99506 | -0.1378 | 0.99505 | -0.13805 | 2.1357
144 | 2.1708 | 0.73546 | -2.1706 | -0.73817 | 0.00012093 | -0.0027144 | 0.066492 | 0.066519 | 0.066519 | 0.99506 | -0.1378 | 0.99499 | -0.13945 | 15.8002
145 | 0.067919 | 0.024163 | -0.067919 | -0.032807 | 3.7502e-07 | -0.008644 | 0.0020819 | 0.0021783 | 0.0021783 | 0.99956 | -0.0091893 | 0.99956 | -0.0093235 | 0.51742
146 | -6.6704 | -2.7452 | 6.6729 | 2.7416 | 0.0024682 | -0.0036698 | 0.20832 | 0.20825 | 0.20832 | 0.99956 | -0.0091893 | 1 | 0 | 49.4822
147 | 0.067919 | 0.032807 | -0.067918 | -0.032894 | 2.3041e-07 | -8.7714e-05 | 0.0021783 | 0.0021795 | 0.0021795 | 0.99956 | -0.0093235 | 0.99955 | -0.0094754 | 0.53157
148 | 0.12461 | 0.060308 | -0.12461 | -0.060351 | 1.0417e-06 | -4.3045e-05 | 0.0039963 | 0.0039969 | 0.0039969 | 1 | 0 | 0.99999 | -5.5185e-05 | 1.9033
149 | 0.12107 | 0.058224 | -0.12106 | -0.058634 | 3.505e-06 | -0.00040988 | 0.0038958 | 0.0039011 | 0.0039011 | 0.99545 | -0.12713 | 0.99541 | -0.12843 | 0.95148
150 | 0.13824 | 0.062276 | -0.13824 | -0.066952 | 1.3157e-06 | -0.0046769 | 0.0044089 | 0.0044665 | 0.0044665 | 0.99275 | -0.21431 | 0.99274 | -0.21443 | 1.2338
151 | -1.4103 | -0.40962 | 1.4103 | 0.40661 | 5.4043e-05 | -0.0030098 | 0.042672 | 0.042647 | 0.042672 | 0.99348 | -0.19462 | 0.99352 | -0.19335 | 10.1359
152 | -1.4878 | -0.44412 | 1.4878 | 0.4431 | 2.0533e-05 | -0.0010208 | 0.045114 | 0.045105 | 0.045114 | 0.99352 | -0.19335 | 0.99354 | -0.1929 | 10.7158
153 | -1.4878 | -0.4431 | 1.4881 | 0.42819 | 0.0002988 | -0.014903 | 0.045105 | 0.044981 | 0.045105 | 0.99354 | -0.1929 | 0.99377 | -0.18627 | 10.7138
154 | 0.12654 | 0.061257 | -0.12654 | -0.061288 | 2.8926e-07 | -3.0679e-05 | 0.0040839 | 0.0040843 | 0.0040843 | 0.99377 | -0.18627 | 0.99377 | -0.18638 | 0.99618
155 | -1.6146 | -0.48945 | 1.6151 | 0.4898 | 0.00049578 | 0.00034749 | 0.049011 | 0.049007 | 0.049011 | 0.99377 | -0.18627 | 0.99417 | -0.16783 | 11.9538
156 | -1.6151 | -0.4898 | 1.6152 | 0.48871 | 2.5831e-05 | -0.001086 | 0.049007 | 0.048998 | 0.049007 | 0.99417 | -0.16783 | 0.99419 | -0.16732 | 11.6407
157 | -1.7586 | -0.55816 | 1.7587 | 0.55251 | 0.0001609 | -0.0056424 | 0.053572 | 0.053521 | 0.053572 | 0.99419 | -0.16732 | 0.9943 | -0.16445 | 12.7249
158 | -1.7587 | -0.55251 | 1.7589 | 0.55263 | 0.00014278 | 0.00011723 | 0.053521 | 0.053521 | 0.053521 | 0.9943 | -0.16445 | 0.9944 | -0.15965 | 13.054
159 | -1.8723 | -0.60756 | 1.8727 | 0.60792 | 0.00040205 | 0.00036093 | 0.057142 | 0.05714 | 0.057142 | 0.9944 | -0.15965 | 0.99469 | -0.14715 | 13.9371
160 | -2.0079 | -0.67342 | 2.0079 | 0.67224 | 4.4594e-05 | -0.0011784 | 0.061463 | 0.061451 | 0.061463 | 0.99469 | -0.14715 | 0.99471 | -0.14648 | 14.5992
161 | -2.0079 | -0.67224 | 2.0081 | 0.66888 | 0.00012683 | -0.0033542 | 0.061451 | 0.06142 | 0.061451 | 0.99471 | -0.14648 | 0.99479 | -0.14458 | 14.5965
162 | 0.1622 | 0.077725 | -0.1622 | -0.078556 | 1.283e-06 | -0.00083148 | 0.0052193 | 0.0052298 | 0.0052298 | 0.99479 | -0.14458 | 0.99478 | -0.14451 | 2.3772
163 | -2.1703 | -0.74661 | 2.1706 | 0.73817 | 0.00037644 | -0.0084331 | 0.066601 | 0.066519 | 0.066601 | 0.99479 | -0.14458 | 0.99499 | -0.13945 | 15.8197
164 | 0.18109 | 0.086787 | -0.18109 | -0.087156 | 7.0725e-07 | -0.0003685 | 0.0058258 | 0.0058304 | 0.0058304 | 0.99505 | -0.13805 | 0.99504 | -0.13802 | 2.6502
165 | 0.060357 | 0.0055954 | -0.060356 | -0.0061134 | 9.155e-08 | -0.00051799 | 0.0017634 | 0.0017649 | 0.0017649 | 0.99228 | -0.23493 | 0.99227 | -0.23495 | 0.80222
166 | -0.060352 | -0.02923 | 0.060352 | 0.02852 | 1.5266e-07 | -0.00070937 | 0.001951 | 0.0019421 | 0.001951 | 0.9922 | -0.23497 | 0.9922 | -0.23499 | 0.88682
167 | -0.060352 | -0.02852 | 0.060356 | 0.0061134 | 4.2468e-06 | -0.022407 | 0.0019421 | 0.0017649 | 0.0019421 | 0.9922 | -0.23499 | 0.99227 | -0.23495 | 0.88277
168 | 0.18109 | 0.087156 | -0.18109 | -0.087704 | 1.0545e-06 | -0.00054835 | 0.0058304 | 0.0058373 | 0.0058373 | 0.99504 | -0.13802 | 0.99504 | -0.13797 | 2.6533

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 9.4699 | 3.8713

## res_load
| p_mw | q_mvar
0 | 0.054544 | 0.026417
1 | 0.070708 | 0.034246
2 | 0.10503 | 0.050866
3 | 0.10395 | 0.050346
4 | 0.095024 | 0.046022
5 | 0.050104 | 0.024266
6 | 0.052545 | 0.025449
7 | 0.29247 | 0.14165
8 | 0.056878 | 0.027547
9 | 0.083737 | 0.040556
10 | 0.087711 | 0.04248
11 | 0.099963 | 0.048414
12 | 0.050158 | 0.024292
13 | 0.14196 | 0.068756
14 | 0.11684 | 0.056587
15 | 0.11116 | 0.053838
16 | 0.056989 | 0.027601
17 | 0.067365 | 0.032626
18 | 0.14779 | 0.071578
19 | 0.087759 | 0.042504
20 | 0.13909 | 0.067362
21 | 0.10235 | 0.04957
22 | 0.10096 | 0.048898
23 | 0.13818 | 0.066922
24 | 0.14827 | 0.071809
25 | 0.11719 | 0.056759
26 | 0.084505 | 0.040928
27 | 0.15607 | 0.075589
28 | 0.058805 | 0.028481
29 | 0.11639 | 0.056371
30 | 0.089156 | 0.04318
31 | 0.06338 | 0.030697
32 | 0.098162 | 0.047542
33 | 0.0646 | 0.031287
34 | 0.15018 | 0.072738
35 | 0.15027 | 0.072781
36 | 0.071993 | 0.034868
37 | 0.12214 | 0.059156
38 | 0.15596 | 0.075535
39 | 0.082839 | 0.040121
40 | 0.15633 | 0.075715
41 | 0.10355 | 0.050154
42 | 0.13278 | 0.064308
43 | 0.14726 | 0.071323
44 | 0.16017 | 0.077572
45 | 0.12197 | 0.059071
46 | 0.12544 | 0.060754
47 | 0.092583 | 0.04484
48 | 0.16207 | 0.078496
49 | 0.122 | 0.059087
50 | 0.11415 | 0.055287
51 | 0.13374 | 0.064772
52 | 0.13944 | 0.067533
53 | 0.083165 | 0.040279
54 | 0.09078 | 0.043967
55 | 0.080844 | 0.039155
56 | 0.084119 | 0.040741
57 | 0.1619 | 0.078414
58 | 0.098878 | 0.047889
59 | 0.1326 | 0.064223
60 | 0.10576 | 0.051222
61 | 0.16324 | 0.079061
62 | 0.072206 | 0.034971
63 | 0.087033 | 0.042152
64 | 0.097376 | 0.047161
65 | 0.15083 | 0.073049
66 | 0.11536 | 0.055874
67 | 0.14314 | 0.069326
68 | 0.074387 | 0.036027
69 | 0.12106 | 0.058634
70 | 0.12461 | 0.060351
71 | 0.067918 | 0.032894
72 | 0.13824 | 0.066952
73 | 0.077452 | 0.037512
74 | 0.12654 | 0.061288
75 | 0.14339 | 0.069445
76 | 0.11342 | 0.05493
77 | 0.13523 | 0.065493
78 | 0.1622 | 0.078556
79 | 0.090914 | 0.044032
80 | 0.14115 | 0.068361
81 | 0.060352 | 0.02923
82 | 0.1308 | 0.06335
83 | 0.18109 | 0.087704

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1