## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_195_1_node_45 | 20 | n |  | TRUE
1 | bus_MV_195_1_node_46 | 20 | n |  | TRUE
2 | bus_MV_195_1_node_47 | 20 | n |  | TRUE
3 | bus_MV_195_1_node_143 | 20 | n |  | TRUE
4 | bus_MV_195_1_node_163 | 20 | n |  | TRUE
5 | bus_MV_195_1_node_108 | 20 | n |  | TRUE
6 | bus_MV_195_1_node_109 | 20 | n |  | TRUE
7 | bus_MV_195_1_node_206 | 20 | n |  | TRUE
8 | bus_MV_195_1_node_110 | 20 | n |  | TRUE
9 | bus_MV_195_1_node_112 | 20 | n |  | TRUE
10 | bus_MV_195_1_node_111 | 20 | n |  | TRUE
11 | bus_MV_195_1_node_208 | 20 | n |  | TRUE
12 | bus_MV_195_1_node_113 | 20 | n |  | TRUE
13 | bus_MV_195_1_node_114 | 20 | n |  | TRUE
14 | bus_MV_195_1_node_115 | 20 | n |  | TRUE
15 | bus_MV_195_1_node_133 | 20 | n |  | TRUE
16 | bus_MV_195_1_node_131 | 20 | n |  | TRUE
17 | bus_MV_195_1_node_130 | 20 | n |  | TRUE
18 | bus_MV_195_1_node_116 | 20 | n |  | TRUE
19 | bus_MV_195_1_node_118 | 20 | n |  | TRUE
20 | bus_MV_195_1_node_119 | 20 | n |  | TRUE
21 | bus_MV_195_1_node_233 | 20 | n |  | TRUE
22 | bus_MV_195_1_node_235 | 20 | n |  | TRUE
23 | bus_MV_195_1_node_120 | 20 | n |  | TRUE
24 | bus_MV_195_1_node_122 | 20 | n |  | TRUE
25 | bus_MV_195_1_node_121 | 20 | n |  | TRUE
26 | bus_MV_195_1_node_123 | 20 | n |  | TRUE
27 | bus_MV_195_1_node_124 | 20 | n |  | TRUE
28 | bus_MV_195_1_node_232 | 20 | n |  | TRUE
29 | bus_MV_195_1_node_132 | 20 | n |  | TRUE
30 | bus_MV_195_1_node_129 | 20 | n |  | TRUE
31 | bus_MV_195_1_node_126 | 20 | n |  | TRUE
32 | bus_MV_195_1_node_127 | 20 | n |  | TRUE
33 | bus_MV_195_1_node_128 | 20 | n |  | TRUE
34 | bus_MV_195_1_node_210 | 20 | n |  | TRUE
35 | bus_MV_195_1_node_135 | 20 | n |  | TRUE
36 | bus_MV_195_1_node_222 | 20 | n |  | TRUE
37 | bus_MV_195_1_node_136 | 20 | n |  | TRUE
38 | bus_MV_195_1_node_137 | 20 | n |  | TRUE
39 | bus_MV_195_1_node_138 | 20 | n |  | TRUE
40 | bus_MV_195_1_node_147 | 20 | n |  | TRUE
41 | bus_MV_195_1_node_139 | 20 | n |  | TRUE
42 | bus_MV_195_1_node_140 | 20 | n |  | TRUE
43 | bus_MV_195_1_node_191 | 20 | n |  | TRUE
44 | bus_MV_195_1_node_141 | 20 | n |  | TRUE
45 | bus_MV_195_1_node_142 | 20 | n |  | TRUE
46 | bus_MV_195_1_node_189 | 20 | n |  | TRUE
47 | bus_MV_195_1_node_192 | 20 | n |  | TRUE
48 | bus_MV_195_1_node_190 | 20 | n |  | TRUE
49 | bus_MV_195_1_node_184 | 20 | n |  | TRUE
50 | bus_MV_195_1_node_145 | 20 | n |  | TRUE
51 | bus_MV_195_1_node_177 | 20 | n |  | TRUE
52 | bus_MV_195_1_node_148 | 20 | n |  | TRUE
53 | bus_MV_195_1_node_149 | 20 | n |  | TRUE
54 | bus_MV_195_1_node_187 | 20 | n |  | TRUE
55 | bus_MV_195_1_node_151 | 20 | n |  | TRUE
56 | bus_MV_195_1_node_152 | 20 | n |  | TRUE
57 | bus_MV_195_1_node_153 | 20 | n |  | TRUE
58 | bus_MV_195_1_node_154 | 20 | n |  | TRUE
59 | bus_MV_195_1_node_155 | 20 | n |  | TRUE
60 | bus_MV_195_1_node_200 | 20 | n |  | TRUE
61 | bus_MV_195_1_node_221 | 20 | n |  | TRUE
62 | bus_MV_195_1_node_156 | 20 | n |  | TRUE
63 | bus_MV_195_1_node_158 | 20 | n |  | TRUE
64 | bus_MV_195_1_node_157 | 20 | n |  | TRUE
65 | bus_MV_195_1_node_159 | 20 | n |  | TRUE
66 | bus_MV_195_1_node_196 | 20 | n |  | TRUE
67 | bus_MV_195_1_node_160 | 20 | n |  | TRUE
68 | bus_MV_195_1_node_161 | 20 | n |  | TRUE
69 | bus_MV_195_1_node_162 | 20 | n |  | TRUE
70 | bus_MV_195_1_node_176 | 20 | n |  | TRUE
71 | bus_MV_195_1_node_164 | 20 | n |  | TRUE
72 | bus_MV_195_1_node_234 | 20 | n |  | TRUE
73 | bus_MV_195_1_node_165 | 20 | n |  | TRUE
74 | bus_MV_195_1_node_166 | 20 | n |  | TRUE
75 | bus_MV_195_1_node_193 | 20 | n |  | TRUE
76 | bus_MV_195_1_node_167 | 20 | n |  | TRUE
77 | bus_MV_195_1_node_168 | 20 | n |  | TRUE
78 | bus_MV_195_1_node_227 | 20 | n |  | TRUE
79 | bus_MV_195_1_node_202 | 20 | n |  | TRUE
80 | bus_MV_195_1_node_226 | 20 | n |  | TRUE
81 | bus_MV_195_1_node_169 | 20 | n |  | TRUE
82 | bus_MV_195_1_node_205 | 20 | n |  | TRUE
83 | bus_MV_195_1_node_204 | 20 | n |  | TRUE
84 | bus_MV_195_1_node_174 | 20 | n |  | TRUE
85 | bus_MV_195_1_node_170 | 20 | n |  | TRUE
86 | bus_MV_195_1_node_171 | 20 | n |  | TRUE
87 | bus_MV_195_1_node_173 | 20 | n |  | TRUE
88 | bus_MV_195_1_node_172 | 20 | n |  | TRUE
89 | bus_MV_195_1_node_201 | 20 | n |  | TRUE
90 | bus_MV_195_1_node_195 | 20 | n |  | TRUE
91 | bus_MV_195_1_node_175 | 20 | n |  | TRUE
92 | bus_MV_195_1_node_178 | 20 | n |  | TRUE
93 | bus_MV_195_1_node_180 | 20 | n |  | TRUE
94 | bus_MV_195_1_node_181 | 20 | n |  | TRUE
95 | bus_MV_195_1_node_179 | 20 | n |  | TRUE
96 | bus_MV_195_1_node_182 | 20 | n |  | TRUE
97 | bus_MV_195_1_node_183 | 20 | n |  | TRUE
98 | bus_MV_195_1_node_185 | 20 | n |  | TRUE
99 | bus_MV_195_1_node_186 | 20 | n |  | TRUE
100 | bus_MV_195_1_node_215 | 20 | n |  | TRUE
101 | bus_MV_195_1_node_188 | 20 | n |  | TRUE
102 | bus_MV_195_1_node_229 | 20 | n |  | TRUE
103 | bus_MV_195_1_node_194 | 20 | n |  | TRUE
104 | bus_MV_195_1_node_197 | 20 | n |  | TRUE
105 | bus_MV_195_1_node_198 | 20 | n |  | TRUE
106 | bus_MV_195_1_node_209 | 20 | n |  | TRUE
107 | bus_MV_195_1_node_199 | 20 | n |  | TRUE
108 | bus_MV_195_1_node_220 | 20 | n |  | TRUE
109 | bus_MV_195_1_node_203 | 20 | n |  | TRUE
110 | bus_MV_195_1_node_228 | 20 | n |  | TRUE
111 | bus_MV_195_1_node_230 | 20 | n |  | TRUE
112 | bus_HV_195_1_node_138 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_195_1_load_45 | 0 | 0.071169 | 0.034469 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_195_1_load_143 | 3 | 0.077319 | 0.037447 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_195_1_load_163 | 4 | 0.088191 | 0.042713 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_195_1_load_108 | 5 | 0.10453 | 0.050625 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_195_1_load_206 | 7 | 0.094517 | 0.045777 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_195_1_load_111 | 10 | 0.10134 | 0.049082 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_195_1_load_208 | 11 | 0.073234 | 0.035469 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_195_1_load_113 | 12 | 0.12603 | 0.06104 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_195_1_load_133 | 15 | 0.11754 | 0.056926 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_195_1_load_116 | 18 | 0.054391 | 0.026343 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_195_1_load_118 | 19 | 0.10637 | 0.051516 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_195_1_load_235 | 22 | 0.24621 | 0.11925 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_195_1_load_120 | 23 | 0.15637 | 0.075733 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_195_1_load_232 | 28 | 0.089795 | 0.04349 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_195_1_load_129 | 30 | 0.12215 | 0.059158 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_195_1_load_126 | 31 | 0.12221 | 0.05919 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_195_1_load_210 | 34 | 0.07674 | 0.037167 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_195_1_load_135 | 35 | 0.10042 | 0.048637 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_195_1_load_222 | 36 | 0.12329 | 0.059712 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_195_1_load_136 | 37 | 0.1301 | 0.063011 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_195_1_load_147 | 40 | 0.073303 | 0.035502 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_195_1_load_139 | 41 | 0.096231 | 0.046607 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_195_1_load_192 | 47 | 0.12323 | 0.059684 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_195_1_load_184 | 49 | 0.069666 | 0.033741 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_195_1_load_151 | 55 | 0.077106 | 0.037344 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_195_1_load_221 | 61 | 0.16484 | 0.079836 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_195_1_load_156 | 62 | 0.16389 | 0.079377 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_195_1_load_158 | 63 | 0.12489 | 0.060489 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_195_1_load_160 | 67 | 0.14817 | 0.071763 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_195_1_load_176 | 70 | 0.12205 | 0.059111 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_195_1_load_165 | 73 | 0.097818 | 0.047375 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_195_1_load_193 | 75 | 0.1047 | 0.050707 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_195_1_load_227 | 78 | 0.13735 | 0.066524 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_195_1_load_226 | 80 | 0.15217 | 0.073701 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_195_1_load_204 | 83 | 0.13006 | 0.062991 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_195_1_load_170 | 85 | 0.12981 | 0.062872 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_195_1_load_172 | 88 | 0.093181 | 0.04513 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_195_1_load_201 | 89 | 0.11551 | 0.055943 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_195_1_load_195 | 90 | 0.13426 | 0.065027 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_195_1_load_175 | 91 | 0.07058 | 0.034183 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_195_1_load_178 | 92 | 0.069882 | 0.033846 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_195_1_load_180 | 93 | 0.071755 | 0.034753 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_195_1_load_182 | 96 | 0.13609 | 0.065914 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_195_1_load_183 | 97 | 0.1509 | 0.073086 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_195_1_load_185 | 98 | 0.077725 | 0.037644 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_195_1_load_215 | 100 | 0.09834 | 0.047628 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_195_1_load_188 | 101 | 0.12337 | 0.059752 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_195_1_load_229 | 102 | 0.052858 | 0.0256 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_195_1_load_198 | 105 | 0.12478 | 0.060434 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_195_1_load_209 | 106 | 0.1331 | 0.064465 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_195_1_load_220 | 108 | 0.14797 | 0.071663 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_195_1_load_203 | 109 | 0.050342 | 0.024382 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_195_1_load_228 | 110 | 0.064069 | 0.03103 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_195_1_load_230 | 111 | 0.054426 | 0.02636 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_195_1_line_0 |  | 0 | 1 | 0.003483 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_195_1_line_1 |  | 1 | 2 | 0.19611 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
2 | MV_195_1_line_2 |  | 1 | 3 | 3.008 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
3 | MV_195_1_line_3 |  | 2 | 4 | 0.020503 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
4 | MV_195_1_line_4 |  | 3 | 50 | 0.11658 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
5 | MV_195_1_line_5 |  | 4 | 71 | 0.018042 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
6 | MV_195_1_line_6 |  | 5 | 6 | 0.15495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_195_1_line_7 |  | 5 | 7 | 3.6848 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_195_1_line_8 |  | 6 | 8 | 0.28451 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_195_1_line_9 |  | 8 | 9 | 0.76576 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_195_1_line_10 |  | 8 | 10 | 0.12439 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_195_1_line_11 |  | 9 | 11 | 0.03214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_195_1_line_12 |  | 11 | 111 | 1.3907 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_195_1_line_13 |  | 12 | 13 | 0.069136 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_195_1_line_14 |  | 13 | 14 | 0.16798 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_195_1_line_15 |  | 13 | 15 | 0.084077 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_195_1_line_16 |  | 14 | 16 | 0.085541 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_195_1_line_17 |  | 14 | 17 | 0.21809 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_195_1_line_18 |  | 16 | 35 | 0.080176 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_195_1_line_19 |  | 17 | 30 | 0.07178 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
20 | MV_195_1_line_20 |  | 18 | 19 | 1.126 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_195_1_line_21 |  | 19 | 20 | 0.030723 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_195_1_line_22 |  | 20 | 21 | 0.83358 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
23 | MV_195_1_line_23 |  | 20 | 22 | 6.0541 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
24 | MV_195_1_line_24 |  | 21 | 28 | 0.19974 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
25 | MV_195_1_line_25 |  | 22 | 72 | 0.60415 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
26 | MV_195_1_line_26 |  | 23 | 24 | 0.001863 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
27 | MV_195_1_line_27 |  | 23 | 25 | 0.06058 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
28 | MV_195_1_line_28 |  | 24 | 27 | 0.23977 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
29 | MV_195_1_line_29 |  | 25 | 26 | 0.12744 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
30 | MV_195_1_line_30 |  | 26 | 28 | 0.049136 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
31 | MV_195_1_line_31 |  | 27 | 29 | 0.033297 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
32 | MV_195_1_line_32 |  | 27 | 30 | 0.032801 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
33 | MV_195_1_line_33 |  | 28 | 33 | 0.13735 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
34 | MV_195_1_line_34 |  | 29 | 36 | 0.054819 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
35 | MV_195_1_line_35 |  | 31 | 32 | 0.077622 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_195_1_line_36 |  | 32 | 33 | 0.049295 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_195_1_line_37 |  | 33 | 34 | 0.040422 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
38 | MV_195_1_line_38 |  | 34 | 109 | 2.5847 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
39 | MV_195_1_line_39 |  | 37 | 38 | 0.043646 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_195_1_line_40 |  | 38 | 39 | 0.13782 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_195_1_line_41 |  | 39 | 40 | 0.19456 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
42 | MV_195_1_line_42 |  | 40 | 52 | 0.099187 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
43 | MV_195_1_line_43 |  | 41 | 42 | 0.016704 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
44 | MV_195_1_line_44 |  | 41 | 43 | 0.22986 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
45 | MV_195_1_line_45 |  | 42 | 44 | 0.17947 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
46 | MV_195_1_line_46 |  | 42 | 45 | 0.34946 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
47 | MV_195_1_line_47 |  | 42 | 46 | 0.2153 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_195_1_line_48 |  | 43 | 102 | 0.095949 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_195_1_line_49 |  | 44 | 47 | 0.12734 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_195_1_line_50 |  | 44 | 48 | 0.22299 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
51 | MV_195_1_line_51 |  | 45 | 49 | 0.31833 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
52 | MV_195_1_line_52 |  | 46 | 101 | 0.054968 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_195_1_line_53 |  | 48 | 100 | 0.051056 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
54 | MV_195_1_line_54 |  | 49 | 94 | 0.25413 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
55 | MV_195_1_line_55 |  | 50 | 51 | 0.74276 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
56 | MV_195_1_line_56 |  | 51 | 91 | 0.28445 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
57 | MV_195_1_line_57 |  | 52 | 53 | 0.051677 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
58 | MV_195_1_line_58 |  | 53 | 54 | 0.17668 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
59 | MV_195_1_line_59 |  | 54 | 100 | 0.027247 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
60 | MV_195_1_line_60 |  | 54 | 99 | 0.13579 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_195_1_line_61 |  | 55 | 56 | 0.025865 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_195_1_line_62 |  | 55 | 57 | 0.096065 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_195_1_line_63 |  | 56 | 58 | 0.05652 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_195_1_line_64 |  | 57 | 59 | 0.055083 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_195_1_line_65 |  | 58 | 60 | 0.037078 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_195_1_line_66 |  | 59 | 61 | 0.051606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_195_1_line_67 |  | 60 | 108 | 0.06079 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
68 | MV_195_1_line_68 |  | 60 | 107 | 0.032216 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_195_1_line_69 |  | 62 | 63 | 0.035745 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
70 | MV_195_1_line_70 |  | 62 | 64 | 0.065839 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
71 | MV_195_1_line_71 |  | 63 | 66 | 0.097875 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
72 | MV_195_1_line_72 |  | 64 | 65 | 0.058351 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
73 | MV_195_1_line_73 |  | 65 | 67 | 0.030947 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
74 | MV_195_1_line_74 |  | 66 | 104 | 0.11764 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
75 | MV_195_1_line_75 |  | 66 | 105 | 0.040105 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_195_1_line_76 |  | 67 | 68 | 0.07894 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
77 | MV_195_1_line_77 |  | 68 | 69 | 0.73262 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
78 | MV_195_1_line_78 |  | 69 | 70 | 0.032608 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
79 | MV_195_1_line_79 |  | 70 | 91 | 0.010118 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
80 | MV_195_1_line_80 |  | 71 | 72 | 2.7125 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
81 | MV_195_1_line_81 |  | 73 | 74 | 0.030954 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
82 | MV_195_1_line_82 |  | 74 | 75 | 0.18437 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_195_1_line_83 |  | 75 | 103 | 0.031954 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
84 | MV_195_1_line_84 |  | 75 | 90 | 0.054859 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
85 | MV_195_1_line_85 |  | 76 | 77 | 0.18152 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
86 | MV_195_1_line_86 |  | 76 | 78 | 0.091923 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
87 | MV_195_1_line_87 |  | 77 | 79 | 0.008522 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
88 | MV_195_1_line_88 |  | 77 | 80 | 0.041845 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
89 | MV_195_1_line_89 |  | 79 | 89 | 0.04345 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
90 | MV_195_1_line_90 |  | 80 | 88 | 0.22162 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
91 | MV_195_1_line_91 |  | 81 | 82 | 0.35385 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
92 | MV_195_1_line_92 |  | 81 | 83 | 0.045974 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_195_1_line_93 |  | 81 | 84 | 0.29807 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
94 | MV_195_1_line_94 |  | 82 | 110 | 0.33541 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
95 | MV_195_1_line_95 |  | 82 | 96 | 0.56262 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
96 | MV_195_1_line_96 |  | 84 | 90 | 0.032744 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
97 | MV_195_1_line_97 |  | 84 | 86 | 0.082875 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
98 | MV_195_1_line_98 |  | 85 | 86 | 0.015083 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_195_1_line_99 |  | 86 | 87 | 0.013359 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
100 | MV_195_1_line_100 |  | 87 | 89 | 0.00354 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
101 | MV_195_1_line_101 |  | 92 | 93 | 0.1008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_195_1_line_102 |  | 92 | 94 | 0.22118 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
103 | MV_195_1_line_103 |  | 92 | 95 | 0.16773 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
104 | MV_195_1_line_104 |  | 93 | 97 | 0.016125 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_195_1_line_105 |  | 95 | 96 | 0.028295 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
106 | MV_195_1_line_106 |  | 98 | 99 | 0.057505 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
107 | MV_195_1_line_107 |  | 103 | 104 | 0.15476 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
108 | MV_195_1_line_108 |  | 104 | 106 | 0.022366 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_195_1_line_109 |  | 105 | 107 | 0.045996 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_195_1_line_110 |  | 110 | 111 | 1.683 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_195_1_trafo_138 | 25 MVA 110/20 kV | 112 | 39 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2640017.7028 | 1159573.886
1 | 2640014.8419 | 1159571.8882
2 | 2640013.3659 | 1159514.9046
3 | 2637170.8742 | 1160551.5784
4 | 2640022.6223 | 1159496.8124
5 | 2636072.2488 | 1164708.6844
6 | 2635944.5012 | 1164795.6315
7 | 2639705.0428 | 1165325.4078
8 | 2635746.5327 | 1164707.9741
9 | 2635322.9996 | 1164754.7199
10 | 2635658.8136 | 1164619.7863
11 | 2635338.5542 | 1164726.594
12 | 2635086.3904 | 1157171.3087
13 | 2635085.2134 | 1157104.8348
14 | 2635100.952 | 1156940.8542
15 | 2635138.4456 | 1157039.7563
16 | 2635097.3535 | 1156866.2286
17 | 2634988.5085 | 1156756.5845
18 | 2634700.1023 | 1155033.0095
19 | 2635543.8371 | 1155778.6146
20 | 2635541.4707 | 1155809.2385
21 | 2634791.2247 | 1156172.546
22 | 2641504.0683 | 1156857.8454
23 | 2634855.6458 | 1156513.8914
24 | 2634856.9648 | 1156515.2108
25 | 2634833.7881 | 1156457.3919
26 | 2634849.9182 | 1156369.296
27 | 2634920.68 | 1156684.6768
28 | 2634814.8989 | 1156335.6432
29 | 2634929.6536 | 1156652.6125
30 | 2634951.5684 | 1156695.0389
31 | 2634734.9717 | 1156549.4128
32 | 2634730.4223 | 1156479.2955
33 | 2634717.8302 | 1156432.8216
34 | 2634691.9571 | 1156403.5091
35 | 2635148.5718 | 1156840.4807
36 | 2634976.5025 | 1156624.1475
37 | 2636235.1862 | 1159978.0275
38 | 2636276.2971 | 1159993.0159
39 | 2636214.3905 | 1160114.9391
40 | 2636120.9189 | 1160285.5761
41 | 2636122.8828 | 1160776.9057
42 | 2636118.6495 | 1160760.8722
43 | 2635932.4044 | 1160905.5654
44 | 2636144.3341 | 1160593.9298
45 | 2636364.8478 | 1160799.5401
46 | 2635907.7247 | 1160717.6889
47 | 2636123.6992 | 1160472.2882
48 | 2635922.3769 | 1160572.4798
49 | 2636274.6962 | 1161092.9132
50 | 2637167.0438 | 1160664.3236
51 | 2636545.6893 | 1161071.285
52 | 2636050.0754 | 1160354.9872
53 | 2636075.8791 | 1160399.5978
54 | 2635926.7514 | 1160494.3437
55 | 2637253.8934 | 1161509.2156
56 | 2637239.9821 | 1161531.0408
57 | 2637248.3918 | 1161415.1778
58 | 2637220.4818 | 1161580.7013
59 | 2637278.7197 | 1161372.8994
60 | 2637193.2948 | 1161605.9129
61 | 2637307.7864 | 1161330.213
62 | 2637004.3037 | 1161505.5859
63 | 2636990.6877 | 1161538.0967
64 | 2637058.4593 | 1161468.1442
65 | 2637017.0456 | 1161427.1018
66 | 2637079.6831 | 1161578.8316
67 | 2637001.4237 | 1161400.7367
68 | 2636994.1522 | 1161347.1646
69 | 2636599.2294 | 1161193.1837
70 | 2636596.4567 | 1161160.6937
71 | 2640036.2446 | 1159484.9412
72 | 2641119.7032 | 1156998.1822
73 | 2636781.9106 | 1161675.4994
74 | 2636802.3411 | 1161652.2456
75 | 2636951.9117 | 1161760.0502
76 | 2636871.771 | 1162046.3725
77 | 2636996.4438 | 1161945.341
78 | 2636798.3517 | 1162101.685
79 | 2636992.1835 | 1161937.9554
80 | 2637038.2765 | 1161946.3653
81 | 2636662.2466 | 1161933.7576
82 | 2636389.5791 | 1162087.8603
83 | 2636632.8762 | 1161968.4188
84 | 2636947.1989 | 1161846.2989
85 | 2637028.1273 | 1161876.2781
86 | 2637014.1035 | 1161881.7947
87 | 2637008.2299 | 1161893.7981
88 | 2637256.9721 | 1161982.2218
89 | 2637007.2283 | 1161897.1936
90 | 2636942.7398 | 1161813.866
91 | 2636588.7626 | 1161154.1223
92 | 2636276.86 | 1161341.6091
93 | 2636311.5204 | 1161319.2843
94 | 2636182.0378 | 1161292.3356
95 | 2636299.5568 | 1161507.7976
96 | 2636317.2374 | 1161529.9155
97 | 2636318.5011 | 1161304.7481
98 | 2635925.7432 | 1160303.7292
99 | 2635915.4661 | 1160360.3079
100 | 2635926.1291 | 1160521.5762
101 | 2635864.3928 | 1160683.8689
102 | 2635836.8951 | 1160914.7455
103 | 2636982.8446 | 1161768.3222
104 | 2637012.3462 | 1161654.2672
105 | 2637119.0512 | 1161581.1087
106 | 2637030.3398 | 1161642.4495
107 | 2637163.4437 | 1161593.5889
108 | 2637253.8989 | 1161601.1628
109 | 2632140.5759 | 1156817.4455
110 | 2636244.0808 | 1162369.6383
111 | 2634914.8611 | 1163401.9565
112 | 2636214.3905 | 1160114.9391

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99372 | -0.31576 | 0.071169 | 0.034469
1 | 0.99372 | -0.31576 | 0 | 0
2 | 0.99368 | -0.31625 | 0 | 0
3 | 0.99516 | -0.21524 | 0.077319 | 0.037447
4 | 0.99367 | -0.3163 | 0.088191 | 0.042713
5 | 0.99517 | -0.17042 | 0.10453 | 0.050625
6 | 0.99521 | -0.17073 | 0 | 0
7 | 0.9945 | -0.17536 | 0.094517 | 0.045777
8 | 0.99528 | -0.17121 | 0 | 0
9 | 0.99557 | -0.17281 | 0 | 0
10 | 0.99526 | -0.17136 | 0.10134 | 0.049082
11 | 0.99558 | -0.17286 | 0.073234 | 0.035469
12 | 0.98944 | -0.56868 | 0.12603 | 0.06104
13 | 0.98945 | -0.56878 | 0 | 0
14 | 0.98951 | -0.56924 | 0 | 0
15 | 0.98944 | -0.56891 | 0.11754 | 0.056926
16 | 0.9895 | -0.56916 | 0 | 0
17 | 0.9896 | -0.56999 | 0 | 0
18 | 0.98987 | -0.55028 | 0.054391 | 0.026343
19 | 0.98999 | -0.54946 | 0.10637 | 0.051516
20 | 0.99 | -0.54951 | 0 | 0
21 | 0.98972 | -0.56759 | 0 | 0
22 | 0.99234 | -0.39936 | 0.24621 | 0.11925
23 | 0.98965 | -0.56888 | 0.15637 | 0.075733
24 | 0.98965 | -0.56889 | 0 | 0
25 | 0.98966 | -0.56799 | 0 | 0
26 | 0.98968 | -0.56789 | 0 | 0
27 | 0.98962 | -0.56949 | 0 | 0
28 | 0.98968 | -0.56785 | 0.089795 | 0.04349
29 | 0.98962 | -0.56951 | 0 | 0
30 | 0.98961 | -0.56956 | 0.12215 | 0.059158
31 | 0.98965 | -0.56835 | 0.12221 | 0.05919
32 | 0.98967 | -0.56846 | 0 | 0
33 | 0.98967 | -0.56852 | 0 | 0
34 | 0.98967 | -0.56853 | 0.07674 | 0.037167
35 | 0.98949 | -0.56906 | 0.10042 | 0.048637
36 | 0.98961 | -0.56962 | 0.12329 | 0.059712
37 | 0.99997 | 0.0002574 | 0.1301 | 0.063011
38 | 0.99998 | 0.00019091 | 0 | 0
39 | 1 | 0 | -5.9011 | -2.0445
40 | 0.99968 | -0.022402 | 0.073303 | 0.035502
41 | 0.99869 | -0.070791 | 0.096231 | 0.046607
42 | 0.99869 | -0.070782 | 0 | 0
43 | 0.99869 | -0.070993 | 0 | 0
44 | 0.99884 | -0.069195 | 0 | 0
45 | 0.99842 | -0.073726 | 0 | 0
46 | 0.99864 | -0.071107 | 0 | 0
47 | 0.99882 | -0.069019 | 0.12323 | 0.059684
48 | 0.99919 | -0.044592 | 0 | 0
49 | 0.99817 | -0.076311 | 0.069666 | 0.033741
50 | 0.99519 | -0.21492 | 0 | 0
51 | 0.99556 | -0.18893 | 0 | 0
52 | 0.99959 | -0.023321 | 0 | 0
53 | 0.99955 | -0.023797 | 0 | 0
54 | 0.99926 | -0.043883 | 0 | 0
55 | 0.99593 | -0.17516 | 0.077106 | 0.037344
56 | 0.99594 | -0.17523 | 0 | 0
57 | 0.99591 | -0.17499 | 0 | 0
58 | 0.99596 | -0.17537 | 0 | 0
59 | 0.9959 | -0.17489 | 0 | 0
60 | 0.99597 | -0.17524 | 0 | 0
61 | 0.99589 | -0.17479 | 0.16484 | 0.079836
62 | 0.99596 | -0.18067 | 0.16389 | 0.079377
63 | 0.99597 | -0.18051 | 0.12489 | 0.060489
64 | 0.99592 | -0.18348 | 0 | 0
65 | 0.99591 | -0.18372 | 0 | 0
66 | 0.99604 | -0.1758 | 0 | 0
67 | 0.9959 | -0.18385 | 0.14817 | 0.071763
68 | 0.99587 | -0.18416 | 0 | 0
69 | 0.99566 | -0.18678 | 0 | 0
70 | 0.99564 | -0.18805 | 0.12205 | 0.059111
71 | 0.99367 | -0.31635 | 0 | 0
72 | 0.99248 | -0.39813 | 0 | 0
73 | 0.99614 | -0.17456 | 0.097818 | 0.047375
74 | 0.99614 | -0.17452 | 0 | 0
75 | 0.99618 | -0.1743 | 0.1047 | 0.050707
76 | 0.9962 | -0.17433 | 0 | 0
77 | 0.9962 | -0.17422 | 0 | 0
78 | 0.99619 | -0.17454 | 0.13735 | 0.066524
79 | 0.99621 | -0.17421 | 0 | 0
80 | 0.99618 | -0.17435 | 0.15217 | 0.073701
81 | 0.99657 | -0.15015 | 0 | 0
82 | 0.9968 | -0.14796 | 0 | 0
83 | 0.99656 | -0.15008 | 0.13006 | 0.062991
84 | 0.99622 | -0.17383 | 0 | 0
85 | 0.99621 | -0.17386 | 0.12981 | 0.062872
86 | 0.99621 | -0.17388 | 0 | 0
87 | 0.99621 | -0.17388 | 0 | 0
88 | 0.99614 | -0.1746 | 0.093181 | 0.04513
89 | 0.99621 | -0.17389 | 0.11551 | 0.055943
90 | 0.9962 | -0.17401 | 0.13426 | 0.065027
91 | 0.99564 | -0.18808 | 0.07058 | 0.034183
92 | 0.9978 | -0.079979 | 0.069882 | 0.033846
93 | 0.99777 | -0.07972 | 0.071755 | 0.034753
94 | 0.99797 | -0.078298 | 0 | 0
95 | 0.99757 | -0.095869 | 0 | 0
96 | 0.99755 | -0.096076 | 0.13609 | 0.065914
97 | 0.99777 | -0.079691 | 0.1509 | 0.073086
98 | 0.99924 | -0.043825 | 0.077725 | 0.037644
99 | 0.99925 | -0.043771 | 0 | 0
100 | 0.99924 | -0.044131 | 0.09834 | 0.047628
101 | 0.99863 | -0.071189 | 0.12337 | 0.059752
102 | 0.99868 | -0.071055 | 0.052858 | 0.0256
103 | 0.99616 | -0.17446 | 0 | 0
104 | 0.99609 | -0.17523 | 0 | 0
105 | 0.99601 | -0.17557 | 0.12478 | 0.060434
106 | 0.99609 | -0.1752 | 0.1331 | 0.064465
107 | 0.99599 | -0.17538 | 0 | 0
108 | 0.99595 | -0.17535 | 0.14797 | 0.071663
109 | 0.98963 | -0.57111 | 0.050342 | 0.024382
110 | 0.99677 | -0.14821 | 0.064069 | 0.03103
111 | 0.99655 | -0.1624 | 0.054426 | 0.02636
112 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.071169 | -0.034469 | 0.071169 | 0.034387 | 2.4524e-08 | -8.2113e-05 | 0.0022972 | 0.0022961 | 0.0022972 | 0.99372 | -0.31576 | 0.99372 | -0.31576 | 1.0442
1 | 1.5833 | 0.54139 | -1.5833 | -0.56568 | 7.1937e-05 | -0.024294 | 0.04861 | 0.048843 | 0.048843 | 0.99372 | -0.31576 | 0.99368 | -0.31625 | 3.8278
2 | -1.6545 | -0.57578 | 1.6559 | 0.57129 | 0.0013884 | -0.0044902 | 0.05089 | 0.050812 | 0.05089 | 0.99372 | -0.31576 | 0.99516 | -0.21524 | 3.945
3 | 1.5833 | 0.56568 | -1.5832 | -0.56822 | 7.561e-06 | -0.0025397 | 0.048843 | 0.048868 | 0.048868 | 0.99368 | -0.31625 | 0.99367 | -0.3163 | 3.8298
4 | -1.7332 | -0.60873 | 1.7333 | 0.59425 | 5.101e-05 | -0.01448 | 0.053287 | 0.053149 | 0.053287 | 0.99516 | -0.21524 | 0.99519 | -0.21492 | 4.1761
5 | 1.4951 | 0.52551 | -1.4951 | -0.52775 | 5.911e-06 | -0.0022353 | 0.046039 | 0.04606 | 0.04606 | 0.99367 | -0.3163 | 0.99367 | -0.31635 | 3.6097
6 | -0.19911 | -0.092086 | 0.19911 | 0.088424 | 8.3183e-06 | -0.0036617 | 0.0063634 | 0.0063195 | 0.0063634 | 0.99517 | -0.17042 | 0.99521 | -0.17073 | 2.8924
7 | 0.094577 | 0.041461 | -0.094517 | -0.045777 | 5.9933e-05 | -0.004316 | 0.0029955 | 0.0030484 | 0.0030484 | 0.99517 | -0.17042 | 0.9945 | -0.17536 | 1.4516
8 | -0.19911 | -0.088424 | 0.19913 | 0.0817 | 1.4982e-05 | -0.0067242 | 0.0063195 | 0.0062428 | 0.0063195 | 0.99521 | -0.17073 | 0.99528 | -0.17121 | 2.8725
9 | -0.30047 | -0.13064 | 0.30056 | 0.11255 | 9.0357e-05 | -0.01809 | 0.0095031 | 0.0093061 | 0.0095031 | 0.99528 | -0.17121 | 0.99557 | -0.17281 | 4.3196
10 | 0.10134 | 0.048936 | -0.10134 | -0.049082 | 2.3626e-06 | -0.00014561 | 0.0032642 | 0.003266 | 0.003266 | 0.99528 | -0.17121 | 0.99526 | -0.17136 | 1.5552
11 | -0.30056 | -0.11255 | 0.30057 | 0.11179 | 3.7128e-06 | -0.00075951 | 0.0093061 | 0.0092984 | 0.0093061 | 0.99557 | -0.17281 | 0.99558 | -0.17286 | 4.23
12 | -0.3738 | -0.14726 | 0.37414 | 0.14582 | 0.00033576 | -0.0014369 | 0.011649 | 0.011632 | 0.011649 | 0.99558 | -0.17286 | 0.99655 | -0.1624 | 5.5473
13 | -0.12603 | -0.06104 | 0.12603 | 0.059424 | 1.5329e-06 | -0.0016156 | 0.0040856 | 0.0040652 | 0.0040856 | 0.98944 | -0.56868 | 0.98945 | -0.56878 | 1.8571
14 | -0.24357 | -0.11625 | 0.24359 | 0.11233 | 1.3818e-05 | -0.0039227 | 0.0078742 | 0.0078255 | 0.0078742 | 0.98945 | -0.56878 | 0.98951 | -0.56924 | 3.5792
15 | 0.11754 | 0.056829 | -0.11754 | -0.056926 | 2.1741e-06 | -9.6902e-05 | 0.003809 | 0.0038103 | 0.0038103 | 0.98945 | -0.56878 | 0.98944 | -0.56891 | 1.8144
16 | 0.10043 | 0.044764 | -0.10042 | -0.046763 | 1.1838e-06 | -0.0019994 | 0.0032077 | 0.0032319 | 0.0032319 | 0.98951 | -0.56924 | 0.9895 | -0.56916 | 1.469
17 | -0.34401 | -0.15709 | 0.34405 | 0.15201 | 3.5245e-05 | -0.0050886 | 0.011033 | 0.010972 | 0.011033 | 0.98951 | -0.56924 | 0.9896 | -0.56999 | 5.015
18 | 0.10042 | 0.046763 | -0.10042 | -0.048637 | 1.126e-06 | -0.0018739 | 0.0032319 | 0.0032553 | 0.0032553 | 0.9895 | -0.56916 | 0.98949 | -0.56906 | 1.4797
19 | -0.34405 | -0.15201 | 0.34405 | 0.15183 | 3.0792e-06 | -0.00017752 | 0.010972 | 0.01097 | 0.010972 | 0.9896 | -0.56999 | 0.98961 | -0.56956 | 1.3381
20 | -0.054391 | -0.026343 | 0.054397 | 0.025029 | 6.173e-06 | -0.0013134 | 0.0017624 | 0.001746 | 0.0017624 | 0.98987 | -0.55028 | 0.98999 | -0.54946 | 0.83925
21 | -0.16076 | -0.076545 | 0.16077 | 0.075827 | 1.1037e-06 | -0.00071861 | 0.005192 | 0.0051831 | 0.005192 | 0.98999 | -0.54946 | 0.99 | -0.54951 | 2.36
22 | 1.0852 | 0.42397 | -1.085 | -0.42577 | 0.00017185 | -0.0017959 | 0.033973 | 0.033997 | 0.033997 | 0.99 | -0.54951 | 0.98972 | -0.56759 | 2.6354
23 | -1.246 | -0.4998 | 1.2476 | 0.48779 | 0.0016485 | -0.01201 | 0.039145 | 0.038969 | 0.039145 | 0.99 | -0.54951 | 0.99234 | -0.39936 | 3.0345
24 | 1.085 | 0.42577 | -1.085 | -0.45033 | 3.5945e-05 | -0.024565 | 0.033997 | 0.034265 | 0.034265 | 0.98972 | -0.56759 | 0.98968 | -0.56785 | 2.6853
25 | -1.4938 | -0.60703 | 1.494 | 0.53237 | 0.0002019 | -0.074658 | 0.046907 | 0.046132 | 0.046907 | 0.99234 | -0.39936 | 0.99248 | -0.39813 | 3.6761
26 | 0.5895 | 0.24755 | -0.5895 | -0.24769 | 1.1859e-07 | -0.0001393 | 0.01865 | 0.018652 | 0.018652 | 0.98965 | -0.56888 | 0.98965 | -0.56889 | 2.2152
27 | -0.74587 | -0.32328 | 0.74588 | 0.32313 | 6.0797e-06 | -0.00014768 | 0.023712 | 0.02371 | 0.023712 | 0.98965 | -0.56888 | 0.98966 | -0.56799 | 1.8382
28 | 0.5895 | 0.24769 | -0.58949 | -0.26561 | 1.5433e-05 | -0.017927 | 0.018652 | 0.018861 | 0.018861 | 0.98965 | -0.56889 | 0.98962 | -0.56949 | 2.24
29 | -0.74588 | -0.32313 | 0.74589 | 0.30745 | 1.0986e-05 | -0.01568 | 0.02371 | 0.023532 | 0.02371 | 0.98966 | -0.56799 | 0.98968 | -0.56789 | 1.8582
30 | -0.74589 | -0.30745 | 0.74589 | 0.30141 | 4.192e-06 | -0.0060455 | 0.023532 | 0.023466 | 0.023532 | 0.98968 | -0.56789 | 0.98968 | -0.56785 | 1.8442
31 | 0.12329 | 0.057082 | -0.12329 | -0.059573 | 9.6456e-08 | -0.0024914 | 0.0039632 | 0.0039943 | 0.0039943 | 0.98962 | -0.56949 | 0.98962 | -0.56951 | 0.47438
32 | 0.4662 | 0.20853 | -0.4662 | -0.21099 | 1.3348e-06 | -0.0024531 | 0.014898 | 0.014927 | 0.014927 | 0.98962 | -0.56949 | 0.98961 | -0.56956 | 1.7728
33 | 0.2493 | 0.10543 | -0.2493 | -0.1058 | 1.5291e-06 | -0.00036782 | 0.0078953 | 0.0078995 | 0.0078995 | 0.98968 | -0.56785 | 0.98967 | -0.56852 | 0.61236
34 | 0.12329 | 0.059573 | -0.12329 | -0.059712 | 3.1184e-07 | -0.00013852 | 0.0039943 | 0.003996 | 0.003996 | 0.98962 | -0.56951 | 0.98961 | -0.56962 | 0.48732
35 | -0.12221 | -0.05919 | 0.12221 | 0.057376 | 1.6164e-06 | -0.0018147 | 0.003961 | 0.0039382 | 0.003961 | 0.98965 | -0.56835 | 0.98967 | -0.56846 | 1.8004
36 | -0.12221 | -0.057376 | 0.12222 | 0.056223 | 1.017e-06 | -0.0011525 | 0.0039382 | 0.003924 | 0.0039382 | 0.98967 | -0.56846 | 0.98967 | -0.56852 | 1.7901
37 | 0.12708 | 0.049578 | -0.12708 | -0.054553 | 1.002e-07 | -0.0049752 | 0.0039789 | 0.004034 | 0.004034 | 0.98967 | -0.56852 | 0.98967 | -0.56853 | 0.31614
38 | 0.050343 | 0.017386 | -0.050342 | -0.024382 | 1.1661e-06 | -0.0069955 | 0.0015535 | 0.0016316 | 0.0016316 | 0.98967 | -0.56853 | 0.98963 | -0.57111 | 0.12648
39 | -0.1301 | -0.063011 | 0.1301 | 0.061969 | 1.0115e-06 | -0.0010417 | 0.0041731 | 0.0041601 | 0.0041731 | 0.99997 | 0.0002574 | 0.99998 | 0.00019091 | 1.8969
40 | -0.1301 | -0.061969 | 0.13011 | 0.058679 | 3.1533e-06 | -0.0032896 | 0.0041601 | 0.0041201 | 0.0041601 | 0.99998 | 0.00019091 | 1 | 0 | 1.891
41 | 5.757 | 1.9753 | -5.7559 | -1.973 | 0.0010721 | 0.0023453 | 0.1757 | 0.17571 | 0.17571 | 1 | 0 | 0.99968 | -0.022402 | 13.6205
42 | 5.6826 | 1.9375 | -5.6821 | -1.9497 | 0.00046092 | -0.012196 | 0.17337 | 0.17349 | 0.17349 | 0.99968 | -0.022402 | 0.99959 | -0.023321 | 13.5961
43 | -0.14909 | -0.0715 | 0.14909 | 0.070227 | 6.9599e-08 | -0.0012729 | 0.0047794 | 0.0047636 | 0.0047794 | 0.99869 | -0.070791 | 0.99869 | -0.070782 | 0.56763
44 | 0.052858 | 0.024893 | -0.052858 | -0.025486 | 2.3467e-07 | -0.00059313 | 0.0016888 | 0.0016962 | 0.0016962 | 0.99869 | -0.070791 | 0.99869 | -0.070993 | 0.20686
45 | -5.3794 | -1.8446 | 5.3802 | 1.8225 | 0.00074828 | -0.022076 | 0.16438 | 0.16417 | 0.16438 | 0.99869 | -0.070782 | 0.99884 | -0.069195 | 12.8825
46 | 5.107 | 1.715 | -5.1056 | -1.758 | 0.0013126 | -0.043049 | 0.15572 | 0.15613 | 0.15613 | 0.99869 | -0.070782 | 0.99842 | -0.073726 | 12.2356
47 | 0.12338 | 0.059435 | -0.12337 | -0.059688 | 6.016e-06 | -0.00025257 | 0.0039586 | 0.0039618 | 0.0039618 | 0.99869 | -0.070782 | 0.99864 | -0.071107 | 1.8866
48 | 0.052858 | 0.025486 | -0.052858 | -0.0256 | 4.9227e-07 | -0.00011394 | 0.0016962 | 0.0016976 | 0.0016976 | 0.99869 | -0.070993 | 0.99868 | -0.071055 | 0.8084
49 | 0.12324 | 0.056652 | -0.12323 | -0.059684 | 2.637e-06 | -0.0030326 | 0.0039199 | 0.0039573 | 0.0039573 | 0.99884 | -0.069195 | 0.99882 | -0.069019 | 1.7988
50 | -5.5034 | -1.8792 | 5.5045 | 1.8816 | 0.0011243 | 0.0024081 | 0.16807 | 0.16806 | 0.16807 | 0.99884 | -0.069195 | 0.99919 | -0.044592 | 13.0287
51 | 5.1056 | 1.758 | -5.1044 | -1.7972 | 0.0012017 | -0.03919 | 0.15613 | 0.15651 | 0.15651 | 0.99842 | -0.073726 | 0.99817 | -0.076311 | 12.2653
52 | 0.12337 | 0.059688 | -0.12337 | -0.059752 | 1.5375e-06 | -6.4479e-05 | 0.0039618 | 0.0039626 | 0.0039626 | 0.99864 | -0.071107 | 0.99863 | -0.071189 | 1.887
53 | -5.5045 | -1.8816 | 5.5048 | 1.8753 | 0.00022273 | -0.0062804 | 0.16806 | 0.16801 | 0.16806 | 0.99919 | -0.044592 | 0.99924 | -0.044131 | 13.1712
54 | 5.0348 | 1.7635 | -5.0338 | -1.7947 | 0.00093641 | -0.031284 | 0.15428 | 0.15459 | 0.15459 | 0.99817 | -0.076311 | 0.99797 | -0.078298 | 12.115
55 | -1.7333 | -0.59425 | 1.7336 | 0.59323 | 0.00037439 | -0.0010277 | 0.053149 | 0.05313 | 0.053149 | 0.99519 | -0.21492 | 0.99556 | -0.18893 | 4.1201
56 | -1.7336 | -0.59323 | 1.7338 | 0.55786 | 0.00012329 | -0.035361 | 0.05313 | 0.052807 | 0.05313 | 0.99556 | -0.18893 | 0.99564 | -0.18808 | 4.1638
57 | 5.6821 | 1.9497 | -5.6819 | -1.956 | 0.00024039 | -0.006353 | 0.17349 | 0.17355 | 0.17355 | 0.99959 | -0.023321 | 0.99955 | -0.023797 | 13.6009
58 | 5.6819 | 1.956 | -5.6809 | -1.9539 | 0.00094989 | 0.0020665 | 0.17355 | 0.17355 | 0.17355 | 0.99955 | -0.023797 | 0.99926 | -0.043883 | 13.4537
59 | 5.6032 | 1.9196 | -5.6031 | -1.923 | 0.00012327 | -0.0033494 | 0.17111 | 0.17114 | 0.17114 | 0.99926 | -0.043883 | 0.99924 | -0.044131 | 13.4121
60 | 0.077727 | 0.034339 | -0.077726 | -0.037576 | 1.1096e-06 | -0.003237 | 0.0024548 | 0.0024941 | 0.0024941 | 0.99926 | -0.043883 | 0.99925 | -0.043771 | 1.1337
61 | -0.24195 | -0.11238 | 0.24196 | 0.11177 | 2.0627e-06 | -0.00061193 | 0.0077327 | 0.0077252 | 0.0077327 | 0.99593 | -0.17516 | 0.99594 | -0.17523 | 3.5149
62 | 0.16485 | 0.075036 | -0.16484 | -0.07731 | 3.5532e-06 | -0.0022739 | 0.0052499 | 0.0052776 | 0.0052776 | 0.99593 | -0.17516 | 0.99591 | -0.17499 | 2.3989
63 | -0.24196 | -0.11177 | 0.24196 | 0.11043 | 4.4936e-06 | -0.0013372 | 0.0077252 | 0.0077091 | 0.0077252 | 0.99594 | -0.17523 | 0.99596 | -0.17537 | 3.5115
64 | 0.16484 | 0.07731 | -0.16484 | -0.078614 | 2.0544e-06 | -0.0013038 | 0.0052776 | 0.0052937 | 0.0052937 | 0.99591 | -0.17499 | 0.9959 | -0.17489 | 2.4062
65 | -0.24196 | -0.11043 | 0.24196 | 0.11039 | 3.9257e-06 | -4.1448e-05 | 0.0077091 | 0.0077085 | 0.0077091 | 0.99596 | -0.17537 | 0.99597 | -0.17524 | 3.671
66 | 0.16484 | 0.078614 | -0.16484 | -0.079836 | 1.9362e-06 | -0.0012215 | 0.0052937 | 0.0053091 | 0.0053091 | 0.9959 | -0.17489 | 0.99589 | -0.17479 | 2.4132
67 | 0.14797 | 0.071593 | -0.14797 | -0.071663 | 2.459e-06 | -7.0446e-05 | 0.0047644 | 0.0047653 | 0.0047653 | 0.99597 | -0.17524 | 0.99595 | -0.17535 | 2.2692
68 | -0.38993 | -0.18198 | 0.38994 | 0.18122 | 6.6851e-06 | -0.00076104 | 0.012472 | 0.012463 | 0.012472 | 0.99597 | -0.17524 | 0.99599 | -0.17538 | 5.6692
69 | -2.239 | -0.68897 | 2.239 | 0.68453 | 2.5447e-05 | -0.0044414 | 0.067899 | 0.067862 | 0.067899 | 0.99596 | -0.18067 | 0.99597 | -0.18051 | 5.3213
70 | 2.0751 | 0.60959 | -2.0751 | -0.60965 | 4.6184e-05 | -5.6351e-05 | 0.062688 | 0.062689 | 0.062689 | 0.99596 | -0.18067 | 0.99592 | -0.18348 | 4.8596
71 | -2.3639 | -0.74502 | 2.364 | 0.74499 | 9.016e-05 | -2.5982e-05 | 0.071839 | 0.071836 | 0.071839 | 0.99597 | -0.18051 | 0.99604 | -0.1758 | 5.5689
72 | 2.0751 | 0.60965 | -2.075 | -0.6169 | 3.5463e-05 | -0.0072529 | 0.062689 | 0.062749 | 0.062749 | 0.99592 | -0.18348 | 0.99591 | -0.18372 | 4.9176
73 | 2.075 | 0.6169 | -2.075 | -0.62075 | 1.8836e-05 | -0.0038465 | 0.062749 | 0.062781 | 0.062781 | 0.99591 | -0.18372 | 0.9959 | -0.18385 | 4.9201
74 | -2.8788 | -0.98461 | 2.8789 | 0.97003 | 0.0001411 | -0.014588 | 0.088178 | 0.088042 | 0.088178 | 0.99604 | -0.1758 | 0.99609 | -0.17523 | 6.9105
75 | 0.51474 | 0.23962 | -0.51473 | -0.24057 | 1.4509e-05 | -0.00094565 | 0.016456 | 0.016467 | 0.016467 | 0.99604 | -0.1758 | 0.99601 | -0.17557 | 7.4852
76 | 1.9268 | 0.54898 | -1.9268 | -0.5588 | 4.119e-05 | -0.0098152 | 0.058075 | 0.058154 | 0.058154 | 0.9959 | -0.18385 | 0.99587 | -0.18416 | 4.5575
77 | 1.9268 | 0.5588 | -1.9264 | -0.64987 | 0.00038784 | -0.091067 | 0.058154 | 0.058946 | 0.058946 | 0.99587 | -0.18416 | 0.99566 | -0.18678 | 4.6196
78 | 1.9264 | 0.64987 | -1.9264 | -0.6499 | 2.0224e-05 | -3.4981e-05 | 0.058946 | 0.058946 | 0.058946 | 0.99566 | -0.18678 | 0.99564 | -0.18805 | 4.5695
79 | 1.8043 | 0.59079 | -1.8043 | -0.59205 | 4.7383e-06 | -0.0012578 | 0.055048 | 0.055059 | 0.055059 | 0.99564 | -0.18805 | 0.99564 | -0.18808 | 4.315
80 | 1.4951 | 0.52775 | -1.494 | -0.53237 | 0.0010288 | -0.004629 | 0.04606 | 0.046132 | 0.046132 | 0.99367 | -0.31635 | 0.99248 | -0.39813 | 3.5761
81 | -0.097818 | -0.047375 | 0.097818 | 0.047339 | 5.4704e-07 | -3.6325e-05 | 0.0031497 | 0.0031492 | 0.0031497 | 0.99614 | -0.17456 | 0.99614 | -0.17452 | 1.4998
82 | -0.097818 | -0.047339 | 0.097822 | 0.047123 | 3.255e-06 | -0.00021638 | 0.0031492 | 0.0031465 | 0.0031492 | 0.99614 | -0.17452 | 0.99618 | -0.1743 | 1.4996
83 | 3.0122 | 1.0108 | -3.0122 | -1.0148 | 4.1869e-05 | -0.0039612 | 0.092074 | 0.09211 | 0.09211 | 0.99618 | -0.1743 | 0.99616 | -0.17446 | 7.2187
84 | -3.2148 | -1.1086 | 3.2148 | 1.1019 | 8.2251e-05 | -0.006795 | 0.098543 | 0.098478 | 0.098543 | 0.99618 | -0.1743 | 0.9962 | -0.17401 | 7.7228
85 | -0.13736 | -0.066289 | 0.13736 | 0.052526 | 6.2469e-07 | -0.013763 | 0.0044195 | 0.0042613 | 0.0044195 | 0.9962 | -0.17433 | 0.9962 | -0.17422 | 0.52488
86 | 0.13736 | 0.066289 | -0.13735 | -0.066524 | 6.4033e-07 | -0.00023522 | 0.0044195 | 0.0044225 | 0.0044225 | 0.9962 | -0.17433 | 0.99619 | -0.17454 | 0.53933
87 | -0.38272 | -0.17105 | 0.38272 | 0.1704 | 2.3004e-07 | -0.00064597 | 0.012147 | 0.01214 | 0.012147 | 0.9962 | -0.17422 | 0.99621 | -0.17421 | 1.4427
88 | 0.24536 | 0.11852 | -0.24536 | -0.11857 | 4.6488e-06 | -4.6664e-05 | 0.0078961 | 0.0078967 | 0.0078967 | 0.9962 | -0.17422 | 0.99618 | -0.17435 | 3.7603
89 | -0.38272 | -0.1704 | 0.38272 | 0.17029 | 1.1429e-06 | -0.00011614 | 0.01214 | 0.012138 | 0.01214 | 0.99621 | -0.17421 | 0.99621 | -0.17389 | 0.94107
90 | 0.093185 | 0.04487 | -0.093181 | -0.04513 | 3.5506e-06 | -0.00026032 | 0.0029971 | 0.0030004 | 0.0030004 | 0.99618 | -0.17435 | 0.99614 | -0.1746 | 1.4287
91 | -4.1081 | -1.5024 | 4.1089 | 1.4587 | 0.00087466 | -0.043679 | 0.12671 | 0.12627 | 0.12671 | 0.99657 | -0.15015 | 0.9968 | -0.14796 | 9.9299
92 | 0.13006 | 0.061901 | -0.13006 | -0.062991 | 1.072e-06 | -0.0010898 | 0.0041724 | 0.004186 | 0.004186 | 0.99657 | -0.15015 | 0.99656 | -0.15008 | 1.9027
93 | 3.978 | 1.4405 | -3.9772 | -1.4391 | 0.00079916 | 0.0013309 | 0.12255 | 0.12256 | 0.12256 | 0.99657 | -0.15015 | 0.99622 | -0.17383 | 9.5008
94 | 0.4927 | 0.15686 | -0.49269 | -0.19873 | 1.1924e-05 | -0.041871 | 0.014974 | 0.015386 | 0.015386 | 0.9968 | -0.14796 | 0.99677 | -0.14821 | 1.2058
95 | -4.6016 | -1.6155 | 4.6036 | 1.6194 | 0.0020032 | 0.00384 | 0.14124 | 0.14122 | 0.14124 | 0.9968 | -0.14796 | 0.99755 | -0.096076 | 10.9488
96 | 3.3492 | 1.1628 | -3.3491 | -1.1669 | 5.3412e-05 | -0.0040535 | 0.10273 | 0.10277 | 0.10277 | 0.99622 | -0.17383 | 0.9962 | -0.17401 | 8.0541
97 | 0.62805 | 0.27631 | -0.62804 | -0.28664 | 5.0926e-06 | -0.010333 | 0.019882 | 0.020005 | 0.020005 | 0.99622 | -0.17383 | 0.99621 | -0.17388 | 1.5678
98 | -0.12981 | -0.062872 | 0.12981 | 0.062514 | 3.5138e-07 | -0.00035729 | 0.0041796 | 0.0041751 | 0.0041796 | 0.99621 | -0.17386 | 0.99621 | -0.17388 | 1.8998
99 | 0.49823 | 0.22412 | -0.49823 | -0.22579 | 5.1785e-07 | -0.0016658 | 0.015831 | 0.015851 | 0.015851 | 0.99621 | -0.17388 | 0.99621 | -0.17388 | 1.2422
100 | 0.49823 | 0.22579 | -0.49823 | -0.22623 | 1.3735e-07 | -0.00044141 | 0.015851 | 0.015856 | 0.015856 | 0.99621 | -0.17388 | 0.99621 | -0.17389 | 1.2426
101 | 0.22267 | 0.10506 | -0.22266 | -0.10746 | 6.856e-06 | -0.0023939 | 0.0071231 | 0.007153 | 0.007153 | 0.9978 | -0.079979 | 0.99777 | -0.07972 | 3.2513
102 | -5.033 | -1.822 | 5.0338 | 1.7947 | 0.00081806 | -0.027216 | 0.15486 | 0.15459 | 0.15486 | 0.9978 | -0.079979 | 0.99797 | -0.078298 | 12.1362
103 | 4.7405 | 1.6831 | -4.7398 | -1.6818 | 0.00063416 | 0.0012437 | 0.14553 | 0.14554 | 0.14554 | 0.9978 | -0.079979 | 0.99757 | -0.095869 | 11.2821
104 | 0.1509 | 0.072703 | -0.1509 | -0.073086 | 5.061e-07 | -0.00038315 | 0.0048463 | 0.0048511 | 0.0048511 | 0.99777 | -0.07972 | 0.99777 | -0.079691 | 2.205
105 | 4.7398 | 1.6818 | -4.7397 | -1.6853 | 9.2619e-05 | -0.0034862 | 0.14554 | 0.14557 | 0.14557 | 0.99757 | -0.095869 | 0.99755 | -0.096076 | 11.4086
106 | -0.077725 | -0.037644 | 0.077726 | 0.037576 | 6.3754e-07 | -6.8146e-05 | 0.0024949 | 0.0024941 | 0.0024949 | 0.99924 | -0.043825 | 0.99925 | -0.043771 | 1.1881
107 | 3.0122 | 1.0148 | -3.012 | -1.034 | 0.00020325 | -0.019182 | 0.09211 | 0.09229 | 0.09229 | 0.99616 | -0.17446 | 0.99609 | -0.17523 | 7.2328
108 | 0.1331 | 0.063935 | -0.1331 | -0.064465 | 5.4766e-07 | -0.00052969 | 0.0042794 | 0.0042861 | 0.0042861 | 0.99609 | -0.17523 | 0.99609 | -0.1752 | 1.9482
109 | 0.38995 | 0.18013 | -0.38994 | -0.18122 | 9.5273e-06 | -0.0010866 | 0.01245 | 0.012463 | 0.012463 | 0.99601 | -0.17557 | 0.99599 | -0.17538 | 5.6649
110 | 0.42862 | 0.1677 | -0.42856 | -0.17218 | 5.3573e-05 | -0.0044777 | 0.01333 | 0.013379 | 0.013379 | 0.99677 | -0.14821 | 0.99655 | -0.1624 | 1.0371

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 5.9011 | 2.0445

## res_load
| p_mw | q_mvar
0 | 0.071169 | 0.034469
1 | 0.077319 | 0.037447
2 | 0.088191 | 0.042713
3 | 0.10453 | 0.050625
4 | 0.094517 | 0.045777
5 | 0.10134 | 0.049082
6 | 0.073234 | 0.035469
7 | 0.12603 | 0.06104
8 | 0.11754 | 0.056926
9 | 0.054391 | 0.026343
10 | 0.10637 | 0.051516
11 | 0.24621 | 0.11925
12 | 0.15637 | 0.075733
13 | 0.089795 | 0.04349
14 | 0.12215 | 0.059158
15 | 0.12221 | 0.05919
16 | 0.07674 | 0.037167
17 | 0.10042 | 0.048637
18 | 0.12329 | 0.059712
19 | 0.1301 | 0.063011
20 | 0.073303 | 0.035502
21 | 0.096231 | 0.046607
22 | 0.12323 | 0.059684
23 | 0.069666 | 0.033741
24 | 0.077106 | 0.037344
25 | 0.16484 | 0.079836
26 | 0.16389 | 0.079377
27 | 0.12489 | 0.060489
28 | 0.14817 | 0.071763
29 | 0.12205 | 0.059111
30 | 0.097818 | 0.047375
31 | 0.1047 | 0.050707
32 | 0.13735 | 0.066524
33 | 0.15217 | 0.073701
34 | 0.13006 | 0.062991
35 | 0.12981 | 0.062872
36 | 0.093181 | 0.04513
37 | 0.11551 | 0.055943
38 | 0.13426 | 0.065027
39 | 0.07058 | 0.034183
40 | 0.069882 | 0.033846
41 | 0.071755 | 0.034753
42 | 0.13609 | 0.065914
43 | 0.1509 | 0.073086
44 | 0.077725 | 0.037644
45 | 0.09834 | 0.047628
46 | 0.12337 | 0.059752
47 | 0.052858 | 0.0256
48 | 0.12478 | 0.060434
49 | 0.1331 | 0.064465
50 | 0.14797 | 0.071663
51 | 0.050342 | 0.024382
52 | 0.064069 | 0.03103
53 | 0.054426 | 0.02636

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1