## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_200_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_200_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_200_0_node_1 | 20 | n |  | TRUE
3 | bus_MV_200_0_node_21 | 20 | n |  | TRUE
4 | bus_MV_200_0_node_3 | 20 | n |  | TRUE
5 | bus_MV_200_0_node_4 | 20 | n |  | TRUE
6 | bus_MV_200_0_node_30 | 20 | n |  | TRUE
7 | bus_MV_200_0_node_192 | 20 | n |  | TRUE
8 | bus_MV_200_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_200_0_node_7 | 20 | n |  | TRUE
10 | bus_MV_200_0_node_81 | 20 | n |  | TRUE
11 | bus_MV_200_0_node_6 | 20 | n |  | TRUE
12 | bus_MV_200_0_node_9 | 20 | n |  | TRUE
13 | bus_MV_200_0_node_195 | 20 | n |  | TRUE
14 | bus_MV_200_0_node_12 | 20 | n |  | TRUE
15 | bus_MV_200_0_node_8 | 20 | n |  | TRUE
16 | bus_MV_200_0_node_31 | 20 | n |  | TRUE
17 | bus_MV_200_0_node_45 | 20 | n |  | TRUE
18 | bus_MV_200_0_node_51 | 20 | n |  | TRUE
19 | bus_MV_200_0_node_10 | 20 | n |  | TRUE
20 | bus_MV_200_0_node_11 | 20 | n |  | TRUE
21 | bus_MV_200_0_node_46 | 20 | n |  | TRUE
22 | bus_MV_200_0_node_27 | 20 | n |  | TRUE
23 | bus_MV_200_0_node_194 | 20 | n |  | TRUE
24 | bus_MV_200_0_node_47 | 20 | n |  | TRUE
25 | bus_MV_200_0_node_13 | 20 | n |  | TRUE
26 | bus_MV_200_0_node_22 | 20 | n |  | TRUE
27 | bus_MV_200_0_node_15 | 20 | n |  | TRUE
28 | bus_MV_200_0_node_160 | 20 | n |  | TRUE
29 | bus_MV_200_0_node_16 | 20 | n |  | TRUE
30 | bus_MV_200_0_node_20 | 20 | n |  | TRUE
31 | bus_MV_200_0_node_32 | 20 | n |  | TRUE
32 | bus_MV_200_0_node_18 | 20 | n |  | TRUE
33 | bus_MV_200_0_node_19 | 20 | n |  | TRUE
34 | bus_MV_200_0_node_179 | 20 | n |  | TRUE
35 | bus_MV_200_0_node_193 | 20 | n |  | TRUE
36 | bus_MV_200_0_node_23 | 20 | n |  | TRUE
37 | bus_MV_200_0_node_24 | 20 | n |  | TRUE
38 | bus_MV_200_0_node_26 | 20 | n |  | TRUE
39 | bus_MV_200_0_node_25 | 20 | n |  | TRUE
40 | bus_MV_200_0_node_44 | 20 | n |  | TRUE
41 | bus_MV_200_0_node_33 | 20 | n |  | TRUE
42 | bus_MV_200_0_node_34 | 20 | n |  | TRUE
43 | bus_MV_200_0_node_28 | 20 | n |  | TRUE
44 | bus_MV_200_0_node_37 | 20 | n |  | TRUE
45 | bus_MV_200_0_node_29 | 20 | n |  | TRUE
46 | bus_MV_200_0_node_36 | 20 | n |  | TRUE
47 | bus_MV_200_0_node_43 | 20 | n |  | TRUE
48 | bus_MV_200_0_node_35 | 20 | n |  | TRUE
49 | bus_MV_200_0_node_41 | 20 | n |  | TRUE
50 | bus_MV_200_0_node_42 | 20 | n |  | TRUE
51 | bus_MV_200_0_node_40 | 20 | n |  | TRUE
52 | bus_MV_200_0_node_50 | 20 | n |  | TRUE
53 | bus_MV_200_0_node_48 | 20 | n |  | TRUE
54 | bus_MV_200_0_node_49 | 20 | n |  | TRUE
55 | bus_MV_200_0_node_177 | 20 | n |  | TRUE
56 | bus_MV_200_0_node_154 | 20 | n |  | TRUE
57 | bus_MV_200_0_node_153 | 20 | n |  | TRUE
58 | bus_MV_200_0_node_157 | 20 | n |  | TRUE
59 | bus_MV_200_0_node_180 | 20 | n |  | TRUE
60 | bus_MV_200_0_node_86 | 20 | n |  | TRUE
61 | bus_MV_200_0_node_159 | 20 | n |  | TRUE
62 | bus_MV_200_0_node_152 | 20 | n |  | TRUE
63 | bus_MV_200_0_node_158 | 20 | n |  | TRUE
64 | bus_MV_200_0_node_151 | 20 | n |  | TRUE
65 | bus_MV_200_0_node_84 | 20 | n |  | TRUE
66 | bus_MV_200_0_node_85 | 20 | n |  | TRUE
67 | bus_MV_200_0_node_156 | 20 | n |  | TRUE
68 | bus_MV_200_0_node_150 | 20 | n |  | TRUE
69 | bus_HV_200_0_node_22 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_200_0_load_0 | 0 | 0.13806 | 0.066864 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_200_0_load_21 | 3 | 0.094185 | 0.045616 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_200_0_load_3 | 4 | 0.11202 | 0.054254 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_200_0_load_192 | 7 | 0.10575 | 0.051219 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_200_0_load_5 | 8 | 0.10294 | 0.049856 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_200_0_load_81 | 10 | 0.084446 | 0.040899 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_200_0_load_195 | 13 | 0.1384 | 0.067033 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_200_0_load_45 | 17 | 0.11273 | 0.054599 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_200_0_load_51 | 18 | 0.12288 | 0.059515 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_200_0_load_46 | 21 | 0.14183 | 0.068693 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_200_0_load_194 | 23 | 0.12474 | 0.060412 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_200_0_load_47 | 24 | 0.15803 | 0.076536 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_200_0_load_13 | 25 | 0.14222 | 0.068878 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_200_0_load_22 | 26 | 0.15603 | 0.07557 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_200_0_load_160 | 28 | 0.12467 | 0.060382 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_200_0_load_32 | 31 | 0.10798 | 0.052298 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_200_0_load_18 | 32 | 0.10584 | 0.051262 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_200_0_load_179 | 34 | 0.064598 | 0.031286 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_200_0_load_193 | 35 | 0.14985 | 0.072574 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_200_0_load_44 | 40 | 0.14978 | 0.072544 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_200_0_load_28 | 43 | 0.092177 | 0.044643 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_200_0_load_37 | 44 | 0.082745 | 0.040075 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_200_0_load_36 | 46 | 0.1205 | 0.05836 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_200_0_load_43 | 47 | 0.081617 | 0.039529 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_200_0_load_41 | 49 | 0.08442 | 0.040887 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_200_0_load_42 | 50 | 0.15651 | 0.075803 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_200_0_load_40 | 51 | 0.11576 | 0.056067 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_200_0_load_177 | 55 | 0.15614 | 0.07562 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_200_0_load_153 | 57 | 0.11004 | 0.053293 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_200_0_load_180 | 59 | 0.09249 | 0.044795 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_200_0_load_159 | 61 | 0.16108 | 0.078014 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_200_0_load_84 | 65 | 0.14347 | 0.069487 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_200_0_load_156 | 67 | 0.15989 | 0.07744 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_200_0_load_150 | 68 | 0.11826 | 0.057274 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_200_0_line_0 |  | 0 | 1 | 0.06818 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_200_0_line_1 |  | 0 | 2 | 0.098795 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_200_0_line_2 |  | 0 | 3 | 0.69681 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_200_0_line_3 |  | 1 | 5 | 0.10967 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_200_0_line_4 |  | 2 | 4 | 0.081151 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_200_0_line_5 |  | 4 | 6 | 0.091316 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_200_0_line_6 |  | 5 | 7 | 0.14108 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_200_0_line_7 |  | 6 | 43 | 0.089509 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_200_0_line_8 |  | 7 | 27 | 0.32908 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_200_0_line_9 |  | 8 | 9 | 0.023829 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_200_0_line_10 |  | 8 | 10 | 1.0262 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_200_0_line_11 |  | 8 | 11 | 0.073344 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_200_0_line_12 |  | 9 | 14 | 0.060663 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_200_0_line_13 |  | 11 | 12 | 0.14905 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_200_0_line_14 |  | 11 | 13 | 0.26646 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_200_0_line_15 |  | 12 | 18 | 0.048456 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_200_0_line_16 |  | 13 | 22 | 0.089771 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_200_0_line_17 |  | 14 | 24 | 0.12715 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_200_0_line_18 |  | 15 | 16 | 0.11404 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_200_0_line_19 |  | 15 | 17 | 0.021595 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_200_0_line_20 |  | 16 | 46 | 0.01885 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_200_0_line_21 |  | 16 | 45 | 0.10227 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_200_0_line_22 |  | 17 | 22 | 0.27383 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_200_0_line_23 |  | 19 | 20 | 0.10168 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_200_0_line_24 |  | 19 | 21 | 0.11137 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_200_0_line_25 |  | 19 | 22 | 0.10151 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_200_0_line_26 |  | 20 | 23 | 0.058134 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_200_0_line_27 |  | 21 | 39 | 0.052894 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_200_0_line_28 |  | 24 | 53 | 0.082307 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_200_0_line_29 |  | 25 | 26 | 0.10795 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_200_0_line_30 |  | 26 | 36 | 0.077069 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
31 | MV_200_0_line_31 |  | 27 | 28 | 0.71453 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_200_0_line_32 |  | 28 | 64 | 0.16667 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_200_0_line_33 |  | 29 | 30 | 0.19293 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_200_0_line_34 |  | 29 | 31 | 0.062223 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_200_0_line_35 |  | 30 | 35 | 0.040832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_200_0_line_36 |  | 30 | 33 | 0.32369 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_200_0_line_37 |  | 31 | 38 | 0.031775 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_200_0_line_38 |  | 32 | 33 | 0.1378 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_200_0_line_39 |  | 32 | 34 | 0.97903 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_200_0_line_40 |  | 34 | 59 | 0.41789 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_200_0_line_41 |  | 36 | 37 | 0.26003 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_200_0_line_42 |  | 36 | 38 | 0.18479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_200_0_line_43 |  | 37 | 39 | 0.14471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_200_0_line_44 |  | 37 | 40 | 0.028529 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_200_0_line_45 |  | 38 | 41 | 0.025209 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_200_0_line_46 |  | 38 | 42 | 0.077808 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_200_0_line_47 |  | 41 | 47 | 0.016985 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_200_0_line_48 |  | 42 | 48 | 0.055356 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_200_0_line_49 |  | 42 | 49 | 0.014813 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_200_0_line_50 |  | 43 | 44 | 0.23729 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_200_0_line_51 |  | 43 | 45 | 0.11223 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_200_0_line_52 |  | 48 | 50 | 0.026757 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_200_0_line_53 |  | 51 | 52 | 0.046821 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_200_0_line_54 |  | 52 | 53 | 0.24736 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_200_0_line_55 |  | 53 | 54 | 0.10501 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_200_0_line_56 |  | 54 | 55 | 1.554 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_200_0_line_57 |  | 56 | 57 | 0.028845 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_200_0_line_58 |  | 56 | 58 | 0.32198 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_200_0_line_59 |  | 58 | 63 | 0.17522 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_200_0_line_60 |  | 58 | 67 | 0.17214 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_200_0_line_61 |  | 59 | 60 | 0.052557 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_200_0_line_62 |  | 60 | 66 | 0.20312 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_200_0_line_63 |  | 61 | 62 | 0.016603 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_200_0_line_64 |  | 61 | 63 | 0.011678 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_200_0_line_65 |  | 62 | 64 | 0.25914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_200_0_line_66 |  | 64 | 68 | 0.11 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_200_0_line_67 |  | 65 | 66 | 0.005906 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_200_0_trafo_22 | 25 MVA 110/20 kV | 69 | 26 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2655110.4215 | 1142373.8885
1 | 2655173.8672 | 1142353.7797
2 | 2655169.2526 | 1142453.2567
3 | 2654497.4101 | 1142705.1982
4 | 2655241.2838 | 1142429.7808
5 | 2655228.9175 | 1142267.5375
6 | 2655332.3825 | 1142423.4784
7 | 2655281.0792 | 1142140.1588
8 | 2656016.8827 | 1142170.0348
9 | 2656017.1847 | 1142193.8169
10 | 2656773.2545 | 1141476.4439
11 | 2655953.7026 | 1142132.7848
12 | 2655876.8771 | 1142231.6811
13 | 2655793.6213 | 1141919.7684
14 | 2656035.5656 | 1142251.6069
15 | 2655654.6115 | 1142201.4453
16 | 2655598.8384 | 1142296.1704
17 | 2655656.7162 | 1142179.9534
18 | 2655860.5274 | 1142277.2984
19 | 2655647.6341 | 1141994.4827
20 | 2655622.533 | 1142090.6245
21 | 2655568.9192 | 1141928.2783
22 | 2655704.3512 | 1141910.2946
23 | 2655566.8492 | 1142073.7583
24 | 2656118.7894 | 1142347.742
25 | 2655243.4676 | 1141770.5861
26 | 2655347.2532 | 1141800.2968
27 | 2654988.0693 | 1141990.3594
28 | 2654284.8519 | 1141863.74
29 | 2655413.1688 | 1141583.9649
30 | 2655382.0867 | 1141422.3389
31 | 2655445.1823 | 1141637.3203
32 | 2655231.0005 | 1141186.5638
33 | 2655185.2047 | 1141316.5359
34 | 2654853.1893 | 1140283.366
35 | 2655344.2746 | 1141406.7172
36 | 2655393.4676 | 1141738.6214
37 | 2655528.6814 | 1141830.801
38 | 2655476.3327 | 1141644.0211
39 | 2655576.5121 | 1141875.9316
40 | 2655510.6269 | 1141808.7122
41 | 2655488.8524 | 1141628.528
42 | 2655532.249 | 1141639.4327
43 | 2655405.2739 | 1142372.5645
44 | 2655568.8559 | 1142544.4588
45 | 2655501.6718 | 1142315.0863
46 | 2655617.4367 | 1142293.2512
47 | 2655490.0537 | 1141611.5856
48 | 2655554.709 | 1141673.2017
49 | 2655534.6206 | 1141624.8135
50 | 2655528.7201 | 1141679.5659
51 | 2655869.888 | 1142424.4517
52 | 2655915.129 | 1142418.1228
53 | 2656147.8669 | 1142424.742
54 | 2656251.056 | 1142444.213
55 | 2657708.2701 | 1142984.0101
56 | 2654377.2105 | 1141328.5227
57 | 2654403.0004 | 1141315.6038
58 | 2654160.0423 | 1141566.2404
59 | 2655225.2743 | 1140093.1457
60 | 2655273.8039 | 1140072.9679
61 | 2654146.9327 | 1141712.9667
62 | 2654146.5379 | 1141729.5608
63 | 2654147.5985 | 1141701.311
64 | 2654137.9851 | 1141942.5295
65 | 2655287.6281 | 1139896.0233
66 | 2655282.6011 | 1139899.1456
67 | 2654154.3058 | 1141394.1984
68 | 2654095.0091 | 1142002.1756
69 | 2655347.2532 | 1141800.2968

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99498 | -0.0057365 | 0.13806 | 0.066864
1 | 0.99492 | -0.0051932 | 0 | 0
2 | 0.99518 | -0.0043068 | 0 | 0
3 | 0.99486 | -0.0065623 | 0.094185 | 0.045616
4 | 0.99528 | -0.005167 | 0.11202 | 0.054254
5 | 0.99481 | -0.0043042 | 0 | 0
6 | 0.99548 | -0.0037053 | 0 | 0
7 | 0.99467 | -0.0031334 | 0.10575 | 0.051219
8 | 0.99651 | -0.0039672 | 0.10294 | 0.049856
9 | 0.9965 | -0.0038603 | 0 | 0
10 | 0.99634 | -0.0050754 | 0.084446 | 0.040899
11 | 0.9966 | -0.003338 | 0 | 0
12 | 0.99657 | -0.0031453 | 0 | 0
13 | 0.99698 | -0.00054359 | 0.1384 | 0.067033
14 | 0.99646 | -0.0035845 | 0 | 0
15 | 0.99626 | -0.0058202 | 0 | 0
16 | 0.99606 | -0.0041094 | 0 | 0
17 | 0.99632 | -0.005382 | 0.11273 | 0.054599
18 | 0.99657 | -0.0030753 | 0.12288 | 0.059515
19 | 0.9976 | 0.0039844 | 0 | 0
20 | 0.99758 | 0.00412 | 0 | 0
21 | 0.99796 | 0.00099347 | 0.14183 | 0.068693
22 | 0.99713 | 0.00055 | 0 | 0
23 | 0.99757 | 0.0042046 | 0.12474 | 0.060412
24 | 0.99636 | -0.0043491 | 0.15803 | 0.076536
25 | 0.99997 | -0.00018612 | 0.14222 | 0.068878
26 | 1 | 0 | -3.9836 | -1.8344
27 | 0.99424 | -0.0062965 | 0 | 0
28 | 0.99331 | -0.013136 | 0.12467 | 0.060382
29 | 0.99933 | -0.0073146 | 0 | 0
30 | 0.9992 | -0.0062476 | 0 | 0
31 | 0.9994 | -0.0067885 | 0.10798 | 0.052298
32 | 0.99892 | -0.0056486 | 0.10584 | 0.051262
33 | 0.99903 | -0.0048908 | 0 | 0
34 | 0.99836 | -0.0097249 | 0.064598 | 0.031286
35 | 0.99919 | -0.0061755 | 0.14985 | 0.072574
36 | 0.99966 | -0.0088618 | 0 | 0
37 | 0.99872 | -0.0011181 | 0 | 0
38 | 0.99943 | -0.0069998 | 0 | 0
39 | 0.99823 | 0.0029824 | 0 | 0
40 | 0.99871 | -0.0011699 | 0.14978 | 0.072544
41 | 0.99942 | -0.0069756 | 0 | 0
42 | 0.9994 | -0.0067883 | 0 | 0
43 | 0.99561 | -0.0047627 | 0.092177 | 0.044643
44 | 0.99557 | -0.0050049 | 0.082745 | 0.040075
45 | 0.99589 | -0.0027035 | 0 | 0
46 | 0.99605 | -0.0040823 | 0.1205 | 0.05836
47 | 0.99942 | -0.0069924 | 0.081617 | 0.039529
48 | 0.99939 | -0.0066869 | 0 | 0
49 | 0.9994 | -0.0067735 | 0.08442 | 0.040887
50 | 0.99938 | -0.0067377 | 0.15651 | 0.075803
51 | 0.99627 | -0.0043403 | 0.11576 | 0.056067
52 | 0.99628 | -0.004404 | 0 | 0
53 | 0.99632 | -0.004685 | 0 | 0
54 | 0.99628 | -0.0049017 | 0 | 0
55 | 0.99581 | -0.0079795 | 0.15614 | 0.07562
56 | 0.99285 | -0.013076 | 0 | 0
57 | 0.99285 | -0.013038 | 0.11004 | 0.053293
58 | 0.99292 | -0.012617 | 0 | 0
59 | 0.99817 | -0.011109 | 0.09249 | 0.044795
60 | 0.99815 | -0.011223 | 0 | 0
61 | 0.99298 | -0.013188 | 0.16108 | 0.078014
62 | 0.99299 | -0.013268 | 0 | 0
63 | 0.99298 | -0.013154 | 0 | 0
64 | 0.99314 | -0.014471 | 0 | 0
65 | 0.99812 | -0.010896 | 0.14347 | 0.069487
66 | 0.99812 | -0.010906 | 0 | 0
67 | 0.99287 | -0.012956 | 0.15989 | 0.07744
68 | 0.99312 | -0.014322 | 0.11826 | 0.057274
69 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.78102 | 0.35463 | -0.78097 | -0.35623 | 5.6416e-05 | -0.0015947 | 0.024886 | 0.024906 | 0.024906 | 0.99498 | -0.0057365 | 0.99492 | -0.0051932 | 11.3208
1 | -1.0133 | -0.46629 | 1.0135 | 0.46629 | 0.00018434 | -1.3213e-06 | 0.032362 | 0.03236 | 0.032362 | 0.99498 | -0.0057365 | 0.99518 | -0.0043068 | 15.4103
2 | 0.094196 | 0.0448 | -0.094185 | -0.045616 | 1.1409e-05 | -0.00081628 | 0.0030263 | 0.0030366 | 0.0030366 | 0.99498 | -0.0057365 | 0.99486 | -0.0065623 | 1.446
3 | 0.78097 | 0.35623 | -0.78087 | -0.35879 | 9.093e-05 | -0.0025646 | 0.024906 | 0.024937 | 0.024937 | 0.99492 | -0.0051932 | 0.99481 | -0.0043042 | 11.335
4 | -1.0135 | -0.46629 | 1.0136 | 0.46441 | 0.00011337 | -0.0018855 | 0.03236 | 0.032337 | 0.03236 | 0.99518 | -0.0043068 | 0.99528 | -0.005167 | 14.7092
5 | -1.1256 | -0.51866 | 1.1258 | 0.51868 | 0.00021022 | 2.3667e-05 | 0.035946 | 0.035945 | 0.035946 | 0.99528 | -0.005167 | 0.99548 | -0.0037053 | 17.1173
6 | 0.78087 | 0.35879 | -0.78076 | -0.36209 | 0.00011731 | -0.0032983 | 0.024937 | 0.024978 | 0.024978 | 0.99481 | -0.0043042 | 0.99467 | -0.0031334 | 11.3534
7 | -1.1258 | -0.51868 | 1.126 | 0.51661 | 0.00015428 | -0.0020723 | 0.035945 | 0.035919 | 0.035945 | 0.99548 | -0.0037053 | 0.99561 | -0.0047627 | 16.3387
8 | 0.675 | 0.31087 | -0.67473 | -0.31109 | 0.0002728 | -0.00021764 | 0.021568 | 0.021573 | 0.021573 | 0.99467 | -0.0031334 | 0.99424 | -0.0062965 | 10.2727
9 | 0.43008 | 0.19712 | -0.43008 | -0.19769 | 5.9782e-06 | -0.0005632 | 0.013705 | 0.013712 | 0.013712 | 0.99651 | -0.0039672 | 0.9965 | -0.0038603 | 6.2327
10 | 0.08446 | 0.039691 | -0.084446 | -0.040899 | 1.3438e-05 | -0.001208 | 0.0027034 | 0.0027186 | 0.0027186 | 0.99651 | -0.0039672 | 0.99634 | -0.0050754 | 1.2946
11 | -0.61748 | -0.28667 | 0.61753 | 0.28661 | 5.0821e-05 | -5.5123e-05 | 0.019721 | 0.01972 | 0.019721 | 0.99651 | -0.0039672 | 0.9966 | -0.003338 | 9.3911
12 | 0.43008 | 0.19769 | -0.43006 | -0.19912 | 1.5246e-05 | -0.0014337 | 0.013712 | 0.013729 | 0.013729 | 0.9965 | -0.0038603 | 0.99646 | -0.0035845 | 6.2407
13 | 0.12289 | 0.054833 | -0.12288 | -0.058367 | 3.0561e-06 | -0.0035335 | 0.0038979 | 0.0039407 | 0.0039407 | 0.9966 | -0.003338 | 0.99657 | -0.0031453 | 1.7912
14 | -0.74042 | -0.34145 | 0.74068 | 0.3413 | 0.00026477 | -0.00015022 | 0.023618 | 0.023614 | 0.023618 | 0.9966 | -0.003338 | 0.99698 | -0.00054359 | 11.2465
15 | 0.12288 | 0.058367 | -0.12288 | -0.059515 | 1.0082e-06 | -0.0011487 | 0.0039407 | 0.0039551 | 0.0039551 | 0.99657 | -0.0031453 | 0.99657 | -0.0030753 | 1.7978
16 | -0.87909 | -0.40833 | 0.87921 | 0.4083 | 0.00012598 | -2.7627e-05 | 0.028066 | 0.028065 | 0.028066 | 0.99698 | -0.00054359 | 0.99713 | 0.00055 | 13.3647
17 | 0.43006 | 0.19912 | -0.43002 | -0.19924 | 4.271e-05 | -0.00012396 | 0.013729 | 0.013731 | 0.013731 | 0.99646 | -0.0035845 | 0.99636 | -0.0043491 | 6.5387
18 | 1.4223 | 0.65409 | -1.422 | -0.6567 | 0.00031348 | -0.0026089 | 0.045361 | 0.045394 | 0.045394 | 0.99626 | -0.0058202 | 0.99606 | -0.0041094 | 20.6334
19 | -1.4223 | -0.65409 | 1.4224 | 0.65411 | 7.9166e-05 | 2.3998e-05 | 0.045361 | 0.04536 | 0.045361 | 0.99626 | -0.0058202 | 0.99632 | -0.005382 | 21.6004
20 | 0.1205 | 0.057913 | -0.1205 | -0.05836 | 3.7833e-07 | -0.00044641 | 0.0038747 | 0.0038803 | 0.0038803 | 0.99606 | -0.0041094 | 0.99605 | -0.0040823 | 1.7638
21 | 1.3015 | 0.59878 | -1.3012 | -0.60114 | 0.00023553 | -0.0023524 | 0.041519 | 0.041549 | 0.041549 | 0.99606 | -0.0041094 | 0.99589 | -0.0027035 | 18.8858
22 | -1.5351 | -0.70871 | 1.5363 | 0.70912 | 0.0011708 | 0.00040859 | 0.048989 | 0.048985 | 0.048989 | 0.99632 | -0.005382 | 0.99713 | 0.00055 | 23.3281
23 | 0.12474 | 0.056616 | -0.12474 | -0.059031 | 2.1485e-06 | -0.0024153 | 0.003964 | 0.0039934 | 0.0039934 | 0.9976 | 0.0039844 | 0.99758 | 0.00412 | 1.8152
24 | -2.5413 | -1.1746 | 2.5423 | 1.1722 | 0.00097541 | -0.002358 | 0.081012 | 0.08098 | 0.081012 | 0.9976 | 0.0039844 | 0.99796 | 0.00099347 | 36.8237
25 | 2.4165 | 1.118 | -2.4155 | -1.1174 | 0.0010737 | 0.00055198 | 0.077048 | 0.07705 | 0.07705 | 0.9976 | 0.0039844 | 0.99713 | 0.00055 | 36.6903
26 | 0.12474 | 0.059031 | -0.12474 | -0.060412 | 1.243e-06 | -0.0013809 | 0.0039934 | 0.0040106 | 0.0040106 | 0.99758 | 0.00412 | 0.99757 | 0.0042046 | 1.823
27 | -2.6841 | -1.2409 | 2.6848 | 1.2413 | 0.00068954 | 0.000369 | 0.085538 | 0.085537 | 0.085538 | 0.99796 | 0.00099347 | 0.99823 | 0.0029824 | 40.7323
28 | 0.27199 | 0.12271 | -0.27198 | -0.1228 | 1.0962e-05 | -9.0674e-05 | 0.0086452 | 0.0086463 | 0.0086463 | 0.99636 | -0.0043491 | 0.99632 | -0.004685 | 4.1173
29 | -0.14222 | -0.068878 | 0.14222 | 0.068752 | 4.0011e-06 | -0.00012637 | 0.0045617 | 0.0045601 | 0.0045617 | 0.99997 | -0.00018612 | 1 | 0 | 2.1722
30 | 3.8273 | 1.7552 | -3.8263 | -1.7541 | 0.0010453 | 0.0010988 | 0.12155 | 0.12155 | 0.12155 | 1 | 0 | 0.99966 | -0.0088618 | 34.7288
31 | 0.67473 | 0.31109 | -0.67414 | -0.31156 | 0.00059274 | -0.00047115 | 0.021573 | 0.021583 | 0.021583 | 0.99424 | -0.0062965 | 0.99331 | -0.013136 | 10.2775
32 | 0.54946 | 0.25118 | -0.54937 | -0.25132 | 9.1555e-05 | -0.00013893 | 0.017558 | 0.01756 | 0.01756 | 0.99331 | -0.013136 | 0.99314 | -0.014471 | 8.362
33 | 0.55665 | 0.24946 | -0.55657 | -0.25403 | 8.0218e-05 | -0.0045759 | 0.017621 | 0.017675 | 0.017675 | 0.99933 | -0.0073146 | 0.9992 | -0.0062476 | 8.0343
34 | -0.55665 | -0.24946 | 0.55669 | 0.2494 | 3.442e-05 | -5.2628e-05 | 0.017621 | 0.01762 | 0.017621 | 0.99933 | -0.0073146 | 0.9994 | -0.0067885 | 8.3908
35 | 0.14985 | 0.071601 | -0.14985 | -0.072574 | 1.2581e-06 | -0.00097296 | 0.004798 | 0.0048102 | 0.0048102 | 0.9992 | -0.0062476 | 0.99919 | -0.0061755 | 2.1865
36 | 0.40673 | 0.18243 | -0.40665 | -0.19012 | 7.2184e-05 | -0.0076934 | 0.012878 | 0.012971 | 0.012971 | 0.9992 | -0.0062476 | 0.99903 | -0.0048908 | 5.896
37 | -0.66467 | -0.3017 | 0.66469 | 0.30095 | 1.8849e-05 | -0.00075218 | 0.021084 | 0.021075 | 0.021084 | 0.9994 | -0.0067885 | 0.99943 | -0.0069998 | 9.5837
38 | -0.40661 | -0.19026 | 0.40665 | 0.19012 | 4.1317e-05 | -0.0001383 | 0.012973 | 0.012971 | 0.012973 | 0.99892 | -0.0056486 | 0.99903 | -0.0048908 | 6.1778
39 | 0.30077 | 0.139 | -0.30061 | -0.14007 | 0.00016016 | -0.0010653 | 0.0095752 | 0.0095894 | 0.0095894 | 0.99892 | -0.0056486 | 0.99836 | -0.0097249 | 4.5664
40 | 0.23601 | 0.10878 | -0.23597 | -0.10925 | 4.2074e-05 | -0.00047079 | 0.0075143 | 0.0075203 | 0.0075203 | 0.99836 | -0.0097249 | 0.99817 | -0.011109 | 3.5811
41 | 2.8388 | 1.3054 | -2.836 | -1.3108 | 0.0028285 | -0.0053593 | 0.09023 | 0.090305 | 0.090305 | 0.99966 | -0.0088618 | 0.99872 | -0.0011181 | 41.0475
42 | 0.98749 | 0.44865 | -0.98725 | -0.45299 | 0.00024243 | -0.0043362 | 0.031321 | 0.031374 | 0.031374 | 0.99966 | -0.0088618 | 0.99943 | -0.0069998 | 14.2611
43 | 2.6862 | 1.2383 | -2.6848 | -1.2413 | 0.0014128 | -0.0030256 | 0.085495 | 0.085537 | 0.085537 | 0.99872 | -0.0011181 | 0.99823 | 0.0029824 | 38.8805
44 | 0.14979 | 0.07251 | -0.14978 | -0.072544 | 1.1761e-06 | -3.3234e-05 | 0.0048101 | 0.0048105 | 0.0048105 | 0.99872 | -0.0011181 | 0.99871 | -0.0011699 | 2.2907
45 | 0.081618 | 0.038908 | -0.081617 | -0.039509 | 2.302e-07 | -0.00060114 | 0.0026116 | 0.0026191 | 0.0026191 | 0.99943 | -0.0069998 | 0.99942 | -0.0069756 | 1.1905
46 | 0.24094 | 0.11313 | -0.24094 | -0.11499 | 6.1585e-06 | -0.0018538 | 0.0076884 | 0.0077114 | 0.0077114 | 0.99943 | -0.0069998 | 0.9994 | -0.0067883 | 3.5052
47 | 0.081617 | 0.039509 | -0.081617 | -0.039529 | 2.0761e-07 | -2.0123e-05 | 0.0026191 | 0.0026194 | 0.0026194 | 0.99942 | -0.0069756 | 0.99942 | -0.0069924 | 1.2473
48 | 0.15652 | 0.074453 | -0.15652 | -0.075772 | 1.8583e-06 | -0.0013195 | 0.0050064 | 0.0050229 | 0.0050229 | 0.9994 | -0.0067883 | 0.99939 | -0.0066869 | 2.2831
49 | 0.08442 | 0.040533 | -0.08442 | -0.040887 | 1.4494e-07 | -0.00035321 | 0.002705 | 0.0027094 | 0.0027094 | 0.9994 | -0.0067883 | 0.9994 | -0.0067735 | 1.2315
50 | 0.082748 | 0.039796 | -0.082745 | -0.040075 | 3.0006e-06 | -0.0002789 | 0.0026623 | 0.0026659 | 0.0026659 | 0.99561 | -0.0047627 | 0.99557 | -0.0050049 | 1.2695
51 | -1.3009 | -0.60105 | 1.3012 | 0.60114 | 0.00034522 | 8.3385e-05 | 0.04155 | 0.041549 | 0.04155 | 0.99561 | -0.0047627 | 0.99589 | -0.0027035 | 19.7859
52 | 0.15652 | 0.075772 | -0.15651 | -0.075803 | 1.2029e-06 | -3.115e-05 | 0.0050229 | 0.0050233 | 0.0050233 | 0.99939 | -0.0066869 | 0.99938 | -0.0067377 | 2.3921
53 | -0.11576 | -0.056067 | 0.11576 | 0.054957 | 8.6499e-07 | -0.0011093 | 0.003727 | 0.0037131 | 0.003727 | 0.99627 | -0.0043403 | 0.99628 | -0.004404 | 1.6941
54 | -0.11576 | -0.054957 | 0.11577 | 0.049096 | 4.4658e-06 | -0.005861 | 0.0037131 | 0.0036435 | 0.0037131 | 0.99628 | -0.004404 | 0.99632 | -0.004685 | 1.6878
55 | 0.15621 | 0.073702 | -0.15621 | -0.073823 | 4.6873e-06 | -0.0001215 | 0.0050045 | 0.0050061 | 0.0050061 | 0.99632 | -0.004685 | 0.99628 | -0.0049017 | 2.3838
56 | 0.15621 | 0.073823 | -0.15614 | -0.07562 | 6.9704e-05 | -0.0017969 | 0.0050061 | 0.0050291 | 0.0050291 | 0.99628 | -0.0049017 | 0.99581 | -0.0079795 | 2.3948
57 | 0.11004 | 0.052615 | -0.11004 | -0.053293 | 4.8545e-07 | -0.00067874 | 0.0035463 | 0.0035549 | 0.0035549 | 0.99285 | -0.013076 | 0.99285 | -0.013038 | 1.6158
58 | -0.11004 | -0.052615 | 0.11004 | 0.05224 | 7.205e-06 | -0.00037442 | 0.0035463 | 0.0035416 | 0.0035463 | 0.99285 | -0.013076 | 0.99292 | -0.012617 | 1.6887
59 | -0.26995 | -0.12948 | 0.26996 | 0.12536 | 1.7618e-05 | -0.0041195 | 0.0087044 | 0.0086532 | 0.0087044 | 0.99292 | -0.012617 | 0.99298 | -0.013154 | 3.9565
60 | 0.1599 | 0.077242 | -0.15989 | -0.07744 | 8.1791e-06 | -0.00019746 | 0.0051629 | 0.0051654 | 0.0051654 | 0.99292 | -0.012617 | 0.99287 | -0.012956 | 2.4597
61 | 0.14348 | 0.064455 | -0.14348 | -0.064516 | 1.938e-06 | -6.1299e-05 | 0.004549 | 0.0045497 | 0.0045497 | 0.99817 | -0.011109 | 0.99815 | -0.011223 | 2.1665
62 | 0.14348 | 0.064516 | -0.14347 | -0.069346 | 5.685e-06 | -0.0048299 | 0.0045497 | 0.0046088 | 0.0046088 | 0.99815 | -0.011223 | 0.99812 | -0.010906 | 2.0949
63 | -0.43104 | -0.2031 | 0.43105 | 0.20271 | 4.2518e-06 | -0.00038961 | 0.013852 | 0.013848 | 0.013852 | 0.99298 | -0.013188 | 0.99299 | -0.013268 | 6.2966
64 | 0.26996 | 0.12509 | -0.26996 | -0.12536 | 1.1669e-06 | -0.00027458 | 0.0086498 | 0.0086532 | 0.0086532 | 0.99298 | -0.013188 | 0.99298 | -0.013154 | 3.9333
65 | -0.43105 | -0.20271 | 0.43111 | 0.19663 | 6.5979e-05 | -0.0060821 | 0.013848 | 0.013773 | 0.013848 | 0.99299 | -0.013268 | 0.99314 | -0.014471 | 6.2944
66 | 0.11826 | 0.054684 | -0.11826 | -0.057274 | 2.124e-06 | -0.0025898 | 0.0037872 | 0.0038194 | 0.0038194 | 0.99314 | -0.014471 | 0.99312 | -0.014322 | 1.7361
67 | -0.14347 | -0.069487 | 0.14347 | 0.069346 | 1.6754e-07 | -0.00014043 | 0.0046106 | 0.0046088 | 0.0046106 | 0.99812 | -0.010896 | 0.99812 | -0.010906 | 2.0957

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 4.1396 | 1.91

## res_load
| p_mw | q_mvar
0 | 0.13806 | 0.066864
1 | 0.094185 | 0.045616
2 | 0.11202 | 0.054254
3 | 0.10575 | 0.051219
4 | 0.10294 | 0.049856
5 | 0.084446 | 0.040899
6 | 0.1384 | 0.067033
7 | 0.11273 | 0.054599
8 | 0.12288 | 0.059515
9 | 0.14183 | 0.068693
10 | 0.12474 | 0.060412
11 | 0.15803 | 0.076536
12 | 0.14222 | 0.068878
13 | 0.15603 | 0.07557
14 | 0.12467 | 0.060382
15 | 0.10798 | 0.052298
16 | 0.10584 | 0.051262
17 | 0.064598 | 0.031286
18 | 0.14985 | 0.072574
19 | 0.14978 | 0.072544
20 | 0.092177 | 0.044643
21 | 0.082745 | 0.040075
22 | 0.1205 | 0.05836
23 | 0.081617 | 0.039529
24 | 0.08442 | 0.040887
25 | 0.15651 | 0.075803
26 | 0.11576 | 0.056067
27 | 0.15614 | 0.07562
28 | 0.11004 | 0.053293
29 | 0.09249 | 0.044795
30 | 0.16108 | 0.078014
31 | 0.14347 | 0.069487
32 | 0.15989 | 0.07744
33 | 0.11826 | 0.057274

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1