## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_201_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_201_0_node_161 | 20 | n |  | TRUE
2 | bus_MV_201_0_node_28 | 20 | n |  | TRUE
3 | bus_MV_201_0_node_160 | 20 | n |  | TRUE
4 | bus_MV_201_0_node_141 | 20 | n |  | TRUE
5 | bus_MV_201_0_node_1 | 20 | n |  | TRUE
6 | bus_MV_201_0_node_2 | 20 | n |  | TRUE
7 | bus_MV_201_0_node_3 | 20 | n |  | TRUE
8 | bus_MV_201_0_node_11 | 20 | n |  | TRUE
9 | bus_MV_201_0_node_4 | 20 | n |  | TRUE
10 | bus_MV_201_0_node_5 | 20 | n |  | TRUE
11 | bus_MV_201_0_node_42 | 20 | n |  | TRUE
12 | bus_MV_201_0_node_158 | 20 | n |  | TRUE
13 | bus_MV_201_0_node_36 | 20 | n |  | TRUE
14 | bus_MV_201_0_node_6 | 20 | n |  | TRUE
15 | bus_MV_201_0_node_9 | 20 | n |  | TRUE
16 | bus_MV_201_0_node_7 | 20 | n |  | TRUE
17 | bus_MV_201_0_node_10 | 20 | n |  | TRUE
18 | bus_MV_201_0_node_8 | 20 | n |  | TRUE
19 | bus_MV_201_0_node_149 | 20 | n |  | TRUE
20 | bus_MV_201_0_node_150 | 20 | n |  | TRUE
21 | bus_MV_201_0_node_148 | 20 | n |  | TRUE
22 | bus_MV_201_0_node_159 | 20 | n |  | TRUE
23 | bus_MV_201_0_node_16 | 20 | n |  | TRUE
24 | bus_MV_201_0_node_12 | 20 | n |  | TRUE
25 | bus_MV_201_0_node_13 | 20 | n |  | TRUE
26 | bus_MV_201_0_node_14 | 20 | n |  | TRUE
27 | bus_MV_201_0_node_15 | 20 | n |  | TRUE
28 | bus_MV_201_0_node_157 | 20 | n |  | TRUE
29 | bus_MV_201_0_node_17 | 20 | n |  | TRUE
30 | bus_MV_201_0_node_18 | 20 | n |  | TRUE
31 | bus_MV_201_0_node_19 | 20 | n |  | TRUE
32 | bus_MV_201_0_node_20 | 20 | n |  | TRUE
33 | bus_MV_201_0_node_30 | 20 | n |  | TRUE
34 | bus_MV_201_0_node_31 | 20 | n |  | TRUE
35 | bus_MV_201_0_node_21 | 20 | n |  | TRUE
36 | bus_MV_201_0_node_151 | 20 | n |  | TRUE
37 | bus_MV_201_0_node_162 | 20 | n |  | TRUE
38 | bus_MV_201_0_node_48 | 20 | n |  | TRUE
39 | bus_MV_201_0_node_24 | 20 | n |  | TRUE
40 | bus_MV_201_0_node_22 | 20 | n |  | TRUE
41 | bus_MV_201_0_node_23 | 20 | n |  | TRUE
42 | bus_MV_201_0_node_25 | 20 | n |  | TRUE
43 | bus_MV_201_0_node_26 | 20 | n |  | TRUE
44 | bus_MV_201_0_node_27 | 20 | n |  | TRUE
45 | bus_MV_201_0_node_29 | 20 | n |  | TRUE
46 | bus_MV_201_0_node_140 | 20 | n |  | TRUE
47 | bus_MV_201_0_node_165 | 20 | n |  | TRUE
48 | bus_MV_201_0_node_41 | 20 | n |  | TRUE
49 | bus_MV_201_0_node_35 | 20 | n |  | TRUE
50 | bus_MV_201_0_node_33 | 20 | n |  | TRUE
51 | bus_MV_201_0_node_144 | 20 | n |  | TRUE
52 | bus_MV_201_0_node_34 | 20 | n |  | TRUE
53 | bus_MV_201_0_node_32 | 20 | n |  | TRUE
54 | bus_MV_201_0_node_143 | 20 | n |  | TRUE
55 | bus_MV_201_0_node_152 | 20 | n |  | TRUE
56 | bus_MV_201_0_node_142 | 20 | n |  | TRUE
57 | bus_MV_201_0_node_37 | 20 | n |  | TRUE
58 | bus_MV_201_0_node_38 | 20 | n |  | TRUE
59 | bus_MV_201_0_node_39 | 20 | n |  | TRUE
60 | bus_MV_201_0_node_40 | 20 | n |  | TRUE
61 | bus_MV_201_0_node_137 | 20 | n |  | TRUE
62 | bus_MV_201_0_node_145 | 20 | n |  | TRUE
63 | bus_MV_201_0_node_146 | 20 | n |  | TRUE
64 | bus_MV_201_0_node_147 | 20 | n |  | TRUE
65 | bus_MV_201_0_node_43 | 20 | n |  | TRUE
66 | bus_MV_201_0_node_44 | 20 | n |  | TRUE
67 | bus_MV_201_0_node_66 | 20 | n |  | TRUE
68 | bus_MV_201_0_node_45 | 20 | n |  | TRUE
69 | bus_MV_201_0_node_67 | 20 | n |  | TRUE
70 | bus_MV_201_0_node_65 | 20 | n |  | TRUE
71 | bus_MV_201_0_node_63 | 20 | n |  | TRUE
72 | bus_MV_201_0_node_64 | 20 | n |  | TRUE
73 | bus_MV_201_0_node_60 | 20 | n |  | TRUE
74 | bus_MV_201_0_node_130 | 20 | n |  | TRUE
75 | bus_MV_201_0_node_132 | 20 | n |  | TRUE
76 | bus_MV_201_0_node_129 | 20 | n |  | TRUE
77 | bus_MV_201_0_node_46 | 20 | n |  | TRUE
78 | bus_MV_201_0_node_47 | 20 | n |  | TRUE
79 | bus_MV_201_0_node_90 | 20 | n |  | TRUE
80 | bus_MV_201_0_node_91 | 20 | n |  | TRUE
81 | bus_MV_201_0_node_49 | 20 | n |  | TRUE
82 | bus_MV_201_0_node_50 | 20 | n |  | TRUE
83 | bus_MV_201_0_node_51 | 20 | n |  | TRUE
84 | bus_MV_201_0_node_84 | 20 | n |  | TRUE
85 | bus_MV_201_0_node_68 | 20 | n |  | TRUE
86 | bus_MV_201_0_node_119 | 20 | n |  | TRUE
87 | bus_MV_201_0_node_156 | 20 | n |  | TRUE
88 | bus_MV_201_0_node_56 | 20 | n |  | TRUE
89 | bus_MV_201_0_node_118 | 20 | n |  | TRUE
90 | bus_MV_201_0_node_85 | 20 | n |  | TRUE
91 | bus_MV_201_0_node_61 | 20 | n |  | TRUE
92 | bus_MV_201_0_node_78 | 20 | n |  | TRUE
93 | bus_MV_201_0_node_59 | 20 | n |  | TRUE
94 | bus_MV_201_0_node_52 | 20 | n |  | TRUE
95 | bus_MV_201_0_node_54 | 20 | n |  | TRUE
96 | bus_MV_201_0_node_53 | 20 | n |  | TRUE
97 | bus_MV_201_0_node_55 | 20 | n |  | TRUE
98 | bus_MV_201_0_node_75 | 20 | n |  | TRUE
99 | bus_MV_201_0_node_155 | 20 | n |  | TRUE
100 | bus_MV_201_0_node_74 | 20 | n |  | TRUE
101 | bus_MV_201_0_node_76 | 20 | n |  | TRUE
102 | bus_MV_201_0_node_57 | 20 | n |  | TRUE
103 | bus_MV_201_0_node_58 | 20 | n |  | TRUE
104 | bus_MV_201_0_node_62 | 20 | n |  | TRUE
105 | bus_MV_201_0_node_92 | 20 | n |  | TRUE
106 | bus_MV_201_0_node_93 | 20 | n |  | TRUE
107 | bus_MV_201_0_node_69 | 20 | n |  | TRUE
108 | bus_MV_201_0_node_71 | 20 | n |  | TRUE
109 | bus_MV_201_0_node_70 | 20 | n |  | TRUE
110 | bus_MV_201_0_node_73 | 20 | n |  | TRUE
111 | bus_MV_201_0_node_72 | 20 | n |  | TRUE
112 | bus_MV_201_0_node_125 | 20 | n |  | TRUE
113 | bus_MV_201_0_node_112 | 20 | n |  | TRUE
114 | bus_MV_201_0_node_133 | 20 | n |  | TRUE
115 | bus_MV_201_0_node_136 | 20 | n |  | TRUE
116 | bus_MV_201_0_node_135 | 20 | n |  | TRUE
117 | bus_MV_201_0_node_134 | 20 | n |  | TRUE
118 | bus_MV_201_0_node_124 | 20 | n |  | TRUE
119 | bus_MV_201_0_node_164 | 20 | n |  | TRUE
120 | bus_MV_201_0_node_77 | 20 | n |  | TRUE
121 | bus_MV_201_0_node_87 | 20 | n |  | TRUE
122 | bus_MV_201_0_node_86 | 20 | n |  | TRUE
123 | bus_MV_201_0_node_88 | 20 | n |  | TRUE
124 | bus_MV_201_0_node_89 | 20 | n |  | TRUE
125 | bus_MV_201_0_node_79 | 20 | n |  | TRUE
126 | bus_MV_201_0_node_81 | 20 | n |  | TRUE
127 | bus_MV_201_0_node_83 | 20 | n |  | TRUE
128 | bus_MV_201_0_node_102 | 20 | n |  | TRUE
129 | bus_MV_201_0_node_106 | 20 | n |  | TRUE
130 | bus_MV_201_0_node_97 | 20 | n |  | TRUE
131 | bus_MV_201_0_node_103 | 20 | n |  | TRUE
132 | bus_MV_201_0_node_94 | 20 | n |  | TRUE
133 | bus_MV_201_0_node_95 | 20 | n |  | TRUE
134 | bus_MV_201_0_node_163 | 20 | n |  | TRUE
135 | bus_MV_201_0_node_128 | 20 | n |  | TRUE
136 | bus_MV_201_0_node_123 | 20 | n |  | TRUE
137 | bus_MV_201_0_node_111 | 20 | n |  | TRUE
138 | bus_MV_201_0_node_121 | 20 | n |  | TRUE
139 | bus_MV_201_0_node_120 | 20 | n |  | TRUE
140 | bus_MV_201_0_node_98 | 20 | n |  | TRUE
141 | bus_MV_201_0_node_99 | 20 | n |  | TRUE
142 | bus_MV_201_0_node_100 | 20 | n |  | TRUE
143 | bus_MV_201_0_node_101 | 20 | n |  | TRUE
144 | bus_MV_201_0_node_104 | 20 | n |  | TRUE
145 | bus_MV_201_0_node_105 | 20 | n |  | TRUE
146 | bus_MV_201_0_node_126 | 20 | n |  | TRUE
147 | bus_MV_201_0_node_110 | 20 | n |  | TRUE
148 | bus_MV_201_0_node_109 | 20 | n |  | TRUE
149 | bus_MV_201_0_node_127 | 20 | n |  | TRUE
150 | bus_MV_201_0_node_116 | 20 | n |  | TRUE
151 | bus_MV_201_0_node_114 | 20 | n |  | TRUE
152 | bus_MV_201_0_node_115 | 20 | n |  | TRUE
153 | bus_MV_201_0_node_108 | 20 | n |  | TRUE
154 | bus_MV_201_0_node_113 | 20 | n |  | TRUE
155 | bus_MV_201_0_node_107 | 20 | n |  | TRUE
156 | bus_MV_201_0_node_117 | 20 | n |  | TRUE
157 | bus_MV_201_0_node_122 | 20 | n |  | TRUE
158 | bus_MV_201_0_node_138 | 20 | n |  | TRUE
159 | bus_MV_201_0_node_139 | 20 | n |  | TRUE
160 | bus_HV_201_0_node_46 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_201_0_load_0 | 0 | 0.083052 | 0.040224 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_201_0_load_161 | 1 | 0.13207 | 0.063967 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_201_0_load_160 | 3 | 0.10494 | 0.050824 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_201_0_load_1 | 5 | 0.12697 | 0.061493 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_201_0_load_2 | 6 | 0.11312 | 0.054786 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_201_0_load_11 | 8 | 0.087578 | 0.042416 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_201_0_load_42 | 11 | 0.12728 | 0.061646 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_201_0_load_6 | 14 | 0.12724 | 0.061627 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_201_0_load_9 | 15 | 0.11828 | 0.057287 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_201_0_load_149 | 19 | 0.15772 | 0.076389 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_201_0_load_150 | 20 | 0.15936 | 0.07718 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_201_0_load_148 | 21 | 0.1479 | 0.071632 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_201_0_load_159 | 22 | 0.09793 | 0.04743 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_201_0_load_12 | 24 | 0.092304 | 0.044705 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_201_0_load_157 | 28 | 0.13334 | 0.064577 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_201_0_load_17 | 29 | 0.11747 | 0.056892 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_201_0_load_30 | 33 | 0.12415 | 0.060128 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_201_0_load_151 | 36 | 0.12079 | 0.058502 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_201_0_load_162 | 37 | 0.14699 | 0.07119 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_201_0_load_22 | 40 | 0.05393 | 0.02612 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_201_0_load_25 | 42 | 0.09942 | 0.048151 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_201_0_load_165 | 47 | 0.15489 | 0.075015 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_201_0_load_41 | 48 | 0.14602 | 0.070719 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_201_0_load_33 | 50 | 0.10486 | 0.050784 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_201_0_load_144 | 51 | 0.10445 | 0.050585 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_201_0_load_152 | 55 | 0.15006 | 0.072677 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_201_0_load_142 | 56 | 0.12214 | 0.059155 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_201_0_load_37 | 57 | 0.14978 | 0.072543 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_201_0_load_137 | 61 | 0.11146 | 0.053981 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_201_0_load_145 | 62 | 0.14817 | 0.07176 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_201_0_load_43 | 65 | 0.065335 | 0.031643 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_201_0_load_66 | 67 | 0.13326 | 0.064539 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_201_0_load_64 | 72 | 0.10538 | 0.05104 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_201_0_load_129 | 76 | 0.13153 | 0.063703 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_201_0_load_46 | 77 | 0.098508 | 0.04771 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_201_0_load_90 | 79 | 0.11763 | 0.056973 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_201_0_load_49 | 81 | 0.10757 | 0.0521 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_201_0_load_84 | 84 | 0.10535 | 0.051025 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_201_0_load_156 | 87 | 0.15071 | 0.072994 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_201_0_load_85 | 90 | 0.1467 | 0.071052 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_201_0_load_52 | 94 | 0.14958 | 0.072443 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_201_0_load_75 | 98 | 0.14748 | 0.071428 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_201_0_load_155 | 99 | 0.16026 | 0.077618 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_201_0_load_74 | 100 | 0.080704 | 0.039087 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_201_0_load_57 | 102 | 0.15916 | 0.077085 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_201_0_load_62 | 104 | 0.10021 | 0.048532 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_201_0_load_93 | 106 | 0.088319 | 0.042775 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_201_0_load_69 | 107 | 0.16353 | 0.079201 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_201_0_load_125 | 112 | 0.069892 | 0.03385 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_201_0_load_133 | 114 | 0.11788 | 0.057091 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_201_0_load_135 | 116 | 0.12067 | 0.058442 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_201_0_load_164 | 119 | 0.12976 | 0.062845 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_201_0_load_87 | 121 | 0.1248 | 0.060444 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_201_0_load_88 | 123 | 0.092882 | 0.044985 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_201_0_load_89 | 124 | 0.078579 | 0.038058 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_201_0_load_79 | 125 | 0.10164 | 0.049227 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_201_0_load_102 | 128 | 0.13388 | 0.06484 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_201_0_load_106 | 129 | 0.12119 | 0.058696 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_201_0_load_97 | 130 | 0.081084 | 0.039271 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_201_0_load_94 | 132 | 0.10997 | 0.053259 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_201_0_load_163 | 134 | 0.15908 | 0.077044 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_201_0_load_128 | 135 | 0.13929 | 0.067463 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_201_0_load_120 | 139 | 0.15173 | 0.073486 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_201_0_load_98 | 140 | 0.057505 | 0.027851 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_201_0_load_126 | 146 | 0.14836 | 0.071853 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_201_0_load_109 | 148 | 0.13958 | 0.067599 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_201_0_load_127 | 149 | 0.076971 | 0.037279 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_201_0_load_116 | 150 | 0.16146 | 0.0782 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_201_0_load_113 | 154 | 0.11102 | 0.053768 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_201_0_load_107 | 155 | 0.13369 | 0.064747 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_201_0_load_117 | 156 | 0.13314 | 0.064481 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_201_0_load_138 | 158 | 0.15261 | 0.073913 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 77 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_201_0_line_0 |  | 0 | 1 | 0.16514 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_201_0_line_1 |  | 1 | 2 | 0.005066 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_201_0_line_2 |  | 2 | 43 | 0.37954 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_201_0_line_3 |  | 3 | 4 | 0.13437 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_201_0_line_4 |  | 4 | 46 | 0.19518 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
5 | MV_201_0_line_5 |  | 4 | 159 | 0.35508 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
6 | MV_201_0_line_6 |  | 5 | 6 | 0.044853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_201_0_line_7 |  | 5 | 7 | 0.049988 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_201_0_line_8 |  | 6 | 8 | 0.075703 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_201_0_line_9 |  | 7 | 9 | 0.039139 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
10 | MV_201_0_line_10 |  | 7 | 10 | 0.050804 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
11 | MV_201_0_line_11 |  | 9 | 14 | 0.02807 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
12 | MV_201_0_line_12 |  | 10 | 15 | 0.061034 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
13 | MV_201_0_line_13 |  | 11 | 12 | 2.227 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
14 | MV_201_0_line_14 |  | 11 | 13 | 0.063551 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
15 | MV_201_0_line_15 |  | 12 | 28 | 0.45512 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
16 | MV_201_0_line_16 |  | 13 | 52 | 0.2075 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
17 | MV_201_0_line_17 |  | 14 | 16 | 0.032616 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
18 | MV_201_0_line_18 |  | 15 | 17 | 0.080394 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
19 | MV_201_0_line_19 |  | 16 | 18 | 0.1684 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
20 | MV_201_0_line_20 |  | 17 | 22 | 0.020665 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
21 | MV_201_0_line_21 |  | 18 | 19 | 0.002403 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
22 | MV_201_0_line_22 |  | 19 | 20 | 0.12302 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
23 | MV_201_0_line_23 |  | 20 | 21 | 0.055545 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
24 | MV_201_0_line_24 |  | 21 | 61 | 4.3359 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
25 | MV_201_0_line_25 |  | 21 | 64 | 0.023183 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_201_0_line_26 |  | 22 | 23 | 0.02866 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
27 | MV_201_0_line_27 |  | 23 | 26 | 0.045994 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
28 | MV_201_0_line_28 |  | 24 | 25 | 0.020456 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
29 | MV_201_0_line_29 |  | 24 | 26 | 0.025602 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
30 | MV_201_0_line_30 |  | 25 | 27 | 0.037921 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
31 | MV_201_0_line_31 |  | 27 | 28 | 0.016924 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
32 | MV_201_0_line_32 |  | 29 | 30 | 0.016626 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_201_0_line_33 |  | 30 | 31 | 0.012112 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
34 | MV_201_0_line_34 |  | 30 | 32 | 0.073888 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
35 | MV_201_0_line_35 |  | 31 | 33 | 0.039518 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
36 | MV_201_0_line_36 |  | 32 | 35 | 0.066659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_201_0_line_37 |  | 32 | 36 | 0.034623 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
38 | MV_201_0_line_38 |  | 33 | 34 | 0.016077 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
39 | MV_201_0_line_39 |  | 34 | 53 | 0.059685 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
40 | MV_201_0_line_40 |  | 35 | 37 | 0.00776 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_201_0_line_41 |  | 36 | 38 | 2.129 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
42 | MV_201_0_line_42 |  | 37 | 39 | 0.014603 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_201_0_line_43 |  | 38 | 79 | 0.013583 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_201_0_line_44 |  | 38 | 78 | 0.62331 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
45 | MV_201_0_line_45 |  | 39 | 41 | 0.07721 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_201_0_line_46 |  | 40 | 41 | 0.0083948 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_201_0_line_47 |  | 42 | 43 | 0.006769 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_201_0_line_48 |  | 42 | 44 | 0.010074 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_201_0_line_49 |  | 44 | 45 | 0.077167 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_201_0_line_50 |  | 45 | 49 | 0.084646 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
51 | MV_201_0_line_51 |  | 45 | 50 | 0.038457 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
52 | MV_201_0_line_52 |  | 46 | 47 | 0.06827 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_201_0_line_53 |  | 46 | 48 | 1.0428 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
54 | MV_201_0_line_54 |  | 48 | 60 | 0.045523 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
55 | MV_201_0_line_55 |  | 49 | 51 | 0.047547 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
56 | MV_201_0_line_56 |  | 50 | 52 | 0.019883 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
57 | MV_201_0_line_57 |  | 51 | 59 | 0.01788 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
58 | MV_201_0_line_58 |  | 53 | 54 | 0.27781 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
59 | MV_201_0_line_59 |  | 53 | 55 | 0.11015 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
60 | MV_201_0_line_60 |  | 54 | 56 | 0.13946 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
61 | MV_201_0_line_61 |  | 56 | 159 | 0.070411 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
62 | MV_201_0_line_62 |  | 57 | 58 | 0.016863 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_201_0_line_63 |  | 58 | 59 | 0.058927 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
64 | MV_201_0_line_64 |  | 58 | 60 | 0.20778 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
65 | MV_201_0_line_65 |  | 62 | 63 | 0.11841 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_201_0_line_66 |  | 63 | 64 | 0.086606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_201_0_line_67 |  | 65 | 66 | 0.046341 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
68 | MV_201_0_line_68 |  | 65 | 67 | 0.16714 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
69 | MV_201_0_line_69 |  | 66 | 68 | 1.0498 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
70 | MV_201_0_line_70 |  | 67 | 69 | 0.027644 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_201_0_line_71 |  | 67 | 70 | 0.065919 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
72 | MV_201_0_line_72 |  | 68 | 77 | 0.055974 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
73 | MV_201_0_line_73 |  | 69 | 85 | 0.038187 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_201_0_line_74 |  | 70 | 72 | 0.063645 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
75 | MV_201_0_line_75 |  | 71 | 72 | 0.054397 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
76 | MV_201_0_line_76 |  | 71 | 73 | 0.089018 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
77 | MV_201_0_line_77 |  | 73 | 104 | 0.03513 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_201_0_line_78 |  | 73 | 103 | 0.10448 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
79 | MV_201_0_line_79 |  | 74 | 75 | 0.13475 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_201_0_line_80 |  | 74 | 76 | 0.11191 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
81 | MV_201_0_line_81 |  | 75 | 87 | 0.061949 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_201_0_line_82 |  | 77 | 78 | 0.12877 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
83 | MV_201_0_line_83 |  | 79 | 80 | 0.02604 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_201_0_line_84 |  | 80 | 105 | 0.041677 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_201_0_line_85 |  | 81 | 82 | 0.0125 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_201_0_line_86 |  | 82 | 83 | 0.034261 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_201_0_line_87 |  | 83 | 90 | 0.016362 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
88 | MV_201_0_line_88 |  | 83 | 91 | 0.050049 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
89 | MV_201_0_line_89 |  | 84 | 85 | 0.05618 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
90 | MV_201_0_line_90 |  | 86 | 87 | 0.006694 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_201_0_line_91 |  | 86 | 88 | 2.0861 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
92 | MV_201_0_line_92 |  | 86 | 89 | 0.15676 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
93 | MV_201_0_line_93 |  | 88 | 99 | 0.027428 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_201_0_line_94 |  | 88 | 95 | 0.009398 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
95 | MV_201_0_line_95 |  | 89 | 156 | 0.084588 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
96 | MV_201_0_line_96 |  | 90 | 92 | 0.013772 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
97 | MV_201_0_line_97 |  | 91 | 93 | 0.093595 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
98 | MV_201_0_line_98 |  | 92 | 122 | 0.076461 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_201_0_line_99 |  | 92 | 120 | 0.093734 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
100 | MV_201_0_line_100 |  | 93 | 102 | 0.008422 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
101 | MV_201_0_line_101 |  | 94 | 95 | 0.018057 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
102 | MV_201_0_line_102 |  | 94 | 96 | 0.04415 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
103 | MV_201_0_line_103 |  | 96 | 97 | 0.054543 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
104 | MV_201_0_line_104 |  | 97 | 98 | 0.042808 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
105 | MV_201_0_line_105 |  | 98 | 100 | 0.064149 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
106 | MV_201_0_line_106 |  | 100 | 101 | 0.007714 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
107 | MV_201_0_line_107 |  | 101 | 120 | 0.057383 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
108 | MV_201_0_line_108 |  | 102 | 103 | 0.08089 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
109 | MV_201_0_line_109 |  | 105 | 106 | 0.03194 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_201_0_line_110 |  | 107 | 108 | 0.037024 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_201_0_line_111 |  | 107 | 109 | 0.33368 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
112 | MV_201_0_line_112 |  | 108 | 110 | 0.089984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_201_0_line_113 |  | 109 | 111 | 1.0581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_201_0_line_114 |  | 110 | 115 | 0.92163 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_201_0_line_115 |  | 110 | 116 | 0.013551 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_201_0_line_116 |  | 111 | 114 | 0.078624 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_201_0_line_117 |  | 112 | 113 | 0.11301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_201_0_line_118 |  | 113 | 142 | 0.29089 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
119 | MV_201_0_line_119 |  | 114 | 117 | 0.14121 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
120 | MV_201_0_line_120 |  | 115 | 119 | 0.099182 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
121 | MV_201_0_line_121 |  | 117 | 118 | 0.48864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_201_0_line_122 |  | 118 | 158 | 0.028733 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_201_0_line_123 |  | 118 | 157 | 0.12346 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_201_0_line_124 |  | 120 | 121 | 0.057943 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_201_0_line_125 |  | 122 | 123 | 0.026944 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_201_0_line_126 |  | 122 | 124 | 0.073866 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
127 | MV_201_0_line_127 |  | 125 | 126 | 0.068486 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_201_0_line_128 |  | 126 | 127 | 0.047798 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_201_0_line_129 |  | 127 | 128 | 0.024406 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_201_0_line_130 |  | 127 | 129 | 0.065495 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
131 | MV_201_0_line_131 |  | 128 | 131 | 0.029625 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_201_0_line_132 |  | 129 | 130 | 0.082997 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
133 | MV_201_0_line_133 |  | 131 | 145 | 0.18606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_201_0_line_134 |  | 132 | 133 | 0.032978 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
135 | MV_201_0_line_135 |  | 132 | 134 | 0.95479 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
136 | MV_201_0_line_136 |  | 133 | 135 | 0.22144 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
137 | MV_201_0_line_137 |  | 134 | 137 | 0.035583 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
138 | MV_201_0_line_138 |  | 135 | 136 | 0.061052 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_201_0_line_139 |  | 136 | 138 | 0.24605 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_201_0_line_140 |  | 137 | 148 | 0.10857 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
141 | MV_201_0_line_141 |  | 138 | 139 | 0.030368 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_201_0_line_142 |  | 139 | 157 | 0.039208 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_201_0_line_143 |  | 140 | 141 | 0.034565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_201_0_line_144 |  | 141 | 142 | 0.11438 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
145 | MV_201_0_line_145 |  | 141 | 143 | 0.13201 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
146 | MV_201_0_line_146 |  | 142 | 147 | 0.12695 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
147 | MV_201_0_line_147 |  | 143 | 146 | 0.076732 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
148 | MV_201_0_line_148 |  | 144 | 145 | 0.30548 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
149 | MV_201_0_line_149 |  | 144 | 146 | 0.32536 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
150 | MV_201_0_line_150 |  | 145 | 150 | 0.007572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_201_0_line_151 |  | 145 | 151 | 0.045678 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
152 | MV_201_0_line_152 |  | 146 | 149 | 0.017629 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_201_0_line_153 |  | 147 | 148 | 0.063447 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
154 | MV_201_0_line_154 |  | 151 | 152 | 0.20222 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
155 | MV_201_0_line_155 |  | 151 | 153 | 0.081949 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
156 | MV_201_0_line_156 |  | 151 | 154 | 0.048323 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
157 | MV_201_0_line_157 |  | 152 | 156 | 0.015081 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
158 | MV_201_0_line_158 |  | 153 | 155 | 0.011754 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_201_0_trafo_46 | 25 MVA 110/20 kV | 160 | 77 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2668229.5788 | 1151619.649
1 | 2668077.3492 | 1151555.6366
2 | 2668074.2186 | 1151559.6256
3 | 2667262.5857 | 1150747.4097
4 | 2667131.24 | 1150777.3063
5 | 2670009.7934 | 1153919.0685
6 | 2670047.7119 | 1153895.111
7 | 2670037.3272 | 1153960.834
8 | 2670089.6781 | 1153832.1045
9 | 2670003.4164 | 1153980.5397
10 | 2670081.3044 | 1153935.1867
11 | 2668111.6787 | 1152135.4447
12 | 2669904.1381 | 1153457.0066
13 | 2668058.3573 | 1152100.6341
14 | 2669978.9943 | 1153994.4971
15 | 2670135.6944 | 1153907.4932
16 | 2669995.8866 | 1154022.3977
17 | 2670205.7212 | 1153869.2765
18 | 2669853.364 | 1154064.9337
19 | 2669851.256 | 1154066.0988
20 | 2669740.1133 | 1154013.3706
21 | 2669720.8586 | 1154065.4767
22 | 2670221.9217 | 1153856.4471
23 | 2670245.5569 | 1153840.9807
24 | 2670296.6552 | 1153810.1484
25 | 2670280.9108 | 1153797.0352
26 | 2670290.254 | 1153834.6652
27 | 2670250.2741 | 1153774.6876
28 | 2670236.5566 | 1153764.7221
29 | 2666398.6222 | 1150924.0384
30 | 2666415.0729 | 1150926.7545
31 | 2666427.1228 | 1150928.2881
32 | 2666364.1068 | 1150958.4994
33 | 2666466.5121 | 1150931.4796
34 | 2666482.3554 | 1150934.2781
35 | 2666371.5586 | 1150995.5796
36 | 2666329.6127 | 1150955.518
37 | 2666376.5825 | 1151001.5048
38 | 2664579.3065 | 1149743.4273
39 | 2666365.5158 | 1151011.066
40 | 2666427.6482 | 1151032.7541
41 | 2666420.0384 | 1151034.7462
42 | 2668098.4133 | 1151820.8099
43 | 2668103.4002 | 1151816.2192
44 | 2668091.6894 | 1151828.3269
45 | 2668024.262 | 1151862.5177
46 | 2667117.812 | 1150882.9037
47 | 2667060.8049 | 1150920.4676
48 | 2667819.9396 | 1151653.8885
49 | 2667959.5459 | 1151836.7399
50 | 2668022.3853 | 1151900.9288
51 | 2667977.9541 | 1151792.9011
52 | 2668042.3182 | 1151901.5097
53 | 2666532.05 | 1150967
54 | 2666688.2422 | 1150737.5223
55 | 2666612.3679 | 1151042.373
56 | 2666804.2177 | 1150814.9714
57 | 2667982.2227 | 1151725.4676
58 | 2667971.6894 | 1151738.6561
59 | 2667990.3189 | 1151779.9557
60 | 2667796.978 | 1151693.1963
61 | 2668350.7416 | 1158179.1794
62 | 2669539.0762 | 1153931.0452
63 | 2669634.765 | 1154000.7894
64 | 2669699.0329 | 1154058.0311
65 | 2663839.0421 | 1148875.2822
66 | 2663870.2696 | 1148902.2498
67 | 2663685.7112 | 1148808.7579
68 | 2664608.5161 | 1149444.4551
69 | 2663658.2218 | 1148812.3474
70 | 2663697.0024 | 1148745.2316
71 | 2663661.876 | 1148670.6868
72 | 2663638.4895 | 1148719.7999
73 | 2663582.22 | 1148631.6251
74 | 2662349.0117 | 1146650.599
75 | 2662230.0085 | 1146709.5798
76 | 2662422.4832 | 1146566.1911
77 | 2664652.1111 | 1149479.5638
78 | 2664669.8631 | 1149352.874
79 | 2664569.6337 | 1149734.0297
80 | 2664559.5474 | 1149710.1865
81 | 2663452.656 | 1148768.4345
82 | 2663440.1836 | 1148767.1693
83 | 2663406.6147 | 1148772.0077
84 | 2663568.1583 | 1148783.9151
85 | 2663622.0254 | 1148799.8697
86 | 2662175.4469 | 1146751.3619
87 | 2662180.8267 | 1146747.3596
88 | 2663195.9302 | 1148570.809
89 | 2662038.481 | 1146813.3295
90 | 2663391.4899 | 1148778.3521
91 | 2663390.2188 | 1148724.7208
92 | 2663378.4124 | 1148782.7837
93 | 2663395.9739 | 1148644.8046
94 | 2663210.1123 | 1148594.3371
95 | 2663200.7833 | 1148578.8642
96 | 2663232.5507 | 1148632.3596
97 | 2663246.5394 | 1148680.8771
98 | 2663211.2252 | 1148704.9421
99 | 2663222.6965 | 1148564.4862
100 | 2663257.9038 | 1148748.9443
101 | 2663263.4762 | 1148754.2946
102 | 2663399.143 | 1148637.0003
103 | 2663478.9005 | 1148623.5099
104 | 2663615.838 | 1148622.219
105 | 2664537.5983 | 1149691.4412
106 | 2664505.854 | 1149695.4815
107 | 2658735.6537 | 1143883.1108
108 | 2658699.9878 | 1143893.4026
109 | 2658953.9744 | 1144135.4521
110 | 2658648.8206 | 1143827.1365
111 | 2659517.9363 | 1144757.0759
112 | 2661109.3102 | 1145848.7921
113 | 2661141.9304 | 1145954.8129
114 | 2659507.0126 | 1144834.6764
115 | 2658649.3618 | 1144281.2395
116 | 2658658.2832 | 1143817.4121
117 | 2659498.3072 | 1144975.6215
118 | 2659804.9716 | 1145212.758
119 | 2658582.6096 | 1144354.597
120 | 2663288.6738 | 1148789.0668
121 | 2663291.2856 | 1148845.2691
122 | 2663381.8128 | 1148858.8385
123 | 2663384.1893 | 1148885.4891
124 | 2663455.4253 | 1148864.9494
125 | 2661652.1458 | 1147086.6713
126 | 2661637.425 | 1147021.7302
127 | 2661631.0062 | 1146975.662
128 | 2661654.8048 | 1146973.8821
129 | 2661581.782 | 1146932.4582
130 | 2661528.258 | 1146995.8906
131 | 2661658.6692 | 1146944.5169
132 | 2660143.8803 | 1145594.6983
133 | 2660111.6622 | 1145587.4289
134 | 2660889.4147 | 1146191.1972
135 | 2660158.374 | 1145370.9673
136 | 2660097.3951 | 1145365.4344
137 | 2660924.7986 | 1146186.5742
138 | 2659852.8719 | 1145340.1679
139 | 2659827.4276 | 1145350.8102
140 | 2661025.2391 | 1146339.316
141 | 2661057.6549 | 1146327.3265
142 | 2661021.2131 | 1146219.4664
143 | 2661146.5655 | 1146423.4232
144 | 2661513.6743 | 1146586.877
145 | 2661711.4759 | 1146787.7501
146 | 2661215.804 | 1146455.9784
147 | 2661062.965 | 1146099.5799
148 | 2660999.999 | 1146108.2587
149 | 2661221.3554 | 1146439.2459
150 | 2661717.5514 | 1146792.2925
151 | 2661749.3115 | 1146769.9833
152 | 2661944.0903 | 1146781.5311
153 | 2661799.7685 | 1146834.5571
154 | 2661756.6525 | 1146722.2216
155 | 2661809.12 | 1146841.7124
156 | 2661957.8448 | 1146787.7758
157 | 2659814.4318 | 1145316.3295
158 | 2659833.3668 | 1145208.3149
159 | 2666797.085 | 1150885.0197
160 | 2664652.1111 | 1149479.5638

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99015 | -0.46156 | 0.083052 | 0.040224
1 | 0.99018 | -0.46138 | 0.13207 | 0.063967
2 | 0.99018 | -0.4614 | 0 | 0
3 | 0.99265 | -0.34662 | 0.10494 | 0.050824
4 | 0.99267 | -0.34678 | 0 | 0
5 | 0.98727 | -0.61366 | 0.12697 | 0.061493
6 | 0.98726 | -0.61355 | 0.11312 | 0.054786
7 | 0.9873 | -0.61386 | 0 | 0
8 | 0.98725 | -0.61364 | 0.087578 | 0.042416
9 | 0.98728 | -0.61391 | 0 | 0
10 | 0.98731 | -0.61376 | 0 | 0
11 | 0.99011 | -0.46632 | 0.12728 | 0.061646
12 | 0.98774 | -0.60805 | 0 | 0
13 | 0.99015 | -0.46612 | 0 | 0
14 | 0.98728 | -0.61395 | 0.12724 | 0.061627
15 | 0.98736 | -0.61096 | 0.11828 | 0.057287
16 | 0.98726 | -0.61487 | 0 | 0
17 | 0.9874 | -0.61079 | 0 | 0
18 | 0.98722 | -0.61506 | 0 | 0
19 | 0.98722 | -0.61506 | 0.15772 | 0.076389
20 | 0.98717 | -0.61777 | 0.15936 | 0.07718
21 | 0.98716 | -0.61791 | 0.1479 | 0.071632
22 | 0.98742 | -0.60975 | 0.09793 | 0.04743
23 | 0.98743 | -0.60968 | 0 | 0
24 | 0.98746 | -0.60952 | 0.092304 | 0.044705
25 | 0.98747 | -0.60947 | 0 | 0
26 | 0.98745 | -0.60958 | 0 | 0
27 | 0.98749 | -0.60938 | 0 | 0
28 | 0.9875 | -0.60934 | 0.13334 | 0.064577
29 | 0.99382 | -0.31371 | 0.11747 | 0.056892
30 | 0.99382 | -0.31373 | 0 | 0
31 | 0.99381 | -0.31381 | 0 | 0
32 | 0.9939 | -0.31324 | 0 | 0
33 | 0.99373 | -0.31879 | 0.12415 | 0.060128
34 | 0.99371 | -0.3189 | 0 | 0
35 | 0.99388 | -0.31309 | 0 | 0
36 | 0.99398 | -0.30845 | 0.12079 | 0.058502
37 | 0.99388 | -0.31307 | 0.14699 | 0.07119
38 | 0.99906 | -0.0055553 | 0 | 0
39 | 0.99388 | -0.31307 | 0 | 0
40 | 0.99388 | -0.31302 | 0.05393 | 0.02612
41 | 0.99388 | -0.31302 | 0 | 0
42 | 0.99029 | -0.46229 | 0.09942 | 0.048151
43 | 0.99029 | -0.46228 | 0 | 0
44 | 0.99029 | -0.46232 | 0 | 0
45 | 0.99032 | -0.46257 | 0 | 0
46 | 0.99249 | -0.34778 | 0 | 0
47 | 0.99247 | -0.34791 | 0.15489 | 0.075015
48 | 0.99074 | -0.45255 | 0.14602 | 0.070719
49 | 0.99038 | -0.46222 | 0 | 0
50 | 0.99028 | -0.46536 | 0.10486 | 0.050784
51 | 0.99045 | -0.45817 | 0.10445 | 0.050585
52 | 0.99027 | -0.46543 | 0 | 0
53 | 0.99365 | -0.31927 | 0 | 0
54 | 0.99339 | -0.32092 | 0 | 0
55 | 0.99362 | -0.31947 | 0.15006 | 0.072677
56 | 0.99312 | -0.33702 | 0.12214 | 0.059155
57 | 0.9905 | -0.45781 | 0.14978 | 0.072543
58 | 0.99051 | -0.45784 | 0 | 0
59 | 0.99046 | -0.4581 | 0 | 0
60 | 0.99067 | -0.45688 | 0 | 0
61 | 0.98659 | -0.63277 | 0.11146 | 0.053981
62 | 0.9871 | -0.61794 | 0.14817 | 0.07176
63 | 0.98714 | -0.61772 | 0 | 0
64 | 0.98716 | -0.61787 | 0 | 0
65 | 0.99815 | -0.020245 | 0.065335 | 0.031643
66 | 0.99822 | -0.019847 | 0 | 0
67 | 0.99764 | -0.050504 | 0.13326 | 0.064539
68 | 0.99983 | -0.010312 | 0 | 0
69 | 0.99763 | -0.050472 | 0 | 0
70 | 0.99754 | -0.051045 | 0 | 0
71 | 0.9973 | -0.060705 | 0 | 0
72 | 0.99745 | -0.051564 | 0.10538 | 0.05104
73 | 0.99717 | -0.061414 | 0 | 0
74 | 0.99186 | -0.34433 | 0 | 0
75 | 0.99188 | -0.34453 | 0 | 0
76 | 0.99183 | -0.34451 | 0.13153 | 0.063703
77 | 1 | 0 | -8.6861 | -3.7235
78 | 0.99984 | -0.00098762 | 0 | 0
79 | 0.99906 | -0.005524 | 0.11763 | 0.056973
80 | 0.99905 | -0.0054999 | 0 | 0
81 | 0.99653 | -0.084119 | 0.10757 | 0.0521
82 | 0.99653 | -0.084135 | 0 | 0
83 | 0.99654 | -0.084178 | 0 | 0
84 | 0.99762 | -0.050497 | 0.10535 | 0.051025
85 | 0.99763 | -0.050425 | 0 | 0
86 | 0.99189 | -0.34463 | 0 | 0
87 | 0.99189 | -0.34461 | 0.15071 | 0.072994
88 | 0.99594 | -0.1005 | 0 | 0
89 | 0.99176 | -0.3455 | 0 | 0
90 | 0.99651 | -0.084297 | 0.1467 | 0.071052
91 | 0.99667 | -0.076266 | 0 | 0
92 | 0.9965 | -0.084395 | 0 | 0
93 | 0.99679 | -0.075565 | 0 | 0
94 | 0.99597 | -0.10034 | 0.14958 | 0.072443
95 | 0.99595 | -0.10044 | 0 | 0
96 | 0.99606 | -0.09467 | 0 | 0
97 | 0.99612 | -0.094329 | 0 | 0
98 | 0.99617 | -0.09406 | 0.14748 | 0.071428
99 | 0.99593 | -0.10045 | 0.16026 | 0.077618
100 | 0.99631 | -0.085465 | 0.080704 | 0.039087
101 | 0.99632 | -0.085414 | 0 | 0
102 | 0.9968 | -0.075501 | 0.15916 | 0.077085
103 | 0.99703 | -0.062224 | 0 | 0
104 | 0.99717 | -0.061373 | 0.10021 | 0.048532
105 | 0.99905 | -0.0054591 | 0 | 0
106 | 0.99905 | -0.0054261 | 0.088319 | 0.042775
107 | 0.98784 | -0.43984 | 0.16353 | 0.079201
108 | 0.98783 | -0.43978 | 0 | 0
109 | 0.98811 | -0.4374 | 0 | 0
110 | 0.9878 | -0.43964 | 0 | 0
111 | 0.98866 | -0.44017 | 0 | 0
112 | 0.99065 | -0.38058 | 0.069892 | 0.03385
113 | 0.99066 | -0.38067 | 0 | 0
114 | 0.9887 | -0.44031 | 0.11788 | 0.057091
115 | 0.98765 | -0.43883 | 0 | 0
116 | 0.9878 | -0.43962 | 0.12067 | 0.058442
117 | 0.98884 | -0.43874 | 0 | 0
118 | 0.98916 | -0.44009 | 0 | 0
119 | 0.98763 | -0.43899 | 0.12976 | 0.062845
120 | 0.99639 | -0.085036 | 0 | 0
121 | 0.99638 | -0.084951 | 0.1248 | 0.060444
122 | 0.99648 | -0.084245 | 0 | 0
123 | 0.99648 | -0.084216 | 0.092882 | 0.044985
124 | 0.99647 | -0.084316 | 0.078579 | 0.038058
125 | 0.99125 | -0.35458 | 0.10164 | 0.049227
126 | 0.99126 | -0.35467 | 0 | 0
127 | 0.99126 | -0.35472 | 0 | 0
128 | 0.99127 | -0.3548 | 0.13388 | 0.06484
129 | 0.99124 | -0.35488 | 0.12119 | 0.058696
130 | 0.99122 | -0.35497 | 0.081084 | 0.039271
131 | 0.99129 | -0.35495 | 0 | 0
132 | 0.9898 | -0.43396 | 0.10997 | 0.053259
133 | 0.98979 | -0.43403 | 0 | 0
134 | 0.99046 | -0.39288 | 0.15908 | 0.077044
135 | 0.98966 | -0.44262 | 0.13929 | 0.067463
136 | 0.98959 | -0.4423 | 0 | 0
137 | 0.99048 | -0.39279 | 0 | 0
138 | 0.98933 | -0.44093 | 0 | 0
139 | 0.9893 | -0.44075 | 0.15173 | 0.073486
140 | 0.99075 | -0.37997 | 0.057505 | 0.027851
141 | 0.99076 | -0.37999 | 0 | 0
142 | 0.9907 | -0.38035 | 0 | 0
143 | 0.99082 | -0.37956 | 0 | 0
144 | 0.99122 | -0.35704 | 0 | 0
145 | 0.99139 | -0.35587 | 0 | 0
146 | 0.99086 | -0.3793 | 0.14836 | 0.071853
147 | 0.99059 | -0.38727 | 0 | 0
148 | 0.99056 | -0.38745 | 0.13958 | 0.067599
149 | 0.99086 | -0.37928 | 0.076971 | 0.037279
150 | 0.99139 | -0.35585 | 0.16146 | 0.0782
151 | 0.99143 | -0.35565 | 0 | 0
152 | 0.99159 | -0.35459 | 0 | 0
153 | 0.9914 | -0.35579 | 0 | 0
154 | 0.99142 | -0.35571 | 0.11102 | 0.053768
155 | 0.9914 | -0.35577 | 0.13369 | 0.064747
156 | 0.99161 | -0.35451 | 0.13314 | 0.064481
157 | 0.98927 | -0.44059 | 0 | 0
158 | 0.98916 | -0.44003 | 0.15261 | 0.073913
159 | 0.99299 | -0.34482 | 0 | 0
160 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.083052 | -0.040224 | 0.083054 | 0.040032 | 2.1278e-06 | -0.00019196 | 0.0026904 | 0.0026879 | 0.0026904 | 0.99015 | -0.46156 | 0.99018 | -0.46138 | 1.2811
1 | -0.21513 | -0.104 | 0.21513 | 0.10388 | 3.2814e-07 | -0.0001185 | 0.0069662 | 0.0069647 | 0.0069662 | 0.99018 | -0.46138 | 0.99018 | -0.4614 | 3.1665
2 | -0.21513 | -0.10388 | 0.21515 | 0.095002 | 2.4189e-05 | -0.0088786 | 0.0069647 | 0.0068561 | 0.0069647 | 0.99018 | -0.4614 | 0.99029 | -0.46228 | 3.1658
3 | -0.10494 | -0.050824 | 0.10494 | 0.047663 | 2.0386e-06 | -0.0031607 | 0.0033908 | 0.0033518 | 0.0033908 | 0.99265 | -0.34662 | 0.99267 | -0.34678 | 1.5413
4 | 2.7302 | 1.1903 | -2.7297 | -1.2021 | 0.00045318 | -0.011827 | 0.086614 | 0.086755 | 0.086755 | 0.99267 | -0.34678 | 0.99249 | -0.34778 | 13.5979
5 | -2.8351 | -1.238 | 2.836 | 1.2165 | 0.00088552 | -0.021493 | 0.089965 | 0.089711 | 0.089965 | 0.99267 | -0.34678 | 0.99299 | -0.34482 | 14.1011
6 | 0.2007 | 0.096072 | -0.2007 | -0.097115 | 2.5398e-06 | -0.0010431 | 0.0065061 | 0.0065194 | 0.0065194 | 0.98727 | -0.61366 | 0.98726 | -0.61355 | 2.9633
7 | -0.32767 | -0.15757 | 0.32768 | 0.1564 | 7.5318e-06 | -0.0011611 | 0.010631 | 0.010616 | 0.010631 | 0.98727 | -0.61366 | 0.9873 | -0.61386 | 4.8323
8 | 0.087579 | 0.042329 | -0.087578 | -0.042416 | 1.0916e-06 | -8.7402e-05 | 0.0028442 | 0.0028454 | 0.0028454 | 0.98726 | -0.61355 | 0.98725 | -0.61364 | 1.3549
9 | 0.85198 | 0.38807 | -0.85197 | -0.39047 | 9.0717e-06 | -0.002392 | 0.027373 | 0.027403 | 0.027403 | 0.9873 | -0.61386 | 0.98728 | -0.61391 | 4.2951
10 | -1.1797 | -0.54448 | 1.1797 | 0.54138 | 2.2632e-05 | -0.0030988 | 0.037989 | 0.037951 | 0.037989 | 0.9873 | -0.61386 | 0.98731 | -0.61376 | 5.9543
11 | 0.85197 | 0.39047 | -0.85196 | -0.39218 | 6.518e-06 | -0.0017154 | 0.027403 | 0.027424 | 0.027424 | 0.98728 | -0.61391 | 0.98728 | -0.61395 | 4.2984
12 | -1.1797 | -0.54138 | 1.1797 | 0.54138 | 3.1381e-05 | 2.1413e-06 | 0.037951 | 0.03795 | 0.037951 | 0.98731 | -0.61376 | 0.98736 | -0.61096 | 5.8838
13 | 1.6242 | 0.71484 | -1.6221 | -0.71212 | 0.0021297 | 0.0027165 | 0.051739 | 0.051775 | 0.051775 | 0.99011 | -0.46632 | 0.98774 | -0.60805 | 8.0271
14 | -1.7515 | -0.77648 | 1.7516 | 0.7726 | 6.1225e-05 | -0.0038801 | 0.05586 | 0.055814 | 0.05586 | 0.99011 | -0.46632 | 0.99015 | -0.46612 | 8.7555
15 | 1.6221 | 0.71212 | -1.6217 | -0.7398 | 0.00037939 | -0.027678 | 0.051775 | 0.052108 | 0.052108 | 0.98774 | -0.60805 | 0.9875 | -0.60934 | 8.1674
16 | -1.7516 | -0.7726 | 1.7518 | 0.75993 | 0.0001992 | -0.012671 | 0.055814 | 0.055665 | 0.055814 | 0.99015 | -0.46612 | 0.99027 | -0.46543 | 8.7483
17 | 0.72472 | 0.33056 | -0.72471 | -0.33058 | 6.3164e-06 | -2.6959e-05 | 0.023291 | 0.023291 | 0.023291 | 0.98728 | -0.61395 | 0.98726 | -0.61487 | 3.611
18 | -1.298 | -0.59867 | 1.298 | 0.59377 | 4.3324e-05 | -0.0049002 | 0.041791 | 0.041731 | 0.041791 | 0.98736 | -0.61096 | 0.9874 | -0.61079 | 6.5504
19 | 0.72471 | 0.33058 | -0.72468 | -0.34088 | 2.8381e-05 | -0.010297 | 0.023291 | 0.023418 | 0.023418 | 0.98726 | -0.61487 | 0.98722 | -0.61506 | 3.6705
20 | -1.298 | -0.59377 | 1.298 | 0.59378 | 1.2848e-05 | 6.698e-06 | 0.041731 | 0.041731 | 0.041731 | 0.9874 | -0.61079 | 0.98742 | -0.60975 | 6.47
21 | 0.72468 | 0.34088 | -0.72468 | -0.34103 | 4.072e-07 | -0.00014692 | 0.023418 | 0.02342 | 0.02342 | 0.98722 | -0.61506 | 0.98722 | -0.61506 | 3.6708
22 | 0.56696 | 0.26464 | -0.56694 | -0.26476 | 1.4702e-05 | -0.00012618 | 0.018296 | 0.018298 | 0.018298 | 0.98722 | -0.61506 | 0.98717 | -0.61777 | 2.8369
23 | 0.40759 | 0.18758 | -0.40758 | -0.18944 | 4.6265e-06 | -0.0018536 | 0.013121 | 0.013143 | 0.013143 | 0.98717 | -0.61777 | 0.98716 | -0.61791 | 3.6308
24 | 0.11151 | 0.048733 | -0.11146 | -0.053981 | 5.1312e-05 | -0.0052478 | 0.0035587 | 0.0036236 | 0.0036236 | 0.98716 | -0.61791 | 0.98659 | -0.63277 | 1.0353
25 | 0.14817 | 0.069072 | -0.14817 | -0.069611 | 7.0835e-07 | -0.00053918 | 0.0047807 | 0.0047874 | 0.0047874 | 0.98716 | -0.61791 | 0.98716 | -0.61787 | 2.1761
26 | -1.396 | -0.64121 | 1.396 | 0.63946 | 1.7854e-05 | -0.0017457 | 0.044911 | 0.04489 | 0.044911 | 0.98742 | -0.60975 | 0.98743 | -0.60968 | 7.0394
27 | -1.396 | -0.63946 | 1.396 | 0.63666 | 2.8617e-05 | -0.0028016 | 0.04489 | 0.044856 | 0.04489 | 0.98743 | -0.60968 | 0.98745 | -0.60958 | 7.036
28 | -1.4883 | -0.6798 | 1.4884 | 0.67856 | 1.4458e-05 | -0.0012451 | 0.047834 | 0.047819 | 0.047834 | 0.98746 | -0.60952 | 0.98747 | -0.60947 | 7.4975
29 | 1.396 | 0.6351 | -1.396 | -0.63666 | 1.591e-05 | -0.0015596 | 0.044837 | 0.044856 | 0.044856 | 0.98746 | -0.60952 | 0.98745 | -0.60958 | 7.0307
30 | -1.4884 | -0.67856 | 1.4884 | 0.67625 | 2.6778e-05 | -0.0023083 | 0.047819 | 0.047791 | 0.047819 | 0.98747 | -0.60947 | 0.98749 | -0.60938 | 7.4951
31 | -1.4884 | -0.67625 | 1.4884 | 0.67522 | 1.1941e-05 | -0.0010302 | 0.047791 | 0.047778 | 0.047791 | 0.98749 | -0.60938 | 0.9875 | -0.60934 | 7.4907
32 | -0.11747 | -0.056892 | 0.11747 | 0.0565 | 3.1861e-07 | -0.00039198 | 0.0037912 | 0.0037862 | 0.0037912 | 0.99382 | -0.31371 | 0.99382 | -0.31373 | 1.7233
33 | 3.2342 | 1.388 | -3.2341 | -1.3887 | 3.9116e-05 | -0.00072961 | 0.10223 | 0.10224 | 0.10224 | 0.99382 | -0.31373 | 0.99381 | -0.31381 | 16.0246
34 | -3.3516 | -1.4445 | 3.3519 | 1.44 | 0.00025646 | -0.0044413 | 0.10601 | 0.10596 | 0.10601 | 0.99382 | -0.31373 | 0.9939 | -0.31324 | 16.6162
35 | 3.2341 | 1.3887 | -3.234 | -1.3884 | 0.00014746 | 0.00034259 | 0.10224 | 0.10224 | 0.10224 | 0.99381 | -0.31381 | 0.99373 | -0.31879 | 15.8508
36 | 0.20092 | 0.093192 | -0.20092 | -0.094763 | 3.6936e-06 | -0.0015711 | 0.0064329 | 0.0064522 | 0.0064522 | 0.9939 | -0.31324 | 0.99388 | -0.31309 | 2.9328
37 | -3.5528 | -1.5332 | 3.553 | 1.5336 | 0.00015613 | 0.00037255 | 0.11239 | 0.11239 | 0.11239 | 0.9939 | -0.31324 | 0.99398 | -0.30845 | 17.4247
38 | 3.1098 | 1.3282 | -3.1098 | -1.3292 | 4.7945e-05 | -0.0009705 | 0.098235 | 0.098246 | 0.098246 | 0.99373 | -0.31879 | 0.99371 | -0.3189 | 15.3991
39 | 3.1098 | 1.3292 | -3.1096 | -1.3328 | 0.00017809 | -0.0036026 | 0.098246 | 0.098288 | 0.098288 | 0.99371 | -0.3189 | 0.99365 | -0.31927 | 15.4057
40 | 0.20092 | 0.094763 | -0.20092 | -0.094946 | 4.3143e-07 | -0.00018289 | 0.0064522 | 0.0064545 | 0.0064545 | 0.99388 | -0.31309 | 0.99388 | -0.31307 | 2.9339
41 | -3.6738 | -1.5921 | 3.684 | 1.6168 | 0.010274 | 0.024706 | 0.11628 | 0.11625 | 0.11628 | 0.99398 | -0.30845 | 0.99906 | -0.0055553 | 18.0283
42 | 0.053931 | 0.023756 | -0.053931 | -0.024101 | 5.7257e-08 | -0.00034439 | 0.0017117 | 0.0017157 | 0.0017157 | 0.99388 | -0.31307 | 0.99388 | -0.31307 | 0.77987
43 | 0.20596 | 0.09705 | -0.20595 | -0.097373 | 7.8525e-07 | -0.00032347 | 0.0065786 | 0.0065826 | 0.0065826 | 0.99906 | -0.0055553 | 0.99906 | -0.005524 | 2.9921
44 | -3.89 | -1.7139 | 3.8929 | 1.6764 | 0.0028949 | -0.03749 | 0.12283 | 0.12237 | 0.12283 | 0.99906 | -0.0055553 | 0.99984 | -0.00098762 | 19.2516
45 | 0.053931 | 0.024101 | -0.05393 | -0.025922 | 3.0731e-07 | -0.0018209 | 0.0017157 | 0.001738 | 0.001738 | 0.99388 | -0.31307 | 0.99388 | -0.31302 | 0.78999
46 | -0.05393 | -0.02612 | 0.05393 | 0.025922 | 3.3891e-08 | -0.00019798 | 0.0017405 | 0.001738 | 0.0017405 | 0.99388 | -0.31302 | 0.99388 | -0.31302 | 0.79112
47 | 0.21515 | 0.094843 | -0.21515 | -0.095002 | 4.2465e-07 | -0.00015837 | 0.0068542 | 0.0068561 | 0.0068561 | 0.99029 | -0.46229 | 0.99029 | -0.46228 | 3.1164
48 | -0.31457 | -0.14299 | 0.31458 | 0.14276 | 1.3642e-06 | -0.00023548 | 0.010073 | 0.01007 | 0.010073 | 0.99029 | -0.46229 | 0.99029 | -0.46232 | 4.5786
49 | -0.31458 | -0.14276 | 0.31459 | 0.14096 | 1.0424e-05 | -0.0018038 | 0.01007 | 0.010048 | 0.01007 | 0.99029 | -0.46232 | 0.99032 | -0.46257 | 4.5773
50 | -2.1713 | -0.95053 | 2.1714 | 0.94539 | 0.00012475 | -0.0051461 | 0.069091 | 0.069031 | 0.069091 | 0.99032 | -0.46257 | 0.99038 | -0.46222 | 10.8294
51 | 1.8567 | 0.80958 | -1.8567 | -0.8095 | 4.7862e-05 | 7.6571e-05 | 0.059043 | 0.059044 | 0.059044 | 0.99032 | -0.46257 | 0.99028 | -0.46536 | 9.1541
52 | 0.15489 | 0.074936 | -0.15489 | -0.075015 | 3.0472e-06 | -7.8372e-05 | 0.0050046 | 0.0050057 | 0.0050057 | 0.99249 | -0.34778 | 0.99247 | -0.34791 | 2.3836
53 | 2.5748 | 1.1272 | -2.5723 | -1.1219 | 0.0024886 | 0.0052748 | 0.081753 | 0.08177 | 0.08177 | 0.99249 | -0.34778 | 0.99074 | -0.45255 | 12.6775
54 | 2.4263 | 1.0512 | -2.4262 | -1.051 | 9.6474e-05 | 0.00019766 | 0.077047 | 0.077047 | 0.077047 | 0.99074 | -0.45255 | 0.99067 | -0.45688 | 11.9453
55 | -2.1714 | -0.94539 | 2.1715 | 0.94554 | 8.0885e-05 | 0.00015304 | 0.069031 | 0.06903 | 0.069031 | 0.99038 | -0.46222 | 0.99045 | -0.45817 | 10.7024
56 | 1.7518 | 0.75872 | -1.7518 | -0.75993 | 1.9032e-05 | -0.0012144 | 0.055651 | 0.055665 | 0.055665 | 0.99028 | -0.46536 | 0.99027 | -0.46543 | 8.7249
57 | -2.2759 | -0.99612 | 2.276 | 0.99504 | 2.8963e-05 | -0.0010858 | 0.07241 | 0.072397 | 0.07241 | 0.99045 | -0.45817 | 0.99046 | -0.4581 | 11.3495
58 | 2.9595 | 1.2603 | -2.9588 | -1.2771 | 0.00075125 | -0.016806 | 0.093451 | 0.093649 | 0.093649 | 0.99365 | -0.31927 | 0.99339 | -0.32092 | 14.6784
59 | 0.15006 | 0.07255 | -0.15006 | -0.072677 | 4.6034e-06 | -0.00012694 | 0.0048424 | 0.0048441 | 0.0048441 | 0.99365 | -0.31927 | 0.99362 | -0.31947 | 2.3067
60 | 2.9588 | 1.2771 | -2.9583 | -1.2761 | 0.00043664 | 0.00098398 | 0.093649 | 0.093651 | 0.093651 | 0.99339 | -0.32092 | 0.99312 | -0.33702 | 14.5195
61 | 2.8362 | 1.2169 | -2.836 | -1.2165 | 0.0002023 | 0.00044801 | 0.08971 | 0.089711 | 0.089711 | 0.99312 | -0.33702 | 0.99299 | -0.34482 | 13.9087
62 | -0.14978 | -0.072543 | 0.14978 | 0.072148 | 5.2907e-07 | -0.00039486 | 0.0048503 | 0.0048453 | 0.0048503 | 0.9905 | -0.45781 | 0.99051 | -0.45784 | 2.2047
63 | 2.2761 | 0.99146 | -2.276 | -0.99504 | 9.538e-05 | -0.0035787 | 0.072354 | 0.072397 | 0.072397 | 0.99051 | -0.45784 | 0.99046 | -0.4581 | 11.3474
64 | -2.4259 | -1.0636 | 2.4262 | 1.051 | 0.00038187 | -0.012596 | 0.077196 | 0.077047 | 0.077196 | 0.99051 | -0.45784 | 0.99067 | -0.45688 | 12.0998
65 | -0.14817 | -0.07176 | 0.14817 | 0.071626 | 4.8884e-06 | -0.00013468 | 0.0048145 | 0.0048128 | 0.0048145 | 0.9871 | -0.61794 | 0.98714 | -0.61772 | 2.2926
66 | -0.14817 | -0.071626 | 0.14817 | 0.069611 | 2.6639e-06 | -0.0020142 | 0.0048128 | 0.0047874 | 0.0048128 | 0.98714 | -0.61772 | 0.98716 | -0.61787 | 2.1876
67 | -4.7705 | -2.1077 | 4.7709 | 2.105 | 0.00032571 | -0.0027177 | 0.15083 | 0.1508 | 0.15083 | 0.99815 | -0.020245 | 0.99822 | -0.019847 | 23.6418
68 | 4.7052 | 2.076 | -4.7039 | -2.0727 | 0.00132 | 0.0033196 | 0.14874 | 0.14874 | 0.14874 | 0.99815 | -0.020245 | 0.99764 | -0.050504 | 23.0603
69 | -4.7709 | -2.105 | 4.7782 | 2.0433 | 0.0073397 | -0.061701 | 0.1508 | 0.15004 | 0.1508 | 0.99822 | -0.019847 | 0.99983 | -0.010312 | 23.6364
70 | 0.10536 | 0.049395 | -0.10535 | -0.050052 | 4.1938e-07 | -0.00065679 | 0.003367 | 0.0033751 | 0.0033751 | 0.99764 | -0.050504 | 0.99763 | -0.050472 | 1.5341
71 | 4.4653 | 1.9588 | -4.4649 | -1.9627 | 0.00040562 | -0.0038935 | 0.14109 | 0.14114 | 0.14114 | 0.99764 | -0.050504 | 0.99754 | -0.051045 | 22.1222
72 | -4.7782 | -2.0433 | 4.7786 | 2.0444 | 0.00044987 | 0.0011324 | 0.15004 | 0.15004 | 0.15004 | 0.99983 | -0.010312 | 1 | 0 | 23.2624
73 | 0.10535 | 0.050052 | -0.10535 | -0.050959 | 5.8266e-07 | -0.00090727 | 0.0033751 | 0.0033864 | 0.0033864 | 0.99763 | -0.050472 | 0.99763 | -0.050425 | 1.5393
74 | 4.4649 | 1.9627 | -4.4645 | -1.9664 | 0.00039189 | -0.0037583 | 0.14114 | 0.14119 | 0.14119 | 0.99754 | -0.051045 | 0.99745 | -0.051564 | 22.1294
75 | -4.3587 | -1.9145 | 4.3591 | 1.9154 | 0.00036876 | 0.00091681 | 0.1378 | 0.1378 | 0.1378 | 0.9973 | -0.060705 | 0.99745 | -0.051564 | 21.3644
76 | 4.3587 | 1.9145 | -4.3582 | -1.9197 | 0.00052256 | -0.005268 | 0.1378 | 0.13786 | 0.13786 | 0.9973 | -0.060705 | 0.99717 | -0.061414 | 21.6089
77 | 0.10021 | 0.047698 | -0.10021 | -0.048532 | 4.8565e-07 | -0.00083388 | 0.0032128 | 0.0032232 | 0.0032232 | 0.99717 | -0.061414 | 0.99717 | -0.061373 | 1.4651
78 | 4.258 | 1.872 | -4.2574 | -1.8782 | 0.0005857 | -0.0061968 | 0.13465 | 0.13473 | 0.13473 | 0.99717 | -0.061414 | 0.99703 | -0.062224 | 21.1175
79 | -0.13153 | -0.063574 | 0.13154 | 0.060409 | 3.2218e-06 | -0.0031641 | 0.0042519 | 0.0042126 | 0.0042519 | 0.99186 | -0.34433 | 0.99188 | -0.34453 | 1.9327
80 | 0.13153 | 0.063574 | -0.13153 | -0.063703 | 3.606e-06 | -0.00012916 | 0.0042519 | 0.0042536 | 0.0042536 | 0.99186 | -0.34433 | 0.99183 | -0.34451 | 2.0255
81 | -0.13154 | -0.060409 | 0.13154 | 0.058955 | 1.4615e-06 | -0.0014548 | 0.0042126 | 0.0041951 | 0.0042126 | 0.99188 | -0.34453 | 0.99189 | -0.34461 | 1.9148
82 | 3.8935 | 1.6686 | -3.8929 | -1.6764 | 0.0005954 | -0.007754 | 0.12228 | 0.12237 | 0.12237 | 1 | 0 | 0.99984 | -0.00098762 | 19.1809
83 | 0.08832 | 0.0404 | -0.08832 | -0.041021 | 2.7451e-07 | -0.00062048 | 0.0028063 | 0.0028138 | 0.0028138 | 0.99906 | -0.005524 | 0.99905 | -0.0054999 | 1.279
84 | 0.08832 | 0.041021 | -0.08832 | -0.042014 | 4.4243e-07 | -0.00099306 | 0.0028138 | 0.002826 | 0.002826 | 0.99905 | -0.0054999 | 0.99905 | -0.0054591 | 1.2846
85 | -0.10757 | -0.0521 | 0.10757 | 0.051804 | 1.9984e-07 | -0.00029632 | 0.0034624 | 0.0034587 | 0.0034624 | 0.99653 | -0.084119 | 0.99653 | -0.084135 | 1.5738
86 | -0.10757 | -0.051804 | 0.10757 | 0.050992 | 5.4554e-07 | -0.0008122 | 0.0034587 | 0.0034486 | 0.0034587 | 0.99653 | -0.084135 | 0.99654 | -0.084178 | 1.5721
87 | 3.9893 | 1.7542 | -3.9892 | -1.7552 | 8.0582e-05 | -0.00097555 | 0.12624 | 0.12625 | 0.12625 | 0.99654 | -0.084178 | 0.99651 | -0.084297 | 19.7888
88 | -4.0969 | -1.8052 | 4.0972 | 1.8059 | 0.00030051 | 0.00073938 | 0.12969 | 0.12969 | 0.12969 | 0.99654 | -0.084178 | 0.99667 | -0.076266 | 20.1067
89 | -0.10535 | -0.051025 | 0.10535 | 0.050959 | 1.1482e-06 | -6.6031e-05 | 0.0033873 | 0.0033864 | 0.0033873 | 0.99762 | -0.050497 | 0.99763 | -0.050425 | 1.613
90 | 0.28225 | 0.13179 | -0.28225 | -0.13195 | 7.3465e-07 | -0.00015703 | 0.0090659 | 0.0090678 | 0.0090678 | 0.99189 | -0.34463 | 0.99189 | -0.34461 | 4.1217
91 | -2.9999 | -1.2863 | 3.0067 | 1.3015 | 0.0067183 | 0.015217 | 0.094996 | 0.094963 | 0.094996 | 0.99189 | -0.34463 | 0.99594 | -0.1005 | 14.728
92 | 2.7177 | 1.1545 | -2.7173 | -1.1639 | 0.00035817 | -0.0094874 | 0.085935 | 0.086045 | 0.086045 | 0.99189 | -0.34463 | 0.99176 | -0.3455 | 13.4867
93 | 0.16026 | 0.076969 | -0.16026 | -0.077618 | 9.7391e-07 | -0.00064927 | 0.0051532 | 0.0051614 | 0.0051614 | 0.99594 | -0.1005 | 0.99593 | -0.10045 | 2.3461
94 | -3.1669 | -1.3784 | 3.167 | 1.3779 | 2.9103e-05 | -0.00056933 | 0.10011 | 0.10011 | 0.10011 | 0.99594 | -0.1005 | 0.99595 | -0.10044 | 15.6916
95 | 2.7173 | 1.1639 | -2.7171 | -1.1635 | 0.00022358 | 0.00048625 | 0.086045 | 0.086047 | 0.086047 | 0.99176 | -0.3455 | 0.99161 | -0.35451 | 13.3406
96 | 3.8425 | 1.6841 | -3.8425 | -1.6849 | 6.2862e-05 | -0.00082389 | 0.12153 | 0.12154 | 0.12154 | 0.99651 | -0.084297 | 0.9965 | -0.084395 | 19.0508
97 | -4.0972 | -1.8059 | 4.0977 | 1.8004 | 0.00048616 | -0.0055686 | 0.12969 | 0.12962 | 0.12969 | 0.99667 | -0.076266 | 0.99679 | -0.075565 | 20.3272
98 | 0.17147 | 0.080505 | -0.17146 | -0.082317 | 3.0862e-06 | -0.0018119 | 0.0054874 | 0.0055099 | 0.0055099 | 0.9965 | -0.084395 | 0.99648 | -0.084245 | 2.5045
99 | 3.671 | 1.6044 | -3.6706 | -1.6101 | 0.00039036 | -0.0056278 | 0.11606 | 0.11613 | 0.11613 | 0.9965 | -0.084395 | 0.99639 | -0.085036 | 18.2016
100 | -4.0977 | -1.8004 | 4.0977 | 1.7999 | 4.3721e-05 | -0.00050117 | 0.12962 | 0.12961 | 0.12962 | 0.99679 | -0.075565 | 0.9968 | -0.075501 | 20.3165
101 | 3.167 | 1.3768 | -3.167 | -1.3779 | 5.5907e-05 | -0.0010939 | 0.10009 | 0.10011 | 0.10011 | 0.99597 | -0.10034 | 0.99595 | -0.10044 | 15.6905
102 | -3.3166 | -1.4492 | 3.3168 | 1.4496 | 0.00017346 | 0.0004059 | 0.10491 | 0.10491 | 0.10491 | 0.99597 | -0.10034 | 0.99606 | -0.09467 | 16.2645
103 | -3.3168 | -1.4496 | 3.3169 | 1.4463 | 0.00018541 | -0.0032959 | 0.10491 | 0.10487 | 0.10491 | 0.99606 | -0.09467 | 0.99612 | -0.094329 | 16.4428
104 | -3.3169 | -1.4463 | 3.3171 | 1.4437 | 0.00014542 | -0.0025871 | 0.10487 | 0.10483 | 0.10487 | 0.99612 | -0.094329 | 0.99617 | -0.09406 | 16.4366
105 | -3.4646 | -1.5152 | 3.4648 | 1.5158 | 0.00027499 | 0.00065146 | 0.10958 | 0.10958 | 0.10958 | 0.99617 | -0.09406 | 0.99631 | -0.085465 | 16.9891
106 | -3.5456 | -1.5549 | 3.5456 | 1.5544 | 2.9992e-05 | -0.00046423 | 0.11217 | 0.11217 | 0.11217 | 0.99631 | -0.085465 | 0.99632 | -0.085414 | 17.5823
107 | -3.5456 | -1.5544 | 3.5458 | 1.551 | 0.00022301 | -0.0034537 | 0.11217 | 0.11213 | 0.11217 | 0.99632 | -0.085414 | 0.99639 | -0.085036 | 17.5814
108 | -4.2569 | -1.8769 | 4.2574 | 1.8782 | 0.0005242 | 0.0012985 | 0.13473 | 0.13473 | 0.13473 | 0.9968 | -0.075501 | 0.99703 | -0.062224 | 20.8885
109 | 0.08832 | 0.042014 | -0.088319 | -0.042775 | 3.4168e-07 | -0.00076105 | 0.002826 | 0.0028355 | 0.0028355 | 0.99905 | -0.0054591 | 0.99905 | -0.0054261 | 1.2889
110 | 0.25046 | 0.09644 | -0.25046 | -0.097301 | 3.0439e-06 | -0.00086171 | 0.007843 | 0.0078521 | 0.0078521 | 0.98784 | -0.43984 | 0.98783 | -0.43978 | 3.5691
111 | -0.41399 | -0.17564 | 0.41409 | 0.17532 | 0.00010264 | -0.00032453 | 0.013142 | 0.013137 | 0.013142 | 0.98784 | -0.43984 | 0.98811 | -0.4374 | 6.258
112 | 0.25046 | 0.097301 | -0.25045 | -0.099396 | 7.4276e-06 | -0.0020942 | 0.0078521 | 0.0078745 | 0.0078745 | 0.98783 | -0.43978 | 0.9878 | -0.43964 | 3.5793
113 | -0.41409 | -0.17532 | 0.41433 | 0.15071 | 0.00023875 | -0.024608 | 0.013137 | 0.012873 | 0.013137 | 0.98811 | -0.4374 | 0.98866 | -0.44017 | 5.9715
114 | 0.12978 | 0.041269 | -0.12976 | -0.062731 | 2.0541e-05 | -0.021462 | 0.0039799 | 0.0042127 | 0.0042127 | 0.9878 | -0.43964 | 0.98765 | -0.43883 | 1.9148
115 | 0.12067 | 0.058126 | -0.12067 | -0.058442 | 2.7744e-07 | -0.00031562 | 0.0039142 | 0.0039182 | 0.0039182 | 0.9878 | -0.43964 | 0.9878 | -0.43962 | 1.781
116 | -0.41433 | -0.15071 | 0.41435 | 0.14888 | 1.737e-05 | -0.0018298 | 0.012873 | 0.012855 | 0.012873 | 0.98866 | -0.44017 | 0.9887 | -0.44031 | 5.8516
117 | -0.069892 | -0.03385 | 0.069893 | 0.031203 | 7.6131e-07 | -0.0026478 | 0.0022629 | 0.0022304 | 0.0022629 | 0.99065 | -0.38058 | 0.99066 | -0.38067 | 1.0286
118 | -0.069893 | -0.031203 | 0.069895 | 0.030863 | 2.5735e-06 | -0.00033921 | 0.0022304 | 0.0022264 | 0.0022304 | 0.99066 | -0.38067 | 0.9907 | -0.38035 | 1.0621
119 | -0.53223 | -0.20597 | 0.5323 | 0.20585 | 6.9849e-05 | -0.00012106 | 0.016663 | 0.016661 | 0.016663 | 0.9887 | -0.44031 | 0.98884 | -0.43874 | 7.9347
120 | 0.12976 | 0.062731 | -0.12976 | -0.062845 | 3.1372e-06 | -0.00011353 | 0.0042127 | 0.0042141 | 0.0042141 | 0.98765 | -0.43883 | 0.98763 | -0.43899 | 2.0067
121 | -0.5323 | -0.20585 | 0.53248 | 0.19449 | 0.00017979 | -0.011358 | 0.016661 | 0.016544 | 0.016661 | 0.98884 | -0.43874 | 0.98916 | -0.44009 | 7.5732
122 | 0.15261 | 0.073242 | -0.15261 | -0.073913 | 9.3776e-07 | -0.00067096 | 0.0049402 | 0.0049487 | 0.0049487 | 0.98916 | -0.44009 | 0.98916 | -0.44003 | 2.2494
123 | -0.68509 | -0.26773 | 0.68517 | 0.26487 | 7.5842e-05 | -0.0028621 | 0.021466 | 0.021436 | 0.021466 | 0.98916 | -0.44009 | 0.98927 | -0.44059 | 9.7573
124 | 0.1248 | 0.059071 | -0.1248 | -0.060444 | 1.2432e-06 | -0.0013731 | 0.0040004 | 0.0040176 | 0.0040176 | 0.99639 | -0.085036 | 0.99638 | -0.084951 | 1.8262
125 | 0.092882 | 0.044346 | -0.092882 | -0.044985 | 3.2066e-07 | -0.0006387 | 0.0029817 | 0.0029897 | 0.0029897 | 0.99648 | -0.084245 | 0.99648 | -0.084216 | 1.359
126 | 0.07858 | 0.037971 | -0.078579 | -0.038058 | 8.416e-07 | -8.7034e-05 | 0.0025283 | 0.0025294 | 0.0025294 | 0.99648 | -0.084245 | 0.99647 | -0.084316 | 1.2045
127 | -0.10164 | -0.049227 | 0.10164 | 0.047621 | 9.8291e-07 | -0.0016064 | 0.0032889 | 0.0032688 | 0.0032889 | 0.99125 | -0.35458 | 0.99126 | -0.35467 | 1.495
128 | -0.10164 | -0.047621 | 0.10164 | 0.046499 | 6.7894e-07 | -0.0011212 | 0.0032688 | 0.0032551 | 0.0032688 | 0.99126 | -0.35467 | 0.99126 | -0.35472 | 1.4858
129 | -0.30392 | -0.1443 | 0.30393 | 0.14372 | 3.1255e-06 | -0.00057166 | 0.0097978 | 0.0097906 | 0.0097978 | 0.99126 | -0.35472 | 0.99127 | -0.3548 | 4.4535
130 | 0.20228 | 0.097796 | -0.20228 | -0.09787 | 4.9967e-06 | -7.3696e-05 | 0.0065432 | 0.0065442 | 0.0065442 | 0.99126 | -0.35472 | 0.99124 | -0.35488 | 3.1163
131 | -0.4378 | -0.20856 | 0.43781 | 0.20787 | 7.883e-06 | -0.00069271 | 0.014122 | 0.014114 | 0.014122 | 0.99127 | -0.3548 | 0.99129 | -0.35495 | 6.4193
132 | 0.081085 | 0.039174 | -0.081084 | -0.039271 | 1.0175e-06 | -9.6714e-05 | 0.0026226 | 0.0026238 | 0.0026238 | 0.99124 | -0.35488 | 0.99122 | -0.35497 | 1.2494
133 | -0.43781 | -0.20787 | 0.43786 | 0.20352 | 4.9287e-05 | -0.0043511 | 0.014114 | 0.01406 | 0.014114 | 0.99129 | -0.35495 | 0.99139 | -0.35587 | 6.4153
134 | 0.97661 | 0.39499 | -0.9766 | -0.39702 | 9.6262e-06 | -0.0020246 | 0.030724 | 0.030746 | 0.030746 | 0.9898 | -0.43396 | 0.98979 | -0.43403 | 4.8192
135 | -1.0866 | -0.44825 | 1.087 | 0.44803 | 0.0004004 | -0.0002172 | 0.03428 | 0.034266 | 0.03428 | 0.9898 | -0.43396 | 0.99046 | -0.39288 | 5.3148
136 | 0.9766 | 0.39702 | -0.97652 | -0.39711 | 7.4742e-05 | -9.8858e-05 | 0.030746 | 0.03075 | 0.03075 | 0.98979 | -0.43403 | 0.98966 | -0.44262 | 4.7674
137 | -1.2461 | -0.52508 | 1.2461 | 0.52289 | 1.7066e-05 | -0.0021837 | 0.03941 | 0.039385 | 0.03941 | 0.99046 | -0.39288 | 0.99048 | -0.39279 | 6.177
138 | 0.83723 | 0.32965 | -0.83717 | -0.33106 | 5.6178e-05 | -0.0014109 | 0.026246 | 0.026261 | 0.026261 | 0.98966 | -0.44262 | 0.98959 | -0.4423 | 11.937
139 | 0.83717 | 0.33106 | -0.83695 | -0.33675 | 0.00022707 | -0.0056841 | 0.026261 | 0.026324 | 0.026324 | 0.98959 | -0.4423 | 0.98933 | -0.44093 | 11.9653
140 | -1.2461 | -0.52289 | 1.2461 | 0.52291 | 6.0122e-05 | 1.4422e-05 | 0.039385 | 0.039383 | 0.039385 | 0.99048 | -0.39279 | 0.99056 | -0.38745 | 6.1062
141 | 0.83695 | 0.33675 | -0.83692 | -0.33745 | 2.8101e-05 | -0.00070133 | 0.026324 | 0.026331 | 0.026331 | 0.98933 | -0.44093 | 0.9893 | -0.44075 | 11.9688
142 | 0.68519 | 0.26396 | -0.68517 | -0.26487 | 2.404e-05 | -0.00090905 | 0.021426 | 0.021436 | 0.021436 | 0.9893 | -0.44075 | 0.98927 | -0.44059 | 9.7434
143 | -0.057505 | -0.027851 | 0.057505 | 0.027041 | 1.5905e-07 | -0.00081004 | 0.0018617 | 0.0018515 | 0.0018617 | 0.99075 | -0.37997 | 0.99076 | -0.37999 | 0.84622
144 | 1.4558 | 0.61053 | -1.4557 | -0.61754 | 7.4907e-05 | -0.0070122 | 0.045996 | 0.046076 | 0.046076 | 0.99076 | -0.37999 | 0.9907 | -0.38035 | 7.222
145 | -1.5133 | -0.63757 | 1.5134 | 0.62948 | 9.3206e-05 | -0.0080902 | 0.047846 | 0.047755 | 0.047846 | 0.99076 | -0.37999 | 0.99082 | -0.37956 | 7.4994
146 | 1.3858 | 0.58668 | -1.3857 | -0.58662 | 8.7149e-05 | 6.2135e-05 | 0.04385 | 0.043852 | 0.043852 | 0.9907 | -0.38035 | 0.99059 | -0.38727 | 6.7988
147 | -1.5134 | -0.62948 | 1.5135 | 0.62478 | 5.4011e-05 | -0.0047029 | 0.047755 | 0.047702 | 0.047755 | 0.99082 | -0.37956 | 0.99086 | -0.3793 | 7.4851
148 | -1.7391 | -0.734 | 1.7394 | 0.7153 | 0.00028418 | -0.018702 | 0.054975 | 0.054764 | 0.054975 | 0.99122 | -0.35704 | 0.99139 | -0.35587 | 8.6168
149 | 1.7391 | 0.734 | -1.7388 | -0.7335 | 0.00035108 | 0.00050236 | 0.054975 | 0.05498 | 0.05498 | 0.99122 | -0.35704 | 0.99086 | -0.3793 | 8.5241
150 | 0.16146 | 0.078023 | -0.16146 | -0.0782 | 2.7576e-07 | -0.00017761 | 0.0052217 | 0.0052239 | 0.0052239 | 0.99139 | -0.35587 | 0.99139 | -0.35585 | 2.3745
151 | -2.3387 | -0.99684 | 2.3388 | 0.99406 | 7.7315e-05 | -0.0027774 | 0.074028 | 0.073996 | 0.074028 | 0.99139 | -0.35587 | 0.99143 | -0.35565 | 11.6031
152 | 0.076971 | 0.036865 | -0.076971 | -0.037279 | 1.458e-07 | -0.00041322 | 0.0024864 | 0.0024916 | 0.0024916 | 0.99086 | -0.3793 | 0.99086 | -0.37928 | 1.1326
153 | 1.3857 | 0.58662 | -1.3857 | -0.59051 | 3.7739e-05 | -0.0038905 | 0.043852 | 0.043897 | 0.043897 | 0.99059 | -0.38727 | 0.99056 | -0.38745 | 6.8804
154 | -2.5835 | -1.1122 | 2.5839 | 1.0999 | 0.00041839 | -0.012255 | 0.081899 | 0.081756 | 0.081899 | 0.99143 | -0.35565 | 0.99159 | -0.35459 | 12.8368
155 | 0.13369 | 0.064377 | -0.13369 | -0.064471 | 2.7262e-06 | -9.4451e-05 | 0.0043204 | 0.0043217 | 0.0043217 | 0.99143 | -0.35565 | 0.9914 | -0.35579 | 2.0579
156 | 0.11102 | 0.053712 | -0.11102 | -0.053768 | 1.1104e-06 | -5.6007e-05 | 0.003591 | 0.0035917 | 0.0035917 | 0.99143 | -0.35565 | 0.99142 | -0.35571 | 1.7103
157 | -2.5839 | -1.0999 | 2.584 | 1.099 | 3.1144e-05 | -0.00091418 | 0.081756 | 0.081745 | 0.081756 | 0.99159 | -0.35459 | 0.99161 | -0.35451 | 12.8144
158 | 0.13369 | 0.064471 | -0.13369 | -0.064747 | 2.933e-07 | -0.00027575 | 0.0043217 | 0.0043251 | 0.0043251 | 0.9914 | -0.35579 | 0.9914 | -0.35577 | 1.966

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 8.7846 | 3.7712

## res_load
| p_mw | q_mvar
0 | 0.083052 | 0.040224
1 | 0.13207 | 0.063967
2 | 0.10494 | 0.050824
3 | 0.12697 | 0.061493
4 | 0.11312 | 0.054786
5 | 0.087578 | 0.042416
6 | 0.12728 | 0.061646
7 | 0.12724 | 0.061627
8 | 0.11828 | 0.057287
9 | 0.15772 | 0.076389
10 | 0.15936 | 0.07718
11 | 0.1479 | 0.071632
12 | 0.09793 | 0.04743
13 | 0.092304 | 0.044705
14 | 0.13334 | 0.064577
15 | 0.11747 | 0.056892
16 | 0.12415 | 0.060128
17 | 0.12079 | 0.058502
18 | 0.14699 | 0.07119
19 | 0.05393 | 0.02612
20 | 0.09942 | 0.048151
21 | 0.15489 | 0.075015
22 | 0.14602 | 0.070719
23 | 0.10486 | 0.050784
24 | 0.10445 | 0.050585
25 | 0.15006 | 0.072677
26 | 0.12214 | 0.059155
27 | 0.14978 | 0.072543
28 | 0.11146 | 0.053981
29 | 0.14817 | 0.07176
30 | 0.065335 | 0.031643
31 | 0.13326 | 0.064539
32 | 0.10538 | 0.05104
33 | 0.13153 | 0.063703
34 | 0.098508 | 0.04771
35 | 0.11763 | 0.056973
36 | 0.10757 | 0.0521
37 | 0.10535 | 0.051025
38 | 0.15071 | 0.072994
39 | 0.1467 | 0.071052
40 | 0.14958 | 0.072443
41 | 0.14748 | 0.071428
42 | 0.16026 | 0.077618
43 | 0.080704 | 0.039087
44 | 0.15916 | 0.077085
45 | 0.10021 | 0.048532
46 | 0.088319 | 0.042775
47 | 0.16353 | 0.079201
48 | 0.069892 | 0.03385
49 | 0.11788 | 0.057091
50 | 0.12067 | 0.058442
51 | 0.12976 | 0.062845
52 | 0.1248 | 0.060444
53 | 0.092882 | 0.044985
54 | 0.078579 | 0.038058
55 | 0.10164 | 0.049227
56 | 0.13388 | 0.06484
57 | 0.12119 | 0.058696
58 | 0.081084 | 0.039271
59 | 0.10997 | 0.053259
60 | 0.15908 | 0.077044
61 | 0.13929 | 0.067463
62 | 0.15173 | 0.073486
63 | 0.057505 | 0.027851
64 | 0.14836 | 0.071853
65 | 0.13958 | 0.067599
66 | 0.076971 | 0.037279
67 | 0.16146 | 0.0782
68 | 0.11102 | 0.053768
69 | 0.13369 | 0.064747
70 | 0.13314 | 0.064481
71 | 0.15261 | 0.073913

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1