## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_212_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_212_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_212_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_212_0_node_31 | 20 | n |  | TRUE
4 | bus_MV_212_0_node_129 | 20 | n |  | TRUE
5 | bus_MV_212_0_node_15 | 20 | n |  | TRUE
6 | bus_MV_212_0_node_135 | 20 | n |  | TRUE
7 | bus_MV_212_0_node_75 | 20 | n |  | TRUE
8 | bus_MV_212_0_node_8 | 20 | n |  | TRUE
9 | bus_MV_212_0_node_9 | 20 | n |  | TRUE
10 | bus_MV_212_0_node_10 | 20 | n |  | TRUE
11 | bus_MV_212_0_node_17 | 20 | n |  | TRUE
12 | bus_MV_212_0_node_11 | 20 | n |  | TRUE
13 | bus_MV_212_0_node_12 | 20 | n |  | TRUE
14 | bus_MV_212_0_node_16 | 20 | n |  | TRUE
15 | bus_MV_212_0_node_27 | 20 | n |  | TRUE
16 | bus_MV_212_0_node_127 | 20 | n |  | TRUE
17 | bus_MV_212_0_node_23 | 20 | n |  | TRUE
18 | bus_MV_212_0_node_18 | 20 | n |  | TRUE
19 | bus_MV_212_0_node_91 | 20 | n |  | TRUE
20 | bus_MV_212_0_node_21 | 20 | n |  | TRUE
21 | bus_MV_212_0_node_22 | 20 | n |  | TRUE
22 | bus_MV_212_0_node_24 | 20 | n |  | TRUE
23 | bus_MV_212_0_node_32 | 20 | n |  | TRUE
24 | bus_MV_212_0_node_28 | 20 | n |  | TRUE
25 | bus_MV_212_0_node_29 | 20 | n |  | TRUE
26 | bus_MV_212_0_node_98 | 20 | n |  | TRUE
27 | bus_MV_212_0_node_33 | 20 | n |  | TRUE
28 | bus_MV_212_0_node_34 | 20 | n |  | TRUE
29 | bus_MV_212_0_node_35 | 20 | n |  | TRUE
30 | bus_MV_212_0_node_38 | 20 | n |  | TRUE
31 | bus_MV_212_0_node_37 | 20 | n |  | TRUE
32 | bus_MV_212_0_node_39 | 20 | n |  | TRUE
33 | bus_MV_212_0_node_40 | 20 | n |  | TRUE
34 | bus_MV_212_0_node_36 | 20 | n |  | TRUE
35 | bus_MV_212_0_node_99 | 20 | n |  | TRUE
36 | bus_MV_212_0_node_73 | 20 | n |  | TRUE
37 | bus_MV_212_0_node_41 | 20 | n |  | TRUE
38 | bus_MV_212_0_node_74 | 20 | n |  | TRUE
39 | bus_HV_212_0_node_0 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_212_0_load_0 | 0 | 0.30912 | 0.14971 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_212_0_load_31 | 3 | 0.28397 | 0.13753 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_212_0_load_129 | 4 | 0.19314 | 0.093544 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_212_0_load_135 | 6 | 0.31087 | 0.15056 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_212_0_load_8 | 8 | 0.26946 | 0.1305 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_212_0_load_17 | 11 | 0.23555 | 0.11408 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_212_0_load_27 | 15 | 0.24742 | 0.11983 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_212_0_load_127 | 16 | 0.23516 | 0.11389 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_212_0_load_18 | 18 | 0.18795 | 0.091028 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_212_0_load_91 | 19 | 0.081343 | 0.039396 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_212_0_load_21 | 20 | 0.38293 | 0.18546 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_212_0_load_32 | 23 | 0.27804 | 0.13466 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_212_0_load_98 | 26 | 0.79446 | 0.38477 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_212_0_load_33 | 27 | 0.30251 | 0.14651 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_212_0_load_40 | 33 | 0.15186 | 0.073547 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_212_0_load_99 | 35 | 0.76011 | 0.36814 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_212_0_load_73 | 36 | 0.24259 | 0.11749 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_212_0_load_41 | 37 | 0.17654 | 0.085503 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_212_0_line_0 |  | 0 | 1 | 0.18354 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
1 | MV_212_0_line_1 |  | 1 | 2 | 0.095804 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
2 | MV_212_0_line_2 |  | 2 | 3 | 0.02607 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
3 | MV_212_0_line_3 |  | 3 | 13 | 0.016909 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
4 | MV_212_0_line_4 |  | 4 | 5 | 0.079546 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_212_0_line_5 |  | 5 | 14 | 0.4308 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_212_0_line_6 |  | 5 | 9 | 0.66151 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_212_0_line_7 |  | 6 | 7 | 0.004682 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_212_0_line_8 |  | 7 | 38 | 0.4249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_212_0_line_9 |  | 8 | 9 | 0.00561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_212_0_line_10 |  | 9 | 10 | 0.36043 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_212_0_line_11 |  | 10 | 11 | 0.025395 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_212_0_line_12 |  | 12 | 13 | 0.41139 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
13 | MV_212_0_line_13 |  | 12 | 14 | 0.44247 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_212_0_line_14 |  | 12 | 15 | 0.021689 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_212_0_line_15 |  | 14 | 16 | 0.004117 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_212_0_line_16 |  | 14 | 17 | 0.020704 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_212_0_line_17 |  | 15 | 24 | 0.054739 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_212_0_line_18 |  | 17 | 23 | 0.075945 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_212_0_line_19 |  | 17 | 21 | 0.76611 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_212_0_line_20 |  | 18 | 19 | 0.43959 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_212_0_line_21 |  | 19 | 22 | 0.048429 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_212_0_line_22 |  | 20 | 21 | 0.060959 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_212_0_line_23 |  | 21 | 22 | 0.54763 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_212_0_line_24 |  | 24 | 25 | 0.91733 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_212_0_line_25 |  | 25 | 26 | 0.055121 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_212_0_line_26 |  | 26 | 34 | 0.064314 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_212_0_line_27 |  | 27 | 28 | 0.003976 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_212_0_line_28 |  | 28 | 29 | 0.49994 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_212_0_line_29 |  | 28 | 30 | 0.40937 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_212_0_line_30 |  | 29 | 31 | 0.30679 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_212_0_line_31 |  | 29 | 32 | 0.48987 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_212_0_line_32 |  | 29 | 33 | 0.066299 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_212_0_line_33 |  | 30 | 36 | 0.027824 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_212_0_line_34 |  | 31 | 35 | 0.24769 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_212_0_line_35 |  | 31 | 34 | 0.20547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_212_0_line_36 |  | 32 | 37 | 0.038655 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_212_0_line_37 |  | 36 | 38 | 0.00398 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_212_0_trafo_0 | 25 MVA 110/20 kV | 39 | 0 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2669713.1336 | 1216529.2371
1 | 2669569.6341 | 1216414.8107
2 | 2669500.5266 | 1216412.759
3 | 2669477.9692 | 1216412.8381
4 | 2668850.2095 | 1216462.334
5 | 2668920.485 | 1216425.0668
6 | 2669907.2551 | 1216014.5174
7 | 2669910.6954 | 1216017.7042
8 | 2669131.5403 | 1216918.289
9 | 2669131.0433 | 1216912.7019
10 | 2669244.6674 | 1216732.9289
11 | 2669261.0573 | 1216713.4959
12 | 2669353.8578 | 1216245.8233
13 | 2669461.6379 | 1216417.2197
14 | 2669207.5248 | 1216448.0396
15 | 2669372.7406 | 1216256.4927
16 | 2669208.8154 | 1216444.1299
17 | 2669221.2239 | 1216458.3274
18 | 2669665.4247 | 1217661.2866
19 | 2669748.5418 | 1217229.622
20 | 2669555.1646 | 1216987.299
21 | 2669502.5427 | 1216956.5269
22 | 2669768.3307 | 1217185.4212
23 | 2669187.8136 | 1216526.5605
24 | 2669418.1627 | 1216260.7588
25 | 2670020.4841 | 1216531.5069
26 | 2670058.8398 | 1216491.9189
27 | 2670256.2111 | 1216344.0723
28 | 2670258.8731 | 1216341.1129
29 | 2670394.9673 | 1216452.8891
30 | 2670152.1317 | 1216142.6191
31 | 2670179.6521 | 1216590.3824
32 | 2670442.7233 | 1216188.4409
33 | 2670446.0676 | 1216495.1306
34 | 2670103.5917 | 1216445.7291
35 | 2670239.5517 | 1216768.8247
36 | 2670132.209 | 1216123.139
37 | 2670410.5175 | 1216166.9246
38 | 2670128.8578 | 1216125.301
39 | 2669713.1336 | 1216529.2371

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -5.1758 | -2.3214
1 | 0.9989 | -0.028936 | 0 | 0
2 | 0.99864 | -0.032125 | 0 | 0
3 | 0.99857 | -0.032992 | 0.28397 | 0.13753
4 | 0.996 | -0.03615 | 0.19314 | 0.093544
5 | 0.99603 | -0.035963 | 0 | 0
6 | 0.99164 | 0.00017036 | 0.31087 | 0.15056
7 | 0.99164 | 0.00015267 | 0 | 0
8 | 0.99561 | -0.032641 | 0.26946 | 0.1305
9 | 0.99561 | -0.032659 | 0 | 0
10 | 0.9955 | -0.031747 | 0 | 0
11 | 0.99549 | -0.031676 | 0.23555 | 0.11408
12 | 0.99745 | -0.046494 | 0 | 0
13 | 0.99852 | -0.033528 | 0 | 0
14 | 0.99641 | -0.038755 | 0 | 0
15 | 0.99737 | -0.045838 | 0.24742 | 0.11983
16 | 0.99641 | -0.038743 | 0.23516 | 0.11389
17 | 0.99639 | -0.038571 | 0 | 0
18 | 0.99539 | -0.033153 | 0.18795 | 0.091028
19 | 0.99555 | -0.032136 | 0.081343 | 0.039396
20 | 0.99573 | -0.033504 | 0.38293 | 0.18546
21 | 0.99576 | -0.033783 | 0 | 0
22 | 0.99557 | -0.03229 | 0 | 0
23 | 0.99636 | -0.038321 | 0.27804 | 0.13466
24 | 0.99718 | -0.044343 | 0 | 0
25 | 0.99398 | -0.01852 | 0 | 0
26 | 0.99379 | -0.016922 | 0.79446 | 0.38477
27 | 0.99212 | -0.0038197 | 0.30251 | 0.14651
28 | 0.99212 | -0.0038344 | 0 | 0
29 | 0.99266 | -0.0081779 | 0 | 0
30 | 0.99183 | -0.0014945 | 0 | 0
31 | 0.99313 | -0.011627 | 0 | 0
32 | 0.99255 | -0.0073392 | 0 | 0
33 | 0.99264 | -0.0083016 | 0.15186 | 0.073547
34 | 0.99363 | -0.015671 | 0 | 0
35 | 0.99288 | -0.0093894 | 0.76011 | 0.36814
36 | 0.99181 | -0.0013262 | 0.24259 | 0.11749
37 | 0.99255 | -0.0072575 | 0.17654 | 0.085503
38 | 0.99181 | -0.0013137 | 0 | 0
39 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 5.1618 | 2.3109 | -5.1573 | -2.306 | 0.0044908 | 0.0049062 | 0.16326 | 0.16326 | 0.16326 | 1 | 0 | 0.9989 | -0.028936 | 46.6461
1 | 5.1573 | 2.306 | -5.156 | -2.3084 | 0.0012337 | -0.0023821 | 0.16326 | 0.1633 | 0.1633 | 0.9989 | -0.028936 | 0.99864 | -0.032125 | 45.1105
2 | 5.156 | 2.3084 | -5.1557 | -2.309 | 0.0003358 | -0.00064783 | 0.1633 | 0.16331 | 0.16331 | 0.99864 | -0.032125 | 0.99857 | -0.032992 | 45.1134
3 | 4.8717 | 2.1715 | -4.8715 | -2.1719 | 0.00019418 | -0.00043728 | 0.15419 | 0.1542 | 0.1542 | 0.99857 | -0.032992 | 0.99852 | -0.033528 | 42.5968
4 | -0.19314 | -0.093544 | 0.19315 | 0.093453 | 5.482e-06 | -9.0773e-05 | 0.0062199 | 0.0062187 | 0.0062199 | 0.996 | -0.03615 | 0.99603 | -0.035963 | 2.9619
5 | -0.69841 | -0.31319 | 0.69869 | 0.30306 | 0.00028149 | -0.010125 | 0.022184 | 0.022064 | 0.022184 | 0.99603 | -0.035963 | 0.99641 | -0.038755 | 10.0835
6 | 0.50526 | 0.21973 | -0.50503 | -0.23533 | 0.00022779 | -0.015595 | 0.015969 | 0.016155 | 0.016155 | 0.99603 | -0.035963 | 0.99561 | -0.032659 | 7.3432
7 | -0.31087 | -0.15056 | 0.31087 | 0.15045 | 6.3188e-07 | -0.00010974 | 0.010055 | 0.010054 | 0.010055 | 0.99164 | 0.00017036 | 0.99164 | 0.00015267 | 4.5706
8 | -0.31087 | -0.15045 | 0.31093 | 0.14049 | 5.6628e-05 | -0.009961 | 0.010054 | 0.0099308 | 0.010054 | 0.99164 | 0.00015267 | 0.99181 | -0.0013137 | 4.57
9 | -0.26946 | -0.1305 | 0.26946 | 0.13037 | 5.6431e-07 | -0.0001326 | 0.008681 | 0.0086793 | 0.008681 | 0.99561 | -0.032641 | 0.99561 | -0.032659 | 3.9459
10 | 0.23557 | 0.10496 | -0.23555 | -0.11348 | 2.7275e-05 | -0.0085211 | 0.0074777 | 0.0075817 | 0.0075817 | 0.99561 | -0.032659 | 0.9955 | -0.031747 | 3.4462
11 | 0.23555 | 0.11348 | -0.23555 | -0.11408 | 1.9507e-06 | -0.00060031 | 0.0075817 | 0.0075893 | 0.0075893 | 0.9955 | -0.031747 | 0.99549 | -0.031676 | 3.4497
12 | -4.8668 | -2.1826 | 4.8715 | 2.1719 | 0.0047298 | -0.010619 | 0.15437 | 0.1542 | 0.15437 | 0.99745 | -0.046494 | 0.99852 | -0.033528 | 42.6426
13 | 1.8667 | 0.82118 | -1.8647 | -0.83107 | 0.002062 | -0.009888 | 0.059022 | 0.059145 | 0.059145 | 0.99745 | -0.046494 | 0.99641 | -0.038755 | 26.8842
14 | 3.0001 | 1.3614 | -2.9998 | -1.3618 | 0.00026324 | -0.00043708 | 0.095347 | 0.095353 | 0.095353 | 0.99745 | -0.046494 | 0.99737 | -0.045838 | 43.3422
15 | 0.23516 | 0.1138 | -0.23516 | -0.11389 | 3.149e-07 | -9.75e-05 | 0.0075687 | 0.0075699 | 0.0075699 | 0.99641 | -0.038755 | 0.99641 | -0.038743 | 3.4409
16 | 0.93083 | 0.41421 | -0.93081 | -0.4147 | 2.4086e-05 | -0.00048362 | 0.029517 | 0.029523 | 0.029523 | 0.99641 | -0.038755 | 0.99639 | -0.038571 | 13.4195
17 | 2.7524 | 1.242 | -2.7518 | -1.2431 | 0.00055829 | -0.0011342 | 0.087398 | 0.087414 | 0.087414 | 0.99737 | -0.045838 | 0.99718 | -0.044343 | 39.7336
18 | 0.27804 | 0.13286 | -0.27804 | -0.13466 | 8.1018e-06 | -0.0017977 | 0.008928 | 0.0089506 | 0.0089506 | 0.99639 | -0.038571 | 0.99636 | -0.038321 | 4.0684
19 | 0.65276 | 0.28184 | -0.65232 | -0.29985 | 0.00043846 | -0.018018 | 0.020599 | 0.020814 | 0.020814 | 0.99639 | -0.038571 | 0.99576 | -0.033783 | 9.4607
20 | -0.18795 | -0.091028 | 0.18798 | 0.090526 | 2.8697e-05 | -0.00050207 | 0.0060564 | 0.0060498 | 0.0060564 | 0.99539 | -0.033153 | 0.99555 | -0.032136 | 2.884
21 | -0.26932 | -0.12992 | 0.26933 | 0.12878 | 4.8524e-06 | -0.0011446 | 0.0086706 | 0.0086562 | 0.0086706 | 0.99555 | -0.032136 | 0.99557 | -0.03229 | 3.9412
22 | -0.38293 | -0.18546 | 0.38294 | 0.18402 | 1.2364e-05 | -0.0014394 | 0.012335 | 0.012317 | 0.012335 | 0.99573 | -0.033504 | 0.99576 | -0.033783 | 5.6069
23 | 0.26938 | 0.11583 | -0.26933 | -0.12878 | 5.378e-05 | -0.012946 | 0.0085009 | 0.0086562 | 0.0086562 | 0.99576 | -0.033783 | 0.99557 | -0.03229 | 3.9346
24 | 2.7518 | 1.2431 | -2.7424 | -1.262 | 0.0093856 | -0.018925 | 0.087414 | 0.087675 | 0.087675 | 0.99718 | -0.044343 | 0.99398 | -0.01852 | 39.8523
25 | 2.7424 | 1.262 | -2.7419 | -1.2632 | 0.00056576 | -0.0011322 | 0.087675 | 0.087691 | 0.087691 | 0.99398 | -0.01852 | 0.99379 | -0.016922 | 39.8595
26 | 1.9474 | 0.8784 | -1.9471 | -0.87982 | 0.00033073 | -0.0014182 | 0.062056 | 0.062074 | 0.062074 | 0.99379 | -0.016922 | 0.99363 | -0.015671 | 28.2156
27 | -0.30251 | -0.14651 | 0.30251 | 0.14642 | 5.0763e-07 | -9.329e-05 | 0.00978 | 0.0097788 | 0.00978 | 0.99212 | -0.0038197 | 0.99212 | -0.0038344 | 4.4454
28 | -0.8562 | -0.39409 | 0.8567 | 0.38248 | 0.00049939 | -0.011607 | 0.027425 | 0.027284 | 0.027425 | 0.99212 | -0.0038344 | 0.99266 | -0.0081779 | 12.4659
29 | 0.5537 | 0.24767 | -0.55353 | -0.25724 | 0.00017134 | -0.009567 | 0.017649 | 0.017765 | 0.017765 | 0.99212 | -0.0038344 | 0.99183 | -0.0014945 | 8.0751
30 | -1.1851 | -0.52903 | 1.1857 | 0.52198 | 0.00058211 | -0.0070486 | 0.037742 | 0.037657 | 0.037742 | 0.99266 | -0.0081779 | 0.99313 | -0.011627 | 17.1556
31 | 0.17656 | 0.073076 | -0.17654 | -0.084594 | 2.0679e-05 | -0.011518 | 0.005557 | 0.0056936 | 0.0056936 | 0.99266 | -0.0081779 | 0.99255 | -0.0073392 | 2.588
32 | 0.15186 | 0.073471 | -0.15186 | -0.073547 | 2.8436e-06 | -7.6209e-05 | 0.0049059 | 0.0049069 | 0.0049069 | 0.99266 | -0.0081779 | 0.99264 | -0.0083016 | 2.3366
33 | 0.55353 | 0.25724 | -0.55351 | -0.25789 | 1.1728e-05 | -0.00065003 | 0.017765 | 0.017773 | 0.017773 | 0.99183 | -0.0014945 | 0.99181 | -0.0013262 | 8.0788
34 | 0.76031 | 0.36236 | -0.76011 | -0.36814 | 0.00019878 | -0.0057724 | 0.024482 | 0.024555 | 0.024555 | 0.99313 | -0.011627 | 0.99288 | -0.0093894 | 11.1614
35 | -1.946 | -0.88434 | 1.9471 | 0.87982 | 0.001058 | -0.0045274 | 0.062132 | 0.062074 | 0.062132 | 0.99313 | -0.011627 | 0.99363 | -0.015671 | 28.2419
36 | 0.17654 | 0.084594 | -0.17654 | -0.085503 | 1.6762e-06 | -0.00090873 | 0.0056936 | 0.0057051 | 0.0057051 | 0.99255 | -0.0073392 | 0.99255 | -0.0072575 | 2.5932
37 | 0.31093 | 0.1404 | -0.31093 | -0.14049 | 5.2393e-07 | -9.3321e-05 | 0.0099297 | 0.0099308 | 0.0099308 | 0.99181 | -0.0013262 | 0.99181 | -0.0013137 | 4.514

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 5.4849 | 2.4711

## res_load
| p_mw | q_mvar
0 | 0.30912 | 0.14971
1 | 0.28397 | 0.13753
2 | 0.19314 | 0.093544
3 | 0.31087 | 0.15056
4 | 0.26946 | 0.1305
5 | 0.23555 | 0.11408
6 | 0.24742 | 0.11983
7 | 0.23516 | 0.11389
8 | 0.18795 | 0.091028
9 | 0.081343 | 0.039396
10 | 0.38293 | 0.18546
11 | 0.27804 | 0.13466
12 | 0.79446 | 0.38477
13 | 0.30251 | 0.14651
14 | 0.15186 | 0.073547
15 | 0.76011 | 0.36814
16 | 0.24259 | 0.11749
17 | 0.17654 | 0.085503

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1