## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_221_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_221_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_221_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_221_0_node_17 | 20 | n |  | TRUE
4 | bus_MV_221_0_node_18 | 20 | n |  | TRUE
5 | bus_MV_221_0_node_4 | 20 | n |  | TRUE
6 | bus_MV_221_0_node_75 | 20 | n |  | TRUE
7 | bus_MV_221_0_node_73 | 20 | n |  | TRUE
8 | bus_MV_221_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_221_0_node_22 | 20 | n |  | TRUE
10 | bus_MV_221_0_node_19 | 20 | n |  | TRUE
11 | bus_MV_221_0_node_6 | 20 | n |  | TRUE
12 | bus_MV_221_0_node_78 | 20 | n |  | TRUE
13 | bus_MV_221_0_node_7 | 20 | n |  | TRUE
14 | bus_MV_221_0_node_66 | 20 | n |  | TRUE
15 | bus_MV_221_0_node_8 | 20 | n |  | TRUE
16 | bus_MV_221_0_node_45 | 20 | n |  | TRUE
17 | bus_MV_221_0_node_67 | 20 | n |  | TRUE
18 | bus_MV_221_0_node_20 | 20 | n |  | TRUE
19 | bus_MV_221_0_node_47 | 20 | n |  | TRUE
20 | bus_MV_221_0_node_65 | 20 | n |  | TRUE
21 | bus_MV_221_0_node_46 | 20 | n |  | TRUE
22 | bus_MV_221_0_node_9 | 20 | n |  | TRUE
23 | bus_MV_221_0_node_10 | 20 | n |  | TRUE
24 | bus_MV_221_0_node_11 | 20 | n |  | TRUE
25 | bus_MV_221_0_node_12 | 20 | n |  | TRUE
26 | bus_MV_221_0_node_50 | 20 | n |  | TRUE
27 | bus_MV_221_0_node_52 | 20 | n |  | TRUE
28 | bus_MV_221_0_node_54 | 20 | n |  | TRUE
29 | bus_MV_221_0_node_57 | 20 | n |  | TRUE
30 | bus_MV_221_0_node_21 | 20 | n |  | TRUE
31 | bus_MV_221_0_node_27 | 20 | n |  | TRUE
32 | bus_MV_221_0_node_74 | 20 | n |  | TRUE
33 | bus_MV_221_0_node_51 | 20 | n |  | TRUE
34 | bus_MV_221_0_node_49 | 20 | n |  | TRUE
35 | bus_MV_221_0_node_13 | 20 | n |  | TRUE
36 | bus_MV_221_0_node_15 | 20 | n |  | TRUE
37 | bus_MV_221_0_node_14 | 20 | n |  | TRUE
38 | bus_MV_221_0_node_16 | 20 | n |  | TRUE
39 | bus_MV_221_0_node_32 | 20 | n |  | TRUE
40 | bus_MV_221_0_node_41 | 20 | n |  | TRUE
41 | bus_MV_221_0_node_30 | 20 | n |  | TRUE
42 | bus_MV_221_0_node_31 | 20 | n |  | TRUE
43 | bus_MV_221_0_node_33 | 20 | n |  | TRUE
44 | bus_MV_221_0_node_29 | 20 | n |  | TRUE
45 | bus_MV_221_0_node_35 | 20 | n |  | TRUE
46 | bus_MV_221_0_node_37 | 20 | n |  | TRUE
47 | bus_MV_221_0_node_43 | 20 | n |  | TRUE
48 | bus_MV_221_0_node_72 | 20 | n |  | TRUE
49 | bus_MV_221_0_node_48 | 20 | n |  | TRUE
50 | bus_MV_221_0_node_59 | 20 | n |  | TRUE
51 | bus_MV_221_0_node_70 | 20 | n |  | TRUE
52 | bus_MV_221_0_node_28 | 20 | n |  | TRUE
53 | bus_MV_221_0_node_26 | 20 | n |  | TRUE
54 | bus_MV_221_0_node_44 | 20 | n |  | TRUE
55 | bus_MV_221_0_node_25 | 20 | n |  | TRUE
56 | bus_MV_221_0_node_34 | 20 | n |  | TRUE
57 | bus_MV_221_0_node_36 | 20 | n |  | TRUE
58 | bus_MV_221_0_node_68 | 20 | n |  | TRUE
59 | bus_MV_221_0_node_69 | 20 | n |  | TRUE
60 | bus_MV_221_0_node_38 | 20 | n |  | TRUE
61 | bus_MV_221_0_node_76 | 20 | n |  | TRUE
62 | bus_MV_221_0_node_39 | 20 | n |  | TRUE
63 | bus_MV_221_0_node_40 | 20 | n |  | TRUE
64 | bus_MV_221_0_node_58 | 20 | n |  | TRUE
65 | bus_MV_221_0_node_56 | 20 | n |  | TRUE
66 | bus_MV_221_0_node_55 | 20 | n |  | TRUE
67 | bus_MV_221_0_node_63 | 20 | n |  | TRUE
68 | bus_MV_221_0_node_62 | 20 | n |  | TRUE
69 | bus_MV_221_0_node_53 | 20 | n |  | TRUE
70 | bus_MV_221_0_node_71 | 20 | n |  | TRUE
71 | bus_MV_221_0_node_64 | 20 | n |  | TRUE
72 | bus_MV_221_0_node_61 | 20 | n |  | TRUE
73 | bus_MV_221_0_node_60 | 20 | n |  | TRUE
74 | bus_MV_221_0_node_77 | 20 | n |  | TRUE
75 | bus_HV_221_0_node_40 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_221_0_load_0 | 0 | 0.30288 | 0.14669 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_221_0_load_17 | 3 | 0.31346 | 0.15182 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_221_0_load_75 | 6 | 0.38297 | 0.18548 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_221_0_load_73 | 7 | 0.18916 | 0.091616 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_221_0_load_22 | 9 | 0.16633 | 0.080556 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_221_0_load_78 | 12 | 0.14431 | 0.069894 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_221_0_load_66 | 14 | 0.25861 | 0.12525 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_221_0_load_45 | 16 | 0.090018 | 0.043598 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_221_0_load_67 | 17 | 0.27849 | 0.13488 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_221_0_load_65 | 20 | 0.40068 | 0.19406 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_221_0_load_9 | 22 | 0.33016 | 0.1599 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_221_0_load_10 | 23 | 0.085443 | 0.041382 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_221_0_load_11 | 24 | 0.14031 | 0.067957 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_221_0_load_57 | 29 | 0.26752 | 0.12957 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_221_0_load_74 | 32 | 0.088976 | 0.043093 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_221_0_load_51 | 33 | 0.19792 | 0.095857 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_221_0_load_49 | 34 | 0.22989 | 0.11134 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_221_0_load_13 | 35 | 0.30349 | 0.14699 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_221_0_load_15 | 36 | 0.094338 | 0.04569 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_221_0_load_41 | 40 | 0.37043 | 0.17941 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_221_0_load_29 | 44 | 0.12501 | 0.060546 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_221_0_load_35 | 45 | 0.27841 | 0.13484 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_221_0_load_37 | 46 | 0.35376 | 0.17133 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_221_0_load_72 | 48 | 0.11114 | 0.05383 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_221_0_load_59 | 50 | 0.17542 | 0.08496 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_221_0_load_70 | 51 | 0.28931 | 0.14012 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_221_0_load_44 | 54 | 0.079718 | 0.038609 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_221_0_load_25 | 55 | 0.28594 | 0.13849 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_221_0_load_36 | 57 | 0.2713 | 0.1314 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_221_0_load_68 | 58 | 0.14718 | 0.071281 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_221_0_load_76 | 61 | 2.563 | 1.2413 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_221_0_load_58 | 64 | 0.10754 | 0.052084 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_221_0_load_56 | 65 | 2.4223 | 1.1732 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_221_0_load_62 | 68 | 1.0092 | 0.48879 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_221_0_load_53 | 69 | 0.54258 | 0.26278 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_221_0_load_71 | 70 | 0.29838 | 0.14451 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_221_0_load_64 | 71 | 0.068083 | 0.032974 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_221_0_load_61 | 72 | 2.3172 | 1.1223 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_221_0_load_60 | 73 | 0.22241 | 0.10772 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_221_0_load_77 | 74 | 0.63543 | 0.30775 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 63 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_221_0_line_0 |  | 0 | 1 | 0.014867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_221_0_line_1 |  | 1 | 2 | 0.15772 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_221_0_line_2 |  | 2 | 6 | 0.019432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_221_0_line_3 |  | 2 | 3 | 0.2335 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_221_0_line_4 |  | 3 | 4 | 0.070528 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_221_0_line_5 |  | 3 | 5 | 0.19972 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_221_0_line_6 |  | 4 | 10 | 0.17599 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_221_0_line_7 |  | 4 | 25 | 0.60754 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_221_0_line_8 |  | 4 | 30 | 0.60962 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_221_0_line_9 |  | 5 | 7 | 0.064497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_221_0_line_10 |  | 8 | 9 | 0.040659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_221_0_line_11 |  | 8 | 10 | 0.36386 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_221_0_line_12 |  | 9 | 17 | 0.17837 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_221_0_line_13 |  | 10 | 18 | 1.0519 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_221_0_line_14 |  | 10 | 19 | 0.10661 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_221_0_line_15 |  | 10 | 20 | 0.035119 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_221_0_line_16 |  | 10 | 11 | 0.21291 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_221_0_line_17 |  | 11 | 12 | 0.006096 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_221_0_line_18 |  | 13 | 14 | 0.010984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_221_0_line_19 |  | 13 | 15 | 0.082231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_221_0_line_20 |  | 15 | 16 | 0.0041281 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_221_0_line_21 |  | 16 | 21 | 0.021709 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_221_0_line_22 |  | 18 | 48 | 0.014034 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_221_0_line_23 |  | 19 | 50 | 0.043609 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_221_0_line_24 |  | 20 | 49 | 0.010935 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_221_0_line_25 |  | 21 | 49 | 0.045089 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_221_0_line_26 |  | 22 | 23 | 0.041101 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_221_0_line_27 |  | 22 | 24 | 0.061059 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_221_0_line_28 |  | 24 | 25 | 0.0090813 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_221_0_line_29 |  | 25 | 26 | 0.093721 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
30 | MV_221_0_line_30 |  | 26 | 33 | 0.018861 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_221_0_line_31 |  | 26 | 34 | 0.058478 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_221_0_line_32 |  | 26 | 27 | 0.081722 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
33 | MV_221_0_line_33 |  | 27 | 28 | 0.073204 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
34 | MV_221_0_line_34 |  | 27 | 29 | 0.049075 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_221_0_line_35 |  | 28 | 69 | 0.11542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_221_0_line_36 |  | 28 | 63 | 0.27053 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
37 | MV_221_0_line_37 |  | 28 | 66 | 0.41146 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_221_0_line_38 |  | 30 | 31 | 1.1196 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_221_0_line_39 |  | 30 | 32 | 0.062202 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_221_0_line_40 |  | 31 | 51 | 0.029439 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_221_0_line_41 |  | 31 | 52 | 0.37313 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_221_0_line_42 |  | 31 | 53 | 0.69092 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_221_0_line_43 |  | 35 | 36 | 0.036108 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_221_0_line_44 |  | 35 | 37 | 0.34617 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_221_0_line_45 |  | 37 | 38 | 0.32761 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_221_0_line_46 |  | 38 | 39 | 0.39762 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_221_0_line_47 |  | 38 | 40 | 0.046395 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_221_0_line_48 |  | 39 | 46 | 0.010138 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
49 | MV_221_0_line_49 |  | 39 | 42 | 0.34843 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
50 | MV_221_0_line_50 |  | 40 | 47 | 0.22961 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_221_0_line_51 |  | 41 | 42 | 0.61412 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_221_0_line_52 |  | 41 | 43 | 0.6025 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_221_0_line_53 |  | 41 | 44 | 0.048381 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_221_0_line_54 |  | 42 | 45 | 0.039203 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_221_0_line_55 |  | 43 | 56 | 0.24375 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_221_0_line_56 |  | 43 | 57 | 0.006675 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_221_0_line_57 |  | 46 | 60 | 0.031411 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
58 | MV_221_0_line_58 |  | 47 | 70 | 0.034235 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_221_0_line_59 |  | 52 | 54 | 0.0075627 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_221_0_line_60 |  | 53 | 55 | 0.04528 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_221_0_line_61 |  | 56 | 58 | 0.072861 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_221_0_line_62 |  | 56 | 59 | 0.59224 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_221_0_line_63 |  | 59 | 61 | 0.012495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_221_0_line_64 |  | 60 | 62 | 0.93167 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
65 | MV_221_0_line_65 |  | 61 | 74 | 0.055979 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_221_0_line_66 |  | 62 | 63 | 0.43006 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
67 | MV_221_0_line_67 |  | 62 | 64 | 0.037454 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_221_0_line_68 |  | 63 | 65 | 0.56878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_221_0_line_69 |  | 66 | 67 | 0.037179 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_221_0_line_70 |  | 66 | 68 | 0.026004 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_221_0_line_71 |  | 67 | 71 | 0.17877 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_221_0_line_72 |  | 68 | 72 | 0.037188 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_221_0_line_73 |  | 72 | 73 | 0.056665 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_221_0_trafo_40 | 25 MVA 110/20 kV | 75 | 63 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2663544.9712 | 1212505.8651
1 | 2663545.084 | 1212491.0016
2 | 2663469.7157 | 1212435.3986
3 | 2663309.8709 | 1212605.6159
4 | 2663310.8695 | 1212676.1365
5 | 2663290.655 | 1212406.8234
6 | 2663489.2042 | 1212435.3392
7 | 2663299.0565 | 1212352.5681
8 | 2663718.6871 | 1212570.6686
9 | 2663756.9433 | 1212564.6959
10 | 2663403.4074 | 1212752.3104
11 | 2663564.4493 | 1212891.5874
12 | 2663560.8113 | 1212896.485
13 | 2663542.8077 | 1212714.5814
14 | 2663531.7914 | 1212714.6085
15 | 2663503.6717 | 1212740.5028
16 | 2663499.5437 | 1212740.4749
17 | 2663872.181 | 1212428.5447
18 | 2663160.4759 | 1213298.4138
19 | 2663485.177 | 1212820.7109
20 | 2663437.8564 | 1212759.1363
21 | 2663477.8355 | 1212740.3278
22 | 2663037.1244 | 1212975.8591
23 | 2663004.2068 | 1213000.4709
24 | 2663073.6871 | 1213024.7607
25 | 2663079.125 | 1213032.0338
26 | 2663125.3927 | 1213109.2484
27 | 2663064.4836 | 1213156.511
28 | 2663005.5532 | 1213199.9262
29 | 2663035.4909 | 1213116.9171
30 | 2662861.2906 | 1212639.5938
31 | 2662333.9024 | 1212049.9333
32 | 2662823.2565 | 1212688.8123
33 | 2663139.3374 | 1213120.8772
34 | 2663103.7267 | 1213057.3246
35 | 2662075.5578 | 1213191.6276
36 | 2662064.8251 | 1213157.3084
37 | 2661891.2311 | 1213484.6366
38 | 2662076.0861 | 1213716.5329
39 | 2662260.801 | 1213692.8099
40 | 2662040.4696 | 1213746.3807
41 | 2662586.9346 | 1214149.259
42 | 2662349.0399 | 1213877.6118
43 | 2662914.3143 | 1214125.2215
44 | 2662549.9883 | 1214180.613
45 | 2662333.5553 | 1213913.6388
46 | 2662259.0823 | 1213682.8192
47 | 2662031.8763 | 1213975.8322
48 | 2663146.5206 | 1213299.9003
49 | 2663439.5667 | 1212748.3368
50 | 2663471.7336 | 1212855.8779
51 | 2662349.9884 | 1212074.5609
52 | 2662193.5172 | 1212169.7528
53 | 2662075.8264 | 1211985.0144
54 | 2662199.6152 | 1212165.2797
55 | 2662038.8555 | 1212011.157
56 | 2662775.9741 | 1213982.1315
57 | 2662918.8474 | 1214120.3108
58 | 2662790.439 | 1213912.6298
59 | 2662842.527 | 1213626.1354
60 | 2662254.4008 | 1213651.7624
61 | 2662853.9534 | 1213630.2805
62 | 2662515.6571 | 1213137.5009
63 | 2662815.4924 | 1213218.0776
64 | 2662482.8878 | 1213119.7477
65 | 2662537.1968 | 1212769.8881
66 | 2662959.6305 | 1213481.3144
67 | 2662982.6576 | 1213509.8083
68 | 2662943.4658 | 1213460.9475
69 | 2662920.863 | 1213130.2697
70 | 2662027.7622 | 1214008.4206
71 | 2663094.0418 | 1213649.546
72 | 2662919.9831 | 1213432.1119
73 | 2662884.2398 | 1213388.1426
74 | 2662903.7453 | 1213604.6986
75 | 2662815.4924 | 1213218.0776

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99549 | 0.011789 | 0.30288 | 0.14669
1 | 0.99549 | 0.011735 | 0 | 0
2 | 0.99556 | 0.011181 | 0 | 0
3 | 0.99587 | 0.013227 | 0.31346 | 0.15182
4 | 0.99603 | 0.014288 | 0 | 0
5 | 0.99579 | 0.012738 | 0 | 0
6 | 0.99555 | 0.01127 | 0.38297 | 0.18548
7 | 0.99578 | 0.012882 | 0.18916 | 0.091616
8 | 0.99535 | 0.015334 | 0 | 0
9 | 0.99533 | 0.01555 | 0.16633 | 0.080556
10 | 0.99566 | 0.017351 | 0 | 0
11 | 0.9956 | 0.016971 | 0 | 0
12 | 0.9956 | 0.016982 | 0.14431 | 0.069894
13 | 0.99555 | 0.017591 | 0 | 0
14 | 0.99555 | 0.017625 | 0.25861 | 0.12525
15 | 0.99558 | 0.01734 | 0 | 0
16 | 0.99558 | 0.017328 | 0.090018 | 0.043598
17 | 0.99523 | 0.014943 | 0.27849 | 0.13488
18 | 0.99552 | 0.017919 | 0 | 0
19 | 0.99563 | 0.017113 | 0 | 0
20 | 0.99561 | 0.017017 | 0.40068 | 0.19406
21 | 0.99559 | 0.01724 | 0 | 0
22 | 0.99873 | -0.0067891 | 0.33016 | 0.1599
23 | 0.99872 | -0.0067482 | 0.085443 | 0.041382
24 | 0.99876 | -0.0070868 | 0.14031 | 0.067957
25 | 0.99877 | -0.0071459 | 0 | 0
26 | 0.99897 | -0.0046955 | 0 | 0
27 | 0.99909 | -0.0040967 | 0 | 0
28 | 0.99921 | -0.0035311 | 0 | 0
29 | 0.99908 | -0.0039412 | 0.26752 | 0.12957
30 | 0.99546 | 0.017417 | 0 | 0
31 | 0.99454 | 0.023448 | 0 | 0
32 | 0.99545 | 0.017349 | 0.088976 | 0.043093
33 | 0.99897 | -0.004651 | 0.19792 | 0.095857
34 | 0.99896 | -0.0045369 | 0.22989 | 0.11134
35 | 0.9965 | -0.0076259 | 0.30349 | 0.14699
36 | 0.9965 | -0.0075859 | 0.094338 | 0.04569
37 | 0.99677 | -0.0059191 | 0 | 0
38 | 0.99694 | -0.0073806 | 0 | 0
39 | 0.99748 | -0.012078 | 0 | 0
40 | 0.9969 | -0.0070119 | 0.37043 | 0.17941
41 | 0.99376 | 0.0053973 | 0 | 0
42 | 0.99671 | -0.02056 | 0 | 0
43 | 0.99096 | 0.0307 | 0 | 0
44 | 0.99375 | 0.0054688 | 0.12501 | 0.060546
45 | 0.9967 | -0.02043 | 0.27841 | 0.13484
46 | 0.9975 | -0.011764 | 0.35376 | 0.17133
47 | 0.99676 | -0.0078638 | 0 | 0
48 | 0.99552 | 0.0179 | 0.11114 | 0.05383
49 | 0.99561 | 0.01706 | 0 | 0
50 | 0.99562 | 0.017203 | 0.17542 | 0.08496
51 | 0.99453 | 0.02355 | 0.28931 | 0.14012
52 | 0.9945 | 0.023697 | 0 | 0
53 | 0.99429 | 0.025472 | 0 | 0
54 | 0.9945 | 0.023704 | 0.079718 | 0.038609
55 | 0.99426 | 0.025314 | 0.28594 | 0.13849
56 | 0.98991 | 0.04033 | 0 | 0
57 | 0.99096 | 0.030722 | 0.2713 | 0.1314
58 | 0.9899 | 0.040456 | 0.14718 | 0.071281
59 | 0.98747 | 0.063186 | 0 | 0
60 | 0.99756 | -0.01152 | 0 | 0
61 | 0.98742 | 0.063675 | 2.563 | 1.2413
62 | 0.99922 | -0.0038584 | 0 | 0
63 | 1 | 0 | -17.0399 | -7.8786
64 | 0.99922 | -0.0038112 | 0.10754 | 0.052084
65 | 0.99825 | 0.016266 | 2.4223 | 1.1732
66 | 0.99731 | 0.013997 | 0 | 0
67 | 0.99731 | 0.014017 | 0 | 0
68 | 0.99719 | 0.015103 | 1.0092 | 0.48879
69 | 0.99913 | -0.0027908 | 0.54258 | 0.26278
70 | 0.99675 | -0.0077417 | 0.29838 | 0.14451
71 | 0.99729 | 0.014139 | 0.068083 | 0.032974
72 | 0.99707 | 0.016235 | 2.3172 | 1.1223
73 | 0.99706 | 0.016385 | 0.22241 | 0.10772
74 | 0.98737 | 0.064109 | 0.63543 | 0.30775
75 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.30288 | -0.14669 | 0.30289 | 0.14634 | 1.8894e-06 | -0.00035121 | 0.009759 | 0.0097546 | 0.009759 | 0.99549 | 0.011789 | 0.99549 | 0.011735 | 4.4359
1 | -0.30289 | -0.14634 | 0.30291 | 0.14262 | 1.9938e-05 | -0.0037261 | 0.0097546 | 0.009708 | 0.0097546 | 0.99549 | 0.011735 | 0.99556 | 0.011181 | 4.4339
2 | 0.38298 | 0.18502 | -0.38297 | -0.18548 | 3.9477e-06 | -0.00045867 | 0.012333 | 0.012339 | 0.012339 | 0.99556 | 0.011181 | 0.99555 | 0.01127 | 5.6086
3 | -0.68588 | -0.32764 | 0.68609 | 0.32749 | 0.00020208 | -0.0001498 | 0.022041 | 0.022037 | 0.022041 | 0.99556 | 0.011181 | 0.99587 | 0.013227 | 10.4956
4 | -1.1887 | -0.56917 | 1.1889 | 0.5692 | 0.0001834 | 3.1362e-05 | 0.038204 | 0.038203 | 0.038204 | 0.99587 | 0.013227 | 0.99603 | 0.014288 | 18.1925
5 | 0.18918 | 0.089862 | -0.18917 | -0.09009 | 1.3122e-05 | -0.00022822 | 0.006071 | 0.006074 | 0.006074 | 0.99587 | 0.013227 | 0.99579 | 0.012738 | 2.8924
6 | 1.6259 | 0.75094 | -1.6253 | -0.75492 | 0.00063364 | -0.0039793 | 0.051906 | 0.051957 | 0.051957 | 0.99603 | 0.014288 | 0.99566 | 0.017351 | 23.6167
7 | -3.5599 | -1.6138 | 3.5703 | 1.6024 | 0.010392 | -0.011348 | 0.11328 | 0.11311 | 0.11328 | 0.99603 | 0.014288 | 0.99877 | -0.0071459 | 51.4919
8 | 0.74512 | 0.29364 | -0.74467 | -0.30794 | 0.00044142 | -0.014301 | 0.023212 | 0.023368 | 0.023368 | 0.99603 | 0.014288 | 0.99546 | 0.017417 | 10.622
9 | 0.18917 | 0.09009 | -0.18916 | -0.091616 | 3.1866e-06 | -0.001526 | 0.006074 | 0.0060932 | 0.0060932 | 0.99579 | 0.012738 | 0.99578 | 0.012882 | 2.7696
10 | 0.44485 | 0.21428 | -0.44484 | -0.21524 | 1.1141e-05 | -0.00095844 | 0.014321 | 0.014333 | 0.014333 | 0.99535 | 0.015334 | 0.99533 | 0.01555 | 6.5149
11 | -0.44485 | -0.21428 | 0.44499 | 0.21393 | 0.0001329 | -0.00034724 | 0.014321 | 0.014315 | 0.014321 | 0.99535 | 0.015334 | 0.99566 | 0.017351 | 6.8193
12 | 0.27851 | 0.13468 | -0.27849 | -0.13488 | 2.5594e-05 | -0.00019491 | 0.0089727 | 0.0089754 | 0.0089754 | 0.99533 | 0.01555 | 0.99523 | 0.014943 | 4.274
13 | 0.11116 | 0.028924 | -0.11114 | -0.053813 | 1.6607e-05 | -0.02489 | 0.0033302 | 0.0035808 | 0.0035808 | 0.99566 | 0.017351 | 0.99552 | 0.017919 | 1.6276
14 | 0.17543 | 0.083806 | -0.17542 | -0.083928 | 6.0368e-06 | -0.00012238 | 0.0056368 | 0.0056384 | 0.0056384 | 0.99566 | 0.017351 | 0.99563 | 0.017113 | 2.685
15 | 0.74937 | 0.35875 | -0.74933 | -0.35877 | 3.6306e-05 | -1.8819e-05 | 0.024088 | 0.024089 | 0.024089 | 0.99566 | 0.017351 | 0.99561 | 0.017017 | 11.4707
16 | 0.14432 | 0.069503 | -0.14431 | -0.06975 | 8.1879e-06 | -0.00024684 | 0.0046443 | 0.0046475 | 0.0046475 | 0.99566 | 0.017351 | 0.9956 | 0.016971 | 2.2131
17 | 0.14431 | 0.06975 | -0.14431 | -0.069894 | 1.7585e-07 | -0.00014422 | 0.0046475 | 0.0046493 | 0.0046493 | 0.9956 | 0.016971 | 0.9956 | 0.016982 | 2.1133
18 | 0.25861 | 0.12499 | -0.25861 | -0.12525 | 1.0176e-06 | -0.00025962 | 0.0083287 | 0.008332 | 0.008332 | 0.99555 | 0.017591 | 0.99555 | 0.017625 | 3.7873
19 | -0.25861 | -0.12499 | 0.25862 | 0.12305 | 7.5926e-06 | -0.0019437 | 0.0083287 | 0.0083043 | 0.0083287 | 0.99555 | 0.017591 | 0.99558 | 0.01734 | 3.7858
20 | -0.25862 | -0.12305 | 0.25862 | 0.12295 | 3.7997e-07 | -9.7581e-05 | 0.0083043 | 0.0083031 | 0.0083043 | 0.99558 | 0.01734 | 0.99558 | 0.017328 | 3.7747
21 | -0.34863 | -0.16655 | 0.34864 | 0.16603 | 3.6354e-06 | -0.00051267 | 0.011203 | 0.011197 | 0.011203 | 0.99558 | 0.017328 | 0.99559 | 0.01724 | 5.0923
22 | 0.11114 | 0.053813 | -0.11114 | -0.05383 | 3.2064e-07 | -1.6403e-05 | 0.0035808 | 0.003581 | 0.003581 | 0.99552 | 0.017919 | 0.99552 | 0.0179 | 1.7052
23 | 0.17542 | 0.083928 | -0.17542 | -0.08496 | 1.8551e-06 | -0.0010316 | 0.0056384 | 0.0056514 | 0.0056514 | 0.99563 | 0.017113 | 0.99562 | 0.017203 | 2.5688
24 | 0.34865 | 0.16471 | -0.34865 | -0.16497 | 1.8253e-06 | -0.00025826 | 0.01118 | 0.011183 | 0.011183 | 0.99561 | 0.017017 | 0.99561 | 0.01706 | 5.0834
25 | -0.34864 | -0.16603 | 0.34865 | 0.16497 | 7.5374e-06 | -0.0010649 | 0.011197 | 0.011183 | 0.011197 | 0.99559 | 0.01724 | 0.99561 | 0.01706 | 5.0894
26 | 0.085443 | 0.040403 | -0.085443 | -0.041382 | 4.1132e-07 | -0.00097872 | 0.0027319 | 0.0027441 | 0.0027441 | 0.99873 | -0.0067891 | 0.99872 | -0.0067482 | 1.2473
27 | -0.41561 | -0.20031 | 0.41562 | 0.19886 | 1.4476e-05 | -0.0014499 | 0.013335 | 0.013317 | 0.013335 | 0.99873 | -0.0067891 | 0.99876 | -0.0070868 | 6.0615
28 | -0.55593 | -0.26682 | 0.55594 | 0.2666 | 3.8506e-06 | -0.00021515 | 0.017823 | 0.01782 | 0.017823 | 0.99876 | -0.0070868 | 0.99877 | -0.0071459 | 8.1014
29 | -4.1263 | -1.869 | 4.127 | 1.8664 | 0.00077573 | -0.0026442 | 0.13093 | 0.13089 | 0.13093 | 0.99877 | -0.0071459 | 0.99897 | -0.0046955 | 36.1674
30 | 0.19792 | 0.095408 | -0.19792 | -0.095857 | 1.0159e-06 | -0.00044911 | 0.0063492 | 0.0063548 | 0.0063548 | 0.99897 | -0.0046955 | 0.99897 | -0.004651 | 2.8886
31 | 0.22989 | 0.10995 | -0.22989 | -0.11134 | 4.2433e-06 | -0.0013921 | 0.0073638 | 0.0073813 | 0.0073813 | 0.99897 | -0.0046955 | 0.99896 | -0.0045369 | 3.3551
32 | -4.5548 | -2.0717 | 4.5554 | 2.0669 | 0.00052776 | -0.0048277 | 0.1446 | 0.14454 | 0.1446 | 0.99897 | -0.0046955 | 0.99909 | -0.0040967 | 22.6642
33 | -4.8229 | -2.1953 | 4.8234 | 2.191 | 0.00053007 | -0.0042933 | 0.15311 | 0.15305 | 0.15311 | 0.99909 | -0.0040967 | 0.99921 | -0.0035311 | 23.9982
34 | 0.26752 | 0.1284 | -0.26752 | -0.12957 | 4.8244e-06 | -0.0011681 | 0.0085739 | 0.0085886 | 0.0085886 | 0.99909 | -0.0040967 | 0.99908 | -0.0039412 | 3.9039
35 | 0.54263 | 0.26005 | -0.54258 | -0.26278 | 4.6656e-05 | -0.0027373 | 0.017384 | 0.017418 | 0.017418 | 0.99921 | -0.0035311 | 0.99913 | -0.0027908 | 7.9175
36 | -8.9912 | -4.1875 | 8.998 | 4.1744 | 0.006859 | -0.013122 | 0.28655 | 0.28634 | 0.28655 | 0.99921 | -0.0035311 | 1 | 0 | 44.9136
37 | 3.6251 | 1.7364 | -3.6177 | -1.744 | 0.0074152 | -0.0075902 | 0.11613 | 0.11625 | 0.11625 | 0.99921 | -0.0035311 | 0.99731 | 0.013997 | 52.8405
38 | 0.6557 | 0.26492 | -0.65506 | -0.29119 | 0.00063764 | -0.026275 | 0.020508 | 0.020808 | 0.020808 | 0.99546 | 0.017417 | 0.99454 | 0.023448 | 9.4581
39 | 0.088976 | 0.04302 | -0.088976 | -0.043093 | 9.1061e-07 | -7.3013e-05 | 0.002866 | 0.0028669 | 0.0028669 | 0.99546 | 0.017417 | 0.99545 | 0.017349 | 1.3652
40 | 0.28931 | 0.13943 | -0.28931 | -0.14012 | 3.4184e-06 | -0.00069421 | 0.0093219 | 0.0093307 | 0.0093307 | 0.99454 | 0.023448 | 0.99453 | 0.02355 | 4.2412
41 | 0.079722 | 0.02962 | -0.079719 | -0.038431 | 3.1532e-06 | -0.0088105 | 0.0024686 | 0.0025689 | 0.0025689 | 0.99454 | 0.023448 | 0.9945 | 0.023697 | 1.1677
42 | 0.28602 | 0.12215 | -0.28595 | -0.13844 | 7.6771e-05 | -0.01629 | 0.0090275 | 0.0092238 | 0.0092238 | 0.99454 | 0.023448 | 0.99429 | 0.025472 | 4.1926
43 | 0.094338 | 0.044834 | -0.094338 | -0.04569 | 4.4289e-07 | -0.00085597 | 0.0030258 | 0.0030365 | 0.0030365 | 0.9965 | -0.0076259 | 0.9965 | -0.0075859 | 1.3802
44 | -0.39783 | -0.19182 | 0.39793 | 0.19147 | 0.00010092 | -0.00034727 | 0.012794 | 0.012789 | 0.012794 | 0.9965 | -0.0076259 | 0.99677 | -0.0059191 | 6.0925
45 | -0.39793 | -0.19147 | 0.398 | 0.18372 | 7.0996e-05 | -0.0077519 | 0.012789 | 0.012693 | 0.012789 | 0.99677 | -0.0059191 | 0.99694 | -0.0073806 | 5.8133
46 | -1.0669 | -0.50549 | 1.0675 | 0.49623 | 0.0006182 | -0.0092572 | 0.034185 | 0.034069 | 0.034185 | 0.99694 | -0.0073806 | 0.99748 | -0.012078 | 15.5386
47 | 0.66888 | 0.32177 | -0.66885 | -0.32286 | 2.863e-05 | -0.0010924 | 0.021493 | 0.021507 | 0.021507 | 0.99694 | -0.0073806 | 0.9969 | -0.0070119 | 9.7757
48 | -5.1263 | -2.3904 | 5.1264 | 2.3901 | 0.0001312 | -0.00025071 | 0.16369 | 0.16369 | 0.16369 | 0.99748 | -0.012078 | 0.9975 | -0.011764 | 45.219
49 | 4.0588 | 1.8941 | -4.0559 | -1.904 | 0.0028309 | -0.0098267 | 0.12962 | 0.12977 | 0.12977 | 0.99748 | -0.012078 | 0.99671 | -0.02056 | 35.848
50 | 0.29842 | 0.14345 | -0.29839 | -0.1437 | 3.7623e-05 | -0.00024881 | 0.0095882 | 0.0095916 | 0.0095916 | 0.9969 | -0.0070119 | 0.99676 | -0.0078638 | 4.5674
51 | -3.7655 | -1.781 | 3.7775 | 1.77 | 0.011986 | -0.010968 | 0.121 | 0.12082 | 0.121 | 0.99376 | 0.0053973 | 0.99671 | -0.02056 | 55.0008
52 | 3.6405 | 1.7216 | -3.6295 | -1.7325 | 0.011024 | -0.010896 | 0.11698 | 0.11716 | 0.11716 | 0.99376 | 0.0053973 | 0.99096 | 0.0307 | 53.2536
53 | 0.12501 | 0.059405 | -0.12501 | -0.060546 | 1.0478e-06 | -0.0011405 | 0.0040206 | 0.0040349 | 0.0040349 | 0.99376 | 0.0053973 | 0.99375 | 0.0054688 | 1.8341
54 | 0.27842 | 0.13391 | -0.27841 | -0.13484 | 4.1958e-06 | -0.00092861 | 0.008948 | 0.0089597 | 0.0089597 | 0.99671 | -0.02056 | 0.9967 | -0.02043 | 4.0726
55 | 3.3582 | 1.6013 | -3.3544 | -1.6058 | 0.0038247 | -0.0045745 | 0.10838 | 0.10845 | 0.10845 | 0.99096 | 0.0307 | 0.98991 | 0.04033 | 49.2956
56 | 0.27131 | 0.13124 | -0.2713 | -0.1314 | 6.8702e-07 | -0.0001563 | 0.0087795 | 0.0087815 | 0.0087815 | 0.99096 | 0.0307 | 0.99096 | 0.030722 | 3.9916
57 | -5.4801 | -2.5614 | 5.4804 | 2.5596 | 0.00029742 | -0.0017964 | 0.17506 | 0.17504 | 0.17506 | 0.9975 | -0.011764 | 0.99756 | -0.01152 | 27.4393
58 | 0.29839 | 0.1437 | -0.29838 | -0.14451 | 4.2092e-06 | -0.00081086 | 0.0095916 | 0.0096018 | 0.0096018 | 0.99676 | -0.0078638 | 0.99675 | -0.0077417 | 4.3645
59 | 0.079719 | 0.038431 | -0.079718 | -0.038609 | 6.6678e-08 | -0.00017857 | 0.0025689 | 0.0025711 | 0.0025711 | 0.9945 | 0.023697 | 0.9945 | 0.023704 | 1.1687
60 | 0.28595 | 0.13844 | -0.28594 | -0.13849 | 6.8643e-06 | -4.9139e-05 | 0.0092238 | 0.0092245 | 0.0092245 | 0.99429 | 0.025472 | 0.99426 | 0.025314 | 4.3926
61 | 0.14718 | 0.069577 | -0.14718 | -0.071281 | 2.2022e-06 | -0.001704 | 0.0047475 | 0.0047689 | 0.0047689 | 0.98991 | 0.04033 | 0.9899 | 0.040456 | 2.1677
62 | 3.2072 | 1.5363 | -3.1987 | -1.5475 | 0.0085171 | -0.011296 | 0.1037 | 0.10388 | 0.10388 | 0.98991 | 0.04033 | 0.98747 | 0.063186 | 47.2172
63 | 3.1987 | 1.5475 | -3.1985 | -1.5478 | 0.00018 | -0.00023749 | 0.10388 | 0.10388 | 0.10388 | 0.98747 | 0.063186 | 0.98742 | 0.063675 | 47.2189
64 | -5.4804 | -2.5596 | 5.4892 | 2.5062 | 0.0087847 | -0.053404 | 0.17504 | 0.17433 | 0.17504 | 0.99756 | -0.01152 | 0.99922 | -0.0038584 | 27.4355
65 | 0.63546 | 0.30646 | -0.63543 | -0.30775 | 3.1818e-05 | -0.0012936 | 0.020626 | 0.020642 | 0.020642 | 0.98742 | 0.063675 | 0.98737 | 0.064109 | 9.3828
66 | -5.5968 | -2.5574 | 5.601 | 2.5328 | 0.004192 | -0.02464 | 0.17777 | 0.17745 | 0.17777 | 0.99922 | -0.0038584 | 1 | 0 | 27.8639
67 | 0.10754 | 0.051191 | -0.10754 | -0.052084 | 5.939e-07 | -0.00089268 | 0.0034409 | 0.003452 | 0.003452 | 0.99922 | -0.0038584 | 0.99922 | -0.0038112 | 1.5691
68 | 2.4269 | 1.161 | -2.4223 | -1.1732 | 0.0045897 | -0.012195 | 0.077661 | 0.077831 | 0.077831 | 1 | 0 | 0.99825 | 0.016266 | 35.3779
69 | 0.068085 | 0.027846 | -0.068084 | -0.028729 | 2.2604e-07 | -0.00088285 | 0.0021292 | 0.002139 | 0.002139 | 0.99731 | 0.013997 | 0.99731 | 0.014017 | 0.97227
70 | 3.5496 | 1.7162 | -3.5492 | -1.7167 | 0.00045216 | -0.00048333 | 0.11412 | 0.11413 | 0.11413 | 0.99731 | 0.013997 | 0.99719 | 0.015103 | 51.878
71 | 0.068084 | 0.028729 | -0.068083 | -0.032974 | 1.1172e-06 | -0.004245 | 0.002139 | 0.0021897 | 0.0021897 | 0.99731 | 0.014017 | 0.99729 | 0.014139 | 0.99532
72 | 2.54 | 1.2279 | -2.5396 | -1.2287 | 0.00033118 | -0.00078458 | 0.08167 | 0.081681 | 0.081681 | 0.99719 | 0.015103 | 0.99707 | 0.016235 | 37.1277
73 | 0.22241 | 0.10637 | -0.22241 | -0.10772 | 3.8633e-06 | -0.0013439 | 0.0071379 | 0.0071548 | 0.0071548 | 0.99707 | 0.016235 | 0.99706 | 0.016385 | 3.2522

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 17.0399 | 7.8786

## res_load
| p_mw | q_mvar
0 | 0.30288 | 0.14669
1 | 0.31346 | 0.15182
2 | 0.38297 | 0.18548
3 | 0.18916 | 0.091616
4 | 0.16633 | 0.080556
5 | 0.14431 | 0.069894
6 | 0.25861 | 0.12525
7 | 0.090018 | 0.043598
8 | 0.27849 | 0.13488
9 | 0.40068 | 0.19406
10 | 0.33016 | 0.1599
11 | 0.085443 | 0.041382
12 | 0.14031 | 0.067957
13 | 0.26752 | 0.12957
14 | 0.088976 | 0.043093
15 | 0.19792 | 0.095857
16 | 0.22989 | 0.11134
17 | 0.30349 | 0.14699
18 | 0.094338 | 0.04569
19 | 0.37043 | 0.17941
20 | 0.12501 | 0.060546
21 | 0.27841 | 0.13484
22 | 0.35376 | 0.17133
23 | 0.11114 | 0.05383
24 | 0.17542 | 0.08496
25 | 0.28931 | 0.14012
26 | 0.079718 | 0.038609
27 | 0.28594 | 0.13849
28 | 0.2713 | 0.1314
29 | 0.14718 | 0.071281
30 | 2.563 | 1.2413
31 | 0.10754 | 0.052084
32 | 2.4223 | 1.1732
33 | 1.0092 | 0.48879
34 | 0.54258 | 0.26278
35 | 0.29838 | 0.14451
36 | 0.068083 | 0.032974
37 | 2.3172 | 1.1223
38 | 0.22241 | 0.10772
39 | 0.63543 | 0.30775

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1