## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_233_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_233_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_233_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_233_0_node_4 | 20 | n |  | TRUE
4 | bus_MV_233_0_node_126 | 20 | n |  | TRUE
5 | bus_MV_233_0_node_3 | 20 | n |  | TRUE
6 | bus_MV_233_0_node_6 | 20 | n |  | TRUE
7 | bus_MV_233_0_node_5 | 20 | n |  | TRUE
8 | bus_MV_233_0_node_122 | 20 | n |  | TRUE
9 | bus_MV_233_0_node_46 | 20 | n |  | TRUE
10 | bus_MV_233_0_node_78 | 20 | n |  | TRUE
11 | bus_MV_233_0_node_13 | 20 | n |  | TRUE
12 | bus_MV_233_0_node_14 | 20 | n |  | TRUE
13 | bus_MV_233_0_node_123 | 20 | n |  | TRUE
14 | bus_MV_233_0_node_79 | 20 | n |  | TRUE
15 | bus_MV_233_0_node_44 | 20 | n |  | TRUE
16 | bus_MV_233_0_node_29 | 20 | n |  | TRUE
17 | bus_MV_233_0_node_30 | 20 | n |  | TRUE
18 | bus_MV_233_0_node_31 | 20 | n |  | TRUE
19 | bus_MV_233_0_node_75 | 20 | n |  | TRUE
20 | bus_MV_233_0_node_67 | 20 | n |  | TRUE
21 | bus_MV_233_0_node_74 | 20 | n |  | TRUE
22 | bus_MV_233_0_node_7 | 20 | n |  | TRUE
23 | bus_MV_233_0_node_9 | 20 | n |  | TRUE
24 | bus_MV_233_0_node_10 | 20 | n |  | TRUE
25 | bus_MV_233_0_node_8 | 20 | n |  | TRUE
26 | bus_MV_233_0_node_11 | 20 | n |  | TRUE
27 | bus_MV_233_0_node_12 | 20 | n |  | TRUE
28 | bus_MV_233_0_node_119 | 20 | n |  | TRUE
29 | bus_MV_233_0_node_66 | 20 | n |  | TRUE
30 | bus_MV_233_0_node_115 | 20 | n |  | TRUE
31 | bus_MV_233_0_node_64 | 20 | n |  | TRUE
32 | bus_MV_233_0_node_42 | 20 | n |  | TRUE
33 | bus_MV_233_0_node_15 | 20 | n |  | TRUE
34 | bus_MV_233_0_node_16 | 20 | n |  | TRUE
35 | bus_MV_233_0_node_40 | 20 | n |  | TRUE
36 | bus_MV_233_0_node_127 | 20 | n |  | TRUE
37 | bus_MV_233_0_node_76 | 20 | n |  | TRUE
38 | bus_MV_233_0_node_45 | 20 | n |  | TRUE
39 | bus_MV_233_0_node_17 | 20 | n |  | TRUE
40 | bus_MV_233_0_node_18 | 20 | n |  | TRUE
41 | bus_MV_233_0_node_19 | 20 | n |  | TRUE
42 | bus_MV_233_0_node_20 | 20 | n |  | TRUE
43 | bus_MV_233_0_node_39 | 20 | n |  | TRUE
44 | bus_MV_233_0_node_38 | 20 | n |  | TRUE
45 | bus_MV_233_0_node_21 | 20 | n |  | TRUE
46 | bus_MV_233_0_node_22 | 20 | n |  | TRUE
47 | bus_MV_233_0_node_23 | 20 | n |  | TRUE
48 | bus_MV_233_0_node_24 | 20 | n |  | TRUE
49 | bus_MV_233_0_node_25 | 20 | n |  | TRUE
50 | bus_MV_233_0_node_121 | 20 | n |  | TRUE
51 | bus_MV_233_0_node_120 | 20 | n |  | TRUE
52 | bus_MV_233_0_node_80 | 20 | n |  | TRUE
53 | bus_MV_233_0_node_125 | 20 | n |  | TRUE
54 | bus_MV_233_0_node_129 | 20 | n |  | TRUE
55 | bus_MV_233_0_node_62 | 20 | n |  | TRUE
56 | bus_MV_233_0_node_81 | 20 | n |  | TRUE
57 | bus_MV_233_0_node_26 | 20 | n |  | TRUE
58 | bus_MV_233_0_node_27 | 20 | n |  | TRUE
59 | bus_MV_233_0_node_28 | 20 | n |  | TRUE
60 | bus_MV_233_0_node_118 | 20 | n |  | TRUE
61 | bus_MV_233_0_node_117 | 20 | n |  | TRUE
62 | bus_MV_233_0_node_83 | 20 | n |  | TRUE
63 | bus_MV_233_0_node_33 | 20 | n |  | TRUE
64 | bus_MV_233_0_node_32 | 20 | n |  | TRUE
65 | bus_MV_233_0_node_77 | 20 | n |  | TRUE
66 | bus_MV_233_0_node_124 | 20 | n |  | TRUE
67 | bus_MV_233_0_node_84 | 20 | n |  | TRUE
68 | bus_MV_233_0_node_85 | 20 | n |  | TRUE
69 | bus_MV_233_0_node_91 | 20 | n |  | TRUE
70 | bus_MV_233_0_node_98 | 20 | n |  | TRUE
71 | bus_MV_233_0_node_51 | 20 | n |  | TRUE
72 | bus_MV_233_0_node_34 | 20 | n |  | TRUE
73 | bus_MV_233_0_node_35 | 20 | n |  | TRUE
74 | bus_MV_233_0_node_37 | 20 | n |  | TRUE
75 | bus_MV_233_0_node_53 | 20 | n |  | TRUE
76 | bus_MV_233_0_node_56 | 20 | n |  | TRUE
77 | bus_MV_233_0_node_55 | 20 | n |  | TRUE
78 | bus_MV_233_0_node_131 | 20 | n |  | TRUE
79 | bus_MV_233_0_node_41 | 20 | n |  | TRUE
80 | bus_MV_233_0_node_43 | 20 | n |  | TRUE
81 | bus_MV_233_0_node_47 | 20 | n |  | TRUE
82 | bus_MV_233_0_node_48 | 20 | n |  | TRUE
83 | bus_MV_233_0_node_105 | 20 | n |  | TRUE
84 | bus_MV_233_0_node_112 | 20 | n |  | TRUE
85 | bus_MV_233_0_node_113 | 20 | n |  | TRUE
86 | bus_MV_233_0_node_114 | 20 | n |  | TRUE
87 | bus_MV_233_0_node_49 | 20 | n |  | TRUE
88 | bus_MV_233_0_node_50 | 20 | n |  | TRUE
89 | bus_MV_233_0_node_52 | 20 | n |  | TRUE
90 | bus_MV_233_0_node_97 | 20 | n |  | TRUE
91 | bus_MV_233_0_node_116 | 20 | n |  | TRUE
92 | bus_MV_233_0_node_96 | 20 | n |  | TRUE
93 | bus_MV_233_0_node_54 | 20 | n |  | TRUE
94 | bus_MV_233_0_node_57 | 20 | n |  | TRUE
95 | bus_MV_233_0_node_68 | 20 | n |  | TRUE
96 | bus_MV_233_0_node_69 | 20 | n |  | TRUE
97 | bus_MV_233_0_node_70 | 20 | n |  | TRUE
98 | bus_MV_233_0_node_73 | 20 | n |  | TRUE
99 | bus_MV_233_0_node_111 | 20 | n |  | TRUE
100 | bus_MV_233_0_node_108 | 20 | n |  | TRUE
101 | bus_MV_233_0_node_72 | 20 | n |  | TRUE
102 | bus_MV_233_0_node_110 | 20 | n |  | TRUE
103 | bus_MV_233_0_node_104 | 20 | n |  | TRUE
104 | bus_MV_233_0_node_65 | 20 | n |  | TRUE
105 | bus_MV_233_0_node_103 | 20 | n |  | TRUE
106 | bus_MV_233_0_node_58 | 20 | n |  | TRUE
107 | bus_MV_233_0_node_59 | 20 | n |  | TRUE
108 | bus_MV_233_0_node_61 | 20 | n |  | TRUE
109 | bus_MV_233_0_node_60 | 20 | n |  | TRUE
110 | bus_MV_233_0_node_102 | 20 | n |  | TRUE
111 | bus_MV_233_0_node_101 | 20 | n |  | TRUE
112 | bus_MV_233_0_node_128 | 20 | n |  | TRUE
113 | bus_MV_233_0_node_63 | 20 | n |  | TRUE
114 | bus_MV_233_0_node_71 | 20 | n |  | TRUE
115 | bus_MV_233_0_node_107 | 20 | n |  | TRUE
116 | bus_MV_233_0_node_82 | 20 | n |  | TRUE
117 | bus_MV_233_0_node_130 | 20 | n |  | TRUE
118 | bus_MV_233_0_node_132 | 20 | n |  | TRUE
119 | bus_MV_233_0_node_86 | 20 | n |  | TRUE
120 | bus_MV_233_0_node_87 | 20 | n |  | TRUE
121 | bus_MV_233_0_node_99 | 20 | n |  | TRUE
122 | bus_MV_233_0_node_100 | 20 | n |  | TRUE
123 | bus_MV_233_0_node_89 | 20 | n |  | TRUE
124 | bus_MV_233_0_node_90 | 20 | n |  | TRUE
125 | bus_MV_233_0_node_88 | 20 | n |  | TRUE
126 | bus_MV_233_0_node_92 | 20 | n |  | TRUE
127 | bus_MV_233_0_node_94 | 20 | n |  | TRUE
128 | bus_MV_233_0_node_106 | 20 | n |  | TRUE
129 | bus_MV_233_0_node_109 | 20 | n |  | TRUE
130 | bus_HV_233_0_node_12 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_233_0_load_0 | 0 | 0.35808 | 0.17342 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_233_0_load_126 | 4 | 0.22057 | 0.10683 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_233_0_load_6 | 6 | 0.41328 | 0.20016 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_233_0_load_122 | 8 | 0.21102 | 0.1022 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_233_0_load_78 | 10 | 0.15259 | 0.073903 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_233_0_load_13 | 11 | 0.23275 | 0.11272 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_233_0_load_123 | 13 | 0.31949 | 0.15474 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_233_0_load_79 | 14 | 0.28433 | 0.13771 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_233_0_load_29 | 16 | 0.40347 | 0.19541 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_233_0_load_74 | 21 | 0.35502 | 0.17194 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_233_0_load_7 | 22 | 0.24882 | 0.12051 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_233_0_load_10 | 24 | 0.080753 | 0.03911 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_233_0_load_8 | 25 | 0.75896 | 0.36758 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_233_0_load_11 | 26 | 0.068437 | 0.033145 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_233_0_load_12 | 27 | 0.25516 | 0.12358 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_233_0_load_119 | 28 | 0.078395 | 0.037969 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_233_0_load_115 | 30 | 0.13444 | 0.065111 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_233_0_load_40 | 35 | 0.23902 | 0.11576 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_233_0_load_127 | 36 | 0.18211 | 0.088198 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_233_0_load_76 | 37 | 0.18349 | 0.088869 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_233_0_load_17 | 39 | 0.11583 | 0.0561 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_233_0_load_19 | 41 | 0.12484 | 0.060464 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_233_0_load_38 | 44 | 0.37826 | 0.1832 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_233_0_load_21 | 45 | 0.40383 | 0.19559 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_233_0_load_120 | 51 | 0.74191 | 0.35932 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_233_0_load_80 | 52 | 0.40492 | 0.19611 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_233_0_load_125 | 53 | 0.27072 | 0.13111 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_233_0_load_129 | 54 | 0.17341 | 0.083987 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_233_0_load_26 | 57 | 0.16916 | 0.081928 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_233_0_load_118 | 60 | 0.14734 | 0.071361 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_233_0_load_117 | 61 | 0.11008 | 0.053316 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_233_0_load_77 | 65 | 0.29195 | 0.1414 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_233_0_load_124 | 66 | 0.32129 | 0.15561 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_233_0_load_91 | 69 | 0.30739 | 0.14888 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_233_0_load_98 | 70 | 0.3361 | 0.16278 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_233_0_load_34 | 72 | 0.39481 | 0.19122 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_233_0_load_53 | 75 | 0.14943 | 0.072374 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_233_0_load_131 | 78 | 0.084465 | 0.040908 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_233_0_load_41 | 79 | 0.30739 | 0.14887 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_233_0_load_105 | 83 | 2.7042 | 1.3097 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_233_0_load_112 | 84 | 0.11716 | 0.056744 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_233_0_load_49 | 87 | 0.2956 | 0.14316 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_233_0_load_97 | 90 | 0.089582 | 0.043387 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_233_0_load_116 | 91 | 0.07556 | 0.036596 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_233_0_load_54 | 93 | 0.1454 | 0.070418 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_233_0_load_68 | 95 | 0.19853 | 0.096151 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_233_0_load_111 | 99 | 0.070799 | 0.03429 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_233_0_load_108 | 100 | 0.068158 | 0.03301 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_233_0_load_104 | 103 | 0.12878 | 0.062373 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_233_0_load_103 | 105 | 0.25147 | 0.12179 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_233_0_load_58 | 106 | 0.40085 | 0.19414 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_233_0_load_101 | 111 | 0.47464 | 0.22988 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_233_0_load_128 | 112 | 0.12713 | 0.061572 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_233_0_load_63 | 113 | 0.17174 | 0.083179 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_233_0_load_71 | 114 | 0.079258 | 0.038386 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_233_0_load_130 | 117 | 0.10539 | 0.051044 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_233_0_load_132 | 118 | 0.083456 | 0.040419 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_233_0_load_99 | 121 | 0.38688 | 0.18737 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_233_0_load_100 | 122 | 0.10237 | 0.049582 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_233_0_load_88 | 125 | 0.30192 | 0.14623 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_233_0_load_92 | 126 | 0.21634 | 0.10478 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_233_0_load_106 | 128 | 0.078837 | 0.038182 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_233_0_load_109 | 129 | 0.2584 | 0.12515 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_233_0_line_0 |  | 0 | 1 | 0.018925 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_233_0_line_1 |  | 1 | 2 | 0.14062 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_233_0_line_2 |  | 1 | 3 | 0.39158 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_233_0_line_3 |  | 2 | 4 | 0.053656 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_233_0_line_4 |  | 3 | 7 | 0.72399 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_233_0_line_5 |  | 3 | 8 | 0.010076 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_233_0_line_6 |  | 3 | 5 | 0.32451 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_233_0_line_7 |  | 5 | 6 | 0.17796 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_233_0_line_8 |  | 7 | 9 | 0.074927 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_233_0_line_9 |  | 7 | 10 | 0.086173 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_233_0_line_10 |  | 8 | 13 | 0.24829 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_233_0_line_11 |  | 9 | 14 | 0.12223 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_233_0_line_12 |  | 9 | 15 | 0.32754 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
13 | MV_233_0_line_13 |  | 11 | 12 | 0.12522 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_233_0_line_14 |  | 12 | 19 | 0.1308 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_233_0_line_15 |  | 13 | 44 | 0.20867 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_233_0_line_16 |  | 14 | 18 | 0.028171 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_233_0_line_17 |  | 15 | 32 | 0.062854 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
18 | MV_233_0_line_18 |  | 15 | 27 | 0.061618 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
19 | MV_233_0_line_19 |  | 16 | 17 | 0.095692 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_233_0_line_20 |  | 17 | 18 | 0.12665 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_233_0_line_21 |  | 18 | 63 | 0.29251 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_233_0_line_22 |  | 19 | 20 | 0.31086 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_233_0_line_23 |  | 19 | 21 | 0.16714 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_233_0_line_24 |  | 20 | 37 | 0.069331 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_233_0_line_25 |  | 21 | 34 | 0.033551 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_233_0_line_26 |  | 22 | 23 | 0.009789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_233_0_line_27 |  | 22 | 24 | 0.044225 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_233_0_line_28 |  | 22 | 25 | 0.014682 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_233_0_line_29 |  | 23 | 26 | 0.011018 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_233_0_line_30 |  | 23 | 27 | 0.057061 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_233_0_line_31 |  | 26 | 28 | 0.0016119 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_233_0_line_32 |  | 29 | 30 | 0.027351 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
33 | MV_233_0_line_33 |  | 29 | 31 | 0.355 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
34 | MV_233_0_line_34 |  | 30 | 86 | 0.0046015 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
35 | MV_233_0_line_35 |  | 31 | 104 | 0.26085 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
36 | MV_233_0_line_36 |  | 31 | 113 | 0.077695 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_233_0_line_37 |  | 32 | 79 | 0.057624 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
38 | MV_233_0_line_38 |  | 33 | 34 | 0.26552 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_233_0_line_39 |  | 33 | 35 | 0.065303 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_233_0_line_40 |  | 35 | 36 | 0.45233 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_233_0_line_41 |  | 36 | 38 | 0.054959 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_233_0_line_42 |  | 38 | 83 | 0.07185 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_233_0_line_43 |  | 39 | 40 | 0.026942 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_233_0_line_44 |  | 40 | 41 | 0.18291 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_233_0_line_45 |  | 41 | 42 | 0.093276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_233_0_line_46 |  | 42 | 43 | 0.086033 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_233_0_line_47 |  | 43 | 44 | 0.012012 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_233_0_line_48 |  | 45 | 46 | 0.10974 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_233_0_line_49 |  | 46 | 47 | 0.199 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_233_0_line_50 |  | 46 | 48 | 0.30933 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_233_0_line_51 |  | 46 | 49 | 0.45186 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_233_0_line_52 |  | 47 | 50 | 0.11067 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_233_0_line_53 |  | 47 | 51 | 0.021853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_233_0_line_54 |  | 48 | 52 | 0.038061 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_233_0_line_55 |  | 49 | 53 | 0.081727 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_233_0_line_56 |  | 50 | 54 | 0.02504 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_233_0_line_57 |  | 51 | 55 | 0.055879 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_233_0_line_58 |  | 52 | 56 | 0.021817 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_233_0_line_59 |  | 55 | 107 | 0.1553 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_233_0_line_60 |  | 56 | 116 | 0.24049 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_233_0_line_61 |  | 56 | 62 | 0.095314 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_233_0_line_62 |  | 57 | 58 | 0.066047 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_233_0_line_63 |  | 58 | 59 | 0.1657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_233_0_line_64 |  | 59 | 60 | 0.079853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_233_0_line_65 |  | 59 | 61 | 0.075939 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_233_0_line_66 |  | 60 | 62 | 0.010936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_233_0_line_67 |  | 63 | 66 | 0.027349 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_233_0_line_68 |  | 63 | 64 | 0.16812 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_233_0_line_69 |  | 64 | 65 | 0.009369 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_233_0_line_70 |  | 65 | 67 | 0.081213 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_233_0_line_71 |  | 66 | 71 | 0.0068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_233_0_line_72 |  | 67 | 68 | 0.33685 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_233_0_line_73 |  | 67 | 69 | 0.10966 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
74 | MV_233_0_line_74 |  | 67 | 70 | 0.082203 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_233_0_line_75 |  | 68 | 118 | 0.074485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_233_0_line_76 |  | 69 | 124 | 0.042789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_233_0_line_77 |  | 71 | 89 | 0.10721 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_233_0_line_78 |  | 71 | 88 | 0.14269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_233_0_line_79 |  | 72 | 73 | 0.17281 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_233_0_line_80 |  | 73 | 74 | 0.58368 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_233_0_line_81 |  | 74 | 75 | 0.11123 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
82 | MV_233_0_line_82 |  | 74 | 76 | 0.72143 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_233_0_line_83 |  | 75 | 77 | 0.6142 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
84 | MV_233_0_line_84 |  | 76 | 78 | 0.096821 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_233_0_line_85 |  | 77 | 94 | 0.41339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_233_0_line_86 |  | 77 | 93 | 0.095767 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
87 | MV_233_0_line_87 |  | 79 | 80 | 0.02506 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
88 | MV_233_0_line_88 |  | 80 | 81 | 0.021151 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
89 | MV_233_0_line_89 |  | 80 | 82 | 0.13923 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_233_0_line_90 |  | 81 | 84 | 0.050897 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
91 | MV_233_0_line_91 |  | 82 | 83 | 0.010062 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_233_0_line_92 |  | 84 | 85 | 0.027132 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
93 | MV_233_0_line_93 |  | 85 | 86 | 0.022922 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
94 | MV_233_0_line_94 |  | 87 | 88 | 0.076301 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_233_0_line_95 |  | 89 | 90 | 0.034336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_233_0_line_96 |  | 89 | 91 | 0.011355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_233_0_line_97 |  | 90 | 92 | 0.0038204 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_233_0_line_98 |  | 92 | 127 | 0.054182 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_233_0_line_99 |  | 94 | 98 | 0.098056 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_233_0_line_100 |  | 94 | 99 | 0.023219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_233_0_line_101 |  | 95 | 96 | 0.083601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_233_0_line_102 |  | 96 | 97 | 1.2627 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_233_0_line_103 |  | 97 | 114 | 0.11802 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_233_0_line_104 |  | 98 | 100 | 0.037489 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_233_0_line_105 |  | 98 | 101 | 0.51913 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_233_0_line_106 |  | 99 | 102 | 0.011604 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_233_0_line_107 |  | 100 | 115 | 0.027613 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_233_0_line_108 |  | 101 | 114 | 0.094954 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_233_0_line_109 |  | 102 | 104 | 0.31151 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_233_0_line_110 |  | 103 | 104 | 0.29622 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
111 | MV_233_0_line_111 |  | 103 | 105 | 0.008921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_233_0_line_112 |  | 105 | 110 | 0.087428 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_233_0_line_113 |  | 106 | 107 | 0.038528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_233_0_line_114 |  | 107 | 108 | 0.2054 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_233_0_line_115 |  | 108 | 112 | 0.04323 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_233_0_line_116 |  | 108 | 109 | 0.056914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_233_0_line_117 |  | 109 | 110 | 0.12957 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_233_0_line_118 |  | 109 | 111 | 0.06408 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_233_0_line_119 |  | 115 | 128 | 0.051824 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_233_0_line_120 |  | 116 | 117 | 0.00822 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_233_0_line_121 |  | 119 | 120 | 0.046842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_233_0_line_122 |  | 119 | 121 | 0.067831 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_233_0_line_123 |  | 120 | 122 | 0.017364 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_233_0_line_124 |  | 122 | 125 | 0.12571 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
125 | MV_233_0_line_125 |  | 123 | 124 | 0.018434 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_233_0_line_126 |  | 123 | 125 | 0.06392 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_233_0_line_127 |  | 126 | 127 | 0.057921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_233_0_line_128 |  | 128 | 129 | 0.077051 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_233_0_trafo_12 | 25 MVA 110/20 kV | 130 | 27 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2739096.7197 | 1249366.5907
1 | 2739100.1924 | 1249348.6669
2 | 2739140.0255 | 1249290.7152
3 | 2738978.9523 | 1249080.878
4 | 2739193.2128 | 1249283.6351
5 | 2738794.7617 | 1249229.6989
6 | 2738714.4824 | 1249388.5208
7 | 2738742.7907 | 1249701.7368
8 | 2738979.3774 | 1249070.8121
9 | 2738696.884 | 1249738.7186
10 | 2738765.4276 | 1249618.5905
11 | 2737897.0205 | 1248864.0705
12 | 2737977.2244 | 1248960.4244
13 | 2739136.8589 | 1248878.8525
14 | 2738758.8834 | 1249844.055
15 | 2738493.0664 | 1249865.2912
16 | 2738926.4419 | 1249769.4114
17 | 2738873.2892 | 1249848.9833
18 | 2738786.4198 | 1249849.9607
19 | 2737938.6799 | 1249085.4191
20 | 2737875.2873 | 1249271.9478
21 | 2738067.806 | 1249191.544
22 | 2738440.5148 | 1249949.6101
23 | 2738444.4227 | 1249940.6349
24 | 2738399.9667 | 1249931.9547
25 | 2738434.6533 | 1249963.0718
26 | 2738448.7318 | 1249930.4942
27 | 2738474.3328 | 1249904.456
28 | 2738449.3622 | 1249929.0108
29 | 2738338.4294 | 1249839.501
30 | 2738365.1046 | 1249833.4604
31 | 2738050.7495 | 1249779.3612
32 | 2738457.8928 | 1249832.9287
33 | 2738205.4633 | 1249288.2845
34 | 2738085.9109 | 1249211.7175
35 | 2738226.6149 | 1249350.0674
36 | 2738600.8589 | 1249604.1271
37 | 2737806.2488 | 1249280.2278
38 | 2738576.4415 | 1249653.0676
39 | 2739230.3672 | 1248307.4138
40 | 2739222.3884 | 1248333.15
41 | 2739202.0962 | 1248514.785
42 | 2739194.4535 | 1248607.545
43 | 2739222.6244 | 1248676.047
44 | 2739221.1581 | 1248687.9679
45 | 2738308.3867 | 1250655.8367
46 | 2738378.3542 | 1250571.2924
47 | 2738395.8676 | 1250425.2451
48 | 2738596.7033 | 1250587.4759
49 | 2738186.8419 | 1250764.6124
50 | 2738326.5468 | 1250454.2201
51 | 2738396.4099 | 1250403.3986
52 | 2738623.7406 | 1250561.3287
53 | 2738110.6298 | 1250794.2965
54 | 2738336.995 | 1250431.4542
55 | 2738394.0787 | 1250347.6433
56 | 2738645.5656 | 1250559.76
57 | 2738699.0186 | 1250731.3683
58 | 2738763.6505 | 1250717.7688
59 | 2738799.9841 | 1250604.9825
60 | 2738720.6453 | 1250595.9338
61 | 2738772.7466 | 1250547.8697
62 | 2738709.7798 | 1250594.6946
63 | 2738938.6335 | 1249963.1971
64 | 2738815.2027 | 1250031.4678
65 | 2738807.6275 | 1250036.9288
66 | 2738958.5197 | 1249944.5684
67 | 2738849.4242 | 1250106.5605
68 | 2738884.1277 | 1250304.6889
69 | 2738745.9667 | 1250142.9268
70 | 2738922.3676 | 1250068.6571
71 | 2738965.0605 | 1249942.6422
72 | 2737861.7668 | 1251243.3583
73 | 2737747.2156 | 1251372.7466
74 | 2737540.7868 | 1250983.1061
75 | 2737597.0337 | 1250887.1461
76 | 2736842.8069 | 1250800.6595
77 | 2737520.9213 | 1250277.6779
78 | 2736756.1274 | 1250843.7981
79 | 2738437.9701 | 1249778.8583
80 | 2738427.4441 | 1249756.1028
81 | 2738406.9989 | 1249760.2403
82 | 2738503.5983 | 1249678.1771
83 | 2738511.6755 | 1249684.1776
84 | 2738401.4805 | 1249803.4176
85 | 2738392.0766 | 1249827.6647
86 | 2738369.5924 | 1249832.4441
87 | 2739098.9846 | 1249875.4107
88 | 2739023.566 | 1249863.8418
89 | 2739057.8951 | 1249958.7342
90 | 2739051.1243 | 1249992.1412
91 | 2739069.0158 | 1249961.0311
92 | 2739050.6469 | 1249995.9317
93 | 2737431.8311 | 1250242.5461
94 | 2737684.9782 | 1249985.3085
95 | 2736145.0849 | 1249611.1995
96 | 2736199.1944 | 1249665.1692
97 | 2737136.9406 | 1249507.3574
98 | 2737706.5752 | 1249895.5282
99 | 2737702.6108 | 1250000.4157
100 | 2737741.1377 | 1249882.0033
101 | 2737334.1404 | 1249587.4847
102 | 2737711.4229 | 1250007.9657
103 | 2738214.987 | 1250100.939
104 | 2737957.0549 | 1249955.2851
105 | 2738223.1717 | 1250104.488
106 | 2738417.7868 | 1250270.3928
107 | 2738400.6533 | 1250242.1334
108 | 2738237.5158 | 1250302.971
109 | 2738251.1902 | 1250256.2026
110 | 2738303.3834 | 1250139.2687
111 | 2738189.1164 | 1250240.296
112 | 2738219.7988 | 1250339.8026
113 | 2737991.4714 | 1249729.1351
114 | 2737246.6258 | 1249550.664
115 | 2737768.6071 | 1249879.9999
116 | 2738733.0203 | 1250405.0533
117 | 2738740.2381 | 1250409.0259
118 | 2738951.1871 | 1250337.5241
119 | 2738727.5353 | 1250384.8285
120 | 2738711.4147 | 1250369.1813
121 | 2738788.1528 | 1250415.3868
122 | 2738695.9864 | 1250361.2147
123 | 2738704.8674 | 1250187.2945
124 | 2738719.636 | 1250176.2077
125 | 2738718.0465 | 1250237.4542
126 | 2739084.9692 | 1250043.3862
127 | 2739030.1018 | 1250044.5499
128 | 2737818.824 | 1249891.9557
129 | 2737866.8533 | 1249952.2058
130 | 2738474.3328 | 1249904.456

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99633 | 0.00909 | 0.35808 | 0.17342
1 | 0.99634 | 0.0090086 | 0 | 0
2 | 0.9963 | 0.0093669 | 0 | 0
3 | 0.99663 | 0.0064919 | 0 | 0
4 | 0.99628 | 0.0092226 | 0.22057 | 0.10683
5 | 0.99646 | 0.0080234 | 0 | 0
6 | 0.99631 | 0.0071266 | 0.41328 | 0.20016
7 | 0.9986 | -0.010304 | 0 | 0
8 | 0.99661 | 0.0066249 | 0.21102 | 0.1022
9 | 0.99881 | -0.01213 | 0 | 0
10 | 0.99857 | -0.010464 | 0.15259 | 0.073903
11 | 0.99702 | -0.011826 | 0.23275 | 0.11272
12 | 0.99706 | -0.012165 | 0 | 0
13 | 0.99616 | 0.0035782 | 0.31949 | 0.15474
14 | 0.99799 | -0.017764 | 0.28433 | 0.13771
15 | 0.99984 | -0.00073685 | 0 | 0
16 | 0.99773 | -0.01662 | 0.40347 | 0.19541
17 | 0.99781 | -0.016151 | 0 | 0
18 | 0.99787 | -0.016752 | 0 | 0
19 | 0.99712 | -0.011761 | 0 | 0
20 | 0.99704 | -0.011181 | 0 | 0
21 | 0.99725 | -0.01074 | 0.35502 | 0.17194
22 | 0.9999 | 0.00096187 | 0.24882 | 0.12051
23 | 0.99991 | 0.0008351 | 0 | 0
24 | 0.99989 | 0.0010031 | 0.080753 | 0.03911
25 | 0.99988 | 0.00082717 | 0.75896 | 0.36758
26 | 0.99991 | 0.00085434 | 0.068437 | 0.033145
27 | 1 | 0 | -17.1569 | -7.9388
28 | 0.99991 | 0.00085585 | 0.078395 | 0.037969
29 | 0.99936 | -0.013242 | 0 | 0
30 | 0.99939 | -0.01311 | 0.13444 | 0.065111
31 | 0.99904 | -0.014889 | 0 | 0
32 | 0.99974 | -0.0012246 | 0 | 0
33 | 0.99754 | -0.01321 | 0 | 0
34 | 0.99728 | -0.011024 | 0 | 0
35 | 0.99764 | -0.012489 | 0.23902 | 0.11576
36 | 0.99852 | -0.0061773 | 0.18211 | 0.088198
37 | 0.99703 | -0.011031 | 0.18349 | 0.088869
38 | 0.9986 | -0.0068919 | 0 | 0
39 | 0.99582 | 0.0025591 | 0.11583 | 0.0561
40 | 0.99583 | 0.002522 | 0 | 0
41 | 0.99585 | 0.0022993 | 0.12484 | 0.060464
42 | 0.99588 | 0.0020649 | 0 | 0
43 | 0.99591 | 0.0018605 | 0 | 0
44 | 0.99591 | 0.0018328 | 0.37826 | 0.1832
45 | 0.99368 | -0.032246 | 0.40383 | 0.19559
46 | 0.99376 | -0.031704 | 0 | 0
47 | 0.99417 | -0.035076 | 0 | 0
48 | 0.99339 | -0.028612 | 0 | 0
49 | 0.99361 | -0.030433 | 0 | 0
50 | 0.99415 | -0.034858 | 0 | 0
51 | 0.99422 | -0.035484 | 0.74191 | 0.35932
52 | 0.99335 | -0.028221 | 0.40492 | 0.19611
53 | 0.99358 | -0.03017 | 0.27072 | 0.13111
54 | 0.99414 | -0.034806 | 0.17341 | 0.083987
55 | 0.9944 | -0.037025 | 0 | 0
56 | 0.99333 | -0.028104 | 0 | 0
57 | 0.99319 | -0.027198 | 0.16916 | 0.081928
58 | 0.99321 | -0.027061 | 0 | 0
59 | 0.99325 | -0.027379 | 0 | 0
60 | 0.99328 | -0.027615 | 0.14734 | 0.071361
61 | 0.99324 | -0.027282 | 0.11008 | 0.053316
62 | 0.99328 | -0.027666 | 0 | 0
63 | 0.99683 | -0.0075166 | 0 | 0
64 | 0.99644 | -0.0040487 | 0 | 0
65 | 0.99642 | -0.0038541 | 0.29195 | 0.1414
66 | 0.99679 | -0.0072059 | 0.32129 | 0.15561
67 | 0.99618 | -0.0054685 | 0 | 0
68 | 0.99615 | -0.0052541 | 0 | 0
69 | 0.99595 | -0.0069955 | 0.30739 | 0.14888
70 | 0.99613 | -0.0058053 | 0.3361 | 0.16278
71 | 0.99679 | -0.0071548 | 0 | 0
72 | 0.99594 | -0.020677 | 0.39481 | 0.19122
73 | 0.99607 | -0.019845 | 0 | 0
74 | 0.99636 | -0.022356 | 0 | 0
75 | 0.99646 | -0.021564 | 0.14943 | 0.072374
76 | 0.99624 | -0.023132 | 0 | 0
77 | 0.9972 | -0.01605 | 0 | 0
78 | 0.99623 | -0.023232 | 0.084465 | 0.040908
79 | 0.99954 | -0.012286 | 0.30739 | 0.14887
80 | 0.99951 | -0.012476 | 0 | 0
81 | 0.99948 | -0.012583 | 0 | 0
82 | 0.99881 | -0.0061785 | 0 | 0
83 | 0.99876 | -0.0057219 | 2.7042 | 1.3097
84 | 0.99944 | -0.01284 | 0.11716 | 0.056744
85 | 0.99941 | -0.012974 | 0 | 0
86 | 0.99939 | -0.013087 | 0 | 0
87 | 0.99669 | -0.0069379 | 0.2956 | 0.14316
88 | 0.99673 | -0.0066632 | 0 | 0
89 | 0.99674 | -0.0066975 | 0 | 0
90 | 0.99672 | -0.0065779 | 0.089582 | 0.043387
91 | 0.99674 | -0.0066872 | 0.07556 | 0.036596
92 | 0.99672 | -0.0065686 | 0 | 0
93 | 0.99718 | -0.01622 | 0.1454 | 0.070418
94 | 0.99761 | -0.01935 | 0 | 0
95 | 0.99696 | -0.016617 | 0.19853 | 0.096151
96 | 0.99698 | -0.016811 | 0 | 0
97 | 0.99729 | -0.018454 | 0 | 0
98 | 0.99753 | -0.01888 | 0 | 0
99 | 0.99765 | -0.019638 | 0.070799 | 0.03429
100 | 0.99751 | -0.018703 | 0.068158 | 0.03301
101 | 0.99735 | -0.018583 | 0 | 0
102 | 0.99768 | -0.019791 | 0 | 0
103 | 0.99691 | -0.058432 | 0.12878 | 0.062373
104 | 0.99827 | -0.02382 | 0 | 0
105 | 0.99686 | -0.058064 | 0.25147 | 0.12179
106 | 0.99488 | -0.041095 | 0.40085 | 0.19414
107 | 0.9949 | -0.041281 | 0 | 0
108 | 0.99567 | -0.047828 | 0 | 0
109 | 0.99589 | -0.049712 | 0 | 0
110 | 0.99647 | -0.05471 | 0 | 0
111 | 0.99585 | -0.049349 | 0.47464 | 0.22988
112 | 0.99566 | -0.047763 | 0.12713 | 0.061572
113 | 0.99901 | -0.015051 | 0.17174 | 0.083179
114 | 0.99732 | -0.018484 | 0.079258 | 0.038386
115 | 0.9975 | -0.018594 | 0 | 0
116 | 0.9933 | -0.027843 | 0 | 0
117 | 0.9933 | -0.027833 | 0.10539 | 0.051044
118 | 0.99614 | -0.0051834 | 0.083456 | 0.040419
119 | 0.99567 | -0.0063334 | 0 | 0
120 | 0.99569 | -0.0065456 | 0 | 0
121 | 0.99564 | -0.0060202 | 0.38688 | 0.18737
122 | 0.9957 | -0.0066234 | 0.10237 | 0.049582
123 | 0.99589 | -0.0064328 | 0 | 0
124 | 0.9959 | -0.0066029 | 0 | 0
125 | 0.99582 | -0.0058392 | 0.30192 | 0.14623
126 | 0.99669 | -0.0062861 | 0.21634 | 0.10478
127 | 0.99671 | -0.0064345 | 0 | 0
128 | 0.99747 | -0.018387 | 0.078837 | 0.038182
129 | 0.99743 | -0.018629 | 0.2584 | 0.12515
130 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.35808 | -0.17342 | 0.35808 | 0.17298 | 3.3557e-06 | -0.00044755 | 0.011528 | 0.011522 | 0.011528 | 0.99633 | 0.00909 | 0.99634 | 0.0090086 | 5.2398
1 | 0.22058 | 0.10344 | -0.22057 | -0.10677 | 9.409e-06 | -0.0033301 | 0.0070589 | 0.0071004 | 0.0071004 | 0.99634 | 0.0090086 | 0.9963 | 0.0093669 | 3.2275
2 | -0.57866 | -0.27641 | 0.57884 | 0.26718 | 0.00017936 | -0.0092306 | 0.018581 | 0.018466 | 0.018581 | 0.99634 | 0.0090086 | 0.99663 | 0.0064919 | 8.4457
3 | 0.22057 | 0.10677 | -0.22057 | -0.10683 | 4.8203e-06 | -6.0561e-05 | 0.0071004 | 0.0071012 | 0.0071012 | 0.9963 | 0.0093669 | 0.99628 | 0.0092226 | 3.3815
4 | -2.1423 | -1.0063 | 2.1468 | 0.99041 | 0.0045287 | -0.01586 | 0.068556 | 0.068346 | 0.068556 | 0.99663 | 0.0064919 | 0.9986 | -0.010304 | 31.162
5 | 1.15 | 0.54678 | -1.15 | -0.54701 | 1.8302e-05 | -0.00023352 | 0.036884 | 0.036887 | 0.036887 | 0.99663 | 0.0064919 | 0.99661 | 0.0066249 | 16.767
6 | 0.41341 | 0.19231 | -0.41333 | -0.19998 | 7.6105e-05 | -0.007672 | 0.013207 | 0.013302 | 0.013302 | 0.99663 | 0.0064919 | 0.99646 | 0.0080234 | 6.0465
7 | 0.41333 | 0.19998 | -0.41328 | -0.20016 | 5.6117e-05 | -0.00017576 | 0.013302 | 0.013305 | 0.013305 | 0.99646 | 0.0080234 | 0.99631 | 0.0071266 | 6.3357
8 | -2.2994 | -1.0642 | 2.2999 | 1.0626 | 0.00053648 | -0.0016252 | 0.073246 | 0.073224 | 0.073246 | 0.9986 | -0.010304 | 0.99881 | -0.01213 | 33.2935
9 | 0.15259 | 0.073802 | -0.15259 | -0.073903 | 3.6874e-06 | -0.00010027 | 0.0049 | 0.0049013 | 0.0049013 | 0.9986 | -0.010304 | 0.99857 | -0.010464 | 2.334
10 | 0.939 | 0.44481 | -0.9386 | -0.44485 | 0.00040075 | -4.3259e-05 | 0.030096 | 0.0301 | 0.0301 | 0.99661 | 0.0066249 | 0.99616 | 0.0035782 | 14.3332
11 | 3.5043 | 1.6548 | -3.5016 | -1.6532 | 0.002732 | 0.0015658 | 0.112 | 0.11201 | 0.11201 | 0.99881 | -0.01213 | 0.99799 | -0.017764 | 53.3363
12 | -5.8042 | -2.7174 | 5.8097 | 2.7101 | 0.0054238 | -0.0072802 | 0.18523 | 0.18509 | 0.18523 | 0.99881 | -0.01213 | 0.99984 | -0.00073685 | 51.1677
13 | -0.23275 | -0.11272 | 0.23276 | 0.10976 | 9.3254e-06 | -0.0029692 | 0.0074877 | 0.0074506 | 0.0074877 | 0.99702 | -0.011826 | 0.99706 | -0.012165 | 3.4035
14 | -0.23276 | -0.10976 | 0.23277 | 0.10961 | 1.2934e-05 | -0.00014714 | 0.0074506 | 0.0074487 | 0.0074506 | 0.99706 | -0.012165 | 0.99712 | -0.011761 | 3.5479
15 | 0.6191 | 0.29012 | -0.61896 | -0.29027 | 0.00014597 | -0.00015571 | 0.019813 | 0.019816 | 0.019816 | 0.99616 | 0.0035782 | 0.99591 | 0.0018328 | 9.4362
16 | 3.2172 | 1.5155 | -3.2168 | -1.516 | 0.000398 | -0.00055178 | 0.10287 | 0.10288 | 0.10288 | 0.99799 | -0.017764 | 0.99787 | -0.016752 | 46.7622
17 | 10.0953 | 4.6292 | -10.0943 | -4.6365 | 0.00099877 | -0.0073327 | 0.32066 | 0.32075 | 0.32075 | 0.99984 | -0.00073685 | 0.99974 | -0.0012246 | 25.1372
18 | -15.905 | -7.3393 | 15.9074 | 7.3329 | 0.0024345 | -0.0063711 | 0.50574 | 0.50565 | 0.50574 | 0.99984 | -0.00073685 | 1 | 0 | 39.635
19 | -0.40347 | -0.19541 | 0.4035 | 0.19531 | 2.868e-05 | -9.5764e-05 | 0.012971 | 0.012969 | 0.012971 | 0.99773 | -0.01662 | 0.99781 | -0.016151 | 6.1765
20 | -0.4035 | -0.19531 | 0.40353 | 0.19231 | 2.8356e-05 | -0.0030025 | 0.012969 | 0.012931 | 0.012969 | 0.99781 | -0.016151 | 0.99787 | -0.016752 | 5.8951
21 | 2.8133 | 1.3237 | -2.8102 | -1.3297 | 0.0031622 | -0.006009 | 0.089945 | 0.090031 | 0.090031 | 0.99787 | -0.016752 | 0.99683 | -0.0075166 | 40.9233
22 | 0.18351 | 0.07985 | -0.18349 | -0.087224 | 1.4141e-05 | -0.0073745 | 0.0057939 | 0.0058824 | 0.0058824 | 0.99712 | -0.011761 | 0.99704 | -0.011181 | 2.6738
23 | -0.41628 | -0.18946 | 0.41633 | 0.18929 | 5.2202e-05 | -0.00016571 | 0.013241 | 0.013239 | 0.013241 | 0.99712 | -0.011761 | 0.99725 | -0.01074 | 6.3053
24 | 0.18349 | 0.087224 | -0.18349 | -0.088869 | 3.2139e-06 | -0.0016446 | 0.0058824 | 0.005903 | 0.005903 | 0.99704 | -0.011181 | 0.99703 | -0.011031 | 2.6832
25 | -0.77135 | -0.36124 | 0.77138 | 0.36045 | 2.7218e-05 | -0.00078862 | 0.024656 | 0.024646 | 0.024656 | 0.99725 | -0.01074 | 0.99728 | -0.011024 | 11.2071
26 | -1.0885 | -0.52613 | 1.0886 | 0.5259 | 1.5921e-05 | -0.00022896 | 0.034905 | 0.034902 | 0.034905 | 0.9999 | 0.00096187 | 0.99991 | 0.0008351 | 15.866
27 | 0.080753 | 0.038055 | -0.080753 | -0.03911 | 3.9416e-07 | -0.0010556 | 0.0025773 | 0.0025904 | 0.0025904 | 0.9999 | 0.00096187 | 0.99989 | 0.0010031 | 1.1775
28 | 0.75897 | 0.36757 | -0.75896 | -0.36758 | 1.5506e-05 | -7.8114e-06 | 0.024346 | 0.024347 | 0.024347 | 0.9999 | 0.00096187 | 0.99988 | 0.00082717 | 11.5936
29 | 0.14683 | 0.070812 | -0.14683 | -0.071075 | 3.2602e-07 | -0.00026293 | 0.0047063 | 0.0047096 | 0.0047096 | 0.99991 | 0.0008351 | 0.99991 | 0.00085434 | 2.1407
30 | -1.2354 | -0.59672 | 1.2355 | 0.59539 | 0.00011946 | -0.0013268 | 0.039608 | 0.039591 | 0.039608 | 0.99991 | 0.0008351 | 1 | 0 | 18.0038
31 | 0.078395 | 0.03793 | -0.078395 | -0.037969 | 1.3656e-08 | -3.8474e-05 | 0.0025143 | 0.0025148 | 0.0025148 | 0.99991 | 0.00085434 | 0.99991 | 0.00085585 | 1.1431
32 | -5.6318 | -2.521 | 5.632 | 2.5176 | 0.00013421 | -0.0033571 | 0.17824 | 0.1782 | 0.17824 | 0.99936 | -0.013242 | 0.99939 | -0.01311 | 13.9683
33 | 5.6318 | 2.521 | -5.6301 | -2.5645 | 0.0017475 | -0.043555 | 0.17824 | 0.17877 | 0.17877 | 0.99936 | -0.013242 | 0.99904 | -0.014889 | 14.0098
34 | -5.7664 | -2.5827 | 5.7664 | 2.5822 | 2.3679e-05 | -0.00056419 | 0.18251 | 0.1825 | 0.18251 | 0.99939 | -0.01311 | 0.99939 | -0.013087 | 14.3031
35 | 5.4583 | 2.4815 | -5.4546 | -2.4876 | 0.0037842 | -0.0061748 | 0.17325 | 0.17336 | 0.17336 | 0.99904 | -0.014889 | 0.99827 | -0.02382 | 47.8897
36 | 0.17175 | 0.083089 | -0.17174 | -0.083179 | 4.2081e-06 | -8.9936e-05 | 0.0055129 | 0.0055141 | 0.0055141 | 0.99904 | -0.014889 | 0.99901 | -0.015051 | 2.6258
37 | 10.0943 | 4.6365 | -10.0932 | -4.6338 | 0.0010582 | 0.0026865 | 0.32075 | 0.32075 | 0.32075 | 0.99974 | -0.0012246 | 0.99954 | -0.012286 | 24.8645
38 | 0.77159 | 0.35421 | -0.77138 | -0.36045 | 0.00021464 | -0.0062431 | 0.024569 | 0.024646 | 0.024646 | 0.99754 | -0.01321 | 0.99728 | -0.011024 | 11.2027
39 | -0.77159 | -0.35421 | 0.77166 | 0.35417 | 7.0232e-05 | -3.3593e-05 | 0.024569 | 0.024568 | 0.024569 | 0.99754 | -0.01321 | 0.99764 | -0.012489 | 11.6996
40 | -1.0107 | -0.46993 | 1.0115 | 0.46992 | 0.00083812 | -1.295e-05 | 0.032252 | 0.032245 | 0.032252 | 0.99764 | -0.012489 | 0.99852 | -0.0061773 | 15.3579
41 | -1.1936 | -0.55812 | 1.1937 | 0.55684 | 0.00010643 | -0.0012769 | 0.038094 | 0.038078 | 0.038094 | 0.99852 | -0.0061773 | 0.9986 | -0.0068919 | 17.3155
42 | -1.1937 | -0.55684 | 1.1939 | 0.55687 | 0.00018561 | 3.0711e-05 | 0.038078 | 0.038077 | 0.038078 | 0.9986 | -0.0068919 | 0.99876 | -0.0057219 | 18.1324
43 | -0.11583 | -0.0561 | 0.11583 | 0.055463 | 4.9958e-07 | -0.00063776 | 0.0037309 | 0.0037229 | 0.0037309 | 0.99582 | 0.0025591 | 0.99583 | 0.002522 | 1.6959
44 | -0.11583 | -0.055463 | 0.11584 | 0.051132 | 3.3361e-06 | -0.00433 | 0.0037229 | 0.0036704 | 0.0037229 | 0.99583 | 0.002522 | 0.99585 | 0.0022993 | 1.6922
45 | -0.24068 | -0.1116 | 0.24069 | 0.10939 | 7.3386e-06 | -0.0022065 | 0.0076902 | 0.0076635 | 0.0076902 | 0.99585 | 0.0022993 | 0.99588 | 0.0020649 | 3.4956
46 | -0.24069 | -0.10939 | 0.24069 | 0.10735 | 6.7239e-06 | -0.0020353 | 0.0076635 | 0.0076393 | 0.0076635 | 0.99588 | 0.0020649 | 0.99591 | 0.0018605 | 3.4834
47 | -0.24069 | -0.10735 | 0.24069 | 0.10707 | 9.3542e-07 | -0.00028418 | 0.0076393 | 0.0076359 | 0.0076393 | 0.99591 | 0.0018605 | 0.99591 | 0.0018328 | 3.4724
48 | -0.40383 | -0.19559 | 0.40387 | 0.19548 | 3.322e-05 | -0.00010856 | 0.013035 | 0.013034 | 0.013035 | 0.99368 | -0.032246 | 0.99376 | -0.031704 | 6.2073
49 | -1.612 | -0.74322 | 1.6127 | 0.73873 | 0.0007056 | -0.004485 | 0.051564 | 0.051507 | 0.051564 | 0.99376 | -0.031704 | 0.99417 | -0.035076 | 23.4382
50 | 0.93738 | 0.42919 | -0.93701 | -0.43637 | 0.00037147 | -0.0071808 | 0.029948 | 0.030037 | 0.030037 | 0.99376 | -0.031704 | 0.99339 | -0.028612 | 13.6531
51 | 0.27077 | 0.11855 | -0.27072 | -0.12919 | 4.5131e-05 | -0.01064 | 0.0085863 | 0.0087151 | 0.0087151 | 0.99376 | -0.031704 | 0.99361 | -0.030433 | 3.9614
52 | 0.17342 | 0.080786 | -0.17341 | -0.083397 | 4.5855e-06 | -0.0026101 | 0.0055551 | 0.0055875 | 0.0055875 | 0.99417 | -0.035076 | 0.99415 | -0.034858 | 2.5398
53 | -1.7861 | -0.81952 | 1.7862 | 0.81903 | 9.4983e-05 | -0.00048756 | 0.057062 | 0.057056 | 0.057062 | 0.99417 | -0.035076 | 0.99422 | -0.035484 | 25.9373
54 | 0.93701 | 0.43637 | -0.93696 | -0.43725 | 4.5859e-05 | -0.00088314 | 0.030037 | 0.030048 | 0.030048 | 0.99339 | -0.028612 | 0.99335 | -0.028221 | 13.6581
55 | 0.27072 | 0.12919 | -0.27072 | -0.13111 | 8.3098e-06 | -0.0019239 | 0.0087151 | 0.0087393 | 0.0087393 | 0.99361 | -0.030433 | 0.99358 | -0.03017 | 3.9724
56 | 0.17341 | 0.083397 | -0.17341 | -0.083987 | 1.045e-06 | -0.00059057 | 0.0055875 | 0.005595 | 0.005595 | 0.99415 | -0.034858 | 0.99414 | -0.034806 | 2.5432
57 | -2.5281 | -1.1784 | 2.5286 | 1.1772 | 0.00048919 | -0.0011739 | 0.080987 | 0.080971 | 0.080987 | 0.99422 | -0.035484 | 0.9944 | -0.037025 | 36.8123
58 | 0.53204 | 0.24114 | -0.53203 | -0.24165 | 8.396e-06 | -0.0005115 | 0.016975 | 0.016982 | 0.016982 | 0.99335 | -0.028221 | 0.99333 | -0.028104 | 7.7189
59 | -2.5286 | -1.1772 | 2.53 | 1.1739 | 0.0013586 | -0.0032655 | 0.080971 | 0.080926 | 0.080971 | 0.9944 | -0.037025 | 0.9949 | -0.041281 | 36.805
60 | 0.1054 | 0.045186 | -0.10539 | -0.05085 | 3.6371e-06 | -0.0056643 | 0.0033325 | 0.0034008 | 0.0034008 | 0.99333 | -0.028104 | 0.9933 | -0.027843 | 1.5458
61 | 0.42663 | 0.19647 | -0.42661 | -0.19871 | 2.3756e-05 | -0.0022383 | 0.01365 | 0.013677 | 0.013677 | 0.99333 | -0.028104 | 0.99328 | -0.027666 | 6.217
62 | -0.16916 | -0.081928 | 0.16916 | 0.081853 | 3.5114e-06 | -7.558e-05 | 0.005463 | 0.005462 | 0.005463 | 0.99319 | -0.027198 | 0.99321 | -0.027061 | 2.6014
63 | -0.16916 | -0.081853 | 0.16917 | 0.077952 | 6.5405e-06 | -0.0039009 | 0.005462 | 0.0054136 | 0.005462 | 0.99321 | -0.027061 | 0.99325 | -0.027379 | 2.4827
64 | -0.27926 | -0.12948 | 0.27927 | 0.1276 | 8.5102e-06 | -0.0018785 | 0.0089462 | 0.0089234 | 0.0089462 | 0.99325 | -0.027379 | 0.99328 | -0.027615 | 4.0665
65 | 0.11009 | 0.051528 | -0.11008 | -0.053316 | 1.2731e-06 | -0.0017883 | 0.0035327 | 0.003555 | 0.003555 | 0.99325 | -0.027379 | 0.99324 | -0.027282 | 1.6159
66 | -0.42661 | -0.19896 | 0.42661 | 0.19871 | 2.7318e-06 | -0.0002568 | 0.013681 | 0.013677 | 0.013681 | 0.99328 | -0.027615 | 0.99328 | -0.027666 | 6.2184
67 | 0.99848 | 0.47291 | -0.99844 | -0.47355 | 3.7384e-05 | -0.00063774 | 0.031995 | 0.032003 | 0.032003 | 0.99683 | -0.0075166 | 0.99679 | -0.0072059 | 14.5466
68 | 1.8117 | 0.85683 | -1.8109 | -0.8606 | 0.00075662 | -0.0037626 | 0.058037 | 0.058086 | 0.058086 | 0.99683 | -0.0075166 | 0.99644 | -0.0040487 | 26.4028
69 | 1.8109 | 0.8606 | -1.8109 | -0.86081 | 4.2203e-05 | -0.00020958 | 0.058086 | 0.058089 | 0.058089 | 0.99644 | -0.0040487 | 0.99642 | -0.0038541 | 26.4041
70 | 1.5189 | 0.71941 | -1.5186 | -0.71929 | 0.00034306 | 0.00011865 | 0.048691 | 0.048692 | 0.048692 | 0.99642 | -0.0038541 | 0.99618 | -0.0054685 | 23.1868
71 | 0.67715 | 0.31794 | -0.67715 | -0.3181 | 4.2612e-06 | -0.00016005 | 0.021665 | 0.021667 | 0.021667 | 0.99679 | -0.0072059 | 0.99679 | -0.0071548 | 9.8484
72 | 0.083459 | 0.030675 | -0.083456 | -0.038655 | 3.0841e-06 | -0.0079801 | 0.0025767 | 0.0026653 | 0.0026653 | 0.99618 | -0.0054685 | 0.99615 | -0.0052541 | 1.2115
73 | 1.099 | 0.52592 | -1.0988 | -0.5259 | 0.00024356 | 2.267e-05 | 0.035306 | 0.035307 | 0.035307 | 0.99618 | -0.0054685 | 0.99595 | -0.0069955 | 16.813
74 | 0.33612 | 0.16269 | -0.3361 | -0.16278 | 1.7152e-05 | -8.6638e-05 | 0.010821 | 0.010822 | 0.010822 | 0.99618 | -0.0054685 | 0.99613 | -0.0058053 | 5.1535
75 | 0.083456 | 0.038655 | -0.083456 | -0.040419 | 7.1216e-07 | -0.0017645 | 0.0026653 | 0.0026872 | 0.0026872 | 0.99615 | -0.0052541 | 0.99614 | -0.0051834 | 1.2215
76 | 0.79136 | 0.37702 | -0.79133 | -0.37802 | 3.6895e-05 | -0.0010024 | 0.025408 | 0.02542 | 0.02542 | 0.99595 | -0.0069955 | 0.9959 | -0.0066029 | 11.5548
77 | 0.38152 | 0.1784 | -0.3815 | -0.18093 | 2.1348e-05 | -0.0025369 | 0.012197 | 0.012229 | 0.012229 | 0.99679 | -0.0071548 | 0.99674 | -0.0066975 | 5.5585
78 | 0.29563 | 0.1397 | -0.29561 | -0.14308 | 1.7157e-05 | -0.0033797 | 0.0094693 | 0.0095116 | 0.0095116 | 0.99679 | -0.0071548 | 0.99673 | -0.0066632 | 4.3235
79 | -0.39481 | -0.19122 | 0.39486 | 0.19104 | 4.977e-05 | -0.00017348 | 0.012715 | 0.012713 | 0.012715 | 0.99594 | -0.020677 | 0.99607 | -0.019845 | 6.0549
80 | -0.39486 | -0.19104 | 0.39499 | 0.17725 | 0.00012423 | -0.013794 | 0.012713 | 0.012543 | 0.012713 | 0.99607 | -0.019845 | 0.99636 | -0.022356 | 5.7785
81 | -0.47946 | -0.21719 | 0.47951 | 0.21709 | 4.6086e-05 | -0.00010297 | 0.01525 | 0.015249 | 0.01525 | 0.99636 | -0.022356 | 0.99646 | -0.021564 | 7.262
82 | 0.084476 | 0.039946 | -0.084467 | -0.040794 | 9.4585e-06 | -0.00084897 | 0.0027074 | 0.002718 | 0.002718 | 0.99636 | -0.022356 | 0.99624 | -0.023132 | 1.2943
83 | -0.62894 | -0.28947 | 0.62938 | 0.28901 | 0.00044006 | -0.00045296 | 0.020058 | 0.020049 | 0.020058 | 0.99646 | -0.021564 | 0.9972 | -0.01605 | 9.5512
84 | 0.084467 | 0.040794 | -0.084465 | -0.040908 | 1.2751e-06 | -0.00011392 | 0.002718 | 0.0027195 | 0.0027195 | 0.99624 | -0.023132 | 0.99623 | -0.023232 | 1.295
85 | -0.77478 | -0.35932 | 0.77512 | 0.3496 | 0.00033571 | -0.0097195 | 0.024723 | 0.024605 | 0.024723 | 0.9972 | -0.01605 | 0.99761 | -0.01935 | 11.2379
86 | 0.1454 | 0.070307 | -0.1454 | -0.070418 | 3.7308e-06 | -0.00011135 | 0.0046753 | 0.0046768 | 0.0046768 | 0.9972 | -0.01605 | 0.99718 | -0.01622 | 2.227
87 | 9.7858 | 4.485 | -9.7855 | -4.4879 | 0.00037426 | -0.0029354 | 0.31089 | 0.31093 | 0.31093 | 0.99954 | -0.012286 | 0.99951 | -0.012476 | 24.3674
88 | 5.8842 | 2.624 | -5.8841 | -2.6265 | 0.00011317 | -0.0025915 | 0.18608 | 0.18611 | 0.18611 | 0.99951 | -0.012476 | 0.99948 | -0.012583 | 14.5854
89 | 3.9012 | 1.8639 | -3.8983 | -1.8664 | 0.0028995 | -0.0024587 | 0.12487 | 0.12492 | 0.12492 | 0.99951 | -0.012476 | 0.99881 | -0.0061785 | 56.7802
90 | 5.8841 | 2.6265 | -5.8838 | -2.6328 | 0.00027248 | -0.0062356 | 0.18611 | 0.18619 | 0.18619 | 0.99948 | -0.012583 | 0.99944 | -0.01284 | 14.5913
91 | 3.8983 | 1.8664 | -3.8981 | -1.8666 | 0.00020962 | -0.00017749 | 0.12492 | 0.12492 | 0.12492 | 0.99881 | -0.0061785 | 0.99876 | -0.0057219 | 56.7815
92 | 5.7667 | 2.576 | -5.7665 | -2.5794 | 0.00013954 | -0.003327 | 0.18243 | 0.18247 | 0.18247 | 0.99944 | -0.01284 | 0.99941 | -0.012974 | 14.2999
93 | 5.7665 | 2.5794 | -5.7664 | -2.5822 | 0.00011793 | -0.0028106 | 0.18247 | 0.1825 | 0.1825 | 0.99941 | -0.012974 | 0.99939 | -0.013087 | 14.3026
94 | -0.2956 | -0.14316 | 0.29561 | 0.14308 | 1.2301e-05 | -8.2786e-05 | 0.0095128 | 0.0095116 | 0.0095128 | 0.99669 | -0.0069379 | 0.99673 | -0.0066632 | 4.5299
95 | 0.30594 | 0.14461 | -0.30593 | -0.14542 | 4.4074e-06 | -0.00081316 | 0.0098005 | 0.0098106 | 0.0098106 | 0.99674 | -0.0066975 | 0.99672 | -0.0065779 | 4.4594
96 | 0.07556 | 0.036326 | -0.07556 | -0.036596 | 8.9516e-08 | -0.00026933 | 0.0024281 | 0.0024315 | 0.0024315 | 0.99674 | -0.0066975 | 0.99674 | -0.0066872 | 1.1052
97 | 0.21635 | 0.10203 | -0.21635 | -0.10212 | 2.4482e-07 | -9.0546e-05 | 0.0069279 | 0.0069291 | 0.0069291 | 0.99672 | -0.0065779 | 0.99672 | -0.0065686 | 3.1496
98 | 0.21635 | 0.10212 | -0.21635 | -0.10341 | 3.4808e-06 | -0.0012841 | 0.0069291 | 0.006945 | 0.006945 | 0.99672 | -0.0065686 | 0.99671 | -0.0064345 | 3.1568
99 | 0.6834 | 0.2764 | -0.68334 | -0.27871 | 5.9637e-05 | -0.0023121 | 0.021332 | 0.021357 | 0.021357 | 0.99761 | -0.01935 | 0.99753 | -0.01888 | 9.7077
100 | -1.4585 | -0.626 | 1.4586 | 0.62547 | 6.5376e-05 | -0.00053237 | 0.045928 | 0.045922 | 0.045928 | 0.99761 | -0.01935 | 0.99765 | -0.019638 | 20.8763
101 | -0.19853 | -0.096151 | 0.19853 | 0.094168 | 4.5354e-06 | -0.0019826 | 0.0063872 | 0.0063624 | 0.0063872 | 0.99696 | -0.016617 | 0.99698 | -0.016811 | 2.9033
102 | -0.19853 | -0.094168 | 0.1986 | 0.064211 | 6.4567e-05 | -0.029957 | 0.0063624 | 0.0060416 | 0.0063624 | 0.99698 | -0.016811 | 0.99729 | -0.018454 | 2.892
103 | -0.1986 | -0.064211 | 0.1986 | 0.06141 | 5.7273e-06 | -0.0028009 | 0.0060416 | 0.0060171 | 0.0060416 | 0.99729 | -0.018454 | 0.99732 | -0.018484 | 2.7462
104 | 0.40542 | 0.19348 | -0.40542 | -0.19437 | 8.4657e-06 | -0.00088815 | 0.013 | 0.013011 | 0.013011 | 0.99753 | -0.01888 | 0.99751 | -0.018703 | 5.9142
105 | 0.27792 | 0.085228 | -0.27787 | -0.097544 | 4.9677e-05 | -0.012317 | 0.0084124 | 0.0085239 | 0.0085239 | 0.99753 | -0.01888 | 0.99735 | -0.018583 | 3.8745
106 | -1.5294 | -0.65976 | 1.5294 | 0.65949 | 3.5981e-05 | -0.0002651 | 0.048195 | 0.048192 | 0.048195 | 0.99765 | -0.019638 | 0.99768 | -0.019791 | 21.907
107 | 0.33726 | 0.16136 | -0.33725 | -0.16202 | 4.3187e-06 | -0.00065472 | 0.01082 | 0.010828 | 0.010828 | 0.99751 | -0.018703 | 0.9975 | -0.018594 | 4.9218
108 | 0.27787 | 0.097544 | -0.27786 | -0.099797 | 9.2337e-06 | -0.0022523 | 0.0085239 | 0.0085457 | 0.0085457 | 0.99735 | -0.018583 | 0.99732 | -0.018484 | 3.8844
109 | -1.5294 | -0.65949 | 1.5304 | 0.65237 | 0.00096416 | -0.0071216 | 0.048192 | 0.048108 | 0.048192 | 0.99768 | -0.019791 | 0.99827 | -0.02382 | 21.9056
110 | -3.9199 | -1.8307 | 3.9242 | 1.8353 | 0.0042676 | 0.0045108 | 0.12528 | 0.12527 | 0.12528 | 0.99691 | -0.058432 | 0.99827 | -0.02382 | 35.7938
111 | 3.7911 | 1.7684 | -3.7909 | -1.7685 | 0.00017476 | -0.00015984 | 0.12114 | 0.12114 | 0.12114 | 0.99691 | -0.058432 | 0.99686 | -0.058064 | 55.0626
112 | 3.5395 | 1.6467 | -3.538 | -1.6484 | 0.0014919 | -0.001631 | 0.11305 | 0.11307 | 0.11307 | 0.99686 | -0.058064 | 0.99647 | -0.05471 | 51.3967
113 | -0.40085 | -0.19414 | 0.40086 | 0.19323 | 8.5827e-06 | -0.00090798 | 0.012923 | 0.012912 | 0.012923 | 0.99488 | -0.041095 | 0.9949 | -0.041281 | 5.8743
114 | -2.9308 | -1.3671 | 2.9333 | 1.363 | 0.002413 | -0.0041423 | 0.093837 | 0.093777 | 0.093837 | 0.9949 | -0.041281 | 0.99567 | -0.047828 | 42.6531
115 | 0.12713 | 0.060549 | -0.12713 | -0.061572 | 9.6496e-07 | -0.0010229 | 0.0040826 | 0.0040955 | 0.0040955 | 0.99567 | -0.047828 | 0.99566 | -0.047763 | 1.8616
116 | -3.0604 | -1.4236 | 3.0611 | 1.4224 | 0.00072751 | -0.0011316 | 0.09786 | 0.097843 | 0.09786 | 0.99567 | -0.047828 | 0.99589 | -0.049712 | 44.4817
117 | -3.5358 | -1.6508 | 3.538 | 1.6484 | 0.0022123 | -0.0024138 | 0.11311 | 0.11307 | 0.11311 | 0.99589 | -0.049712 | 0.99647 | -0.05471 | 51.4138
118 | 0.47466 | 0.22837 | -0.47464 | -0.22988 | 1.9968e-05 | -0.0015114 | 0.015268 | 0.015287 | 0.015287 | 0.99589 | -0.049712 | 0.99585 | -0.049349 | 6.9488
119 | 0.33725 | 0.16202 | -0.33725 | -0.16325 | 8.1232e-06 | -0.0012287 | 0.010828 | 0.010843 | 0.010843 | 0.9975 | -0.018594 | 0.99747 | -0.018387 | 4.9288
120 | 0.10539 | 0.05085 | -0.10539 | -0.051044 | 1.2701e-07 | -0.0001936 | 0.0034008 | 0.0034032 | 0.0034032 | 0.9933 | -0.027843 | 0.9933 | -0.027833 | 1.5469
121 | -0.38689 | -0.18577 | 0.3869 | 0.18467 | 9.6718e-06 | -0.0011059 | 0.012443 | 0.012429 | 0.012443 | 0.99567 | -0.0063334 | 0.99569 | -0.0065456 | 5.6561
122 | 0.38689 | 0.18577 | -0.38688 | -0.18737 | 1.4044e-05 | -0.0016013 | 0.012443 | 0.012464 | 0.012464 | 0.99567 | -0.0063334 | 0.99564 | -0.0060202 | 5.6653
123 | -0.3869 | -0.18467 | 0.38691 | 0.18426 | 3.5798e-06 | -0.00040996 | 0.012429 | 0.012424 | 0.012429 | 0.99569 | -0.0065456 | 0.9957 | -0.0066234 | 5.6498
124 | -0.48928 | -0.23384 | 0.48934 | 0.23373 | 5.5358e-05 | -0.00011413 | 0.015722 | 0.01572 | 0.015722 | 0.9957 | -0.0066234 | 0.99582 | -0.0058392 | 7.4867
125 | -0.79131 | -0.37845 | 0.79133 | 0.37802 | 1.5906e-05 | -0.00043181 | 0.025426 | 0.02542 | 0.025426 | 0.99589 | -0.0064328 | 0.9959 | -0.0066029 | 11.5572
126 | 0.79131 | 0.37845 | -0.79126 | -0.37995 | 5.5207e-05 | -0.0014971 | 0.025426 | 0.025445 | 0.025445 | 0.99589 | -0.0064328 | 0.99582 | -0.0058392 | 11.5659
127 | -0.21634 | -0.10478 | 0.21635 | 0.10341 | 3.7389e-06 | -0.0013727 | 0.0069623 | 0.006945 | 0.0069623 | 0.99669 | -0.0062861 | 0.99671 | -0.0064345 | 3.1647
128 | 0.25841 | 0.12506 | -0.2584 | -0.12515 | 9.4777e-06 | -8.558e-05 | 0.0083083 | 0.0083095 | 0.0083095 | 0.99747 | -0.018387 | 0.99743 | -0.018629 | 3.9569

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 17.4121 | 8.0624

## res_load
| p_mw | q_mvar
0 | 0.35808 | 0.17342
1 | 0.22057 | 0.10683
2 | 0.41328 | 0.20016
3 | 0.21102 | 0.1022
4 | 0.15259 | 0.073903
5 | 0.23275 | 0.11272
6 | 0.31949 | 0.15474
7 | 0.28433 | 0.13771
8 | 0.40347 | 0.19541
9 | 0.35502 | 0.17194
10 | 0.24882 | 0.12051
11 | 0.080753 | 0.03911
12 | 0.75896 | 0.36758
13 | 0.068437 | 0.033145
14 | 0.25516 | 0.12358
15 | 0.078395 | 0.037969
16 | 0.13444 | 0.065111
17 | 0.23902 | 0.11576
18 | 0.18211 | 0.088198
19 | 0.18349 | 0.088869
20 | 0.11583 | 0.0561
21 | 0.12484 | 0.060464
22 | 0.37826 | 0.1832
23 | 0.40383 | 0.19559
24 | 0.74191 | 0.35932
25 | 0.40492 | 0.19611
26 | 0.27072 | 0.13111
27 | 0.17341 | 0.083987
28 | 0.16916 | 0.081928
29 | 0.14734 | 0.071361
30 | 0.11008 | 0.053316
31 | 0.29195 | 0.1414
32 | 0.32129 | 0.15561
33 | 0.30739 | 0.14888
34 | 0.3361 | 0.16278
35 | 0.39481 | 0.19122
36 | 0.14943 | 0.072374
37 | 0.084465 | 0.040908
38 | 0.30739 | 0.14887
39 | 2.7042 | 1.3097
40 | 0.11716 | 0.056744
41 | 0.2956 | 0.14316
42 | 0.089582 | 0.043387
43 | 0.07556 | 0.036596
44 | 0.1454 | 0.070418
45 | 0.19853 | 0.096151
46 | 0.070799 | 0.03429
47 | 0.068158 | 0.03301
48 | 0.12878 | 0.062373
49 | 0.25147 | 0.12179
50 | 0.40085 | 0.19414
51 | 0.47464 | 0.22988
52 | 0.12713 | 0.061572
53 | 0.17174 | 0.083179
54 | 0.079258 | 0.038386
55 | 0.10539 | 0.051044
56 | 0.083456 | 0.040419
57 | 0.38688 | 0.18737
58 | 0.10237 | 0.049582
59 | 0.30192 | 0.14623
60 | 0.21634 | 0.10478
61 | 0.078837 | 0.038182
62 | 0.2584 | 0.12515

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1