## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_23_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_23_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_23_0_node_1 | 20 | n |  | TRUE
3 | bus_MV_23_0_node_6 | 20 | n |  | TRUE
4 | bus_MV_23_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_23_0_node_5 | 20 | n |  | TRUE
6 | bus_MV_23_0_node_92 | 20 | n |  | TRUE
7 | bus_MV_23_0_node_93 | 20 | n |  | TRUE
8 | bus_MV_23_0_node_91 | 20 | n |  | TRUE
9 | bus_MV_23_0_node_17 | 20 | n |  | TRUE
10 | bus_MV_23_0_node_7 | 20 | n |  | TRUE
11 | bus_MV_23_0_node_8 | 20 | n |  | TRUE
12 | bus_MV_23_0_node_29 | 20 | n |  | TRUE
13 | bus_MV_23_0_node_200 | 20 | n |  | TRUE
14 | bus_MV_23_0_node_15 | 20 | n |  | TRUE
15 | bus_MV_23_0_node_31 | 20 | n |  | TRUE
16 | bus_MV_23_0_node_28 | 20 | n |  | TRUE
17 | bus_MV_23_0_node_11 | 20 | n |  | TRUE
18 | bus_MV_23_0_node_134 | 20 | n |  | TRUE
19 | bus_MV_23_0_node_12 | 20 | n |  | TRUE
20 | bus_MV_23_0_node_34 | 20 | n |  | TRUE
21 | bus_MV_23_0_node_21 | 20 | n |  | TRUE
22 | bus_MV_23_0_node_24 | 20 | n |  | TRUE
23 | bus_MV_23_0_node_22 | 20 | n |  | TRUE
24 | bus_MV_23_0_node_23 | 20 | n |  | TRUE
25 | bus_MV_23_0_node_32 | 20 | n |  | TRUE
26 | bus_MV_23_0_node_37 | 20 | n |  | TRUE
27 | bus_MV_23_0_node_35 | 20 | n |  | TRUE
28 | bus_MV_23_0_node_68 | 20 | n |  | TRUE
29 | bus_MV_23_0_node_13 | 20 | n |  | TRUE
30 | bus_MV_23_0_node_14 | 20 | n |  | TRUE
31 | bus_MV_23_0_node_16 | 20 | n |  | TRUE
32 | bus_MV_23_0_node_133 | 20 | n |  | TRUE
33 | bus_MV_23_0_node_18 | 20 | n |  | TRUE
34 | bus_MV_23_0_node_20 | 20 | n |  | TRUE
35 | bus_MV_23_0_node_40 | 20 | n |  | TRUE
36 | bus_MV_23_0_node_188 | 20 | n |  | TRUE
37 | bus_MV_23_0_node_41 | 20 | n |  | TRUE
38 | bus_MV_23_0_node_36 | 20 | n |  | TRUE
39 | bus_MV_23_0_node_33 | 20 | n |  | TRUE
40 | bus_MV_23_0_node_27 | 20 | n |  | TRUE
41 | bus_MV_23_0_node_38 | 20 | n |  | TRUE
42 | bus_MV_23_0_node_25 | 20 | n |  | TRUE
43 | bus_MV_23_0_node_26 | 20 | n |  | TRUE
44 | bus_MV_23_0_node_39 | 20 | n |  | TRUE
45 | bus_MV_23_0_node_42 | 20 | n |  | TRUE
46 | bus_MV_23_0_node_43 | 20 | n |  | TRUE
47 | bus_MV_23_0_node_44 | 20 | n |  | TRUE
48 | bus_MV_23_0_node_46 | 20 | n |  | TRUE
49 | bus_MV_23_0_node_48 | 20 | n |  | TRUE
50 | bus_MV_23_0_node_45 | 20 | n |  | TRUE
51 | bus_MV_23_0_node_47 | 20 | n |  | TRUE
52 | bus_MV_23_0_node_139 | 20 | n |  | TRUE
53 | bus_MV_23_0_node_138 | 20 | n |  | TRUE
54 | bus_MV_23_0_node_101 | 20 | n |  | TRUE
55 | bus_MV_23_0_node_69 | 20 | n |  | TRUE
56 | bus_MV_23_0_node_51 | 20 | n |  | TRUE
57 | bus_MV_23_0_node_111 | 20 | n |  | TRUE
58 | bus_MV_23_0_node_49 | 20 | n |  | TRUE
59 | bus_MV_23_0_node_186 | 20 | n |  | TRUE
60 | bus_MV_23_0_node_52 | 20 | n |  | TRUE
61 | bus_MV_23_0_node_50 | 20 | n |  | TRUE
62 | bus_MV_23_0_node_185 | 20 | n |  | TRUE
63 | bus_MV_23_0_node_67 | 20 | n |  | TRUE
64 | bus_MV_23_0_node_175 | 20 | n |  | TRUE
65 | bus_MV_23_0_node_65 | 20 | n |  | TRUE
66 | bus_MV_23_0_node_66 | 20 | n |  | TRUE
67 | bus_MV_23_0_node_63 | 20 | n |  | TRUE
68 | bus_MV_23_0_node_100 | 20 | n |  | TRUE
69 | bus_MV_23_0_node_108 | 20 | n |  | TRUE
70 | bus_MV_23_0_node_102 | 20 | n |  | TRUE
71 | bus_MV_23_0_node_103 | 20 | n |  | TRUE
72 | bus_MV_23_0_node_104 | 20 | n |  | TRUE
73 | bus_MV_23_0_node_106 | 20 | n |  | TRUE
74 | bus_MV_23_0_node_187 | 20 | n |  | TRUE
75 | bus_MV_23_0_node_98 | 20 | n |  | TRUE
76 | bus_MV_23_0_node_105 | 20 | n |  | TRUE
77 | bus_MV_23_0_node_81 | 20 | n |  | TRUE
78 | bus_MV_23_0_node_64 | 20 | n |  | TRUE
79 | bus_MV_23_0_node_124 | 20 | n |  | TRUE
80 | bus_MV_23_0_node_176 | 20 | n |  | TRUE
81 | bus_MV_23_0_node_155 | 20 | n |  | TRUE
82 | bus_MV_23_0_node_53 | 20 | n |  | TRUE
83 | bus_MV_23_0_node_54 | 20 | n |  | TRUE
84 | bus_MV_23_0_node_55 | 20 | n |  | TRUE
85 | bus_MV_23_0_node_199 | 20 | n |  | TRUE
86 | bus_MV_23_0_node_62 | 20 | n |  | TRUE
87 | bus_MV_23_0_node_56 | 20 | n |  | TRUE
88 | bus_MV_23_0_node_60 | 20 | n |  | TRUE
89 | bus_MV_23_0_node_57 | 20 | n |  | TRUE
90 | bus_MV_23_0_node_184 | 20 | n |  | TRUE
91 | bus_MV_23_0_node_94 | 20 | n |  | TRUE
92 | bus_MV_23_0_node_58 | 20 | n |  | TRUE
93 | bus_MV_23_0_node_154 | 20 | n |  | TRUE
94 | bus_MV_23_0_node_59 | 20 | n |  | TRUE
95 | bus_MV_23_0_node_110 | 20 | n |  | TRUE
96 | bus_MV_23_0_node_144 | 20 | n |  | TRUE
97 | bus_MV_23_0_node_197 | 20 | n |  | TRUE
98 | bus_MV_23_0_node_61 | 20 | n |  | TRUE
99 | bus_MV_23_0_node_79 | 20 | n |  | TRUE
100 | bus_MV_23_0_node_78 | 20 | n |  | TRUE
101 | bus_MV_23_0_node_85 | 20 | n |  | TRUE
102 | bus_MV_23_0_node_153 | 20 | n |  | TRUE
103 | bus_MV_23_0_node_145 | 20 | n |  | TRUE
104 | bus_MV_23_0_node_142 | 20 | n |  | TRUE
105 | bus_MV_23_0_node_80 | 20 | n |  | TRUE
106 | bus_MV_23_0_node_141 | 20 | n |  | TRUE
107 | bus_MV_23_0_node_82 | 20 | n |  | TRUE
108 | bus_MV_23_0_node_83 | 20 | n |  | TRUE
109 | bus_MV_23_0_node_97 | 20 | n |  | TRUE
110 | bus_MV_23_0_node_84 | 20 | n |  | TRUE
111 | bus_MV_23_0_node_112 | 20 | n |  | TRUE
112 | bus_MV_23_0_node_198 | 20 | n |  | TRUE
113 | bus_MV_23_0_node_109 | 20 | n |  | TRUE
114 | bus_MV_23_0_node_113 | 20 | n |  | TRUE
115 | bus_MV_23_0_node_196 | 20 | n |  | TRUE
116 | bus_MV_23_0_node_107 | 20 | n |  | TRUE
117 | bus_MV_23_0_node_143 | 20 | n |  | TRUE
118 | bus_MV_23_0_node_137 | 20 | n |  | TRUE
119 | bus_MV_23_0_node_136 | 20 | n |  | TRUE
120 | bus_MV_23_0_node_135 | 20 | n |  | TRUE
121 | bus_MV_23_0_node_70 | 20 | n |  | TRUE
122 | bus_MV_23_0_node_71 | 20 | n |  | TRUE
123 | bus_MV_23_0_node_73 | 20 | n |  | TRUE
124 | bus_MV_23_0_node_75 | 20 | n |  | TRUE
125 | bus_MV_23_0_node_76 | 20 | n |  | TRUE
126 | bus_MV_23_0_node_77 | 20 | n |  | TRUE
127 | bus_MV_23_0_node_140 | 20 | n |  | TRUE
128 | bus_MV_23_0_node_192 | 20 | n |  | TRUE
129 | bus_MV_23_0_node_86 | 20 | n |  | TRUE
130 | bus_MV_23_0_node_87 | 20 | n |  | TRUE
131 | bus_MV_23_0_node_90 | 20 | n |  | TRUE
132 | bus_MV_23_0_node_88 | 20 | n |  | TRUE
133 | bus_MV_23_0_node_89 | 20 | n |  | TRUE
134 | bus_MV_23_0_node_146 | 20 | n |  | TRUE
135 | bus_MV_23_0_node_181 | 20 | n |  | TRUE
136 | bus_MV_23_0_node_147 | 20 | n |  | TRUE
137 | bus_MV_23_0_node_195 | 20 | n |  | TRUE
138 | bus_MV_23_0_node_182 | 20 | n |  | TRUE
139 | bus_MV_23_0_node_114 | 20 | n |  | TRUE
140 | bus_MV_23_0_node_178 | 20 | n |  | TRUE
141 | bus_MV_23_0_node_179 | 20 | n |  | TRUE
142 | bus_MV_23_0_node_180 | 20 | n |  | TRUE
143 | bus_MV_23_0_node_183 | 20 | n |  | TRUE
144 | bus_MV_23_0_node_190 | 20 | n |  | TRUE
145 | bus_MV_23_0_node_189 | 20 | n |  | TRUE
146 | bus_MV_23_0_node_191 | 20 | n |  | TRUE
147 | bus_MV_23_0_node_177 | 20 | n |  | TRUE
148 | bus_MV_23_0_node_117 | 20 | n |  | TRUE
149 | bus_MV_23_0_node_118 | 20 | n |  | TRUE
150 | bus_MV_23_0_node_119 | 20 | n |  | TRUE
151 | bus_MV_23_0_node_120 | 20 | n |  | TRUE
152 | bus_MV_23_0_node_173 | 20 | n |  | TRUE
153 | bus_MV_23_0_node_126 | 20 | n |  | TRUE
154 | bus_MV_23_0_node_156 | 20 | n |  | TRUE
155 | bus_MV_23_0_node_160 | 20 | n |  | TRUE
156 | bus_MV_23_0_node_121 | 20 | n |  | TRUE
157 | bus_MV_23_0_node_194 | 20 | n |  | TRUE
158 | bus_MV_23_0_node_123 | 20 | n |  | TRUE
159 | bus_MV_23_0_node_165 | 20 | n |  | TRUE
160 | bus_MV_23_0_node_125 | 20 | n |  | TRUE
161 | bus_MV_23_0_node_151 | 20 | n |  | TRUE
162 | bus_MV_23_0_node_129 | 20 | n |  | TRUE
163 | bus_MV_23_0_node_161 | 20 | n |  | TRUE
164 | bus_MV_23_0_node_130 | 20 | n |  | TRUE
165 | bus_MV_23_0_node_158 | 20 | n |  | TRUE
166 | bus_MV_23_0_node_131 | 20 | n |  | TRUE
167 | bus_MV_23_0_node_157 | 20 | n |  | TRUE
168 | bus_MV_23_0_node_128 | 20 | n |  | TRUE
169 | bus_MV_23_0_node_159 | 20 | n |  | TRUE
170 | bus_MV_23_0_node_162 | 20 | n |  | TRUE
171 | bus_MV_23_0_node_163 | 20 | n |  | TRUE
172 | bus_MV_23_0_node_164 | 20 | n |  | TRUE
173 | bus_MV_23_0_node_132 | 20 | n |  | TRUE
174 | bus_MV_23_0_node_166 | 20 | n |  | TRUE
175 | bus_MV_23_0_node_167 | 20 | n |  | TRUE
176 | bus_MV_23_0_node_127 | 20 | n |  | TRUE
177 | bus_MV_23_0_node_201 | 20 | n |  | TRUE
178 | bus_MV_23_0_node_172 | 20 | n |  | TRUE
179 | bus_MV_23_0_node_174 | 20 | n |  | TRUE
180 | bus_MV_23_0_node_168 | 20 | n |  | TRUE
181 | bus_MV_23_0_node_148 | 20 | n |  | TRUE
182 | bus_MV_23_0_node_149 | 20 | n |  | TRUE
183 | bus_MV_23_0_node_150 | 20 | n |  | TRUE
184 | bus_MV_23_0_node_152 | 20 | n |  | TRUE
185 | bus_MV_23_0_node_170 | 20 | n |  | TRUE
186 | bus_MV_23_0_node_169 | 20 | n |  | TRUE
187 | bus_MV_23_0_node_193 | 20 | n |  | TRUE
188 | bus_MV_23_0_node_171 | 20 | n |  | TRUE
189 | bus_HV_23_0_node_47 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_23_0_load_0 | 0 | 0.30612 | 0.14826 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_23_0_load_1 | 2 | 0.071158 | 0.034463 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_23_0_load_5 | 5 | 0.22626 | 0.10958 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_23_0_load_93 | 7 | 0.098733 | 0.047819 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_23_0_load_17 | 9 | 0.26467 | 0.12819 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_23_0_load_29 | 12 | 0.40295 | 0.19516 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_23_0_load_200 | 13 | 0.40463 | 0.19597 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_23_0_load_11 | 17 | 0.4154 | 0.20119 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_23_0_load_134 | 18 | 0.085606 | 0.041461 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_23_0_load_12 | 19 | 0.25786 | 0.12489 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_23_0_load_34 | 20 | 0.31487 | 0.1525 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_23_0_load_22 | 23 | 0.18747 | 0.090796 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_23_0_load_37 | 26 | 0.11238 | 0.054428 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_23_0_load_35 | 27 | 0.089826 | 0.043505 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_23_0_load_68 | 28 | 0.37512 | 0.18168 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_23_0_load_13 | 29 | 0.36214 | 0.17539 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_23_0_load_133 | 32 | 0.13483 | 0.065302 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_23_0_load_18 | 33 | 0.20027 | 0.096994 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_23_0_load_40 | 35 | 0.30727 | 0.14882 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_23_0_load_188 | 36 | 0.33504 | 0.16227 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_23_0_load_41 | 37 | 0.21395 | 0.10362 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_23_0_load_36 | 38 | 0.29299 | 0.1419 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_23_0_load_27 | 40 | 0.16695 | 0.080857 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_23_0_load_25 | 42 | 0.32289 | 0.15638 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_23_0_load_39 | 44 | 0.18052 | 0.08743 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_23_0_load_42 | 45 | 0.2194 | 0.10626 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_23_0_load_139 | 52 | 0.074288 | 0.035979 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_23_0_load_138 | 53 | 0.25466 | 0.12334 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_23_0_load_101 | 54 | 0.28054 | 0.13587 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_23_0_load_69 | 55 | 0.39258 | 0.19014 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_23_0_load_111 | 57 | 0.23339 | 0.11304 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_23_0_load_186 | 59 | 0.29563 | 0.14318 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_23_0_load_185 | 62 | 0.29945 | 0.14503 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_23_0_load_175 | 64 | 0.35874 | 0.17374 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_23_0_load_63 | 67 | 0.14661 | 0.071008 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_23_0_load_102 | 70 | 0.1916 | 0.092798 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_23_0_load_187 | 74 | 0.091451 | 0.044292 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_23_0_load_98 | 75 | 0.17916 | 0.08677 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_23_0_load_124 | 79 | 0.21609 | 0.10466 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_23_0_load_176 | 80 | 0.33969 | 0.16452 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_23_0_load_155 | 81 | 0.16306 | 0.078973 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_23_0_load_53 | 82 | 0.24366 | 0.11801 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_23_0_load_199 | 85 | 0.23806 | 0.1153 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_23_0_load_184 | 90 | 0.28949 | 0.14021 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_23_0_load_94 | 91 | 0.25787 | 0.12489 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_23_0_load_154 | 93 | 0.23613 | 0.11436 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_23_0_load_110 | 95 | 0.35964 | 0.17418 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_23_0_load_144 | 96 | 0.083776 | 0.040574 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_23_0_load_197 | 97 | 0.34204 | 0.16566 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_23_0_load_78 | 100 | 0.30273 | 0.14662 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_23_0_load_85 | 101 | 0.22567 | 0.1093 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_23_0_load_145 | 103 | 0.090542 | 0.043852 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_23_0_load_142 | 104 | 0.13133 | 0.063608 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_23_0_load_141 | 106 | 0.068003 | 0.032935 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_23_0_load_97 | 109 | 0.32175 | 0.15583 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_23_0_load_112 | 111 | 0.17339 | 0.083975 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_23_0_load_198 | 112 | 0.22811 | 0.11048 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_23_0_load_113 | 114 | 0.29808 | 0.14437 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_23_0_load_196 | 115 | 0.1585 | 0.076765 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_23_0_load_143 | 117 | 0.069256 | 0.033542 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_23_0_load_137 | 118 | 0.25146 | 0.12179 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_23_0_load_135 | 120 | 0.26803 | 0.12981 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_23_0_load_70 | 121 | 0.14168 | 0.06862 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_23_0_load_73 | 123 | 0.12939 | 0.062665 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_23_0_load_77 | 126 | 0.095422 | 0.046215 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_23_0_load_140 | 127 | 0.074674 | 0.036166 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_23_0_load_192 | 128 | 0.36118 | 0.17493 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_23_0_load_86 | 129 | 0.11099 | 0.053755 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_23_0_load_87 | 130 | 0.10779 | 0.052204 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_23_0_load_90 | 131 | 0.13488 | 0.065327 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_23_0_load_181 | 135 | 0.16932 | 0.082007 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_23_0_load_195 | 137 | 0.39133 | 0.18953 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_23_0_load_182 | 138 | 0.21702 | 0.10511 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_23_0_load_114 | 139 | 0.33332 | 0.16143 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_23_0_load_183 | 143 | 0.15084 | 0.073055 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_23_0_load_190 | 144 | 0.40033 | 0.19389 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_23_0_load_177 | 147 | 0.16199 | 0.078455 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_23_0_load_117 | 148 | 0.36418 | 0.17638 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_23_0_load_173 | 152 | 0.19719 | 0.095505 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_23_0_load_126 | 153 | 0.14221 | 0.068877 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_23_0_load_156 | 154 | 0.17864 | 0.086518 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_23_0_load_160 | 155 | 0.070911 | 0.034344 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_23_0_load_194 | 157 | 0.14737 | 0.071374 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_23_0_load_165 | 159 | 0.082844 | 0.040123 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_23_0_load_125 | 160 | 0.31765 | 0.15384 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_23_0_load_157 | 167 | 0.075483 | 0.036558 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_23_0_load_159 | 169 | 0.22885 | 0.11084 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_23_0_load_162 | 170 | 0.10048 | 0.048665 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_23_0_load_163 | 171 | 0.1796 | 0.086983 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_23_0_load_166 | 174 | 0.093654 | 0.045359 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_23_0_load_127 | 176 | 0.3075 | 0.14893 | 0 | 0 |  | 1 | TRUE | wye
91 | MV_23_0_load_201 | 177 | 0.12672 | 0.061373 | 0 | 0 |  | 1 | TRUE | wye
92 | MV_23_0_load_174 | 179 | 0.27338 | 0.13241 | 0 | 0 |  | 1 | TRUE | wye
93 | MV_23_0_load_148 | 181 | 0.18778 | 0.090944 | 0 | 0 |  | 1 | TRUE | wye
94 | MV_23_0_load_152 | 184 | 0.12773 | 0.061861 | 0 | 0 |  | 1 | TRUE | wye
95 | MV_23_0_load_193 | 187 | 0.24622 | 0.11925 | 0 | 0 |  | 1 | TRUE | wye
96 | MV_23_0_load_171 | 188 | 0.18187 | 0.088086 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 51 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_23_0_line_0 |  | 0 | 1 | 0.035908 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_23_0_line_1 |  | 0 | 2 | 0.10521 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_23_0_line_2 |  | 1 | 3 | 0.20276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_23_0_line_3 |  | 2 | 4 | 0.05434 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_23_0_line_4 |  | 3 | 9 | 0.028673 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_23_0_line_5 |  | 4 | 5 | 0.016034 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_23_0_line_6 |  | 6 | 7 | 0.1086 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_23_0_line_7 |  | 6 | 8 | 0.65079 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_23_0_line_8 |  | 8 | 131 | 0.12354 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_23_0_line_9 |  | 9 | 14 | 0.017426 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_23_0_line_10 |  | 10 | 11 | 0.24771 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_23_0_line_11 |  | 10 | 12 | 0.033545 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_23_0_line_12 |  | 11 | 13 | 0.005395 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_23_0_line_13 |  | 12 | 15 | 0.1847 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_23_0_line_14 |  | 13 | 16 | 0.055597 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
15 | MV_23_0_line_15 |  | 14 | 30 | 0.24623 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_23_0_line_16 |  | 15 | 25 | 0.15668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_23_0_line_17 |  | 15 | 37 | 0.079031 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_23_0_line_18 |  | 16 | 43 | 0.12681 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
19 | MV_23_0_line_19 |  | 17 | 18 | 0.25266 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_23_0_line_20 |  | 18 | 24 | 0.03507 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_23_0_line_21 |  | 19 | 20 | 0.26567 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_23_0_line_22 |  | 20 | 27 | 0.2227 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
23 | MV_23_0_line_23 |  | 20 | 28 | 1.2502 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
24 | MV_23_0_line_24 |  | 21 | 22 | 0.036924 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_23_0_line_25 |  | 21 | 23 | 0.13725 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_23_0_line_26 |  | 22 | 26 | 0.16216 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_23_0_line_27 |  | 22 | 24 | 0.069022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_23_0_line_28 |  | 23 | 32 | 0.20773 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_23_0_line_29 |  | 24 | 25 | 0.091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_23_0_line_30 |  | 25 | 38 | 0.026146 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_23_0_line_31 |  | 26 | 41 | 0.066942 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_23_0_line_32 |  | 27 | 39 | 0.072914 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
33 | MV_23_0_line_33 |  | 28 | 36 | 0.26894 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
34 | MV_23_0_line_34 |  | 29 | 30 | 0.058731 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_23_0_line_35 |  | 30 | 31 | 0.49006 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_23_0_line_36 |  | 31 | 32 | 0.062343 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_23_0_line_37 |  | 31 | 33 | 0.11469 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_23_0_line_38 |  | 32 | 34 | 0.46563 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_23_0_line_39 |  | 34 | 35 | 0.019552 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_23_0_line_40 |  | 36 | 72 | 0.065211 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
41 | MV_23_0_line_41 |  | 39 | 40 | 0.083007 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
42 | MV_23_0_line_42 |  | 40 | 42 | 0.022005 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
43 | MV_23_0_line_43 |  | 41 | 44 | 0.061806 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_23_0_line_44 |  | 42 | 43 | 0.043283 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
45 | MV_23_0_line_45 |  | 45 | 46 | 0.00351 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
46 | MV_23_0_line_46 |  | 45 | 47 | 0.037924 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
47 | MV_23_0_line_47 |  | 46 | 48 | 0.24545 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
48 | MV_23_0_line_48 |  | 47 | 49 | 0.22798 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
49 | MV_23_0_line_49 |  | 48 | 54 | 0.006481 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_23_0_line_50 |  | 48 | 50 | 0.35627 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
51 | MV_23_0_line_51 |  | 49 | 56 | 0.4025 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
52 | MV_23_0_line_52 |  | 49 | 57 | 0.004354 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_23_0_line_53 |  | 50 | 51 | 0.17088 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
54 | MV_23_0_line_54 |  | 50 | 52 | 0.087864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_23_0_line_55 |  | 50 | 53 | 0.15508 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
56 | MV_23_0_line_56 |  | 51 | 55 | 0.06949 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_23_0_line_57 |  | 53 | 68 | 0.031986 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
58 | MV_23_0_line_58 |  | 55 | 69 | 0.068917 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_23_0_line_59 |  | 56 | 64 | 0.040184 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
60 | MV_23_0_line_60 |  | 56 | 58 | 0.29094 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_23_0_line_61 |  | 58 | 59 | 0.006044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_23_0_line_62 |  | 58 | 60 | 0.491 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_23_0_line_63 |  | 60 | 65 | 0.3729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_23_0_line_64 |  | 60 | 66 | 0.34481 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_23_0_line_65 |  | 60 | 67 | 0.015172 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_23_0_line_66 |  | 61 | 62 | 0.004596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_23_0_line_67 |  | 61 | 63 | 0.6464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_23_0_line_68 |  | 63 | 75 | 0.032691 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
69 | MV_23_0_line_69 |  | 63 | 68 | 0.14149 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
70 | MV_23_0_line_70 |  | 63 | 76 | 0.18946 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_23_0_line_71 |  | 63 | 73 | 0.32675 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
72 | MV_23_0_line_72 |  | 64 | 77 | 0.010349 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
73 | MV_23_0_line_73 |  | 65 | 80 | 0.028846 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
74 | MV_23_0_line_74 |  | 65 | 78 | 0.16534 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_23_0_line_75 |  | 66 | 81 | 0.091536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_23_0_line_76 |  | 68 | 113 | 0.1074 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_23_0_line_77 |  | 69 | 74 | 0.050724 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_23_0_line_78 |  | 70 | 71 | 0.01774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_23_0_line_79 |  | 71 | 72 | 0.005417 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
80 | MV_23_0_line_80 |  | 71 | 73 | 0.12647 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
81 | MV_23_0_line_81 |  | 73 | 115 | 0.003553 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_23_0_line_82 |  | 73 | 116 | 0.031775 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_23_0_line_83 |  | 76 | 114 | 0.050876 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_23_0_line_84 |  | 77 | 107 | 0.83967 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_23_0_line_85 |  | 77 | 108 | 0.61527 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_23_0_line_86 |  | 77 | 99 | 0.27144 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
87 | MV_23_0_line_87 |  | 77 | 105 | 0.25766 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_23_0_line_88 |  | 78 | 79 | 0.032917 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_23_0_line_89 |  | 82 | 83 | 0.01897 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_23_0_line_90 |  | 83 | 84 | 0.11096 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_23_0_line_91 |  | 84 | 85 | 0.029466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_23_0_line_92 |  | 84 | 86 | 0.29839 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_23_0_line_93 |  | 86 | 101 | 0.003643 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_23_0_line_94 |  | 86 | 87 | 0.48949 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
95 | MV_23_0_line_95 |  | 86 | 98 | 0.18113 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
96 | MV_23_0_line_96 |  | 87 | 88 | 0.32157 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_23_0_line_97 |  | 87 | 89 | 0.57615 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
98 | MV_23_0_line_98 |  | 87 | 90 | 0.019592 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_23_0_line_99 |  | 87 | 91 | 0.43182 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_23_0_line_100 |  | 88 | 97 | 0.003352 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_23_0_line_101 |  | 89 | 92 | 0.30711 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_23_0_line_102 |  | 89 | 93 | 0.011581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_23_0_line_103 |  | 92 | 94 | 0.24243 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_23_0_line_104 |  | 92 | 95 | 0.049917 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_23_0_line_105 |  | 93 | 102 | 0.004095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_23_0_line_106 |  | 94 | 96 | 0.087743 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_23_0_line_107 |  | 96 | 103 | 0.026468 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_23_0_line_108 |  | 98 | 99 | 0.11707 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
109 | MV_23_0_line_109 |  | 98 | 100 | 0.011661 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_23_0_line_110 |  | 99 | 104 | 0.027305 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_23_0_line_111 |  | 102 | 184 | 0.02771 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_23_0_line_112 |  | 105 | 106 | 0.01907 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_23_0_line_113 |  | 106 | 127 | 0.034392 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_23_0_line_114 |  | 107 | 109 | 0.15161 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
115 | MV_23_0_line_115 |  | 108 | 110 | 0.38578 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_23_0_line_116 |  | 108 | 111 | 0.045356 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
117 | MV_23_0_line_117 |  | 109 | 128 | 0.45112 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
118 | MV_23_0_line_118 |  | 110 | 112 | 0.025369 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_23_0_line_119 |  | 111 | 122 | 0.23501 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
120 | MV_23_0_line_120 |  | 113 | 118 | 0.0045824 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_23_0_line_121 |  | 113 | 119 | 0.022195 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_23_0_line_122 |  | 116 | 117 | 0.033729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_23_0_line_123 |  | 119 | 120 | 0.0038735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_23_0_line_124 |  | 121 | 122 | 0.028485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_23_0_line_125 |  | 121 | 123 | 0.19545 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
126 | MV_23_0_line_126 |  | 123 | 124 | 0.027337 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_23_0_line_127 |  | 124 | 125 | 0.22437 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_23_0_line_128 |  | 125 | 126 | 0.12536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_23_0_line_129 |  | 128 | 146 | 0.062129 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_23_0_line_130 |  | 129 | 130 | 0.090659 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
131 | MV_23_0_line_131 |  | 129 | 131 | 0.47559 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
132 | MV_23_0_line_132 |  | 130 | 132 | 0.093208 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_23_0_line_133 |  | 132 | 133 | 0.10791 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_23_0_line_134 |  | 133 | 134 | 0.99919 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_23_0_line_135 |  | 133 | 135 | 0.075491 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
136 | MV_23_0_line_136 |  | 134 | 136 | 0.4359 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_23_0_line_137 |  | 134 | 137 | 0.042282 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
138 | MV_23_0_line_138 |  | 136 | 138 | 0.10421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_23_0_line_139 |  | 137 | 140 | 1.1033 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
140 | MV_23_0_line_140 |  | 139 | 140 | 0.85811 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
141 | MV_23_0_line_141 |  | 140 | 147 | 0.064706 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
142 | MV_23_0_line_142 |  | 140 | 142 | 0.98758 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_23_0_line_143 |  | 141 | 142 | 0.35566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_23_0_line_144 |  | 141 | 143 | 0.00606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_23_0_line_145 |  | 142 | 144 | 0.049144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_23_0_line_146 |  | 144 | 145 | 0.015707 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_23_0_line_147 |  | 145 | 146 | 0.51841 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_23_0_line_148 |  | 148 | 149 | 0.058755 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
149 | MV_23_0_line_149 |  | 149 | 150 | 0.1036 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_23_0_line_150 |  | 149 | 151 | 0.3796 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_23_0_line_151 |  | 150 | 152 | 0.0086825 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_23_0_line_152 |  | 151 | 153 | 0.00727 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_23_0_line_153 |  | 151 | 154 | 0.092133 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
154 | MV_23_0_line_154 |  | 151 | 155 | 0.082892 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
155 | MV_23_0_line_155 |  | 152 | 161 | 0.03444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_23_0_line_156 |  | 154 | 166 | 0.054072 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_23_0_line_157 |  | 155 | 162 | 0.052928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_23_0_line_158 |  | 156 | 157 | 0.022654 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_23_0_line_159 |  | 156 | 158 | 0.42442 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_23_0_line_160 |  | 156 | 159 | 0.08648 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
161 | MV_23_0_line_161 |  | 158 | 160 | 0.034331 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_23_0_line_162 |  | 159 | 172 | 0.053711 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_23_0_line_163 |  | 161 | 183 | 0.22139 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_23_0_line_164 |  | 162 | 163 | 0.072347 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_23_0_line_165 |  | 163 | 170 | 0.00057229 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_23_0_line_166 |  | 164 | 165 | 0.006199 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_23_0_line_167 |  | 164 | 166 | 0.12659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_23_0_line_168 |  | 164 | 167 | 0.043872 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_23_0_line_169 |  | 165 | 169 | 0.016514 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_23_0_line_170 |  | 166 | 168 | 0.38521 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
171 | MV_23_0_line_171 |  | 168 | 177 | 0.1568 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
172 | MV_23_0_line_172 |  | 168 | 176 | 0.031064 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_23_0_line_173 |  | 171 | 172 | 0.022878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
174 | MV_23_0_line_174 |  | 172 | 173 | 0.060757 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_23_0_line_175 |  | 173 | 179 | 0.047333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_23_0_line_176 |  | 174 | 175 | 0.0044369 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_23_0_line_177 |  | 175 | 185 | 0.17068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
178 | MV_23_0_line_178 |  | 175 | 180 | 0.030205 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
179 | MV_23_0_line_179 |  | 177 | 178 | 0.009612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
180 | MV_23_0_line_180 |  | 178 | 185 | 0.043242 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
181 | MV_23_0_line_181 |  | 179 | 180 | 0.068886 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
182 | MV_23_0_line_182 |  | 181 | 182 | 0.0067 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
183 | MV_23_0_line_183 |  | 182 | 183 | 0.23573 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
184 | MV_23_0_line_184 |  | 183 | 184 | 0.015756 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
185 | MV_23_0_line_185 |  | 185 | 188 | 0.035583 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
186 | MV_23_0_line_186 |  | 185 | 186 | 0.65995 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
187 | MV_23_0_line_187 |  | 186 | 187 | 0.028556 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_23_0_trafo_47 | 25 MVA 110/20 kV | 189 | 51 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2666657.1073 | 1204861.5935
1 | 2666668.9274 | 1204827.6827
2 | 2666622.3605 | 1204960.8958
3 | 2666654.6142 | 1204641.9882
4 | 2666604.4124 | 1205012.186
5 | 2666599.3285 | 1205027.394
6 | 2667530.2556 | 1206112.3837
7 | 2667631.7581 | 1206151.0114
8 | 2667945.3938 | 1206008.1951
9 | 2666639.0902 | 1204617.856
10 | 2666262.6786 | 1205012.6858
11 | 2666401.2814 | 1205126.8496
12 | 2666233.6071 | 1205029.5626
13 | 2666398.4461 | 1205131.4431
14 | 2666629.6606 | 1204603.1864
15 | 2666053.0411 | 1204990.6842
16 | 2666378.729 | 1205180.6871
17 | 2666291.1875 | 1204636.1075
18 | 2666094.3681 | 1204794.5351
19 | 2666453.9602 | 1205445.2618
20 | 2666210.4364 | 1205551.4553
21 | 2666033.8288 | 1204726.2674
22 | 2666019.203 | 1204750.7205
23 | 2666080.4556 | 1204599.7509
24 | 2666060.218 | 1204797.1909
25 | 2666075.5117 | 1204875.2962
26 | 2665952.6347 | 1204867.378
27 | 2666236.1255 | 1205330.2444
28 | 2665732.4122 | 1206706.6652
29 | 2666446.2158 | 1204454.2531
30 | 2666492.5857 | 1204418.0471
31 | 2666220.6314 | 1204407.9649
32 | 2666239.8039 | 1204466.4826
33 | 2666109.0668 | 1204381.3688
34 | 2665789.314 | 1204584.2505
35 | 2665787.084 | 1204603.6711
36 | 2665887.6462 | 1206926.2872
37 | 2666003.9547 | 1205051.6896
38 | 2666060.6492 | 1204853.7855
39 | 2666193.3018 | 1205271.3067
40 | 2666263.1549 | 1205226.4659
41 | 2665891.8502 | 1204893.0672
42 | 2666275.4659 | 1205208.2273
43 | 2666309.5657 | 1205234.8852
44 | 2665835.1247 | 1204916.3337
45 | 2666264.9762 | 1207487.1706
46 | 2666265.1898 | 1207483.682
47 | 2666303.0102 | 1207487.2707
48 | 2666294.3856 | 1207346.4112
49 | 2666348.9555 | 1207671.0598
50 | 2666100.1473 | 1207431.3208
51 | 2666105.926 | 1207266.6066
52 | 2666097.3591 | 1207519.1406
53 | 2665949.3896 | 1207394.9473
54 | 2666297.2259 | 1207340.5836
55 | 2666036.5788 | 1207262.1478
56 | 2666214.0666 | 1207841.5443
57 | 2666353.3151 | 1207670.8192
58 | 2666103.7569 | 1207715.0338
59 | 2666097.6994 | 1207714.7999
60 | 2665795.3555 | 1207791.2073
61 | 2665702.5923 | 1207538.3985
62 | 2665700.3324 | 1207534.3934
63 | 2665794.9581 | 1207327.2425
64 | 2666251.0791 | 1207857.4312
65 | 2665548.7482 | 1207944.9108
66 | 2665582.0068 | 1207793.2725
67 | 2665810.5162 | 1207789.9069
68 | 2665917.5402 | 1207397.9041
69 | 2665967.6614 | 1207262.1416
70 | 2665973.5691 | 1206945.781
71 | 2665956.6721 | 1206940.2243
72 | 2665951.2631 | 1206939.7198
73 | 2665887.5537 | 1207013.8839
74 | 2665973.2789 | 1207312.5454
75 | 2665827.1443 | 1207332.9674
76 | 2665684.1457 | 1207173.5735
77 | 2666255.0705 | 1207847.8808
78 | 2665625.1656 | 1208026.878
79 | 2665630.1834 | 1208059.3974
80 | 2665523.6082 | 1207959.0546
81 | 2665492.0459 | 1207800.5913
82 | 2665934.9204 | 1208083.5696
83 | 2665923.5846 | 1208091.7717
84 | 2665971.8292 | 1208150.7072
85 | 2665959.8985 | 1208177.6585
86 | 2666214.4752 | 1208193.9085
87 | 2666169.193 | 1208380.2314
88 | 2666386.5897 | 1208268.7655
89 | 2665823.3873 | 1208602.667
90 | 2666161.9746 | 1208362.0181
91 | 2666451.9267 | 1208706.6159
92 | 2665981.9142 | 1208519.6218
93 | 2665820.8072 | 1208613.9566
94 | 2665935.5891 | 1208642.952
95 | 2666015.1244 | 1208482.355
96 | 2665890.4519 | 1208717.7775
97 | 2666385.5303 | 1208265.5851
98 | 2666316.3915 | 1208116.8814
99 | 2666332.3075 | 1208013.3728
100 | 2666320.618 | 1208106.0106
101 | 2666212.7819 | 1208197.1361
102 | 2665816.811 | 1208613.012
103 | 2665880.9126 | 1208742.4633
104 | 2666307.3813 | 1208002.2257
105 | 2666161.5497 | 1208006.0626
106 | 2666152.7173 | 1208022.9639
107 | 2666587.4339 | 1208175.8008
108 | 2666563.9328 | 1207603.2221
109 | 2666669.7686 | 1208048.4973
110 | 2666566.8837 | 1207789.2575
111 | 2666603.9171 | 1207581.8105
112 | 2666573.3424 | 1207813.4999
113 | 2665950.1568 | 1207326.0983
114 | 2665634.3159 | 1207164.4312
115 | 2665888.6178 | 1207010.4935
116 | 2665860.6835 | 1207006.5941
117 | 2665843.9485 | 1206979.4709
118 | 2665950.5779 | 1207330.6613
119 | 2665948.0589 | 1207304.0061
120 | 2665947.7517 | 1207300.1448
121 | 2666735.1424 | 1207375.3162
122 | 2666706.9685 | 1207370.5985
123 | 2666770.2196 | 1207183.0354
124 | 2666795.3858 | 1207187.4973
125 | 2666916.9732 | 1207199.6216
126 | 2667002.0836 | 1207109.3319
127 | 2666118.9912 | 1208029.1302
128 | 2667005.6222 | 1208349.6747
129 | 2668338.0491 | 1206455.3039
130 | 2668354.3299 | 1206544.4893
131 | 2668044.4737 | 1206081.1343
132 | 2668360.2602 | 1206632.2887
133 | 2668407.1053 | 1206723.4142
134 | 2668269.033 | 1207392.4554
135 | 2668467.5517 | 1206678.1904
136 | 2668426.3963 | 1207128.9282
137 | 2668288.4577 | 1207430.0116
138 | 2668363.1831 | 1207056.9712
139 | 2668034.8253 | 1209356.7121
140 | 2668014.8442 | 1208498.8339
141 | 2667454.5171 | 1208161.0361
142 | 2667428.3353 | 1208438.5884
143 | 2667452.8723 | 1208155.2028
144 | 2667386.4742 | 1208455.4261
145 | 2667370.9568 | 1208458.1304
146 | 2667055.873 | 1208320.2987
147 | 2668031.8849 | 1208561.2554
148 | 2665637.8146 | 1208499.1941
149 | 2665618.9638 | 1208554.8431
150 | 2665654.4662 | 1208634.4598
151 | 2665445.8008 | 1208784.8161
152 | 2665652.2143 | 1208640.2167
153 | 2665449.6318 | 1208778.6321
154 | 2665355.3682 | 1208802.435
155 | 2665458.946 | 1208866.6596
156 | 2665408.0301 | 1208441.059
157 | 2665422.9891 | 1208424.0125
158 | 2665578.7266 | 1208311.0411
159 | 2665367.7071 | 1208517.5634
160 | 2665555.4132 | 1208320.9911
161 | 2665669.8525 | 1208669.795
162 | 2665431.2037 | 1208911.7336
163 | 2665478.7822 | 1208937.6711
164 | 2665253.8534 | 1208901.2972
165 | 2665248.9539 | 1208905.1126
166 | 2665328.2256 | 1208849.201
167 | 2665223.624 | 1208869.5027
168 | 2665121.4843 | 1208645.0177
169 | 2665234.7963 | 1208912.985
170 | 2665479.0849 | 1208937.1854
171 | 2665404.19 | 1208569.3106
172 | 2665381.3129 | 1208569.5225
173 | 2665331.5517 | 1208598.8957
174 | 2665238.6816 | 1208485.4375
175 | 2665239.7356 | 1208489.7474
176 | 2665099.5534 | 1208666.4138
177 | 2665091.6818 | 1208491.0766
178 | 2665100.6311 | 1208487.5054
179 | 2665293.4035 | 1208571.6729
180 | 2665250.046 | 1208518.144
181 | 2665762.8903 | 1208647.7143
182 | 2665756.7634 | 1208645.0032
183 | 2665803.5579 | 1208653.8575
184 | 2665806.3505 | 1208638.3576
185 | 2665124.5273 | 1208460.2494
186 | 2664836.99 | 1208349.2634
187 | 2664819.3648 | 1208329.1375
188 | 2665111.1491 | 1208427.2775
189 | 2666105.926 | 1207266.6066

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98773 | -0.25253 | 0.30612 | 0.14826
1 | 0.98776 | -0.25279 | 0 | 0
2 | 0.98767 | -0.25293 | 0.071158 | 0.034463
3 | 0.98792 | -0.25422 | 0 | 0
4 | 0.98765 | -0.25279 | 0 | 0
5 | 0.98765 | -0.25274 | 0.22626 | 0.10958
6 | 0.98252 | -0.0088853 | 0 | 0
7 | 0.9825 | -0.0090202 | 0.098733 | 0.047819
8 | 0.9826 | -0.009354 | 0 | 0
9 | 0.98794 | -0.25442 | 0.26467 | 0.12819
10 | 0.99288 | -0.26658 | 0 | 0
11 | 0.99407 | -0.27703 | 0 | 0
12 | 0.99271 | -0.26515 | 0.40295 | 0.19516
13 | 0.9941 | -0.27726 | 0.40463 | 0.19597
14 | 0.98796 | -0.2546 | 0 | 0
15 | 0.99151 | -0.27363 | 0 | 0
16 | 0.99422 | -0.27586 | 0 | 0
17 | 0.99032 | -0.26628 | 0.4154 | 0.20119
18 | 0.99052 | -0.26498 | 0.085606 | 0.041461
19 | 0.9948 | -0.24477 | 0.25786 | 0.12489
20 | 0.99493 | -0.24393 | 0.31487 | 0.1525
21 | 0.99024 | -0.26255 | 0 | 0
22 | 0.99034 | -0.2634 | 0 | 0
23 | 0.98988 | -0.25937 | 0.18747 | 0.090796
24 | 0.99054 | -0.26519 | 0 | 0
25 | 0.99088 | -0.2681 | 0 | 0
26 | 0.99028 | -0.26287 | 0.11238 | 0.054428
27 | 0.99457 | -0.26426 | 0.089826 | 0.043505
28 | 0.99719 | -0.11651 | 0.37512 | 0.18168
29 | 0.98821 | -0.25678 | 0.36214 | 0.17539
30 | 0.98823 | -0.25704 | 0 | 0
31 | 0.98901 | -0.26374 | 0 | 0
32 | 0.98912 | -0.26472 | 0.13483 | 0.065302
33 | 0.98896 | -0.26402 | 0.20027 | 0.096994
34 | 0.98884 | -0.26651 | 0 | 0
35 | 0.98883 | -0.26644 | 0.30727 | 0.14882
36 | 0.99771 | -0.087264 | 0.33504 | 0.16227
37 | 0.99149 | -0.27343 | 0.21395 | 0.10362
38 | 0.99086 | -0.26819 | 0.29299 | 0.1419
39 | 0.99452 | -0.26451 | 0 | 0
40 | 0.99439 | -0.27194 | 0.16695 | 0.080857
41 | 0.99026 | -0.26273 | 0 | 0
42 | 0.99437 | -0.27201 | 0.32289 | 0.15638
43 | 0.99431 | -0.27548 | 0 | 0
44 | 0.99025 | -0.2626 | 0.18052 | 0.08743
45 | 0.99821 | -0.0098351 | 0.2194 | 0.10626
46 | 0.99821 | -0.0097965 | 0 | 0
47 | 0.99813 | -0.010246 | 0 | 0
48 | 0.9987 | -0.0070709 | 0 | 0
49 | 0.99769 | -0.012693 | 0 | 0
50 | 0.99943 | -0.0029616 | 0 | 0
51 | 1 | 0 | -21.2722 | -9.5827
52 | 0.99942 | -0.0028893 | 0.074288 | 0.035979
53 | 0.99901 | -0.026568 | 0.25466 | 0.12334
54 | 0.9987 | -0.0070491 | 0.28054 | 0.13587
55 | 0.99993 | -0.00041436 | 0.39258 | 0.19014
56 | 0.99691 | -0.016844 | 0 | 0
57 | 0.99769 | -0.012681 | 0.23339 | 0.11304
58 | 0.99649 | -0.013513 | 0 | 0
59 | 0.99648 | -0.013492 | 0.29563 | 0.14318
60 | 0.99595 | -0.0093385 | 0 | 0
61 | 0.99838 | -0.044223 | 0 | 0
62 | 0.99837 | -0.044206 | 0.29945 | 0.14503
63 | 0.99862 | -0.046223 | 0 | 0
64 | 0.99684 | -0.017211 | 0.35874 | 0.17374
65 | 0.99568 | -0.0070571 | 0 | 0
66 | 0.99588 | -0.0087988 | 0 | 0
67 | 0.99595 | -0.0093118 | 0.14661 | 0.071008
68 | 0.99897 | -0.026741 | 0 | 0
69 | 0.99992 | -0.00049788 | 0 | 0
70 | 0.99777 | -0.086933 | 0.1916 | 0.092798
71 | 0.99778 | -0.086974 | 0 | 0
72 | 0.99777 | -0.086996 | 0 | 0
73 | 0.99791 | -0.086428 | 0 | 0
74 | 0.99992 | -0.00044433 | 0.091451 | 0.044292
75 | 0.99861 | -0.046294 | 0.17916 | 0.08677
76 | 0.99851 | -0.046929 | 0 | 0
77 | 0.99683 | -0.017303 | 0 | 0
78 | 0.99564 | -0.006655 | 0 | 0
79 | 0.99563 | -0.00657 | 0.21609 | 0.10466
80 | 0.99567 | -0.0071766 | 0.33969 | 0.16452
81 | 0.99586 | -0.0086251 | 0.16306 | 0.078973
82 | 0.99561 | -0.02413 | 0.24366 | 0.11801
83 | 0.99562 | -0.024186 | 0 | 0
84 | 0.99565 | -0.0245 | 0 | 0
85 | 0.99564 | -0.024416 | 0.23806 | 0.1153
86 | 0.99583 | -0.026094 | 0 | 0
87 | 0.99443 | -0.042307 | 0 | 0
88 | 0.99429 | -0.041056 | 0 | 0
89 | 0.99305 | -0.058189 | 0 | 0
90 | 0.99442 | -0.042376 | 0.28949 | 0.14021
91 | 0.99421 | -0.043677 | 0.25787 | 0.12489
92 | 0.99285 | -0.056438 | 0 | 0
93 | 0.993 | -0.057706 | 0.23613 | 0.11436
94 | 0.99279 | -0.056012 | 0 | 0
95 | 0.99281 | -0.056659 | 0.35964 | 0.17418
96 | 0.99277 | -0.055836 | 0.083776 | 0.040574
97 | 0.99429 | -0.041042 | 0.34204 | 0.16566
98 | 0.99642 | -0.019291 | 0 | 0
99 | 0.99654 | -0.018713 | 0 | 0
100 | 0.99642 | -0.019248 | 0.30273 | 0.14662
101 | 0.99583 | -0.026084 | 0.22567 | 0.1093
102 | 0.99298 | -0.057548 | 0 | 0
103 | 0.99277 | -0.055807 | 0.090542 | 0.043852
104 | 0.99654 | -0.01867 | 0.13133 | 0.063608
105 | 0.99678 | -0.016932 | 0 | 0
106 | 0.99678 | -0.0169 | 0.068003 | 0.032935
107 | 0.99366 | 0.006518 | 0 | 0
108 | 0.99623 | -0.012683 | 0 | 0
109 | 0.99279 | -0.0004353 | 0.32175 | 0.15583
110 | 0.99612 | -0.01175 | 0 | 0
111 | 0.99618 | -0.013021 | 0.17339 | 0.083975
112 | 0.99611 | -0.011681 | 0.22811 | 0.11048
113 | 0.9989 | -0.026085 | 0 | 0
114 | 0.99849 | -0.046749 | 0.29808 | 0.14437
115 | 0.99791 | -0.086421 | 0.1585 | 0.076765
116 | 0.9979 | -0.086404 | 0 | 0
117 | 0.9979 | -0.086376 | 0.069256 | 0.033542
118 | 0.99889 | -0.026072 | 0.25146 | 0.12179
119 | 0.99889 | -0.026015 | 0 | 0
120 | 0.99889 | -0.026002 | 0.26803 | 0.12981
121 | 0.996 | -0.014162 | 0.14168 | 0.06862
122 | 0.99602 | -0.014271 | 0 | 0
123 | 0.99592 | -0.014849 | 0.12939 | 0.062665
124 | 0.99592 | -0.014833 | 0 | 0
125 | 0.99589 | -0.014655 | 0 | 0
126 | 0.99587 | -0.014523 | 0.095422 | 0.046215
127 | 0.99677 | -0.01687 | 0.074674 | 0.036166
128 | 0.9905 | -0.019393 | 0.36118 | 0.17493
129 | 0.98283 | -0.0072153 | 0.11099 | 0.053755
130 | 0.98289 | -0.0066762 | 0.10779 | 0.052204
131 | 0.98262 | -0.0093702 | 0.13488 | 0.065327
132 | 0.98294 | -0.0070773 | 0 | 0
133 | 0.983 | -0.0075252 | 0 | 0
134 | 0.9838 | -0.012915 | 0 | 0
135 | 0.98298 | -0.0076853 | 0.16932 | 0.082007
136 | 0.98367 | -0.011959 | 0 | 0
137 | 0.98386 | -0.012252 | 0.39133 | 0.18953
138 | 0.98365 | -0.011688 | 0.21702 | 0.10511
139 | 0.98591 | 0.0068362 | 0.33332 | 0.16143
140 | 0.98647 | 0.010427 | 0 | 0
141 | 0.98858 | -0.0052923 | 0 | 0
142 | 0.98865 | -0.0058495 | 0 | 0
143 | 0.98858 | -0.0052811 | 0.15084 | 0.073055
144 | 0.98877 | -0.0066825 | 0.40033 | 0.19389
145 | 0.98881 | -0.0070248 | 0 | 0
146 | 0.99032 | -0.018096 | 0 | 0
147 | 0.98645 | 0.010297 | 0.16199 | 0.078455
148 | 0.9912 | -0.043255 | 0.36418 | 0.17638
149 | 0.99125 | -0.042992 | 0 | 0
150 | 0.99166 | -0.046472 | 0 | 0
151 | 0.98991 | -0.031761 | 0 | 0
152 | 0.99169 | -0.046763 | 0.19719 | 0.095505
153 | 0.98991 | -0.031748 | 0.14221 | 0.068877
154 | 0.98947 | -0.034977 | 0.17864 | 0.086518
155 | 0.98988 | -0.031958 | 0.070911 | 0.034344
156 | 0.98712 | -0.026343 | 0 | 0
157 | 0.98711 | -0.026303 | 0.14737 | 0.071374
158 | 0.98694 | -0.024847 | 0 | 0
159 | 0.98719 | -0.02576 | 0.082844 | 0.040123
160 | 0.98693 | -0.024714 | 0.31765 | 0.15384
161 | 0.99184 | -0.047998 | 0 | 0
162 | 0.98987 | -0.031901 | 0 | 0
163 | 0.98986 | -0.031816 | 0 | 0
164 | 0.98927 | -0.033224 | 0 | 0
165 | 0.98926 | -0.033207 | 0 | 0
166 | 0.98932 | -0.03367 | 0 | 0
167 | 0.98926 | -0.033185 | 0.075483 | 0.036558
168 | 0.98835 | -0.025543 | 0 | 0
169 | 0.98926 | -0.033161 | 0.22885 | 0.11084
170 | 0.98986 | -0.031815 | 0.10048 | 0.048665
171 | 0.98723 | -0.026029 | 0.1796 | 0.086983
172 | 0.98723 | -0.026079 | 0 | 0
173 | 0.98729 | -0.026567 | 0 | 0
174 | 0.98751 | -0.026328 | 0.093654 | 0.045359
175 | 0.98751 | -0.026333 | 0 | 0
176 | 0.98834 | -0.025427 | 0.3075 | 0.14893
177 | 0.98785 | -0.029275 | 0.12672 | 0.061373
178 | 0.98783 | -0.02912 | 0 | 0
179 | 0.98733 | -0.026943 | 0.27338 | 0.13241
180 | 0.98747 | -0.025994 | 0 | 0
181 | 0.99272 | -0.055376 | 0.18778 | 0.090944
182 | 0.99272 | -0.055391 | 0 | 0
183 | 0.99278 | -0.055884 | 0 | 0
184 | 0.99285 | -0.056472 | 0.12773 | 0.061861
185 | 0.98775 | -0.028419 | 0 | 0
186 | 0.98754 | -0.026786 | 0 | 0
187 | 0.98753 | -0.026701 | 0.24622 | 0.11925
188 | 0.98774 | -0.028341 | 0.18187 | 0.088086
189 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.60355 | -0.29055 | 0.60357 | 0.28972 | 1.8362e-05 | -0.00083101 | 0.019577 | 0.019566 | 0.019577 | 0.98773 | -0.25253 | 0.98776 | -0.25279 | 8.8987
1 | 0.29744 | 0.14229 | -0.29742 | -0.14241 | 1.7409e-05 | -0.00011162 | 0.0096364 | 0.009638 | 0.009638 | 0.98773 | -0.25253 | 0.98767 | -0.25293 | 4.5895
2 | -0.60357 | -0.28972 | 0.60367 | 0.28503 | 0.00010332 | -0.0046934 | 0.019566 | 0.019507 | 0.019566 | 0.98776 | -0.25279 | 0.98792 | -0.25422 | 8.8938
3 | 0.22626 | 0.10794 | -0.22626 | -0.10921 | 3.9031e-06 | -0.0012644 | 0.0073271 | 0.0073432 | 0.0073432 | 0.98767 | -0.25293 | 0.98765 | -0.25279 | 3.3378
4 | -0.60367 | -0.28503 | 0.60369 | 0.28437 | 1.456e-05 | -0.00066385 | 0.019507 | 0.019499 | 0.019507 | 0.98792 | -0.25422 | 0.98794 | -0.25442 | 8.8669
5 | 0.22626 | 0.10921 | -0.22626 | -0.10958 | 1.155e-06 | -0.00037309 | 0.0073432 | 0.0073479 | 0.0073479 | 0.98765 | -0.25279 | 0.98765 | -0.25274 | 3.34
6 | 0.098735 | 0.047695 | -0.098733 | -0.047819 | 2.0094e-06 | -0.0001239 | 0.0032217 | 0.0032233 | 0.0032233 | 0.98252 | -0.0088853 | 0.9825 | -0.0090202 | 1.5349
7 | -0.098735 | -0.047695 | 0.098744 | 0.032696 | 8.5231e-06 | -0.014999 | 0.0032217 | 0.0030559 | 0.0032217 | 0.98252 | -0.0088853 | 0.9826 | -0.009354 | 1.4644
8 | -0.098744 | -0.032696 | 0.098745 | 0.029849 | 1.5272e-06 | -0.0028475 | 0.0030559 | 0.0030306 | 0.0030559 | 0.9826 | -0.009354 | 0.98262 | -0.0093702 | 1.389
9 | -0.86836 | -0.41255 | 0.86838 | 0.41215 | 1.8355e-05 | -0.00040065 | 0.028091 | 0.028086 | 0.028091 | 0.98794 | -0.25442 | 0.98796 | -0.2546 | 12.7688
10 | -3.7765 | -1.7764 | 3.7813 | 1.772 | 0.004866 | -0.004394 | 0.12134 | 0.12127 | 0.12134 | 0.99288 | -0.26658 | 0.99407 | -0.27703 | 55.1546
11 | 3.7765 | 1.7764 | -3.7758 | -1.777 | 0.00065941 | -0.00059382 | 0.12134 | 0.12135 | 0.12135 | 0.99288 | -0.26658 | 0.99271 | -0.26515 | 55.159
12 | -3.7813 | -1.772 | 3.7814 | 1.7719 | 0.00010592 | -9.5874e-05 | 0.12127 | 0.12127 | 0.12127 | 0.99407 | -0.27703 | 0.9941 | -0.27726 | 55.1218
13 | 3.3729 | 1.5818 | -3.369 | -1.5796 | 0.0038622 | 0.0022021 | 0.10833 | 0.10833 | 0.10833 | 0.99271 | -0.26515 | 0.99151 | -0.27363 | 51.5876
14 | -4.1861 | -1.9679 | 4.1866 | 1.9663 | 0.00048441 | -0.0015331 | 0.13432 | 0.1343 | 0.13432 | 0.9941 | -0.27726 | 0.99422 | -0.27586 | 37.1053
15 | -0.86838 | -0.41215 | 0.86864 | 0.40649 | 0.00025864 | -0.0056631 | 0.028086 | 0.028015 | 0.028086 | 0.98796 | -0.2546 | 0.98823 | -0.25704 | 12.7665
16 | 3.155 | 1.4778 | -3.1529 | -1.4809 | 0.0021532 | -0.0030367 | 0.10144 | 0.10148 | 0.10148 | 0.99151 | -0.27363 | 0.99088 | -0.2681 | 46.1279
17 | 0.21396 | 0.10177 | -0.21395 | -0.10362 | 5.0374e-06 | -0.0018535 | 0.0068982 | 0.0069215 | 0.0069215 | 0.99151 | -0.27363 | 0.99149 | -0.27343 | 3.1462
18 | -4.1866 | -1.9663 | 4.1869 | 1.9508 | 0.00035286 | -0.015555 | 0.1343 | 0.1341 | 0.1343 | 0.99422 | -0.27586 | 0.99431 | -0.27548 | 10.5249
19 | -0.4154 | -0.20119 | 0.41548 | 0.20094 | 8.1466e-05 | -0.00024485 | 0.013454 | 0.013451 | 0.013454 | 0.99032 | -0.26628 | 0.99052 | -0.26498 | 6.4068
20 | -0.50109 | -0.24241 | 0.5011 | 0.24159 | 1.2314e-05 | -0.00081791 | 0.016223 | 0.016212 | 0.016223 | 0.99052 | -0.26498 | 0.99054 | -0.26519 | 7.374
21 | -0.25786 | -0.12489 | 0.25789 | 0.12459 | 3.2703e-05 | -0.00029343 | 0.008314 | 0.00831 | 0.008314 | 0.9948 | -0.24477 | 0.99493 | -0.24393 | 3.959
22 | 4.7683 | 2.2227 | -4.7674 | -2.2208 | 0.00092625 | 0.0018815 | 0.15264 | 0.15265 | 0.15265 | 0.99493 | -0.24393 | 0.99457 | -0.26426 | 11.8334
23 | -5.3411 | -2.4998 | 5.3476 | 2.5139 | 0.0065317 | 0.014135 | 0.1711 | 0.17106 | 0.1711 | 0.99493 | -0.24393 | 0.99719 | -0.11651 | 13.2637
24 | -2.0641 | -0.96644 | 2.0643 | 0.96564 | 0.00021757 | -0.00080003 | 0.066442 | 0.066431 | 0.066442 | 0.99024 | -0.26255 | 0.99034 | -0.2634 | 30.2008
25 | 2.0641 | 0.96644 | -2.0633 | -0.96942 | 0.00080935 | -0.0029721 | 0.066442 | 0.066481 | 0.066481 | 0.99024 | -0.26255 | 0.98988 | -0.25937 | 30.2188
26 | 0.29293 | 0.13505 | -0.29291 | -0.13885 | 1.9233e-05 | -0.0037913 | 0.0094024 | 0.0094493 | 0.0094493 | 0.99034 | -0.2634 | 0.99028 | -0.26287 | 4.2951
27 | -2.3572 | -1.1007 | 2.3578 | 1.0992 | 0.00052975 | -0.0014595 | 0.075833 | 0.075813 | 0.075833 | 0.99034 | -0.2634 | 0.99054 | -0.26519 | 34.4697
28 | 1.8758 | 0.87862 | -1.8745 | -0.87802 | 0.0013506 | 0.00060318 | 0.060407 | 0.06041 | 0.06041 | 0.98988 | -0.25937 | 0.98912 | -0.26472 | 28.7668
29 | -2.8589 | -1.3408 | 2.8599 | 1.339 | 0.0010285 | -0.0018275 | 0.092024 | 0.091998 | 0.092024 | 0.99054 | -0.26519 | 0.99088 | -0.2681 | 41.8293
30 | 0.293 | 0.14188 | -0.29299 | -0.1419 | 4.1903e-06 | -2.8021e-05 | 0.009484 | 0.0094844 | 0.0094844 | 0.99088 | -0.2681 | 0.99086 | -0.26819 | 4.5164
31 | 0.18053 | 0.084417 | -0.18052 | -0.085984 | 3.0262e-06 | -0.0015665 | 0.0058095 | 0.005829 | 0.005829 | 0.99028 | -0.26287 | 0.99026 | -0.26273 | 2.6495
32 | 4.6775 | 2.1773 | -4.6773 | -2.1862 | 0.00025283 | -0.0089207 | 0.14975 | 0.14987 | 0.14987 | 0.99457 | -0.26426 | 0.99452 | -0.26451 | 11.7449
33 | -5.7227 | -2.6956 | 5.7243 | 2.6992 | 0.0016098 | 0.0035892 | 0.18313 | 0.18312 | 0.18313 | 0.99719 | -0.11651 | 0.99771 | -0.087264 | 14.1957
34 | -0.36214 | -0.17539 | 0.36215 | 0.17403 | 1.0817e-05 | -0.0013662 | 0.011754 | 0.011737 | 0.011754 | 0.98821 | -0.25678 | 0.98823 | -0.25704 | 5.3428
35 | -1.2308 | -0.58051 | 1.2318 | 0.56938 | 0.0010301 | -0.01113 | 0.039751 | 0.03961 | 0.039751 | 0.98823 | -0.25704 | 0.98901 | -0.26374 | 18.0688
36 | -1.4321 | -0.66625 | 1.4323 | 0.66485 | 0.00017683 | -0.0014037 | 0.046103 | 0.046085 | 0.046103 | 0.98901 | -0.26374 | 0.98912 | -0.26472 | 20.9558
37 | 0.20028 | 0.096866 | -0.20027 | -0.096994 | 8.6189e-06 | -0.00012852 | 0.0064936 | 0.0064953 | 0.0064953 | 0.98901 | -0.26374 | 0.98896 | -0.26402 | 3.093
38 | 0.30735 | 0.14787 | -0.30727 | -0.14836 | 8.2262e-05 | -0.00049216 | 0.0099543 | 0.0099612 | 0.0099612 | 0.98912 | -0.26472 | 0.98884 | -0.26651 | 4.7434
39 | 0.30727 | 0.14836 | -0.30727 | -0.14882 | 2.5915e-06 | -0.00045569 | 0.0099612 | 0.009967 | 0.009967 | 0.98884 | -0.26651 | 0.98883 | -0.26644 | 4.5305
40 | -6.0594 | -2.8615 | 6.0597 | 2.8535 | 0.00037855 | -0.0079445 | 0.19389 | 0.19379 | 0.19389 | 0.99771 | -0.087264 | 0.99777 | -0.086996 | 15.1949
41 | 4.6773 | 2.1862 | -4.677 | -2.1856 | 0.00033278 | 0.00066794 | 0.14987 | 0.14987 | 0.14987 | 0.99452 | -0.26451 | 0.99439 | -0.27194 | 11.6177
42 | 4.51 | 2.1047 | -4.5099 | -2.1074 | 7.0987e-05 | -0.0026942 | 0.14448 | 0.14452 | 0.14452 | 0.99439 | -0.27194 | 0.99437 | -0.27201 | 11.3258
43 | 0.18052 | 0.085984 | -0.18052 | -0.08743 | 2.8122e-06 | -0.0014462 | 0.005829 | 0.0058472 | 0.0058472 | 0.99026 | -0.26273 | 0.99025 | -0.2626 | 2.6578
44 | 4.1871 | 1.951 | -4.1869 | -1.9508 | 0.00013894 | 0.00025532 | 0.1341 | 0.1341 | 0.1341 | 0.99437 | -0.27201 | 0.99431 | -0.27548 | 10.3957
45 | -12.3564 | -5.4731 | 12.3565 | 5.4727 | 8.2831e-05 | -0.00039286 | 0.39082 | 0.39082 | 0.39082 | 0.99821 | -0.0098351 | 0.99821 | -0.0097965 | 30.6288
46 | 12.137 | 5.3668 | -12.1361 | -5.3711 | 0.00086311 | -0.0042622 | 0.38378 | 0.38383 | 0.38383 | 0.99821 | -0.0098351 | 0.99813 | -0.010246 | 30.081
47 | -12.3565 | -5.4727 | 12.3623 | 5.4452 | 0.0057869 | -0.027491 | 0.39082 | 0.39046 | 0.39082 | 0.99821 | -0.0097965 | 0.9987 | -0.0070709 | 30.6284
48 | 12.1361 | 5.3711 | -12.1309 | -5.3967 | 0.0051939 | -0.025605 | 0.38383 | 0.38417 | 0.38417 | 0.99813 | -0.010246 | 0.99769 | -0.012693 | 30.1072
49 | 0.28055 | 0.13572 | -0.28054 | -0.13587 | 7.0226e-07 | -0.00015413 | 0.0090082 | 0.0090102 | 0.0090102 | 0.9987 | -0.0070709 | 0.9987 | -0.0070491 | 4.0955
50 | -12.6428 | -5.5809 | 12.6516 | 5.5412 | 0.0087718 | -0.039747 | 0.39946 | 0.39894 | 0.39946 | 0.9987 | -0.0070709 | 0.99943 | -0.0029616 | 31.3058
51 | 11.8975 | 5.2838 | -11.8887 | -5.3291 | 0.008837 | -0.045331 | 0.37667 | 0.37726 | 0.37726 | 0.99769 | -0.012693 | 0.99691 | -0.016844 | 29.5661
52 | 0.23339 | 0.11293 | -0.23339 | -0.11304 | 3.272e-07 | -0.00010338 | 0.0075021 | 0.0075034 | 0.0075034 | 0.99769 | -0.012693 | 0.99769 | -0.012681 | 3.4107
53 | -20.7628 | -9.3542 | 20.7742 | 9.3392 | 0.011418 | -0.015031 | 0.65777 | 0.65751 | 0.65777 | 0.99943 | -0.0029616 | 1 | 0 | 51.5491
54 | 0.074289 | 0.033884 | -0.074288 | -0.035979 | 6.5949e-07 | -0.0020952 | 0.0023584 | 0.0023842 | 0.0023842 | 0.99943 | -0.0029616 | 0.99942 | -0.0028893 | 1.0837
55 | 8.0369 | 3.7791 | -8.0351 | -3.7747 | 0.0018216 | 0.0044704 | 0.25652 | 0.25653 | 0.25653 | 0.99943 | -0.0029616 | 0.99901 | -0.026568 | 19.8858
56 | 0.48406 | 0.23307 | -0.48403 | -0.23313 | 2.9783e-05 | -6.4298e-05 | 0.015509 | 0.01551 | 0.01551 | 1 | 0 | 0.99993 | -0.00041436 | 7.3858
57 | 7.7804 | 3.6513 | -7.7801 | -3.6552 | 0.00030487 | -0.0038397 | 0.24835 | 0.2484 | 0.2484 | 0.99901 | -0.026568 | 0.99897 | -0.026741 | 19.4671
58 | 0.091452 | 0.042999 | -0.091451 | -0.043081 | 1.0455e-06 | -8.1607e-05 | 0.0029174 | 0.0029185 | 0.0029185 | 0.99993 | -0.00041436 | 0.99992 | -0.00049788 | 1.3897
59 | 10.7264 | 4.8093 | -10.7257 | -4.8139 | 0.00071949 | -0.0046131 | 0.34039 | 0.34045 | 0.34045 | 0.99691 | -0.016844 | 0.99684 | -0.017211 | 26.6814
60 | 1.1623 | 0.51977 | -1.1618 | -0.52652 | 0.00052913 | -0.0067438 | 0.036869 | 0.036951 | 0.036951 | 0.99691 | -0.016844 | 0.99649 | -0.013513 | 16.7958
61 | 0.29563 | 0.14304 | -0.29563 | -0.14318 | 7.3051e-07 | -0.00014308 | 0.009514 | 0.0095158 | 0.0095158 | 0.99649 | -0.013513 | 0.99648 | -0.013492 | 4.3254
62 | 0.86614 | 0.38348 | -0.86564 | -0.39497 | 0.00049605 | -0.011487 | 0.027441 | 0.027579 | 0.027579 | 0.99649 | -0.013513 | 0.99595 | -0.0093385 | 12.5359
63 | 0.55596 | 0.25567 | -0.5558 | -0.26446 | 0.00015756 | -0.0087823 | 0.017737 | 0.017845 | 0.017845 | 0.99595 | -0.0093385 | 0.99568 | -0.0070571 | 8.1114
64 | 0.16307 | 0.068645 | -0.16306 | -0.076807 | 1.233e-05 | -0.0081619 | 0.0051284 | 0.0052248 | 0.0052248 | 0.99595 | -0.0093385 | 0.99588 | -0.0087988 | 2.3749
65 | 0.14661 | 0.070649 | -0.14661 | -0.071008 | 4.5115e-07 | -0.00035918 | 0.0047172 | 0.0047218 | 0.0047218 | 0.99595 | -0.0093385 | 0.99595 | -0.0093118 | 2.1463
66 | 0.29945 | 0.14492 | -0.29945 | -0.14503 | 5.6779e-07 | -0.00010921 | 0.009619 | 0.0096204 | 0.0096204 | 0.99838 | -0.044223 | 0.99837 | -0.044206 | 4.3729
67 | -0.29945 | -0.14492 | 0.29952 | 0.12956 | 7.8278e-05 | -0.015364 | 0.009619 | 0.0094337 | 0.009619 | 0.99838 | -0.044223 | 0.99862 | -0.046223 | 4.3723
68 | 0.17916 | 0.086732 | -0.17916 | -0.08677 | 1.9286e-06 | -3.7711e-05 | 0.005754 | 0.0057545 | 0.0057545 | 0.99862 | -0.046223 | 0.99861 | -0.046294 | 2.7402
69 | -7.2592 | -3.4036 | 7.2606 | 3.4068 | 0.0013566 | 0.0032578 | 0.23177 | 0.23176 | 0.23177 | 0.99862 | -0.046223 | 0.99897 | -0.026741 | 17.9663
70 | 0.29811 | 0.14295 | -0.29808 | -0.14316 | 3.0841e-05 | -0.00020621 | 0.0095572 | 0.0095601 | 0.0095601 | 0.99862 | -0.046223 | 0.99851 | -0.046929 | 4.5524
71 | 6.4824 | 3.0443 | -6.4799 | -3.0385 | 0.0024999 | 0.0058223 | 0.20703 | 0.20704 | 0.20704 | 0.99862 | -0.046223 | 0.99791 | -0.086428 | 16.0493
72 | 10.3669 | 4.6402 | -10.3668 | -4.6414 | 0.00017299 | -0.0011949 | 0.32892 | 0.32893 | 0.32893 | 0.99684 | -0.017211 | 0.99683 | -0.017303 | 25.7783
73 | 0.3397 | 0.16449 | -0.33969 | -0.16452 | 6.1541e-06 | -3.0284e-05 | 0.010943 | 0.010943 | 0.010943 | 0.99568 | -0.0070571 | 0.99567 | -0.0071766 | 5.2109
74 | 0.2161 | 0.099968 | -0.21609 | -0.10388 | 1.0592e-05 | -0.0039105 | 0.0069033 | 0.0069517 | 0.0069517 | 0.99568 | -0.0070571 | 0.99564 | -0.006655 | 3.1599
75 | 0.16306 | 0.076807 | -0.16306 | -0.078973 | 3.3531e-06 | -0.0021665 | 0.0052248 | 0.0052519 | 0.0052519 | 0.99588 | -0.0087988 | 0.99586 | -0.0086251 | 2.3872
76 | 0.51954 | 0.24833 | -0.5195 | -0.25087 | 3.9777e-05 | -0.002547 | 0.01664 | 0.016672 | 0.016672 | 0.99897 | -0.026741 | 0.9989 | -0.026085 | 7.5783
77 | 0.091451 | 0.043081 | -0.091451 | -0.044292 | 5.7973e-07 | -0.0012107 | 0.0029185 | 0.0029335 | 0.0029335 | 0.99992 | -0.00049788 | 0.99992 | -0.00044433 | 1.3334
78 | -0.1916 | -0.092798 | 0.1916 | 0.092376 | 8.9771e-07 | -0.00042141 | 0.0061594 | 0.0061541 | 0.0061594 | 0.99777 | -0.086933 | 0.99778 | -0.086974 | 2.7997
79 | 6.0598 | 2.8529 | -6.0597 | -2.8535 | 3.1428e-05 | -0.00066 | 0.19378 | 0.19379 | 0.19379 | 0.99778 | -0.086974 | 0.99777 | -0.086996 | 15.187
80 | -6.2514 | -2.9452 | 6.2522 | 2.9298 | 0.00078026 | -0.015384 | 0.19993 | 0.19974 | 0.19993 | 0.99778 | -0.086974 | 0.99791 | -0.086428 | 15.6686
81 | 0.1585 | 0.07668 | -0.1585 | -0.076765 | 1.2307e-07 | -8.444e-05 | 0.0050935 | 0.0050945 | 0.0050945 | 0.99791 | -0.086428 | 0.99791 | -0.086421 | 2.3157
82 | 0.069256 | 0.031985 | -0.069256 | -0.03274 | 2.0744e-07 | -0.00075544 | 0.0022068 | 0.002216 | 0.002216 | 0.99791 | -0.086428 | 0.9979 | -0.086404 | 1.0073
83 | 0.29808 | 0.14316 | -0.29808 | -0.14437 | 6.2173e-06 | -0.0012092 | 0.0095601 | 0.0095753 | 0.0095753 | 0.99851 | -0.046929 | 0.99849 | -0.046749 | 4.3524
84 | 2.9902 | 1.3179 | -2.9801 | -1.3347 | 0.010063 | -0.016873 | 0.094632 | 0.094865 | 0.094865 | 0.99683 | -0.017303 | 0.99366 | 0.006518 | 43.1206
85 | 0.76861 | 0.33767 | -0.76812 | -0.35212 | 0.00048893 | -0.014443 | 0.024312 | 0.024485 | 0.024485 | 0.99683 | -0.017303 | 0.99623 | -0.012683 | 11.1295
86 | 6.4653 | 2.9241 | -6.4635 | -2.957 | 0.0017744 | -0.032886 | 0.20549 | 0.2059 | 0.2059 | 0.99683 | -0.017303 | 0.99654 | -0.018713 | 16.1361
87 | 0.14268 | 0.061723 | -0.14268 | -0.067833 | 7.0836e-06 | -0.0061106 | 0.0045021 | 0.0045753 | 0.0045753 | 0.99683 | -0.017303 | 0.99678 | -0.016932 | 2.0797
88 | 0.21609 | 0.10388 | -0.21609 | -0.10466 | 2.1266e-06 | -0.00077845 | 0.0069517 | 0.0069615 | 0.0069615 | 0.99564 | -0.006655 | 0.99563 | -0.00657 | 3.1643
89 | -0.24366 | -0.11801 | 0.24367 | 0.11756 | 1.5595e-06 | -0.0004485 | 0.00785 | 0.0078444 | 0.00785 | 0.99561 | -0.02413 | 0.99562 | -0.024186 | 3.5682
90 | -0.24367 | -0.11756 | 0.24368 | 0.11494 | 9.0768e-06 | -0.0026235 | 0.0078444 | 0.0078116 | 0.0078444 | 0.99562 | -0.024186 | 0.99565 | -0.0245 | 3.5656
91 | 0.23806 | 0.1146 | -0.23806 | -0.1153 | 2.3109e-06 | -0.00069673 | 0.0076603 | 0.0076691 | 0.0076691 | 0.99565 | -0.0245 | 0.99564 | -0.024416 | 3.4859
92 | -0.48173 | -0.22954 | 0.48183 | 0.2225 | 9.4817e-05 | -0.0070358 | 0.015472 | 0.015385 | 0.015472 | 0.99565 | -0.0245 | 0.99583 | -0.026094 | 7.0326
93 | 0.22567 | 0.10921 | -0.22567 | -0.1093 | 2.5693e-07 | -8.6181e-05 | 0.0072675 | 0.0072686 | 0.0072686 | 0.99583 | -0.026094 | 0.99583 | -0.026084 | 3.3039
94 | 5.318 | 2.434 | -5.3112 | -2.4457 | 0.0068037 | -0.011685 | 0.16954 | 0.16974 | 0.16974 | 0.99583 | -0.026094 | 0.99443 | -0.042307 | 46.8895
95 | -6.0255 | -2.7657 | 6.0287 | 2.7619 | 0.0032302 | -0.0038184 | 0.19219 | 0.19211 | 0.19219 | 0.99583 | -0.026094 | 0.99642 | -0.019291 | 53.091
96 | 0.34209 | 0.158 | -0.34204 | -0.16558 | 5.1806e-05 | -0.0075761 | 0.010939 | 0.011033 | 0.011033 | 0.99443 | -0.042307 | 0.99429 | -0.041056 | 5.0149
97 | 4.4217 | 2.0231 | -4.4161 | -2.0386 | 0.005554 | -0.015483 | 0.14115 | 0.14139 | 0.14139 | 0.99443 | -0.042307 | 0.99305 | -0.058189 | 39.0585
98 | 0.28949 | 0.14018 | -0.28949 | -0.14021 | 3.0433e-06 | -2.1222e-05 | 0.0093371 | 0.0093374 | 0.0093374 | 0.99443 | -0.042307 | 0.99442 | -0.042376 | 4.4464
99 | 0.25792 | 0.12441 | -0.25787 | -0.12489 | 5.3207e-05 | -0.00047634 | 0.0083128 | 0.0083193 | 0.0083193 | 0.99443 | -0.042307 | 0.99421 | -0.043677 | 3.9616
100 | 0.34204 | 0.16558 | -0.34204 | -0.16566 | 5.4475e-07 | -7.896e-05 | 0.011033 | 0.011034 | 0.011034 | 0.99429 | -0.041056 | 0.99429 | -0.041042 | 5.0154
101 | 0.5341 | 0.24297 | -0.53398 | -0.25017 | 0.0001199 | -0.0071941 | 0.017057 | 0.017145 | 0.017145 | 0.99305 | -0.058189 | 0.99285 | -0.056438 | 7.7932
102 | 3.882 | 1.7956 | -3.8818 | -1.7958 | 0.00023902 | -0.00020177 | 0.12433 | 0.12434 | 0.12434 | 0.99305 | -0.058189 | 0.993 | -0.057706 | 56.5174
103 | 0.17433 | 0.076037 | -0.17432 | -0.081739 | 1.0018e-05 | -0.0057025 | 0.0055299 | 0.0055983 | 0.0055983 | 0.99285 | -0.056438 | 0.99279 | -0.056012 | 2.5447
104 | 0.35965 | 0.17413 | -0.35964 | -0.17418 | 1.2006e-05 | -5.122e-05 | 0.011618 | 0.011619 | 0.011619 | 0.99285 | -0.056438 | 0.99281 | -0.056659 | 5.5328
105 | 3.6456 | 1.6814 | -3.6456 | -1.6815 | 7.4468e-05 | -7.4317e-05 | 0.11671 | 0.11671 | 0.11671 | 0.993 | -0.057706 | 0.99298 | -0.057548 | 53.0515
106 | 0.17432 | 0.081739 | -0.17432 | -0.083803 | 3.6881e-06 | -0.0020637 | 0.0055983 | 0.0056241 | 0.0056241 | 0.99279 | -0.056012 | 0.99277 | -0.055836 | 2.5564
107 | 0.090543 | 0.043229 | -0.090542 | -0.043852 | 3.0156e-07 | -0.00062276 | 0.0029174 | 0.0029253 | 0.0029253 | 0.99277 | -0.055836 | 0.99277 | -0.055807 | 1.3297
108 | -6.3314 | -2.9083 | 6.3322 | 2.8941 | 0.0007363 | -0.014193 | 0.20185 | 0.20168 | 0.20185 | 0.99642 | -0.019291 | 0.99654 | -0.018713 | 15.8193
109 | 0.30274 | 0.14635 | -0.30273 | -0.14662 | 1.4779e-06 | -0.00027599 | 0.0097417 | 0.0097451 | 0.0097451 | 0.99642 | -0.019291 | 0.99642 | -0.019248 | 4.4296
110 | 0.13133 | 0.06296 | -0.13133 | -0.063608 | 6.5011e-07 | -0.00064724 | 0.004219 | 0.0042272 | 0.0042272 | 0.99654 | -0.018713 | 0.99654 | -0.01867 | 1.9214
111 | 3.6456 | 1.6815 | -3.6451 | -1.682 | 0.00050395 | -0.00050278 | 0.11671 | 0.11672 | 0.11672 | 0.99298 | -0.057548 | 0.99285 | -0.056472 | 53.0551
112 | 0.14268 | 0.067833 | -0.14268 | -0.068286 | 5.3357e-07 | -0.00045223 | 0.0045753 | 0.0045809 | 0.0045809 | 0.99678 | -0.016932 | 0.99678 | -0.0169 | 2.0822
113 | 0.074674 | 0.03535 | -0.074674 | -0.036166 | 2.6398e-07 | -0.00081579 | 0.0023927 | 0.0024029 | 0.0024029 | 0.99678 | -0.0169 | 0.99677 | -0.01687 | 1.0922
114 | 2.9801 | 1.3347 | -2.9777 | -1.3334 | 0.002431 | 0.0013442 | 0.094865 | 0.094868 | 0.094868 | 0.99366 | 0.006518 | 0.99279 | -0.0004353 | 45.175
115 | 0.22813 | 0.10074 | -0.22811 | -0.10988 | 2.7303e-05 | -0.0091325 | 0.0072265 | 0.0073375 | 0.0073375 | 0.99623 | -0.012683 | 0.99612 | -0.01175 | 3.3352
116 | 0.53998 | 0.25137 | -0.53996 | -0.25141 | 2.4073e-05 | -3.8658e-05 | 0.017259 | 0.01726 | 0.01726 | 0.99623 | -0.012683 | 0.99618 | -0.013021 | 8.2191
117 | 2.656 | 1.1776 | -2.6502 | -1.1745 | 0.0057364 | 0.0030635 | 0.084478 | 0.084484 | 0.084484 | 0.99279 | -0.0004353 | 0.9905 | -0.019393 | 40.2305
118 | 0.22811 | 0.10988 | -0.22811 | -0.11048 | 1.8253e-06 | -0.00060047 | 0.0073375 | 0.0073451 | 0.0073451 | 0.99612 | -0.01175 | 0.99611 | -0.011681 | 3.3387
119 | 0.36657 | 0.16744 | -0.36652 | -0.16768 | 5.7122e-05 | -0.00024259 | 0.011678 | 0.011682 | 0.011682 | 0.99618 | -0.013021 | 0.99602 | -0.014271 | 5.5627
120 | 0.25146 | 0.12168 | -0.25146 | -0.12179 | 3.9878e-07 | -0.00010905 | 0.0080733 | 0.0080746 | 0.0080746 | 0.9989 | -0.026085 | 0.99889 | -0.026072 | 3.6703
121 | 0.26803 | 0.12919 | -0.26803 | -0.12972 | 2.1926e-06 | -0.00052811 | 0.0085989 | 0.0086055 | 0.0086055 | 0.9989 | -0.026085 | 0.99889 | -0.026015 | 3.9116
122 | 0.069256 | 0.03274 | -0.069256 | -0.033542 | 2.2212e-07 | -0.00080188 | 0.002216 | 0.002226 | 0.002226 | 0.9979 | -0.086404 | 0.9979 | -0.086376 | 1.0118
123 | 0.26803 | 0.12972 | -0.26803 | -0.12981 | 3.8298e-07 | -9.2165e-05 | 0.0086055 | 0.0086067 | 0.0086067 | 0.99889 | -0.026015 | 0.99889 | -0.026002 | 3.9121
124 | -0.36651 | -0.16835 | 0.36652 | 0.16768 | 5.1929e-06 | -0.00067315 | 0.01169 | 0.011682 | 0.01169 | 0.996 | -0.014162 | 0.99602 | -0.014271 | 5.3135
125 | 0.22483 | 0.099731 | -0.22481 | -0.099952 | 1.7704e-05 | -0.00022036 | 0.0071287 | 0.0071314 | 0.0071314 | 0.996 | -0.014162 | 0.99592 | -0.014849 | 3.3959
126 | 0.095426 | 0.037287 | -0.095426 | -0.037934 | 3.2259e-07 | -0.00064729 | 0.0029697 | 0.0029765 | 0.0029765 | 0.99592 | -0.014849 | 0.99592 | -0.014833 | 1.353
127 | 0.095426 | 0.037934 | -0.095423 | -0.043247 | 2.7063e-06 | -0.0053125 | 0.0029765 | 0.0030368 | 0.0030368 | 0.99592 | -0.014833 | 0.99589 | -0.014655 | 1.3804
128 | 0.095423 | 0.043247 | -0.095422 | -0.046215 | 1.5617e-06 | -0.002968 | 0.0030368 | 0.0030733 | 0.0030733 | 0.99589 | -0.014655 | 0.99587 | -0.014523 | 1.397
129 | 2.2891 | 0.99957 | -2.2886 | -1.0009 | 0.00043964 | -0.0013247 | 0.072796 | 0.072813 | 0.072813 | 0.9905 | -0.019393 | 0.99032 | -0.018096 | 33.0968
130 | -0.34466 | -0.14841 | 0.34468 | 0.14832 | 1.9621e-05 | -9.226e-05 | 0.011022 | 0.011021 | 0.011022 | 0.98283 | -0.0072153 | 0.98289 | -0.0066762 | 5.2486
131 | 0.23367 | 0.094656 | -0.23363 | -0.095175 | 4.6505e-05 | -0.00051919 | 0.0074052 | 0.0074113 | 0.0074113 | 0.98283 | -0.0072153 | 0.98262 | -0.0093702 | 3.5292
132 | -0.45247 | -0.20052 | 0.4525 | 0.19838 | 2.6245e-05 | -0.0021423 | 0.014536 | 0.01451 | 0.014536 | 0.98289 | -0.0066762 | 0.98294 | -0.0070773 | 6.6071
133 | -0.4525 | -0.19838 | 0.45253 | 0.1959 | 3.0271e-05 | -0.0024805 | 0.01451 | 0.014481 | 0.01451 | 0.98294 | -0.0070773 | 0.983 | -0.0075252 | 6.5956
134 | -0.62186 | -0.27782 | 0.62238 | 0.25491 | 0.00052643 | -0.022915 | 0.020001 | 0.019735 | 0.020001 | 0.983 | -0.0075252 | 0.9838 | -0.012915 | 9.0916
135 | 0.16933 | 0.081923 | -0.16932 | -0.082007 | 4.1051e-06 | -8.4511e-05 | 0.005524 | 0.0055251 | 0.0055251 | 0.983 | -0.0075252 | 0.98298 | -0.0076853 | 2.631
136 | 0.21706 | 0.092639 | -0.21703 | -0.1027 | 2.8386e-05 | -0.010063 | 0.0069249 | 0.0070462 | 0.0070462 | 0.9838 | -0.012915 | 0.98367 | -0.011959 | 3.2028
137 | -0.83944 | -0.34755 | 0.83949 | 0.34753 | 5.354e-05 | -1.5322e-05 | 0.026659 | 0.026659 | 0.026659 | 0.9838 | -0.012915 | 0.98386 | -0.012252 | 12.6949
138 | 0.21703 | 0.1027 | -0.21702 | -0.10511 | 6.9369e-06 | -0.0024054 | 0.0070462 | 0.0070767 | 0.0070767 | 0.98367 | -0.011959 | 0.98365 | -0.011688 | 3.2167
139 | -1.2308 | -0.53706 | 1.2339 | 0.5377 | 0.0030507 | 0.0006325 | 0.039402 | 0.039387 | 0.039402 | 0.98386 | -0.012252 | 0.98647 | 0.010427 | 18.7628
140 | -0.33332 | -0.16143 | 0.3335 | 0.16055 | 0.00017958 | -0.00088384 | 0.010844 | 0.010831 | 0.010844 | 0.98591 | 0.0068362 | 0.98647 | 0.010427 | 5.1638
141 | 0.16199 | 0.078382 | -0.16199 | -0.078455 | 3.1978e-06 | -7.3166e-05 | 0.0052662 | 0.0052672 | 0.0052672 | 0.98647 | 0.010427 | 0.98645 | 0.010297 | 2.5082
142 | -1.7294 | -0.77663 | 1.7334 | 0.75483 | 0.0040376 | -0.021799 | 0.055476 | 0.055204 | 0.055476 | 0.98647 | 0.010427 | 0.98865 | -0.0058495 | 25.2164
143 | -0.15084 | -0.072914 | 0.15085 | 0.064618 | 1.1126e-05 | -0.0082963 | 0.0048923 | 0.0047918 | 0.0048923 | 0.98858 | -0.0052923 | 0.98865 | -0.0058495 | 2.2238
144 | 0.15084 | 0.072914 | -0.15084 | -0.073055 | 1.9369e-07 | -0.00014135 | 0.0048923 | 0.0048941 | 0.0048941 | 0.98858 | -0.0052923 | 0.98858 | -0.0052811 | 2.2246
145 | -1.8843 | -0.81945 | 1.8845 | 0.81837 | 0.0002361 | -0.001077 | 0.059996 | 0.059982 | 0.059996 | 0.98865 | -0.0058495 | 0.98877 | -0.0066825 | 27.2708
146 | -2.2848 | -1.0123 | 2.2849 | 1.0119 | 0.00011161 | -0.00033355 | 0.07296 | 0.072955 | 0.07296 | 0.98877 | -0.0066825 | 0.98881 | -0.0070248 | 33.1635
147 | -2.2849 | -1.0119 | 2.2886 | 1.0009 | 0.0036764 | -0.01103 | 0.072955 | 0.072813 | 0.072955 | 0.98881 | -0.0070248 | 0.99032 | -0.018096 | 33.1616
148 | -0.36418 | -0.17638 | 0.36419 | 0.17632 | 1.4537e-05 | -5.9811e-05 | 0.011785 | 0.011784 | 0.011785 | 0.9912 | -0.043255 | 0.99125 | -0.042992 | 5.6117
149 | -3.1267 | -1.4468 | 3.1281 | 1.4447 | 0.0013918 | -0.0020185 | 0.10033 | 0.1003 | 0.10033 | 0.99125 | -0.042992 | 0.99166 | -0.046472 | 45.6056
150 | 2.7625 | 1.2704 | -2.7585 | -1.2781 | 0.0039786 | -0.0077133 | 0.088551 | 0.088659 | 0.088659 | 0.99125 | -0.042992 | 0.98991 | -0.031761 | 40.2997
151 | -3.1281 | -1.4447 | 3.1282 | 1.4446 | 0.00011661 | -0.00016928 | 0.1003 | 0.1003 | 0.1003 | 0.99166 | -0.046472 | 0.99169 | -0.046763 | 45.5921
152 | 0.14221 | 0.068707 | -0.14221 | -0.068877 | 2.0598e-07 | -0.00017003 | 0.0046058 | 0.004608 | 0.004608 | 0.98991 | -0.031761 | 0.98991 | -0.031748 | 2.0945
153 | 2.4449 | 1.1295 | -2.4439 | -1.1289 | 0.0010126 | 0.00052651 | 0.078539 | 0.07854 | 0.07854 | 0.98991 | -0.031761 | 0.98947 | -0.034977 | 37.3999
154 | 0.1714 | 0.07997 | -0.17139 | -0.080065 | 4.4938e-06 | -9.4153e-05 | 0.0055155 | 0.0055167 | 0.0055167 | 0.98991 | -0.031761 | 0.98988 | -0.031958 | 2.627
155 | -3.3254 | -1.5401 | 3.3259 | 1.5394 | 0.00052318 | -0.00065363 | 0.10668 | 0.10667 | 0.10668 | 0.99169 | -0.046763 | 0.99184 | -0.047998 | 48.4896
156 | 2.2653 | 1.0424 | -2.2649 | -1.0436 | 0.00038213 | -0.0011504 | 0.07275 | 0.072766 | 0.072766 | 0.98947 | -0.034977 | 0.98932 | -0.03367 | 33.0753
157 | 0.10048 | 0.045721 | -0.10048 | -0.046959 | 7.3576e-07 | -0.001238 | 0.0032194 | 0.0032345 | 0.0032345 | 0.98988 | -0.031958 | 0.98987 | -0.031901 | 1.4702
158 | 0.14737 | 0.070847 | -0.14737 | -0.071374 | 6.9251e-07 | -0.00052683 | 0.0047819 | 0.0047886 | 0.0047886 | 0.98712 | -0.026343 | 0.98711 | -0.026303 | 2.1766
159 | 0.31771 | 0.14319 | -0.31765 | -0.15305 | 5.9546e-05 | -0.0098547 | 0.010191 | 0.010313 | 0.010313 | 0.98712 | -0.026343 | 0.98694 | -0.024847 | 4.6879
160 | -0.46508 | -0.21404 | 0.46512 | 0.21396 | 3.4537e-05 | -7.8973e-05 | 0.014972 | 0.014971 | 0.014972 | 0.98712 | -0.026343 | 0.98719 | -0.02576 | 7.1296
161 | 0.31765 | 0.15305 | -0.31765 | -0.15384 | 4.8797e-06 | -0.00079697 | 0.010313 | 0.010324 | 0.010324 | 0.98694 | -0.024847 | 0.98693 | -0.024714 | 4.6925
162 | -0.54796 | -0.25408 | 0.54798 | 0.25284 | 2.2349e-05 | -0.0012432 | 0.017662 | 0.017647 | 0.017662 | 0.98719 | -0.02576 | 0.98723 | -0.026079 | 8.0283
163 | -3.3259 | -1.5394 | 3.3293 | 1.5352 | 0.0033608 | -0.0042081 | 0.10667 | 0.1066 | 0.10667 | 0.99184 | -0.047998 | 0.99278 | -0.055884 | 48.4851
164 | 0.10048 | 0.046959 | -0.10048 | -0.048651 | 1.0171e-06 | -0.0016922 | 0.0032345 | 0.0032557 | 0.0032557 | 0.98987 | -0.031901 | 0.98986 | -0.031816 | 1.4799
165 | 0.10048 | 0.048651 | -0.10048 | -0.048665 | 8.0393e-09 | -1.3386e-05 | 0.0032557 | 0.0032559 | 0.0032559 | 0.98986 | -0.031816 | 0.98986 | -0.031815 | 1.48
166 | 0.22886 | 0.11031 | -0.22885 | -0.11045 | 4.5492e-07 | -0.00014471 | 0.0074134 | 0.0074153 | 0.0074153 | 0.98927 | -0.033224 | 0.98926 | -0.033207 | 3.3706
167 | -0.30434 | -0.14584 | 0.30435 | 0.14289 | 1.6328e-05 | -0.0029532 | 0.0098479 | 0.0098109 | 0.0098479 | 0.98927 | -0.033224 | 0.98932 | -0.03367 | 4.4763
168 | 0.075483 | 0.035533 | -0.075483 | -0.036558 | 3.4896e-07 | -0.001025 | 0.0024345 | 0.0024474 | 0.0024474 | 0.98927 | -0.033224 | 0.98926 | -0.033185 | 1.1124
169 | 0.22885 | 0.11045 | -0.22885 | -0.11084 | 1.213e-06 | -0.00038551 | 0.0074153 | 0.0074202 | 0.0074202 | 0.98926 | -0.033207 | 0.98926 | -0.033161 | 3.3728
170 | 1.9605 | 0.90069 | -1.9585 | -0.90908 | 0.0020417 | -0.0083874 | 0.062955 | 0.063065 | 0.063065 | 0.98932 | -0.03367 | 0.98835 | -0.025543 | 28.6659
171 | 1.651 | 0.76087 | -1.6502 | -0.76056 | 0.00078763 | 0.00031059 | 0.053096 | 0.053098 | 0.053098 | 0.98835 | -0.025543 | 0.98785 | -0.029275 | 25.2849
172 | 0.30751 | 0.14821 | -0.3075 | -0.14893 | 4.1263e-06 | -0.00072327 | 0.0099703 | 0.0099795 | 0.0099795 | 0.98835 | -0.025543 | 0.98834 | -0.025427 | 4.5361
173 | -0.1796 | -0.086983 | 0.1796 | 0.086451 | 1.0387e-06 | -0.00053207 | 0.0058351 | 0.0058284 | 0.0058351 | 0.98723 | -0.026029 | 0.98723 | -0.026079 | 2.6523
174 | -0.72758 | -0.33929 | 0.72763 | 0.33789 | 4.4664e-05 | -0.0014007 | 0.023475 | 0.023457 | 0.023475 | 0.98723 | -0.026079 | 0.98729 | -0.026567 | 10.6703
175 | -0.72763 | -0.33789 | 0.72766 | 0.3368 | 3.4749e-05 | -0.0010913 | 0.023457 | 0.023444 | 0.023457 | 0.98729 | -0.026567 | 0.98733 | -0.026943 | 10.6624
176 | -0.093654 | -0.045359 | 0.093654 | 0.045255 | 5.4791e-08 | -0.00010329 | 0.003042 | 0.0030406 | 0.003042 | 0.98751 | -0.026328 | 0.98751 | -0.026333 | 1.3827
177 | -1.0949 | -0.51377 | 1.0952 | 0.50988 | 0.00028441 | -0.0038905 | 0.035355 | 0.035305 | 0.035355 | 0.98751 | -0.026333 | 0.98775 | -0.028419 | 16.0703
178 | 1.0012 | 0.46851 | -1.0012 | -0.4692 | 4.2118e-05 | -0.00069075 | 0.032314 | 0.032323 | 0.032323 | 0.98751 | -0.026333 | 0.98747 | -0.025994 | 14.6922
179 | 1.5235 | 0.69919 | -1.5234 | -0.6994 | 3.0792e-05 | -0.00021482 | 0.048985 | 0.048987 | 0.048987 | 0.98785 | -0.029275 | 0.98783 | -0.02912 | 22.2669
180 | 1.5234 | 0.6994 | -1.5233 | -0.70037 | 0.00013857 | -0.00096628 | 0.048987 | 0.049 | 0.049 | 0.98783 | -0.02912 | 0.98775 | -0.028419 | 22.2725
181 | -1.001 | -0.4692 | 1.0012 | 0.4692 | 0.00012823 | 1.4399e-07 | 0.032324 | 0.032323 | 0.032324 | 0.98733 | -0.026943 | 0.98747 | -0.025994 | 15.3923
182 | -0.18778 | -0.090944 | 0.18778 | 0.090786 | 3.2914e-07 | -0.00015755 | 0.0060671 | 0.0060651 | 0.0060671 | 0.99272 | -0.055376 | 0.99272 | -0.055391 | 2.7578
183 | -0.18778 | -0.090786 | 0.18779 | 0.085243 | 1.1444e-05 | -0.0055436 | 0.0060651 | 0.0059966 | 0.0060651 | 0.99272 | -0.055391 | 0.99278 | -0.055884 | 2.7569
184 | -3.5171 | -1.6205 | 3.5173 | 1.6202 | 0.00026668 | -0.00029171 | 0.1126 | 0.1126 | 0.1126 | 0.99278 | -0.055884 | 0.99285 | -0.056472 | 51.1819
185 | 0.18188 | 0.087258 | -0.18187 | -0.088086 | 1.654e-06 | -0.00082838 | 0.0058955 | 0.0059061 | 0.0059061 | 0.98775 | -0.028419 | 0.98774 | -0.028341 | 2.6846
186 | 0.24628 | 0.10323 | -0.24622 | -0.11858 | 5.49e-05 | -0.015354 | 0.0078043 | 0.0079887 | 0.0079887 | 0.98775 | -0.028419 | 0.98754 | -0.026786 | 3.6312
187 | 0.24622 | 0.11858 | -0.24622 | -0.11925 | 2.4355e-06 | -0.00066419 | 0.0079887 | 0.0079972 | 0.0079972 | 0.98754 | -0.026786 | 0.98753 | -0.026701 | 3.6351

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 21.2722 | 9.5827

## res_load
| p_mw | q_mvar
0 | 0.30612 | 0.14826
1 | 0.071158 | 0.034463
2 | 0.22626 | 0.10958
3 | 0.098733 | 0.047819
4 | 0.26467 | 0.12819
5 | 0.40295 | 0.19516
6 | 0.40463 | 0.19597
7 | 0.4154 | 0.20119
8 | 0.085606 | 0.041461
9 | 0.25786 | 0.12489
10 | 0.31487 | 0.1525
11 | 0.18747 | 0.090796
12 | 0.11238 | 0.054428
13 | 0.089826 | 0.043505
14 | 0.37512 | 0.18168
15 | 0.36214 | 0.17539
16 | 0.13483 | 0.065302
17 | 0.20027 | 0.096994
18 | 0.30727 | 0.14882
19 | 0.33504 | 0.16227
20 | 0.21395 | 0.10362
21 | 0.29299 | 0.1419
22 | 0.16695 | 0.080857
23 | 0.32289 | 0.15638
24 | 0.18052 | 0.08743
25 | 0.2194 | 0.10626
26 | 0.074288 | 0.035979
27 | 0.25466 | 0.12334
28 | 0.28054 | 0.13587
29 | 0.39258 | 0.19014
30 | 0.23339 | 0.11304
31 | 0.29563 | 0.14318
32 | 0.29945 | 0.14503
33 | 0.35874 | 0.17374
34 | 0.14661 | 0.071008
35 | 0.1916 | 0.092798
36 | 0.091451 | 0.044292
37 | 0.17916 | 0.08677
38 | 0.21609 | 0.10466
39 | 0.33969 | 0.16452
40 | 0.16306 | 0.078973
41 | 0.24366 | 0.11801
42 | 0.23806 | 0.1153
43 | 0.28949 | 0.14021
44 | 0.25787 | 0.12489
45 | 0.23613 | 0.11436
46 | 0.35964 | 0.17418
47 | 0.083776 | 0.040574
48 | 0.34204 | 0.16566
49 | 0.30273 | 0.14662
50 | 0.22567 | 0.1093
51 | 0.090542 | 0.043852
52 | 0.13133 | 0.063608
53 | 0.068003 | 0.032935
54 | 0.32175 | 0.15583
55 | 0.17339 | 0.083975
56 | 0.22811 | 0.11048
57 | 0.29808 | 0.14437
58 | 0.1585 | 0.076765
59 | 0.069256 | 0.033542
60 | 0.25146 | 0.12179
61 | 0.26803 | 0.12981
62 | 0.14168 | 0.06862
63 | 0.12939 | 0.062665
64 | 0.095422 | 0.046215
65 | 0.074674 | 0.036166
66 | 0.36118 | 0.17493
67 | 0.11099 | 0.053755
68 | 0.10779 | 0.052204
69 | 0.13488 | 0.065327
70 | 0.16932 | 0.082007
71 | 0.39133 | 0.18953
72 | 0.21702 | 0.10511
73 | 0.33332 | 0.16143
74 | 0.15084 | 0.073055
75 | 0.40033 | 0.19389
76 | 0.16199 | 0.078455
77 | 0.36418 | 0.17638
78 | 0.19719 | 0.095505
79 | 0.14221 | 0.068877
80 | 0.17864 | 0.086518
81 | 0.070911 | 0.034344
82 | 0.14737 | 0.071374
83 | 0.082844 | 0.040123
84 | 0.31765 | 0.15384
85 | 0.075483 | 0.036558
86 | 0.22885 | 0.11084
87 | 0.10048 | 0.048665
88 | 0.1796 | 0.086983
89 | 0.093654 | 0.045359
90 | 0.3075 | 0.14893
91 | 0.12672 | 0.061373
92 | 0.27338 | 0.13241
93 | 0.18778 | 0.090944
94 | 0.12773 | 0.061861
95 | 0.24622 | 0.11925
96 | 0.18187 | 0.088086

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1