## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_263_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_263_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_263_0_node_175 | 20 | n |  | TRUE
3 | bus_MV_263_0_node_2 | 20 | n |  | TRUE
4 | bus_MV_263_0_node_3 | 20 | n |  | TRUE
5 | bus_MV_263_0_node_4 | 20 | n |  | TRUE
6 | bus_MV_263_0_node_174 | 20 | n |  | TRUE
7 | bus_MV_263_0_node_185 | 20 | n |  | TRUE
8 | bus_MV_263_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_263_0_node_6 | 20 | n |  | TRUE
10 | bus_MV_263_0_node_11 | 20 | n |  | TRUE
11 | bus_MV_263_0_node_56 | 20 | n |  | TRUE
12 | bus_MV_263_0_node_12 | 20 | n |  | TRUE
13 | bus_MV_263_0_node_177 | 20 | n |  | TRUE
14 | bus_MV_263_0_node_8 | 20 | n |  | TRUE
15 | bus_MV_263_0_node_13 | 20 | n |  | TRUE
16 | bus_MV_263_0_node_14 | 20 | n |  | TRUE
17 | bus_MV_263_0_node_187 | 20 | n |  | TRUE
18 | bus_MV_263_0_node_7 | 20 | n |  | TRUE
19 | bus_MV_263_0_node_16 | 20 | n |  | TRUE
20 | bus_MV_263_0_node_55 | 20 | n |  | TRUE
21 | bus_MV_263_0_node_9 | 20 | n |  | TRUE
22 | bus_MV_263_0_node_10 | 20 | n |  | TRUE
23 | bus_MV_263_0_node_15 | 20 | n |  | TRUE
24 | bus_MV_263_0_node_186 | 20 | n |  | TRUE
25 | bus_MV_263_0_node_189 | 20 | n |  | TRUE
26 | bus_MV_263_0_node_190 | 20 | n |  | TRUE
27 | bus_MV_263_0_node_19 | 20 | n |  | TRUE
28 | bus_MV_263_0_node_136 | 20 | n |  | TRUE
29 | bus_MV_263_0_node_17 | 20 | n |  | TRUE
30 | bus_MV_263_0_node_18 | 20 | n |  | TRUE
31 | bus_MV_263_0_node_22 | 20 | n |  | TRUE
32 | bus_MV_263_0_node_26 | 20 | n |  | TRUE
33 | bus_MV_263_0_node_23 | 20 | n |  | TRUE
34 | bus_MV_263_0_node_21 | 20 | n |  | TRUE
35 | bus_MV_263_0_node_20 | 20 | n |  | TRUE
36 | bus_MV_263_0_node_31 | 20 | n |  | TRUE
37 | bus_MV_263_0_node_24 | 20 | n |  | TRUE
38 | bus_MV_263_0_node_25 | 20 | n |  | TRUE
39 | bus_MV_263_0_node_27 | 20 | n |  | TRUE
40 | bus_MV_263_0_node_28 | 20 | n |  | TRUE
41 | bus_MV_263_0_node_29 | 20 | n |  | TRUE
42 | bus_MV_263_0_node_30 | 20 | n |  | TRUE
43 | bus_MV_263_0_node_170 | 20 | n |  | TRUE
44 | bus_MV_263_0_node_32 | 20 | n |  | TRUE
45 | bus_MV_263_0_node_33 | 20 | n |  | TRUE
46 | bus_MV_263_0_node_35 | 20 | n |  | TRUE
47 | bus_MV_263_0_node_34 | 20 | n |  | TRUE
48 | bus_MV_263_0_node_138 | 20 | n |  | TRUE
49 | bus_MV_263_0_node_137 | 20 | n |  | TRUE
50 | bus_MV_263_0_node_36 | 20 | n |  | TRUE
51 | bus_MV_263_0_node_184 | 20 | n |  | TRUE
52 | bus_MV_263_0_node_59 | 20 | n |  | TRUE
53 | bus_MV_263_0_node_98 | 20 | n |  | TRUE
54 | bus_MV_263_0_node_128 | 20 | n |  | TRUE
55 | bus_MV_263_0_node_61 | 20 | n |  | TRUE
56 | bus_MV_263_0_node_57 | 20 | n |  | TRUE
57 | bus_MV_263_0_node_37 | 20 | n |  | TRUE
58 | bus_MV_263_0_node_38 | 20 | n |  | TRUE
59 | bus_MV_263_0_node_51 | 20 | n |  | TRUE
60 | bus_MV_263_0_node_53 | 20 | n |  | TRUE
61 | bus_MV_263_0_node_54 | 20 | n |  | TRUE
62 | bus_MV_263_0_node_39 | 20 | n |  | TRUE
63 | bus_MV_263_0_node_41 | 20 | n |  | TRUE
64 | bus_MV_263_0_node_43 | 20 | n |  | TRUE
65 | bus_MV_263_0_node_63 | 20 | n |  | TRUE
66 | bus_MV_263_0_node_50 | 20 | n |  | TRUE
67 | bus_MV_263_0_node_42 | 20 | n |  | TRUE
68 | bus_MV_263_0_node_40 | 20 | n |  | TRUE
69 | bus_MV_263_0_node_65 | 20 | n |  | TRUE
70 | bus_MV_263_0_node_62 | 20 | n |  | TRUE
71 | bus_MV_263_0_node_44 | 20 | n |  | TRUE
72 | bus_MV_263_0_node_104 | 20 | n |  | TRUE
73 | bus_MV_263_0_node_47 | 20 | n |  | TRUE
74 | bus_MV_263_0_node_48 | 20 | n |  | TRUE
75 | bus_MV_263_0_node_49 | 20 | n |  | TRUE
76 | bus_MV_263_0_node_118 | 20 | n |  | TRUE
77 | bus_MV_263_0_node_156 | 20 | n |  | TRUE
78 | bus_MV_263_0_node_120 | 20 | n |  | TRUE
79 | bus_MV_263_0_node_116 | 20 | n |  | TRUE
80 | bus_MV_263_0_node_103 | 20 | n |  | TRUE
81 | bus_MV_263_0_node_58 | 20 | n |  | TRUE
82 | bus_MV_263_0_node_60 | 20 | n |  | TRUE
83 | bus_MV_263_0_node_147 | 20 | n |  | TRUE
84 | bus_MV_263_0_node_146 | 20 | n |  | TRUE
85 | bus_MV_263_0_node_133 | 20 | n |  | TRUE
86 | bus_MV_263_0_node_134 | 20 | n |  | TRUE
87 | bus_MV_263_0_node_72 | 20 | n |  | TRUE
88 | bus_MV_263_0_node_81 | 20 | n |  | TRUE
89 | bus_MV_263_0_node_64 | 20 | n |  | TRUE
90 | bus_MV_263_0_node_167 | 20 | n |  | TRUE
91 | bus_MV_263_0_node_102 | 20 | n |  | TRUE
92 | bus_MV_263_0_node_106 | 20 | n |  | TRUE
93 | bus_MV_263_0_node_183 | 20 | n |  | TRUE
94 | bus_MV_263_0_node_171 | 20 | n |  | TRUE
95 | bus_MV_263_0_node_66 | 20 | n |  | TRUE
96 | bus_MV_263_0_node_68 | 20 | n |  | TRUE
97 | bus_MV_263_0_node_69 | 20 | n |  | TRUE
98 | bus_MV_263_0_node_73 | 20 | n |  | TRUE
99 | bus_MV_263_0_node_74 | 20 | n |  | TRUE
100 | bus_MV_263_0_node_67 | 20 | n |  | TRUE
101 | bus_MV_263_0_node_71 | 20 | n |  | TRUE
102 | bus_MV_263_0_node_148 | 20 | n |  | TRUE
103 | bus_MV_263_0_node_75 | 20 | n |  | TRUE
104 | bus_MV_263_0_node_84 | 20 | n |  | TRUE
105 | bus_MV_263_0_node_113 | 20 | n |  | TRUE
106 | bus_MV_263_0_node_114 | 20 | n |  | TRUE
107 | bus_MV_263_0_node_182 | 20 | n |  | TRUE
108 | bus_MV_263_0_node_161 | 20 | n |  | TRUE
109 | bus_MV_263_0_node_166 | 20 | n |  | TRUE
110 | bus_MV_263_0_node_165 | 20 | n |  | TRUE
111 | bus_MV_263_0_node_76 | 20 | n |  | TRUE
112 | bus_MV_263_0_node_139 | 20 | n |  | TRUE
113 | bus_MV_263_0_node_82 | 20 | n |  | TRUE
114 | bus_MV_263_0_node_83 | 20 | n |  | TRUE
115 | bus_MV_263_0_node_163 | 20 | n |  | TRUE
116 | bus_MV_263_0_node_162 | 20 | n |  | TRUE
117 | bus_MV_263_0_node_96 | 20 | n |  | TRUE
118 | bus_MV_263_0_node_112 | 20 | n |  | TRUE
119 | bus_MV_263_0_node_169 | 20 | n |  | TRUE
120 | bus_MV_263_0_node_131 | 20 | n |  | TRUE
121 | bus_MV_263_0_node_129 | 20 | n |  | TRUE
122 | bus_MV_263_0_node_94 | 20 | n |  | TRUE
123 | bus_MV_263_0_node_109 | 20 | n |  | TRUE
124 | bus_MV_263_0_node_107 | 20 | n |  | TRUE
125 | bus_MV_263_0_node_140 | 20 | n |  | TRUE
126 | bus_MV_263_0_node_77 | 20 | n |  | TRUE
127 | bus_MV_263_0_node_79 | 20 | n |  | TRUE
128 | bus_MV_263_0_node_80 | 20 | n |  | TRUE
129 | bus_MV_263_0_node_78 | 20 | n |  | TRUE
130 | bus_MV_263_0_node_95 | 20 | n |  | TRUE
131 | bus_MV_263_0_node_97 | 20 | n |  | TRUE
132 | bus_MV_263_0_node_85 | 20 | n |  | TRUE
133 | bus_MV_263_0_node_87 | 20 | n |  | TRUE
134 | bus_MV_263_0_node_90 | 20 | n |  | TRUE
135 | bus_MV_263_0_node_88 | 20 | n |  | TRUE
136 | bus_MV_263_0_node_86 | 20 | n |  | TRUE
137 | bus_MV_263_0_node_89 | 20 | n |  | TRUE
138 | bus_MV_263_0_node_91 | 20 | n |  | TRUE
139 | bus_MV_263_0_node_150 | 20 | n |  | TRUE
140 | bus_MV_263_0_node_151 | 20 | n |  | TRUE
141 | bus_MV_263_0_node_149 | 20 | n |  | TRUE
142 | bus_MV_263_0_node_92 | 20 | n |  | TRUE
143 | bus_MV_263_0_node_122 | 20 | n |  | TRUE
144 | bus_MV_263_0_node_93 | 20 | n |  | TRUE
145 | bus_MV_263_0_node_130 | 20 | n |  | TRUE
146 | bus_MV_263_0_node_123 | 20 | n |  | TRUE
147 | bus_MV_263_0_node_121 | 20 | n |  | TRUE
148 | bus_MV_263_0_node_99 | 20 | n |  | TRUE
149 | bus_MV_263_0_node_101 | 20 | n |  | TRUE
150 | bus_MV_263_0_node_100 | 20 | n |  | TRUE
151 | bus_MV_263_0_node_172 | 20 | n |  | TRUE
152 | bus_MV_263_0_node_108 | 20 | n |  | TRUE
153 | bus_MV_263_0_node_111 | 20 | n |  | TRUE
154 | bus_MV_263_0_node_110 | 20 | n |  | TRUE
155 | bus_MV_263_0_node_124 | 20 | n |  | TRUE
156 | bus_MV_263_0_node_178 | 20 | n |  | TRUE
157 | bus_MV_263_0_node_125 | 20 | n |  | TRUE
158 | bus_MV_263_0_node_132 | 20 | n |  | TRUE
159 | bus_MV_263_0_node_141 | 20 | n |  | TRUE
160 | bus_MV_263_0_node_115 | 20 | n |  | TRUE
161 | bus_MV_263_0_node_117 | 20 | n |  | TRUE
162 | bus_MV_263_0_node_119 | 20 | n |  | TRUE
163 | bus_MV_263_0_node_160 | 20 | n |  | TRUE
164 | bus_MV_263_0_node_173 | 20 | n |  | TRUE
165 | bus_MV_263_0_node_153 | 20 | n |  | TRUE
166 | bus_MV_263_0_node_126 | 20 | n |  | TRUE
167 | bus_MV_263_0_node_181 | 20 | n |  | TRUE
168 | bus_MV_263_0_node_180 | 20 | n |  | TRUE
169 | bus_MV_263_0_node_135 | 20 | n |  | TRUE
170 | bus_MV_263_0_node_155 | 20 | n |  | TRUE
171 | bus_MV_263_0_node_154 | 20 | n |  | TRUE
172 | bus_MV_263_0_node_142 | 20 | n |  | TRUE
173 | bus_MV_263_0_node_143 | 20 | n |  | TRUE
174 | bus_MV_263_0_node_144 | 20 | n |  | TRUE
175 | bus_MV_263_0_node_145 | 20 | n |  | TRUE
176 | bus_MV_263_0_node_168 | 20 | n |  | TRUE
177 | bus_MV_263_0_node_152 | 20 | n |  | TRUE
178 | bus_MV_263_0_node_157 | 20 | n |  | TRUE
179 | bus_MV_263_0_node_158 | 20 | n |  | TRUE
180 | bus_MV_263_0_node_159 | 20 | n |  | TRUE
181 | bus_MV_263_0_node_179 | 20 | n |  | TRUE
182 | bus_MV_263_0_node_164 | 20 | n |  | TRUE
183 | bus_HV_263_0_node_184 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_263_0_load_0 | 0 | 0.34108 | 0.16519 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_263_0_load_3 | 4 | 0.18118 | 0.087749 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_263_0_load_174 | 6 | 0.10879 | 0.05269 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_263_0_load_185 | 7 | 0.33731 | 0.16337 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_263_0_load_11 | 10 | 0.13947 | 0.067548 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_263_0_load_56 | 11 | 0.14297 | 0.069242 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_263_0_load_177 | 13 | 0.15014 | 0.072715 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_263_0_load_187 | 17 | 0.24661 | 0.11944 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_263_0_load_7 | 18 | 0.29106 | 0.14097 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_263_0_load_15 | 23 | 0.20747 | 0.10048 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_263_0_load_186 | 24 | 0.31383 | 0.15199 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_263_0_load_190 | 26 | 0.16966 | 0.082168 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_263_0_load_136 | 28 | 0.080036 | 0.038763 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_263_0_load_17 | 29 | 0.21092 | 0.10215 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_263_0_load_23 | 33 | 0.25425 | 0.12314 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_263_0_load_20 | 35 | 0.27415 | 0.13278 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_263_0_load_31 | 36 | 0.35432 | 0.1716 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_263_0_load_27 | 39 | 0.31973 | 0.15485 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_263_0_load_170 | 43 | 0.30862 | 0.14947 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_263_0_load_32 | 44 | 0.19295 | 0.093451 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_263_0_load_138 | 48 | 0.1838 | 0.089017 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_263_0_load_137 | 49 | 0.075857 | 0.036739 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_263_0_load_184 | 51 | 0.2453 | 0.1188 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_263_0_load_98 | 53 | 0.25929 | 0.12558 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_263_0_load_128 | 54 | 0.41399 | 0.2005 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_263_0_load_57 | 56 | 0.34674 | 0.16794 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_263_0_load_37 | 57 | 0.25249 | 0.12229 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_263_0_load_54 | 61 | 0.25321 | 0.12263 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_263_0_load_43 | 64 | 0.26586 | 0.12876 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_263_0_load_50 | 66 | 0.40665 | 0.19695 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_263_0_load_40 | 68 | 0.3112 | 0.15072 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_263_0_load_62 | 70 | 0.30944 | 0.14987 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_263_0_load_44 | 71 | 0.31768 | 0.15386 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_263_0_load_104 | 72 | 0.40372 | 0.19553 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_263_0_load_47 | 73 | 0.30265 | 0.14658 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_263_0_load_156 | 77 | 0.37575 | 0.18198 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_263_0_load_120 | 78 | 0.40257 | 0.19497 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_263_0_load_147 | 83 | 0.10563 | 0.051158 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_263_0_load_146 | 84 | 1.6619 | 0.80492 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_263_0_load_133 | 85 | 0.32987 | 0.15976 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_263_0_load_81 | 88 | 0.39643 | 0.192 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_263_0_load_64 | 89 | 0.13214 | 0.064001 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_263_0_load_167 | 90 | 0.076338 | 0.036972 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_263_0_load_183 | 93 | 0.11263 | 0.054551 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_263_0_load_171 | 94 | 0.1528 | 0.074002 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_263_0_load_66 | 95 | 0.35722 | 0.17301 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_263_0_load_68 | 96 | 0.081158 | 0.039307 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_263_0_load_148 | 102 | 0.073374 | 0.035536 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_263_0_load_75 | 103 | 0.24958 | 0.12088 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_263_0_load_182 | 107 | 0.22782 | 0.11034 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_263_0_load_161 | 108 | 0.070134 | 0.033968 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_263_0_load_166 | 109 | 0.38458 | 0.18626 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_263_0_load_165 | 110 | 0.33342 | 0.16148 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_263_0_load_139 | 112 | 0.1968 | 0.095313 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_263_0_load_83 | 114 | 0.19461 | 0.094253 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_263_0_load_162 | 116 | 0.40326 | 0.19531 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_263_0_load_169 | 119 | 0.1579 | 0.076474 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_263_0_load_129 | 121 | 0.28391 | 0.1375 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_263_0_load_107 | 124 | 0.3087 | 0.14951 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_263_0_load_140 | 125 | 0.11323 | 0.054839 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_263_0_load_80 | 128 | 0.26734 | 0.12948 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_263_0_load_95 | 130 | 0.074473 | 0.036069 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_263_0_load_85 | 132 | 0.24012 | 0.1163 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_263_0_load_90 | 134 | 0.12291 | 0.059529 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_263_0_load_88 | 135 | 0.17419 | 0.084365 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_263_0_load_89 | 137 | 0.0695 | 0.03366 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_263_0_load_151 | 140 | 0.40451 | 0.19591 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_263_0_load_149 | 141 | 0.10031 | 0.048585 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_263_0_load_92 | 142 | 0.38999 | 0.18888 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_263_0_load_93 | 144 | 0.28231 | 0.13673 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_263_0_load_130 | 145 | 0.28943 | 0.14018 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_263_0_load_121 | 147 | 0.23552 | 0.11407 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_263_0_load_99 | 148 | 0.22841 | 0.11062 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_263_0_load_124 | 155 | 0.32371 | 0.15678 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_263_0_load_178 | 156 | 0.09979 | 0.04833 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_263_0_load_115 | 160 | 0.32736 | 0.15855 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_263_0_load_119 | 162 | 0.2504 | 0.12127 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_263_0_load_153 | 165 | 0.10401 | 0.050372 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_263_0_load_126 | 166 | 0.070575 | 0.034181 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_263_0_load_181 | 167 | 0.40605 | 0.19666 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_263_0_load_155 | 170 | 0.35475 | 0.17181 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_263_0_load_154 | 171 | 0.071246 | 0.034506 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_263_0_load_144 | 174 | 0.13529 | 0.065524 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_263_0_load_168 | 176 | 0.09127 | 0.044204 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_263_0_load_152 | 177 | 0.097792 | 0.047363 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_263_0_load_157 | 178 | 0.091762 | 0.044442 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_263_0_load_159 | 180 | 0.11256 | 0.054513 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_263_0_load_179 | 181 | 0.27375 | 0.13258 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_263_0_load_164 | 182 | 0.068205 | 0.033033 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 51 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_263_0_line_0 |  | 0 | 1 | 0.087706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_263_0_line_1 |  | 0 | 2 | 0.36511 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_263_0_line_2 |  | 1 | 3 | 0.15713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_263_0_line_3 |  | 2 | 6 | 0.036557 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_263_0_line_4 |  | 3 | 7 | 0.32296 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_263_0_line_5 |  | 3 | 4 | 0.072801 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_263_0_line_6 |  | 4 | 5 | 0.15651 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_263_0_line_7 |  | 5 | 8 | 0.3879 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_263_0_line_8 |  | 6 | 21 | 0.064203 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_263_0_line_9 |  | 8 | 9 | 0.66886 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_263_0_line_10 |  | 8 | 10 | 0.013006 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_263_0_line_11 |  | 9 | 11 | 0.17084 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_263_0_line_12 |  | 11 | 20 | 0.081261 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_263_0_line_13 |  | 12 | 13 | 0.035993 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_263_0_line_14 |  | 12 | 14 | 0.43429 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_263_0_line_15 |  | 14 | 21 | 0.22384 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_263_0_line_16 |  | 14 | 22 | 0.28475 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_263_0_line_17 |  | 14 | 18 | 0.067782 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_263_0_line_18 |  | 15 | 16 | 0.46765 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_263_0_line_19 |  | 15 | 17 | 0.062862 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_263_0_line_20 |  | 15 | 18 | 0.53506 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_263_0_line_21 |  | 16 | 19 | 0.20636 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_263_0_line_22 |  | 17 | 25 | 0.38612 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_263_0_line_23 |  | 19 | 28 | 0.018102 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_263_0_line_24 |  | 19 | 23 | 0.14225 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_263_0_line_25 |  | 20 | 60 | 0.50502 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_263_0_line_26 |  | 22 | 24 | 0.031164 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_263_0_line_27 |  | 24 | 27 | 0.002397 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_263_0_line_28 |  | 25 | 26 | 0.067877 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_263_0_line_29 |  | 27 | 31 | 1.3598 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_263_0_line_30 |  | 27 | 30 | 0.18637 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_263_0_line_31 |  | 29 | 30 | 0.10859 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_263_0_line_32 |  | 31 | 32 | 0.58792 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_263_0_line_33 |  | 31 | 33 | 0.070252 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
34 | MV_263_0_line_34 |  | 31 | 34 | 0.20356 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_263_0_line_35 |  | 32 | 36 | 0.014524 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_263_0_line_36 |  | 33 | 37 | 0.078893 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
37 | MV_263_0_line_37 |  | 34 | 35 | 0.006467 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_263_0_line_38 |  | 37 | 38 | 0.54108 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
39 | MV_263_0_line_39 |  | 38 | 39 | 0.023053 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
40 | MV_263_0_line_40 |  | 39 | 40 | 0.031492 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
41 | MV_263_0_line_41 |  | 40 | 41 | 0.49643 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_263_0_line_42 |  | 40 | 42 | 0.52766 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
43 | MV_263_0_line_43 |  | 41 | 43 | 0.081919 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_263_0_line_44 |  | 42 | 44 | 0.10836 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
45 | MV_263_0_line_45 |  | 44 | 45 | 0.08426 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
46 | MV_263_0_line_46 |  | 45 | 46 | 0.498 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
47 | MV_263_0_line_47 |  | 46 | 50 | 0.4226 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
48 | MV_263_0_line_48 |  | 46 | 51 | 0.055746 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
49 | MV_263_0_line_49 |  | 47 | 48 | 0.050269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_263_0_line_50 |  | 47 | 49 | 0.050608 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_263_0_line_51 |  | 48 | 54 | 0.090523 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_263_0_line_52 |  | 50 | 52 | 0.098905 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
53 | MV_263_0_line_53 |  | 50 | 53 | 0.017427 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_263_0_line_54 |  | 52 | 55 | 0.092845 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_263_0_line_55 |  | 52 | 56 | 0.071628 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
56 | MV_263_0_line_56 |  | 54 | 166 | 0.041255 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_263_0_line_57 |  | 55 | 84 | 0.038228 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_263_0_line_58 |  | 56 | 81 | 0.091735 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
59 | MV_263_0_line_59 |  | 57 | 58 | 0.085831 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_263_0_line_60 |  | 58 | 59 | 0.45691 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_263_0_line_61 |  | 58 | 60 | 0.6545 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_263_0_line_62 |  | 59 | 66 | 0.036901 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_263_0_line_63 |  | 60 | 61 | 0.15361 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_263_0_line_64 |  | 62 | 63 | 0.19588 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_263_0_line_65 |  | 62 | 64 | 0.087971 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_263_0_line_66 |  | 62 | 65 | 0.25767 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_263_0_line_67 |  | 63 | 67 | 0.2058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_263_0_line_68 |  | 63 | 68 | 0.007379 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_263_0_line_69 |  | 65 | 69 | 0.37842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_263_0_line_70 |  | 65 | 70 | 0.13429 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_263_0_line_71 |  | 67 | 71 | 0.041593 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_263_0_line_72 |  | 69 | 72 | 0.014894 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_263_0_line_73 |  | 70 | 89 | 0.023369 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_263_0_line_74 |  | 70 | 90 | 0.22917 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_263_0_line_75 |  | 73 | 74 | 0.075209 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
76 | MV_263_0_line_76 |  | 74 | 75 | 0.11029 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_263_0_line_77 |  | 75 | 76 | 0.11457 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_263_0_line_78 |  | 75 | 77 | 0.062113 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_263_0_line_79 |  | 76 | 78 | 0.027175 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_263_0_line_80 |  | 76 | 79 | 0.061129 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_263_0_line_81 |  | 77 | 80 | 0.031305 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_263_0_line_82 |  | 79 | 160 | 0.09258 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_263_0_line_83 |  | 80 | 149 | 0.18188 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_263_0_line_84 |  | 81 | 82 | 0.12742 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
85 | MV_263_0_line_85 |  | 82 | 83 | 0.042162 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
86 | MV_263_0_line_86 |  | 83 | 85 | 0.11411 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
87 | MV_263_0_line_87 |  | 85 | 86 | 0.007641 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_263_0_line_88 |  | 85 | 87 | 0.083064 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
89 | MV_263_0_line_89 |  | 85 | 88 | 0.19744 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
90 | MV_263_0_line_90 |  | 86 | 169 | 0.05306 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_263_0_line_91 |  | 87 | 104 | 0.049966 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_263_0_line_92 |  | 87 | 101 | 0.24661 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
93 | MV_263_0_line_93 |  | 88 | 113 | 0.008967 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_263_0_line_94 |  | 90 | 91 | 0.051645 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_263_0_line_95 |  | 91 | 150 | 0.07367 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_263_0_line_96 |  | 92 | 93 | 0.007426 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_263_0_line_97 |  | 92 | 94 | 0.59796 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_263_0_line_98 |  | 94 | 151 | 0.072969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_263_0_line_99 |  | 95 | 96 | 0.0096081 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
100 | MV_263_0_line_100 |  | 95 | 97 | 0.029456 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
101 | MV_263_0_line_101 |  | 96 | 98 | 0.042154 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
102 | MV_263_0_line_102 |  | 97 | 99 | 0.063417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_263_0_line_103 |  | 97 | 100 | 0.0673 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
104 | MV_263_0_line_104 |  | 98 | 105 | 0.11887 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
105 | MV_263_0_line_105 |  | 98 | 106 | 0.16746 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_263_0_line_106 |  | 99 | 107 | 0.011556 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_263_0_line_107 |  | 100 | 101 | 0.16792 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
108 | MV_263_0_line_108 |  | 101 | 102 | 0.016711 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_263_0_line_109 |  | 101 | 103 | 0.17528 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
110 | MV_263_0_line_110 |  | 103 | 111 | 0.017141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_263_0_line_111 |  | 104 | 112 | 0.02556 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_263_0_line_112 |  | 105 | 115 | 0.026041 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_263_0_line_113 |  | 105 | 116 | 0.022034 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
114 | MV_263_0_line_114 |  | 105 | 117 | 0.074229 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
115 | MV_263_0_line_115 |  | 106 | 125 | 0.0077001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_263_0_line_116 |  | 106 | 123 | 0.37082 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_263_0_line_117 |  | 108 | 109 | 0.067231 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
118 | MV_263_0_line_118 |  | 109 | 110 | 0.035435 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_263_0_line_119 |  | 110 | 182 | 0.033972 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
120 | MV_263_0_line_120 |  | 110 | 115 | 0.02207 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_263_0_line_121 |  | 111 | 126 | 0.25063 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_263_0_line_122 |  | 113 | 114 | 0.060563 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_263_0_line_123 |  | 117 | 121 | 0.04623 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
124 | MV_263_0_line_124 |  | 117 | 122 | 0.084694 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_263_0_line_125 |  | 118 | 119 | 0.041276 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
126 | MV_263_0_line_126 |  | 118 | 120 | 0.074835 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
127 | MV_263_0_line_127 |  | 120 | 158 | 0.26747 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
128 | MV_263_0_line_128 |  | 120 | 145 | 0.052158 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
129 | MV_263_0_line_129 |  | 121 | 145 | 0.054989 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
130 | MV_263_0_line_130 |  | 122 | 144 | 0.011268 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_263_0_line_131 |  | 123 | 124 | 0.035412 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_263_0_line_132 |  | 124 | 152 | 0.014705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_263_0_line_133 |  | 125 | 159 | 0.030878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_263_0_line_134 |  | 126 | 127 | 0.12086 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_263_0_line_135 |  | 126 | 128 | 0.056145 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_263_0_line_136 |  | 127 | 129 | 0.12141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_263_0_line_137 |  | 129 | 130 | 0.017314 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_263_0_line_138 |  | 130 | 131 | 0.037479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_263_0_line_139 |  | 131 | 143 | 0.00944 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_263_0_line_140 |  | 131 | 142 | 0.064946 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
141 | MV_263_0_line_141 |  | 132 | 133 | 0.014791 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_263_0_line_142 |  | 133 | 134 | 0.0031931 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_263_0_line_143 |  | 133 | 135 | 0.070062 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
144 | MV_263_0_line_144 |  | 135 | 136 | 0.0041298 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_263_0_line_145 |  | 136 | 137 | 0.010667 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_263_0_line_146 |  | 137 | 138 | 0.012254 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_263_0_line_147 |  | 138 | 139 | 0.059362 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_263_0_line_148 |  | 139 | 140 | 0.008779 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_263_0_line_149 |  | 139 | 141 | 0.037686 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_263_0_line_150 |  | 140 | 177 | 0.024164 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_263_0_line_151 |  | 143 | 146 | 0.23936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_263_0_line_152 |  | 143 | 147 | 0.028504 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_263_0_line_153 |  | 146 | 165 | 0.032837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_263_0_line_154 |  | 148 | 149 | 0.011307 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_263_0_line_155 |  | 148 | 150 | 0.059575 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
156 | MV_263_0_line_156 |  | 151 | 164 | 0.16565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_263_0_line_157 |  | 152 | 153 | 0.099785 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_263_0_line_158 |  | 153 | 156 | 0.03103 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_263_0_line_159 |  | 153 | 154 | 0.12489 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_263_0_line_160 |  | 154 | 155 | 0.040864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_263_0_line_161 |  | 155 | 157 | 0.091865 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
162 | MV_263_0_line_162 |  | 157 | 166 | 0.037738 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_263_0_line_163 |  | 158 | 167 | 0.029426 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
164 | MV_263_0_line_164 |  | 159 | 172 | 0.008294 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_263_0_line_165 |  | 159 | 173 | 0.077904 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_263_0_line_166 |  | 160 | 161 | 0.057914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_263_0_line_167 |  | 161 | 162 | 0.002911 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_263_0_line_168 |  | 162 | 163 | 0.021053 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_263_0_line_169 |  | 163 | 164 | 0.1494 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
170 | MV_263_0_line_170 |  | 164 | 181 | 0.019284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
171 | MV_263_0_line_171 |  | 164 | 179 | 0.13321 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
172 | MV_263_0_line_172 |  | 167 | 168 | 0.016523 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
173 | MV_263_0_line_173 |  | 168 | 180 | 0.15326 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
174 | MV_263_0_line_174 |  | 169 | 170 | 0.020753 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_263_0_line_175 |  | 170 | 171 | 0.020022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_263_0_line_176 |  | 172 | 174 | 0.03284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_263_0_line_177 |  | 172 | 175 | 0.025219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
178 | MV_263_0_line_178 |  | 173 | 176 | 0.01678 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
179 | MV_263_0_line_179 |  | 175 | 177 | 0.034508 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
180 | MV_263_0_line_180 |  | 178 | 179 | 0.011842 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
181 | MV_263_0_line_181 |  | 178 | 180 | 0.05686 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_263_0_trafo_184 | 25 MVA 110/20 kV | 183 | 51 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2553720.0299 | 1147701.5077
1 | 2553800.9566 | 1147735.1585
2 | 2553447.5821 | 1147458.4512
3 | 2553918.0865 | 1147840.2031
4 | 2553957.9188 | 1147901.1406
5 | 2553980.6662 | 1148055.7131
6 | 2553410.9985 | 1147456.0332
7 | 2554167.8704 | 1147635.4775
8 | 2553925.0341 | 1148330.7812
9 | 2554226.804 | 1148690.0735
10 | 2553937.2874 | 1148326.474
11 | 2554356.7005 | 1148578.7842
12 | 2553055.418 | 1147923.0954
13 | 2553034.4459 | 1147935.9547
14 | 2553179.8643 | 1147507.021
15 | 2553088.4705 | 1148039.2199
16 | 2553507.0131 | 1148114.1308
17 | 2553025.7787 | 1148034.5957
18 | 2553243.9738 | 1147527.2504
19 | 2553665.0474 | 1148232.1166
20 | 2554420.2938 | 1148528.0201
21 | 2553346.8287 | 1147450.7278
22 | 2552979.7353 | 1147437.8908
23 | 2553533.8766 | 1148287.1683
24 | 2552949.9996 | 1147428.2962
25 | 2552829.7938 | 1148367.2799
26 | 2552763.4514 | 1148352.0928
27 | 2552947.7353 | 1147427.4912
28 | 2553673.2796 | 1148248.2315
29 | 2552667.5291 | 1147377.1636
30 | 2552775.748 | 1147381.7154
31 | 2552955.1952 | 1146893.8676
32 | 2552397.9208 | 1146890.8168
33 | 2553021.8716 | 1146871.1681
34 | 2552847.6459 | 1146750.5354
35 | 2552841.2765 | 1146749.3181
36 | 2552390.7696 | 1146878.1668
37 | 2553098.9798 | 1146854.48
38 | 2553417.2093 | 1146585.3902
39 | 2553439.865 | 1146580.9348
40 | 2553470.3283 | 1146572.9505
41 | 2553518.2785 | 1146908.2976
42 | 2553730.9099 | 1146800.1135
43 | 2553438.5968 | 1146889.2818
44 | 2553839.4556 | 1146804.0038
45 | 2553850.4079 | 1146720.8657
46 | 2553872.5568 | 1146578.2888
47 | 2553914.7811 | 1146372.9591
48 | 2553959.0453 | 1146349.2929
49 | 2553951.4983 | 1146407.6271
50 | 2553735.0365 | 1146333.2071
51 | 2553926.0513 | 1146562.6041
52 | 2553738.9032 | 1146246.7216
53 | 2553750.07 | 1146324.3203
54 | 2554047.3273 | 1146369.3099
55 | 2553678.2933 | 1146271.3896
56 | 2553762.049 | 1146178.9309
57 | 2555008.3927 | 1147722.1868
58 | 2554930.2275 | 1147691.3006
59 | 2554536.7536 | 1147923.5709
60 | 2554674.843 | 1148293.9197
61 | 2554791.6687 | 1148393.6584
62 | 2554554.6318 | 1146873.1826
63 | 2554449.6553 | 1146747.0672
64 | 2554587.8521 | 1146954.6404
65 | 2554804.1823 | 1146809.0026
66 | 2554532.0605 | 1147960.0029
67 | 2554318.8573 | 1146829.0903
68 | 2554452.0911 | 1146740.1007
69 | 2554971.8502 | 1146832.8686
70 | 2554728.9394 | 1146697.7689
71 | 2554294.1243 | 1146862.3509
72 | 2554974.0902 | 1146818.1442
73 | 2554147.096 | 1146685.8343
74 | 2554172.4183 | 1146615.0159
75 | 2554208.1492 | 1146540.1607
76 | 2554255.0331 | 1146438.9073
77 | 2554270.1755 | 1146543.4381
78 | 2554233.5291 | 1146422.24
79 | 2554291.6348 | 1146390.404
80 | 2554301.4367 | 1146545.0871
81 | 2553687.4327 | 1146125.5661
82 | 2553727.3996 | 1146004.6072
83 | 2553766.8395 | 1146019.5122
84 | 2553656.0577 | 1146302.4855
85 | 2553834.965 | 1145927.9746
86 | 2553842.415 | 1145929.7628
87 | 2553855.9116 | 1145847.5946
88 | 2553827.3199 | 1145730.6869
89 | 2554748.1767 | 1146684.5003
90 | 2554601.1767 | 1146507.5122
91 | 2554571.5501 | 1146465.2111
92 | 2555204.8275 | 1146695.0247
93 | 2555211.3683 | 1146691.4741
94 | 2554702.1538 | 1146371.1888
95 | 2554093.1688 | 1145816.7525
96 | 2554101.4692 | 1145821.5917
97 | 2554073.5322 | 1145838.747
98 | 2554136.563 | 1145844.6581
99 | 2554031.5362 | 1145886.259
100 | 2554033.8228 | 1145784.4111
101 | 2553910.6709 | 1145755.5384
102 | 2553894.6566 | 1145750.7636
103 | 2553973.6039 | 1145591.95
104 | 2553812.4544 | 1145827.6622
105 | 2554185.6158 | 1145803.641
106 | 2554134.0272 | 1145954.3341
107 | 2554039.7263 | 1145894.4339
108 | 2554105.4044 | 1145746.0503
109 | 2554168.1693 | 1145721.954
110 | 2554175.9306 | 1145756.5238
111 | 2553979.8247 | 1145577.6394
112 | 2553815.0216 | 1145803.286
113 | 2553818.7037 | 1145728.1184
114 | 2553760.6659 | 1145710.8125
115 | 2554180.3359 | 1145778.1458
116 | 2554165.3313 | 1145812.2444
117 | 2554229.6151 | 1145789.9768
118 | 2554269.4451 | 1145872.5276
119 | 2554293.7437 | 1145905.8935
120 | 2554334.3913 | 1145835.3485
121 | 2554265.2007 | 1145819.4881
122 | 2554238.0262 | 1145716.1636
123 | 2554255.1061 | 1146098.1531
124 | 2554225.6968 | 1146117.8644
125 | 2554128.7108 | 1145959.9042
126 | 2554140.0014 | 1145593.4134
127 | 2554239.2542 | 1145605.9752
128 | 2554091.0996 | 1145620.9839
129 | 2554236.3833 | 1145653.7328
130 | 2554253.6912 | 1145654.1526
131 | 2554291.1526 | 1145653.961
132 | 2553920.0941 | 1146135.0733
133 | 2553931.0249 | 1146145.0614
134 | 2553928.7739 | 1146147.3261
135 | 2553980.4294 | 1146095.3838
136 | 2553983.3421 | 1146092.4561
137 | 2553990.8627 | 1146084.8917
138 | 2553999.48 | 1146076.1798
139 | 2554043.9512 | 1146043.1673
140 | 2554047.0796 | 1146035.3616
141 | 2554070.6937 | 1146069.7097
142 | 2554304.1516 | 1145590.3295
143 | 2554300.1618 | 1145655.6935
144 | 2554249.2231 | 1145714.6444
145 | 2554311.147 | 1145789.0789
146 | 2554452.7891 | 1145745.2044
147 | 2554316.7904 | 1145677.4562
148 | 2554464.1581 | 1146508.9012
149 | 2554468.2246 | 1146519.4536
150 | 2554518.0108 | 1146483.425
151 | 2554674.6058 | 1146303.6282
152 | 2554213.2892 | 1146125.7521
153 | 2554201.1127 | 1146197.2261
154 | 2554129.5679 | 1146208.5993
155 | 2554157.1599 | 1146238.7601
156 | 2554174.9619 | 1146214.0451
157 | 2554094.5843 | 1146306.0165
158 | 2554417.3588 | 1145914.4601
159 | 2554112.0817 | 1145982.7717
160 | 2554365.3662 | 1146334.4153
161 | 2554415.2401 | 1146304.7663
162 | 2554417.7951 | 1146303.3574
163 | 2554435.5609 | 1146292.0058
164 | 2554572.7597 | 1146232.8821
165 | 2554434.0668 | 1145770.0254
166 | 2554072.0503 | 1146336.2873
167 | 2554441.8574 | 1145930.7607
168 | 2554449.9329 | 1145945.1848
169 | 2553881.2796 | 1145965.9945
170 | 2553896.4833 | 1145980.1631
171 | 2553911.1275 | 1145993.8167
172 | 2554106.1186 | 1145988.5535
173 | 2554159.9614 | 1146042.9933
174 | 2554128.0984 | 1146012.954
175 | 2554087.0663 | 1145992.4453
176 | 2554172.7402 | 1146032.1173
177 | 2554063.8156 | 1146017.9322
178 | 2554458.0058 | 1146152.7644
179 | 2554458.3856 | 1146164.6006
180 | 2554444.3228 | 1146098.3408
181 | 2554587.5916 | 1146220.5082
182 | 2554208.6055 | 1145747.2268
183 | 2553926.0513 | 1146562.6041

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98707 | 0.011269 | 0.34108 | 0.16519
1 | 0.98688 | 0.012799 | 0 | 0
2 | 0.98853 | 0.022402 | 0 | 0
3 | 0.98654 | 0.01557 | 0 | 0
4 | 0.98634 | 0.014 | 0.18118 | 0.087749
5 | 0.9861 | 0.015806 | 0 | 0
6 | 0.98862 | 0.021616 | 0.10879 | 0.05269
7 | 0.98632 | 0.014212 | 0.33731 | 0.16337
8 | 0.98551 | 0.020446 | 0 | 0
9 | 0.9846 | 0.027861 | 0 | 0
10 | 0.98551 | 0.020468 | 0.13947 | 0.067548
11 | 0.98437 | 0.029867 | 0.14297 | 0.069242
12 | 0.9893 | 0.014271 | 0 | 0
13 | 0.98929 | 0.014336 | 0.15014 | 0.072715
14 | 0.98942 | 0.015117 | 0 | 0
15 | 0.98861 | 0.010329 | 0 | 0
16 | 0.98844 | 0.011644 | 0 | 0
17 | 0.98856 | 0.0099941 | 0.24661 | 0.11944
18 | 0.98934 | 0.015854 | 0.29106 | 0.14097
19 | 0.98836 | 0.01233 | 0 | 0
20 | 0.98427 | 0.030693 | 0 | 0
21 | 0.9888 | 0.020156 | 0 | 0
22 | 0.99063 | 0.0052528 | 0 | 0
23 | 0.9883 | 0.011964 | 0.20747 | 0.10048
24 | 0.99076 | 0.0041822 | 0.31383 | 0.15199
25 | 0.98843 | 0.0091232 | 0 | 0
26 | 0.98842 | 0.0092607 | 0.16966 | 0.082168
27 | 0.99077 | 0.0040908 | 0 | 0
28 | 0.98836 | 0.012348 | 0.080036 | 0.038763
29 | 0.99069 | 0.0047828 | 0.21092 | 0.10215
30 | 0.99072 | 0.0045126 | 0 | 0
31 | 0.99744 | -0.048903 | 0 | 0
32 | 0.99718 | -0.046674 | 0 | 0
33 | 0.99761 | -0.046865 | 0.25425 | 0.12314
34 | 0.99737 | -0.048266 | 0 | 0
35 | 0.99737 | -0.048245 | 0.27415 | 0.13278
36 | 0.99717 | -0.046612 | 0.35432 | 0.1716
37 | 0.99805 | -0.035405 | 0 | 0
38 | 0.99846 | -0.033126 | 0 | 0
39 | 0.99848 | -0.033023 | 0.31973 | 0.15485
40 | 0.99853 | -0.029944 | 0 | 0
41 | 0.99834 | -0.028296 | 0 | 0
42 | 0.99899 | -0.027212 | 0 | 0
43 | 0.99829 | -0.028602 | 0.30862 | 0.14947
44 | 0.99908 | -0.02662 | 0.19295 | 0.093451
45 | 0.99916 | -0.026142 | 0 | 0
46 | 0.9996 | -0.023186 | 0 | 0
47 | 0.99313 | -0.10798 | 0 | 0
48 | 0.99314 | -0.10803 | 0.1838 | 0.089017
49 | 0.99313 | -0.10794 | 0.075857 | 0.036739
50 | 0.99849 | -0.028121 | 0 | 0
51 | 1 | 0 | -21.8155 | -9.8555
52 | 0.99823 | -0.029238 | 0 | 0
53 | 0.99848 | -0.028067 | 0.25929 | 0.12558
54 | 0.99319 | -0.10772 | 0.41399 | 0.2005
55 | 0.99803 | -0.027397 | 0 | 0
56 | 0.99806 | -0.029971 | 0.34674 | 0.16794
57 | 0.9828 | 0.030713 | 0.25249 | 0.12229
58 | 0.98283 | 0.03045 | 0 | 0
59 | 0.98247 | 0.02808 | 0 | 0
60 | 0.98368 | 0.036058 | 0 | 0
61 | 0.9836 | 0.035571 | 0.25321 | 0.12263
62 | 0.98806 | -0.16899 | 0 | 0
63 | 0.9879 | -0.16758 | 0 | 0
64 | 0.98802 | -0.16928 | 0.26586 | 0.12876
65 | 0.98851 | -0.16589 | 0 | 0
66 | 0.98245 | 0.028265 | 0.40665 | 0.19695
67 | 0.98782 | -0.16683 | 0 | 0
68 | 0.9879 | -0.16755 | 0.3112 | 0.15072
69 | 0.98832 | -0.16413 | 0 | 0
70 | 0.98885 | -0.1635 | 0.30944 | 0.14987
71 | 0.9878 | -0.16667 | 0.31768 | 0.15386
72 | 0.9883 | -0.16421 | 0.40372 | 0.19553
73 | 0.99082 | -0.16614 | 0.30265 | 0.14658
74 | 0.99087 | -0.16586 | 0 | 0
75 | 0.99091 | -0.16626 | 0 | 0
76 | 0.99131 | -0.16981 | 0 | 0
77 | 0.99072 | -0.16454 | 0.37575 | 0.18198
78 | 0.9913 | -0.16967 | 0.40257 | 0.19497
79 | 0.99156 | -0.17199 | 0 | 0
80 | 0.99064 | -0.16382 | 0 | 0
81 | 0.99763 | -0.054258 | 0 | 0
82 | 0.99735 | -0.055532 | 0 | 0
83 | 0.99725 | -0.055951 | 0.10563 | 0.051158
84 | 0.99795 | -0.026635 | 1.6619 | 0.80492
85 | 0.99672 | -0.085954 | 0.32987 | 0.15976
86 | 0.99672 | -0.085916 | 0 | 0
87 | 0.99637 | -0.10569 | 0 | 0
88 | 0.99649 | -0.087403 | 0.39643 | 0.192
89 | 0.98885 | -0.16347 | 0.13214 | 0.064001
90 | 0.98963 | -0.15817 | 0.076338 | 0.036972
91 | 0.98975 | -0.15925 | 0 | 0
92 | 0.99335 | -0.16424 | 0 | 0
93 | 0.99335 | -0.16423 | 0.11263 | 0.054551
94 | 0.99348 | -0.16339 | 0.1528 | 0.074002
95 | 0.99529 | -0.12335 | 0.35722 | 0.17301
96 | 0.99527 | -0.12342 | 0.081158 | 0.039307
97 | 0.99534 | -0.12313 | 0 | 0
98 | 0.9952 | -0.12372 | 0 | 0
99 | 0.99532 | -0.12296 | 0 | 0
100 | 0.99558 | -0.10918 | 0 | 0
101 | 0.99588 | -0.10789 | 0 | 0
102 | 0.99588 | -0.10787 | 0.073374 | 0.035536
103 | 0.99543 | -0.11105 | 0.24958 | 0.12088
104 | 0.99636 | -0.10558 | 0 | 0
105 | 0.99506 | -0.12433 | 0 | 0
106 | 0.99455 | -0.11795 | 0 | 0
107 | 0.99532 | -0.12292 | 0.22782 | 0.11034
108 | 0.99498 | -0.1237 | 0.070134 | 0.033968
109 | 0.99499 | -0.12364 | 0.38458 | 0.18626
110 | 0.99501 | -0.12383 | 0.33342 | 0.16148
111 | 0.99541 | -0.11085 | 0 | 0
112 | 0.99635 | -0.10552 | 0.1968 | 0.095313
113 | 0.99649 | -0.087383 | 0 | 0
114 | 0.99648 | -0.087244 | 0.19461 | 0.094253
115 | 0.99503 | -0.12406 | 0 | 0
116 | 0.99504 | -0.12444 | 0.40326 | 0.19531
117 | 0.99499 | -0.12464 | 0 | 0
118 | 0.99479 | -0.13015 | 0 | 0
119 | 0.99478 | -0.13023 | 0.1579 | 0.076474
120 | 0.99481 | -0.13 | 0 | 0
121 | 0.9949 | -0.1296 | 0.28391 | 0.1375
122 | 0.99496 | -0.12436 | 0 | 0
123 | 0.99385 | -0.11173 | 0 | 0
124 | 0.99379 | -0.11113 | 0.3087 | 0.14951
125 | 0.99454 | -0.11781 | 0.11323 | 0.054839
126 | 0.99507 | -0.10791 | 0 | 0
127 | 0.99495 | -0.10683 | 0 | 0
128 | 0.99505 | -0.10773 | 0.26734 | 0.12948
129 | 0.99482 | -0.10573 | 0 | 0
130 | 0.9948 | -0.10558 | 0.074473 | 0.036069
131 | 0.99477 | -0.10526 | 0 | 0
132 | 0.99421 | -0.11557 | 0.24012 | 0.1163
133 | 0.99422 | -0.11562 | 0 | 0
134 | 0.99422 | -0.11561 | 0.12291 | 0.059529
135 | 0.99427 | -0.1153 | 0.17419 | 0.084365
136 | 0.99427 | -0.11533 | 0 | 0
137 | 0.99428 | -0.1154 | 0.0695 | 0.03366
138 | 0.99429 | -0.11549 | 0 | 0
139 | 0.99433 | -0.11592 | 0 | 0
140 | 0.99434 | -0.11599 | 0.40451 | 0.19591
141 | 0.99433 | -0.11587 | 0.10031 | 0.048585
142 | 0.99472 | -0.10557 | 0.38999 | 0.18888
143 | 0.99476 | -0.10523 | 0 | 0
144 | 0.99495 | -0.12432 | 0.28231 | 0.13673
145 | 0.99485 | -0.12981 | 0.28943 | 0.14018
146 | 0.99473 | -0.10498 | 0 | 0
147 | 0.99476 | -0.10515 | 0.23552 | 0.11407
148 | 0.99013 | -0.15932 | 0.22841 | 0.11062
149 | 0.99016 | -0.15958 | 0 | 0
150 | 0.98992 | -0.16077 | 0 | 0
151 | 0.99351 | -0.16361 | 0 | 0
152 | 0.99376 | -0.11093 | 0 | 0
153 | 0.99362 | -0.10958 | 0 | 0
154 | 0.99345 | -0.10802 | 0 | 0
155 | 0.99339 | -0.10751 | 0.32371 | 0.15678
156 | 0.99361 | -0.10955 | 0.09979 | 0.04833
157 | 0.99326 | -0.10838 | 0 | 0
158 | 0.9946 | -0.13091 | 0 | 0
159 | 0.99448 | -0.1173 | 0 | 0
160 | 0.99212 | -0.16812 | 0.32736 | 0.15855
161 | 0.99238 | -0.17041 | 0 | 0
162 | 0.99239 | -0.17052 | 0.2504 | 0.12127
163 | 0.99249 | -0.17142 | 0 | 0
164 | 0.99356 | -0.1641 | 0 | 0
165 | 0.99473 | -0.10494 | 0.10401 | 0.050372
166 | 0.99322 | -0.10805 | 0.070575 | 0.034181
167 | 0.99455 | -0.13364 | 0.40605 | 0.19666
168 | 0.99454 | -0.13369 | 0 | 0
169 | 0.99669 | -0.085649 | 0 | 0
170 | 0.99668 | -0.085543 | 0.35475 | 0.17181
171 | 0.99667 | -0.085526 | 0.071246 | 0.034506
172 | 0.99447 | -0.11716 | 0 | 0
173 | 0.99447 | -0.11722 | 0 | 0
174 | 0.99446 | -0.11711 | 0.13529 | 0.065524
175 | 0.99443 | -0.1168 | 0 | 0
176 | 0.99447 | -0.1172 | 0.09127 | 0.044204
177 | 0.99437 | -0.11631 | 0.097792 | 0.047363
178 | 0.99426 | -0.14693 | 0.091762 | 0.044442
179 | 0.99424 | -0.14723 | 0 | 0
180 | 0.99431 | -0.14676 | 0.11256 | 0.054513
181 | 0.99356 | -0.16403 | 0.27375 | 0.13258
182 | 0.995 | -0.12386 | 0.068205 | 0.033033
183 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 1.7184 | 0.77525 | -1.718 | -0.77718 | 0.00035606 | -0.0019343 | 0.055132 | 0.055157 | 0.055157 | 0.98707 | 0.011269 | 0.98688 | 0.012799 | 25.0714
1 | -2.0595 | -0.94044 | 2.0623 | 0.9418 | 0.0028517 | 0.0013609 | 0.066213 | 0.066207 | 0.066213 | 0.98707 | 0.011269 | 0.98853 | 0.022402 | 31.5298
2 | 1.718 | 0.77718 | -1.7174 | -0.78064 | 0.00063871 | -0.0034632 | 0.055157 | 0.055201 | 0.055201 | 0.98688 | 0.012799 | 0.98654 | 0.01557 | 25.0914
3 | -2.0623 | -0.9418 | 2.0625 | 0.94101 | 0.00021389 | -0.00078956 | 0.066207 | 0.066197 | 0.066207 | 0.98853 | 0.022402 | 0.98862 | 0.021616 | 30.0943
4 | 0.33738 | 0.16304 | -0.33731 | -0.16337 | 6.9209e-05 | -0.00033181 | 0.010965 | 0.010969 | 0.010969 | 0.98654 | 0.01557 | 0.98632 | 0.014212 | 5.2235
5 | 1.38 | 0.61761 | -1.3797 | -0.61753 | 0.00025387 | 7.445e-05 | 0.04424 | 0.044241 | 0.044241 | 0.98654 | 0.01557 | 0.98634 | 0.014 | 21.0673
6 | 1.1986 | 0.52978 | -1.1983 | -0.53333 | 0.00030768 | -0.0035433 | 0.038353 | 0.038396 | 0.038396 | 0.98634 | 0.014 | 0.9861 | 0.015806 | 17.4526
7 | 1.1983 | 0.53333 | -1.1975 | -0.5421 | 0.00076558 | -0.0087735 | 0.038396 | 0.038504 | 0.038504 | 0.9861 | 0.015806 | 0.98551 | 0.020446 | 17.5017
8 | -2.1713 | -0.9937 | 2.1717 | 0.99233 | 0.00041659 | -0.0013749 | 0.069726 | 0.069708 | 0.069726 | 0.98862 | 0.021616 | 0.9888 | 0.020156 | 31.6936
9 | 1.058 | 0.47485 | -1.057 | -0.49004 | 0.0010361 | -0.015189 | 0.03397 | 0.034158 | 0.034158 | 0.98551 | 0.020446 | 0.9846 | 0.027861 | 15.5265
10 | 0.13947 | 0.067246 | -0.13947 | -0.067548 | 3.5745e-07 | -0.00030149 | 0.0045354 | 0.0045392 | 0.0045392 | 0.98551 | 0.020446 | 0.98551 | 0.020468 | 2.0633
11 | 1.057 | 0.49004 | -1.0567 | -0.49392 | 0.00026649 | -0.0038744 | 0.034158 | 0.034207 | 0.034207 | 0.9846 | 0.027861 | 0.98437 | 0.029867 | 15.5487
12 | 0.91375 | 0.42467 | -0.91366 | -0.42653 | 9.4798e-05 | -0.0018517 | 0.029549 | 0.029573 | 0.029573 | 0.98437 | 0.029867 | 0.98427 | 0.030693 | 13.4421
13 | 0.15014 | 0.071874 | -0.15014 | -0.072715 | 1.1361e-06 | -0.00084073 | 0.0048572 | 0.0048678 | 0.0048678 | 0.9893 | 0.014271 | 0.98929 | 0.014336 | 2.2126
14 | -0.15014 | -0.071874 | 0.15016 | 0.071378 | 1.8231e-05 | -0.00049606 | 0.0048572 | 0.0048508 | 0.0048572 | 0.9893 | 0.014271 | 0.98942 | 0.015117 | 2.3129
15 | 2.1732 | 0.98753 | -2.1717 | -0.99233 | 0.0014507 | -0.0047983 | 0.069644 | 0.069708 | 0.069708 | 0.98942 | 0.015117 | 0.9888 | 0.020156 | 31.6853
16 | -3.3189 | -1.5205 | 3.3232 | 1.5151 | 0.0043092 | -0.0053855 | 0.10651 | 0.10643 | 0.10651 | 0.98942 | 0.015117 | 0.99063 | 0.0052528 | 48.4138
17 | 0.99555 | 0.46158 | -0.99545 | -0.46314 | 9.2812e-05 | -0.0015567 | 0.032016 | 0.032036 | 0.032036 | 0.98942 | 0.015117 | 0.98934 | 0.015854 | 14.5617
18 | 0.28759 | 0.12296 | -0.28754 | -0.13386 | 5.2805e-05 | -0.010895 | 0.009133 | 0.0092629 | 0.0092629 | 0.98861 | 0.010329 | 0.98844 | 0.011644 | 4.2104
19 | 0.41631 | 0.19953 | -0.41629 | -0.19959 | 2.0355e-05 | -6.0592e-05 | 0.01348 | 0.013481 | 0.013481 | 0.98861 | 0.010329 | 0.98856 | 0.0099941 | 6.4197
20 | -0.7039 | -0.32249 | 0.70439 | 0.32217 | 0.00048712 | -0.00031964 | 0.022608 | 0.022601 | 0.022608 | 0.98861 | 0.010329 | 0.98934 | 0.015854 | 10.7659
21 | 0.28754 | 0.13386 | -0.28751 | -0.13866 | 2.379e-05 | -0.0048063 | 0.0092629 | 0.0093231 | 0.0093231 | 0.98844 | 0.011644 | 0.98836 | 0.01233 | 4.2378
22 | 0.16968 | 0.080148 | -0.16966 | -0.080586 | 2.068e-05 | -0.00043745 | 0.0054799 | 0.0054855 | 0.0054855 | 0.98856 | 0.0099941 | 0.98843 | 0.0091232 | 2.6121
23 | 0.080036 | 0.038341 | -0.080036 | -0.038763 | 1.6268e-07 | -0.00042214 | 0.002592 | 0.0025974 | 0.0025974 | 0.98836 | 0.01233 | 0.98836 | 0.012348 | 1.1806
24 | 0.20748 | 0.10032 | -0.20747 | -0.10048 | 1.1487e-05 | -0.00015869 | 0.0067311 | 0.0067332 | 0.0067332 | 0.98836 | 0.01233 | 0.9883 | 0.011964 | 3.2063
25 | 0.91366 | 0.42653 | -0.91307 | -0.43802 | 0.00059252 | -0.011499 | 0.029573 | 0.029719 | 0.029719 | 0.98427 | 0.030693 | 0.98368 | 0.036058 | 13.5087
26 | -3.3232 | -1.5151 | 3.3237 | 1.5145 | 0.00047122 | -0.00059052 | 0.10643 | 0.10642 | 0.10643 | 0.99063 | 0.0052528 | 0.99076 | 0.0041822 | 48.3771
27 | -3.6375 | -1.6665 | 3.6375 | 1.6665 | 4.3489e-05 | -4.3279e-05 | 0.11658 | 0.11658 | 0.11658 | 0.99076 | 0.0041822 | 0.99077 | 0.0040908 | 52.99
28 | 0.16966 | 0.080586 | -0.16966 | -0.082168 | 2.7366e-06 | -0.0015825 | 0.0054855 | 0.0055055 | 0.0055055 | 0.98843 | 0.0091232 | 0.98842 | 0.0092607 | 2.5025
29 | -3.8485 | -1.7617 | 3.876 | 1.7378 | 0.027522 | -0.023922 | 0.12332 | 0.12294 | 0.12332 | 0.99077 | 0.0040908 | 0.99744 | -0.048903 | 56.0549
30 | 0.21094 | 0.095246 | -0.21093 | -0.09961 | 1.1403e-05 | -0.0043643 | 0.0067434 | 0.0067968 | 0.0067968 | 0.99077 | 0.0040908 | 0.99072 | 0.0045126 | 3.0895
31 | -0.21092 | -0.10215 | 0.21093 | 0.09961 | 6.7281e-06 | -0.0025426 | 0.0068288 | 0.0067968 | 0.0068288 | 0.99069 | 0.0047828 | 0.99072 | 0.0045126 | 3.104
32 | 0.35442 | 0.15733 | -0.35432 | -0.17126 | 0.00010033 | -0.013932 | 0.011223 | 0.011393 | 0.011393 | 0.99744 | -0.048903 | 0.99718 | -0.046674 | 5.1785
33 | -4.5046 | -2.0229 | 4.5053 | 2.021 | 0.00069288 | -0.0018946 | 0.14291 | 0.14288 | 0.14291 | 0.99744 | -0.048903 | 0.99761 | -0.046865 | 39.4786
34 | 0.27417 | 0.12779 | -0.27415 | -0.13262 | 2.097e-05 | -0.0048289 | 0.0087546 | 0.0088147 | 0.0088147 | 0.99744 | -0.048903 | 0.99737 | -0.048266 | 4.0067
35 | 0.35432 | 0.17126 | -0.35432 | -0.1716 | 2.5176e-06 | -0.00034407 | 0.011393 | 0.011397 | 0.011397 | 0.99718 | -0.046674 | 0.99717 | -0.046612 | 5.1805
36 | -4.7595 | -2.1442 | 4.7612 | 2.1459 | 0.0016525 | 0.0017915 | 0.15106 | 0.15105 | 0.15106 | 0.99761 | -0.046865 | 0.99805 | -0.035405 | 43.1587
37 | 0.27415 | 0.13262 | -0.27415 | -0.13278 | 6.7096e-07 | -0.0001534 | 0.0088147 | 0.0088166 | 0.0088166 | 0.99737 | -0.048266 | 0.99737 | -0.048245 | 4.0075
38 | -4.7612 | -2.1459 | 4.7631 | 2.0793 | 0.0018974 | -0.066688 | 0.15105 | 0.15026 | 0.15105 | 0.99805 | -0.035405 | 0.99846 | -0.033126 | 11.8381
39 | -4.7631 | -2.0793 | 4.7632 | 2.0764 | 8.0398e-05 | -0.0028428 | 0.15026 | 0.15023 | 0.15026 | 0.99846 | -0.033126 | 0.99848 | -0.033023 | 11.7758
40 | -5.0829 | -2.2313 | 5.083 | 2.2316 | 0.00014479 | 0.00030254 | 0.16049 | 0.16049 | 0.16049 | 0.99848 | -0.033023 | 0.99853 | -0.029944 | 12.441
41 | 0.3087 | 0.13759 | -0.30864 | -0.14938 | 6.419e-05 | -0.011797 | 0.0097708 | 0.0099148 | 0.0099148 | 0.99853 | -0.029944 | 0.99834 | -0.028296 | 4.5067
42 | -5.3917 | -2.3692 | 5.3941 | 2.3043 | 0.0023526 | -0.064818 | 0.17026 | 0.1695 | 0.17026 | 0.99853 | -0.029944 | 0.99899 | -0.027212 | 13.3432
43 | 0.30864 | 0.14938 | -0.30862 | -0.14947 | 1.435e-05 | -8.8478e-05 | 0.0099148 | 0.009916 | 0.009916 | 0.99834 | -0.028296 | 0.99829 | -0.028602 | 4.7219
44 | -5.3941 | -2.3043 | 5.3946 | 2.291 | 0.00048055 | -0.01332 | 0.1695 | 0.16935 | 0.1695 | 0.99899 | -0.027212 | 0.99908 | -0.02662 | 13.2836
45 | -5.5875 | -2.3845 | 5.5879 | 2.3741 | 0.00040084 | -0.010344 | 0.17553 | 0.17541 | 0.17553 | 0.99908 | -0.02662 | 0.99916 | -0.026142 | 13.7565
46 | -5.5879 | -2.3741 | 5.5903 | 2.3129 | 0.002358 | -0.061175 | 0.17541 | 0.17471 | 0.17541 | 0.99916 | -0.026142 | 0.9996 | -0.023186 | 13.7471
47 | 16.2065 | 7.5195 | -16.1891 | -7.5627 | 0.017403 | -0.043205 | 0.51595 | 0.5166 | 0.5166 | 0.9996 | -0.023186 | 0.99849 | -0.028121 | 40.4858
48 | -21.7968 | -9.8324 | 21.8015 | 9.845 | 0.0047451 | 0.012606 | 0.69055 | 0.69055 | 0.69055 | 0.9996 | -0.023186 | 1 | 0 | 53.5311
49 | -0.075857 | -0.035547 | 0.075857 | 0.034364 | 3.9555e-07 | -0.0011837 | 0.002435 | 0.0024206 | 0.002435 | 0.99313 | -0.10798 | 0.99314 | -0.10803 | 1.1068
50 | 0.075857 | 0.035547 | -0.075857 | -0.036739 | 4.0303e-07 | -0.0011917 | 0.002435 | 0.0024499 | 0.0024499 | 0.99313 | -0.10798 | 0.99313 | -0.10794 | 1.1136
51 | -0.25966 | -0.12338 | 0.25967 | 0.12328 | 1.126e-05 | -9.9541e-05 | 0.0083561 | 0.0083548 | 0.0083561 | 0.99314 | -0.10803 | 0.99319 | -0.10772 | 3.9791
52 | 15.9298 | 7.4375 | -15.9258 | -7.4477 | 0.0039489 | -0.010164 | 0.50827 | 0.50843 | 0.50843 | 0.99849 | -0.028121 | 0.99823 | -0.029238 | 39.8453
53 | 0.25929 | 0.12517 | -0.25929 | -0.12558 | 1.6131e-06 | -0.00041435 | 0.0083242 | 0.0083295 | 0.0083295 | 0.99849 | -0.028121 | 0.99848 | -0.028067 | 3.7861
54 | 1.6624 | 0.80195 | -1.6621 | -0.80405 | 0.00035332 | -0.0021037 | 0.053377 | 0.053405 | 0.053405 | 0.99823 | -0.029238 | 0.99803 | -0.027397 | 24.2749
55 | 14.2634 | 6.6457 | -14.2611 | -6.6534 | 0.0022921 | -0.007677 | 0.45505 | 0.45516 | 0.45516 | 0.99823 | -0.029238 | 0.99806 | -0.029971 | 35.6711
56 | -0.67365 | -0.32379 | 0.67368 | 0.32282 | 2.5978e-05 | -0.00096395 | 0.021724 | 0.021712 | 0.021724 | 0.99319 | -0.10772 | 0.99322 | -0.10805 | 9.8747
57 | 1.6621 | 0.80405 | -1.6619 | -0.80492 | 0.00014558 | -0.00086589 | 0.053405 | 0.053416 | 0.053416 | 0.99803 | -0.027397 | 0.99795 | -0.026635 | 24.2801
58 | 13.9144 | 6.4855 | -13.9111 | -6.477 | 0.0032284 | 0.0084289 | 0.44402 | 0.44402 | 0.44402 | 0.99806 | -0.029971 | 0.99763 | -0.054258 | 34.4205
59 | -0.25249 | -0.12229 | 0.2525 | 0.12031 | 7.7568e-06 | -0.0019772 | 0.0082403 | 0.0082151 | 0.0082403 | 0.9828 | 0.030713 | 0.98283 | 0.03045 | 3.7456
60 | 0.40681 | 0.19567 | -0.40666 | -0.1961 | 0.00014319 | -0.00043702 | 0.013259 | 0.013266 | 0.013266 | 0.98283 | 0.03045 | 0.98247 | 0.02808 | 6.317
61 | -0.6593 | -0.31598 | 0.65984 | 0.31556 | 0.0005375 | -0.00041873 | 0.021474 | 0.021464 | 0.021474 | 0.98283 | 0.03045 | 0.98368 | 0.036058 | 10.2257
62 | 0.40666 | 0.1961 | -0.40665 | -0.19695 | 8.6762e-06 | -0.00084784 | 0.013266 | 0.013276 | 0.013276 | 0.98247 | 0.02808 | 0.98245 | 0.028265 | 6.0348
63 | 0.25322 | 0.12247 | -0.25321 | -0.12263 | 1.8654e-05 | -0.00016575 | 0.0082547 | 0.008257 | 0.008257 | 0.98368 | 0.036058 | 0.9836 | 0.035571 | 3.9319
64 | 0.62902 | 0.29412 | -0.62891 | -0.29865 | 0.00010793 | -0.0045332 | 0.020287 | 0.020344 | 0.020344 | 0.98806 | -0.16899 | 0.9879 | -0.16758 | 9.2473
65 | 0.26587 | 0.12867 | -0.26586 | -0.12876 | 1.1674e-05 | -9.5211e-05 | 0.0086296 | 0.0086309 | 0.0086309 | 0.98806 | -0.16899 | 0.98802 | -0.16928 | 4.11
66 | -0.89489 | -0.42279 | 0.89527 | 0.42273 | 0.00038382 | -6.003e-05 | 0.028916 | 0.028913 | 0.028916 | 0.98806 | -0.16899 | 0.98851 | -0.16589 | 13.7697
67 | 0.31771 | 0.1481 | -0.31768 | -0.15289 | 2.8994e-05 | -0.0047866 | 0.010243 | 0.010303 | 0.010303 | 0.9879 | -0.16758 | 0.98782 | -0.16683 | 4.6832
68 | 0.3112 | 0.15055 | -0.3112 | -0.15072 | 1.0054e-06 | -0.00017165 | 0.010102 | 0.010104 | 0.010104 | 0.9879 | -0.16758 | 0.9879 | -0.16755 | 4.5927
69 | 0.40381 | 0.18671 | -0.40372 | -0.19551 | 8.5991e-05 | -0.0088015 | 0.012992 | 0.013102 | 0.013102 | 0.98851 | -0.16589 | 0.98832 | -0.16413 | 5.9556
70 | -1.2991 | -0.60944 | 1.2995 | 0.60955 | 0.00042013 | 0.00010645 | 0.041904 | 0.041902 | 0.041904 | 0.98851 | -0.16589 | 0.98885 | -0.1635 | 19.9544
71 | 0.31768 | 0.15289 | -0.31768 | -0.15386 | 5.9012e-06 | -0.00096727 | 0.010303 | 0.010315 | 0.010315 | 0.98782 | -0.16683 | 0.9878 | -0.16667 | 4.6887
72 | 0.40372 | 0.19551 | -0.40372 | -0.19553 | 4.5555e-06 | -1.4514e-05 | 0.013102 | 0.013103 | 0.013103 | 0.98832 | -0.16413 | 0.9883 | -0.16421 | 6.2393
73 | 0.13215 | 0.063455 | -0.13214 | -0.064001 | 5.7227e-07 | -0.00054543 | 0.0042794 | 0.0042864 | 0.0042864 | 0.98885 | -0.1635 | 0.98885 | -0.16347 | 1.9483
74 | -1.7411 | -0.82287 | 1.7424 | 0.82341 | 0.0012904 | 0.00054054 | 0.056218 | 0.056215 | 0.056218 | 0.98885 | -0.1635 | 0.98963 | -0.15817 | 26.7706
75 | -0.30265 | -0.14658 | 0.30266 | 0.1465 | 1.2861e-05 | -8.0094e-05 | 0.0097973 | 0.0097962 | 0.0097973 | 0.99082 | -0.16614 | 0.99087 | -0.16586 | 4.6654
76 | -0.30266 | -0.1465 | 0.30267 | 0.14392 | 1.4082e-05 | -0.0025813 | 0.0097962 | 0.0097636 | 0.0097962 | 0.99087 | -0.16586 | 0.99091 | -0.16626 | 4.4528
77 | -2.7283 | -1.2881 | 2.7295 | 1.2858 | 0.0011812 | -0.0023368 | 0.087895 | 0.087862 | 0.087895 | 0.99091 | -0.16626 | 0.99131 | -0.16981 | 39.9523
78 | 2.4256 | 1.1442 | -2.4251 | -1.1455 | 0.00050631 | -0.0013057 | 0.078131 | 0.07815 | 0.07815 | 0.99091 | -0.16626 | 0.99072 | -0.16454 | 35.5225
79 | 0.40257 | 0.19434 | -0.40257 | -0.19497 | 6.1515e-06 | -0.00063577 | 0.013018 | 0.013026 | 0.013026 | 0.99131 | -0.16981 | 0.9913 | -0.16967 | 5.9207
80 | -3.132 | -1.4801 | 3.1329 | 1.4789 | 0.00083033 | -0.0011883 | 0.10088 | 0.10086 | 0.10088 | 0.99131 | -0.16981 | 0.99156 | -0.17199 | 45.8539
81 | 2.0494 | 0.96353 | -2.0492 | -0.96421 | 0.00018199 | -0.00067958 | 0.065985 | 0.065994 | 0.065994 | 0.99072 | -0.16454 | 0.99064 | -0.16382 | 29.9974
82 | -3.1329 | -1.4789 | 3.1346 | 1.4799 | 0.001678 | 0.00094232 | 0.10086 | 0.10086 | 0.10086 | 0.99156 | -0.17199 | 0.99212 | -0.16812 | 48.029
83 | 2.0492 | 0.96421 | -2.0481 | -0.96816 | 0.0010583 | -0.0039456 | 0.065994 | 0.066047 | 0.066047 | 0.99064 | -0.16382 | 0.99016 | -0.15958 | 30.0215
84 | 13.9111 | 6.477 | -13.9072 | -6.4908 | 0.003883 | -0.013745 | 0.44402 | 0.44422 | 0.44422 | 0.99763 | -0.054258 | 0.99735 | -0.055532 | 34.8134
85 | 13.9072 | 6.4908 | -13.906 | -6.4953 | 0.0012856 | -0.0045457 | 0.44422 | 0.44428 | 0.44428 | 0.99735 | -0.055532 | 0.99725 | -0.055951 | 34.8185
86 | 13.8003 | 6.4442 | -13.7964 | -6.4338 | 0.0039592 | 0.010333 | 0.44089 | 0.44089 | 0.44089 | 0.99725 | -0.055951 | 0.99672 | -0.085954 | 34.1776
87 | 0.42602 | 0.20392 | -0.42601 | -0.2041 | 1.9091e-06 | -0.00018068 | 0.013679 | 0.013681 | 0.013681 | 0.99672 | -0.085954 | 0.99672 | -0.085916 | 6.2188
88 | 12.4493 | 5.7857 | -12.447 | -5.7796 | 0.0023439 | 0.006075 | 0.3976 | 0.3976 | 0.3976 | 0.99672 | -0.085954 | 0.99637 | -0.10569 | 30.8218
89 | 0.59117 | 0.28445 | -0.59105 | -0.28461 | 0.00012702 | -0.00015454 | 0.019001 | 0.019004 | 0.019004 | 0.99672 | -0.085954 | 0.99649 | -0.087403 | 9.0494
90 | 0.42601 | 0.2041 | -0.426 | -0.20535 | 1.3274e-05 | -0.0012546 | 0.013681 | 0.013697 | 0.013697 | 0.99672 | -0.085916 | 0.99669 | -0.085649 | 6.226
91 | 0.1968 | 0.093524 | -0.1968 | -0.094707 | 2.6646e-06 | -0.0011836 | 0.0063129 | 0.0063277 | 0.0063277 | 0.99637 | -0.10569 | 0.99636 | -0.10558 | 2.8762
92 | 12.2502 | 5.6861 | -12.2443 | -5.7136 | 0.0058393 | -0.027463 | 0.39129 | 0.39167 | 0.39167 | 0.99637 | -0.10569 | 0.99588 | -0.10789 | 30.6948
93 | 0.19461 | 0.092605 | -0.19461 | -0.092818 | 4.6684e-07 | -0.00021246 | 0.0062434 | 0.0062461 | 0.0062461 | 0.99649 | -0.087403 | 0.99649 | -0.087383 | 2.8391
94 | -1.8187 | -0.86038 | 1.819 | 0.85924 | 0.00023742 | -0.0011374 | 0.058689 | 0.058674 | 0.058689 | 0.98963 | -0.15817 | 0.98975 | -0.15925 | 26.6769
95 | -1.819 | -0.85924 | 1.8193 | 0.85762 | 0.00033846 | -0.001623 | 0.058674 | 0.058653 | 0.058674 | 0.98975 | -0.15925 | 0.98992 | -0.16077 | 26.67
96 | 0.11263 | 0.054376 | -0.11263 | -0.054551 | 1.3105e-07 | -0.00017492 | 0.0036347 | 0.0036369 | 0.0036369 | 0.99335 | -0.16424 | 0.99335 | -0.16423 | 1.6531
97 | -0.11263 | -0.054376 | 0.11265 | 0.05368 | 1.404e-05 | -0.00069568 | 0.0036347 | 0.0036258 | 0.0036347 | 0.99335 | -0.16424 | 0.99348 | -0.16339 | 1.7308
98 | -0.26544 | -0.12768 | 0.26545 | 0.12597 | 7.118e-06 | -0.0017175 | 0.0085589 | 0.0085373 | 0.0085589 | 0.99348 | -0.16339 | 0.99351 | -0.16361 | 3.8904
99 | 10.2586 | 4.7976 | -10.2585 | -4.7988 | 0.00016017 | -0.0011058 | 0.32848 | 0.32849 | 0.32849 | 0.99529 | -0.12335 | 0.99527 | -0.12342 | 25.7437
100 | -10.6159 | -4.9707 | 10.6164 | 4.9673 | 0.00052598 | -0.0033707 | 0.33999 | 0.33994 | 0.33999 | 0.99529 | -0.12335 | 0.99534 | -0.12313 | 26.6447
101 | 10.1773 | 4.7594 | -10.1766 | -4.7643 | 0.00069176 | -0.0048574 | 0.32587 | 0.32594 | 0.32594 | 0.99527 | -0.12342 | 0.9952 | -0.12372 | 25.5438
102 | 0.22783 | 0.10857 | -0.22782 | -0.11007 | 4.5473e-06 | -0.0014987 | 0.0073194 | 0.0073383 | 0.0073383 | 0.99534 | -0.12313 | 0.99532 | -0.12296 | 3.3356
103 | -10.8442 | -5.0759 | 10.8457 | 5.0796 | 0.0014486 | 0.0037111 | 0.34726 | 0.34726 | 0.34726 | 0.99534 | -0.12313 | 0.99558 | -0.10918 | 26.9194
104 | 7.1467 | 3.3327 | -7.1458 | -3.347 | 0.00096168 | -0.014252 | 0.22874 | 0.22892 | 0.22892 | 0.9952 | -0.12372 | 0.99506 | -0.12433 | 17.9403
105 | 3.0299 | 1.4316 | -3.0278 | -1.4349 | 0.0021133 | -0.0033305 | 0.097204 | 0.097253 | 0.097253 | 0.9952 | -0.12372 | 0.99455 | -0.11795 | 44.2058
106 | 0.22782 | 0.11007 | -0.22782 | -0.11034 | 8.3115e-07 | -0.00027309 | 0.0073383 | 0.0073417 | 0.0073417 | 0.99532 | -0.12296 | 0.99532 | -0.12292 | 3.3371
107 | -10.8457 | -5.0796 | 10.8488 | 5.0604 | 0.0031262 | -0.019161 | 0.34726 | 0.347 | 0.34726 | 0.99558 | -0.10918 | 0.99588 | -0.10789 | 27.2146
108 | 0.073374 | 0.035141 | -0.073374 | -0.035536 | 1.2432e-07 | -0.00039568 | 0.0023582 | 0.0023632 | 0.0023632 | 0.99588 | -0.10789 | 0.99588 | -0.10787 | 1.0742
109 | 1.3222 | 0.61802 | -1.3216 | -0.61787 | 0.00055896 | 0.00014268 | 0.042306 | 0.042308 | 0.042308 | 0.99588 | -0.10789 | 0.99543 | -0.11105 | 20.1468
110 | 1.072 | 0.497 | -1.072 | -0.49739 | 2.6874e-05 | -0.00039755 | 0.034267 | 0.034272 | 0.034272 | 0.99543 | -0.11105 | 0.99541 | -0.11085 | 15.5783
111 | 0.1968 | 0.094707 | -0.1968 | -0.095313 | 1.3679e-06 | -0.00060542 | 0.0063277 | 0.0063353 | 0.0063353 | 0.99636 | -0.10558 | 0.99635 | -0.10552 | 2.8797
112 | 0.8564 | 0.41267 | -0.85637 | -0.41328 | 2.6449e-05 | -0.00060777 | 0.027579 | 0.027587 | 0.027587 | 0.99506 | -0.12433 | 0.99503 | -0.12406 | 12.5393
113 | 0.40326 | 0.19528 | -0.40326 | -0.19531 | 6.6332e-06 | -2.1889e-05 | 0.012999 | 0.012999 | 0.012999 | 0.99506 | -0.12433 | 0.99504 | -0.12444 | 6.1899
114 | 5.8861 | 2.739 | -5.8857 | -2.748 | 0.00040707 | -0.0090061 | 0.18834 | 0.18846 | 0.18846 | 0.99506 | -0.12433 | 0.99499 | -0.12464 | 14.7694
115 | 1.5495 | 0.74065 | -1.5495 | -0.74082 | 2.5545e-05 | -0.00017427 | 0.049849 | 0.049851 | 0.049851 | 0.99455 | -0.11795 | 0.99454 | -0.11781 | 22.6596
116 | 1.4783 | 0.69427 | -1.4772 | -0.70269 | 0.001115 | -0.0084206 | 0.047404 | 0.047513 | 0.047513 | 0.99455 | -0.11795 | 0.99385 | -0.11173 | 21.5969
117 | -0.070134 | -0.033968 | 0.070135 | 0.033888 | 6.1204e-07 | -7.9074e-05 | 0.0022609 | 0.0022599 | 0.0022609 | 0.99498 | -0.1237 | 0.99499 | -0.12364 | 1.0766
118 | -0.45471 | -0.22015 | 0.45473 | 0.21931 | 1.0156e-05 | -0.00083459 | 0.014657 | 0.014647 | 0.014657 | 0.99499 | -0.12364 | 0.99501 | -0.12383 | 6.6625
119 | 0.068206 | 0.032993 | -0.068205 | -0.033033 | 2.9254e-07 | -3.9968e-05 | 0.0021982 | 0.0021987 | 0.0021987 | 0.99501 | -0.12383 | 0.995 | -0.12386 | 1.047
120 | -0.85635 | -0.41379 | 0.85637 | 0.41328 | 2.2428e-05 | -0.00051506 | 0.027593 | 0.027587 | 0.027593 | 0.99501 | -0.12383 | 0.99503 | -0.12406 | 12.5423
121 | 1.072 | 0.49739 | -1.0716 | -0.50321 | 0.00039384 | -0.0058104 | 0.034272 | 0.034345 | 0.034345 | 0.99541 | -0.11085 | 0.99507 | -0.10791 | 15.6114
122 | 0.19461 | 0.092818 | -0.19461 | -0.094253 | 3.1634e-06 | -0.0014349 | 0.0062461 | 0.0062641 | 0.0062641 | 0.99649 | -0.087383 | 0.99648 | -0.087244 | 2.8473
123 | 5.6034 | 2.6136 | -5.6031 | -2.613 | 0.00026555 | 0.00058756 | 0.17938 | 0.17939 | 0.17939 | 0.99499 | -0.12464 | 0.9949 | -0.1296 | 13.9059
124 | 0.28232 | 0.13447 | -0.28231 | -0.13646 | 9.3325e-06 | -0.0019991 | 0.0090726 | 0.0090977 | 0.0090977 | 0.99499 | -0.12464 | 0.99496 | -0.12436 | 4.1353
125 | 0.1579 | 0.076426 | -0.1579 | -0.076474 | 1.906e-06 | -4.7569e-05 | 0.0050906 | 0.0050912 | 0.0050912 | 0.99479 | -0.13015 | 0.99478 | -0.13023 | 2.4244
126 | -0.1579 | -0.076426 | 0.1579 | 0.07634 | 3.4545e-06 | -8.6248e-05 | 0.0050906 | 0.0050895 | 0.0050906 | 0.99479 | -0.13015 | 0.99481 | -0.13 | 2.4241
127 | 4.8714 | 2.272 | -4.8704 | -2.3047 | 0.001008 | -0.032689 | 0.15598 | 0.15639 | 0.15639 | 0.99481 | -0.13 | 0.9946 | -0.13091 | 12.2562
128 | -5.0293 | -2.3484 | 5.0295 | 2.342 | 0.00020895 | -0.0063691 | 0.16107 | 0.16099 | 0.16107 | 0.99481 | -0.13 | 0.99485 | -0.12981 | 12.6228
129 | 5.3192 | 2.4755 | -5.319 | -2.4822 | 0.00024633 | -0.0067008 | 0.17023 | 0.17032 | 0.17032 | 0.9949 | -0.1296 | 0.99485 | -0.12981 | 13.3478
130 | 0.28231 | 0.13646 | -0.28231 | -0.13673 | 1.2455e-06 | -0.00026596 | 0.0090977 | 0.0091011 | 0.0091011 | 0.99496 | -0.12436 | 0.99495 | -0.12432 | 4.1369
131 | 1.4772 | 0.70269 | -1.4771 | -0.7035 | 0.00010675 | -0.00080343 | 0.047513 | 0.047524 | 0.047524 | 0.99385 | -0.11173 | 0.99379 | -0.11113 | 21.6016
132 | 1.1684 | 0.55399 | -1.1683 | -0.55433 | 2.7699e-05 | -0.00033853 | 0.03756 | 0.037565 | 0.037565 | 0.99379 | -0.11113 | 0.99376 | -0.11093 | 17.0748
133 | 1.4362 | 0.68598 | -1.4362 | -0.68669 | 8.8001e-05 | -0.00070307 | 0.046199 | 0.046208 | 0.046208 | 0.99454 | -0.11781 | 0.99448 | -0.1173 | 21.0039
134 | 0.80426 | 0.37505 | -0.80416 | -0.37788 | 0.00010708 | -0.002825 | 0.025744 | 0.02578 | 0.02578 | 0.99507 | -0.10791 | 0.99495 | -0.10683 | 11.718
135 | 0.26735 | 0.12815 | -0.26734 | -0.12948 | 5.5556e-06 | -0.0013257 | 0.008601 | 0.0086177 | 0.0086177 | 0.99507 | -0.10791 | 0.99505 | -0.10773 | 3.9171
136 | 0.80416 | 0.37788 | -0.80405 | -0.38071 | 0.00010787 | -0.0028373 | 0.02578 | 0.025815 | 0.025815 | 0.99495 | -0.10683 | 0.99482 | -0.10573 | 11.7341
137 | 0.80405 | 0.38071 | -0.80403 | -0.38112 | 1.5406e-05 | -0.00040453 | 0.025815 | 0.02582 | 0.02582 | 0.99482 | -0.10573 | 0.9948 | -0.10558 | 11.7364
138 | 0.72956 | 0.34505 | -0.72953 | -0.34593 | 2.7454e-05 | -0.00087741 | 0.023419 | 0.02343 | 0.02343 | 0.9948 | -0.10558 | 0.99477 | -0.10526 | 10.65
139 | 0.33953 | 0.15711 | -0.33953 | -0.15734 | 1.4858e-06 | -0.0002226 | 0.010857 | 0.010859 | 0.010859 | 0.99477 | -0.10526 | 0.99476 | -0.10523 | 4.9361
140 | 0.39 | 0.18881 | -0.38999 | -0.18888 | 1.8297e-05 | -6.5259e-05 | 0.012574 | 0.012575 | 0.012575 | 0.99477 | -0.10526 | 0.99472 | -0.10557 | 5.9882
141 | -0.24012 | -0.1163 | 0.24012 | 0.11595 | 1.1843e-06 | -0.00034873 | 0.0077467 | 0.0077423 | 0.0077467 | 0.99421 | -0.11557 | 0.99422 | -0.11562 | 3.5212
142 | 0.12291 | 0.059454 | -0.12291 | -0.059529 | 6.7003e-08 | -7.5339e-05 | 0.0039644 | 0.0039653 | 0.0039653 | 0.99422 | -0.11562 | 0.99422 | -0.11561 | 1.8024
143 | -0.36303 | -0.1754 | 0.36305 | 0.17533 | 1.7106e-05 | -7.1965e-05 | 0.011707 | 0.011706 | 0.011707 | 0.99422 | -0.11562 | 0.99427 | -0.1153 | 5.5746
144 | -0.53724 | -0.25969 | 0.53724 | 0.2596 | 1.6548e-06 | -9.6986e-05 | 0.017325 | 0.017324 | 0.017325 | 0.99427 | -0.1153 | 0.99427 | -0.11533 | 7.875
145 | -0.53724 | -0.2596 | 0.53725 | 0.25935 | 4.2729e-06 | -0.0002505 | 0.017324 | 0.017321 | 0.017324 | 0.99427 | -0.11533 | 0.99428 | -0.1154 | 7.8745
146 | -0.60675 | -0.29301 | 0.60675 | 0.29272 | 6.2593e-06 | -0.00028738 | 0.019563 | 0.019559 | 0.019563 | 0.99428 | -0.1154 | 0.99429 | -0.11549 | 8.8921
147 | -0.60675 | -0.29272 | 0.60678 | 0.29133 | 3.0289e-05 | -0.0013923 | 0.019559 | 0.019541 | 0.019559 | 0.99429 | -0.11549 | 0.99433 | -0.11592 | 8.8905
148 | -0.7071 | -0.33902 | 0.70711 | 0.33882 | 6.0737e-06 | -0.00020544 | 0.022766 | 0.022764 | 0.022766 | 0.99433 | -0.11592 | 0.99434 | -0.11599 | 10.3482
149 | 0.10032 | 0.047695 | -0.10031 | -0.048585 | 5.2499e-07 | -0.00088946 | 0.0032248 | 0.003236 | 0.003236 | 0.99433 | -0.11592 | 0.99433 | -0.11587 | 1.4709
150 | -1.1116 | -0.53473 | 1.1117 | 0.53417 | 4.1363e-05 | -0.00055817 | 0.035812 | 0.035805 | 0.035812 | 0.99434 | -0.11599 | 0.99437 | -0.11631 | 16.2781
151 | 0.10401 | 0.043943 | -0.10401 | -0.049597 | 3.4997e-06 | -0.005654 | 0.0032766 | 0.0033439 | 0.0033439 | 0.99476 | -0.10523 | 0.99473 | -0.10498 | 1.52
152 | 0.23552 | 0.11339 | -0.23552 | -0.11407 | 2.192e-06 | -0.0006728 | 0.0075855 | 0.007594 | 0.007594 | 0.99476 | -0.10523 | 0.99476 | -0.10515 | 3.4518
153 | 0.10401 | 0.049597 | -0.10401 | -0.050372 | 4.9161e-07 | -0.00077563 | 0.0033439 | 0.0033537 | 0.0033537 | 0.99473 | -0.10498 | 0.99473 | -0.10494 | 1.5244
154 | -2.0481 | -0.9684 | 2.0481 | 0.96816 | 6.5851e-05 | -0.00024514 | 0.066051 | 0.066047 | 0.066051 | 0.99013 | -0.15932 | 0.99016 | -0.15958 | 30.023
155 | 1.8197 | 0.85778 | -1.8193 | -0.85762 | 0.00036514 | 0.00015901 | 0.058652 | 0.058653 | 0.058653 | 0.99013 | -0.15932 | 0.98992 | -0.16077 | 27.9298
156 | -0.26545 | -0.12597 | 0.26547 | 0.12207 | 1.6027e-05 | -0.0038994 | 0.0085373 | 0.0084893 | 0.0085373 | 0.99351 | -0.16361 | 0.99356 | -0.1641 | 3.8806
157 | 1.1683 | 0.55433 | -1.1681 | -0.55662 | 0.00018812 | -0.0022967 | 0.037565 | 0.037594 | 0.037594 | 0.99376 | -0.11093 | 0.99362 | -0.10958 | 17.0882
158 | 0.09979 | 0.047599 | -0.09979 | -0.04833 | 4.2864e-07 | -0.00073132 | 0.0032121 | 0.0032213 | 0.0032213 | 0.99362 | -0.10958 | 0.99361 | -0.10955 | 1.4642
159 | 1.0684 | 0.50902 | -1.0682 | -0.51191 | 0.0001973 | -0.0028849 | 0.034382 | 0.034419 | 0.034419 | 0.99362 | -0.10958 | 0.99345 | -0.10802 | 15.6449
160 | 1.0682 | 0.51191 | -1.0681 | -0.51285 | 6.4649e-05 | -0.00094369 | 0.034419 | 0.034431 | 0.034431 | 0.99345 | -0.10802 | 0.99339 | -0.10751 | 15.6504
161 | 0.74438 | 0.35607 | -0.74428 | -0.35612 | 9.4116e-05 | -4.9258e-05 | 0.023979 | 0.02398 | 0.02398 | 0.99339 | -0.10751 | 0.99326 | -0.10838 | 11.4191
162 | 0.74428 | 0.35612 | -0.74426 | -0.357 | 2.8984e-05 | -0.00088028 | 0.02398 | 0.023991 | 0.023991 | 0.99326 | -0.10838 | 0.99322 | -0.10805 | 10.9051
163 | 4.8704 | 2.3047 | -4.8703 | -2.3044 | 0.00012846 | 0.00026498 | 0.15639 | 0.15639 | 0.15639 | 0.9946 | -0.13091 | 0.99455 | -0.13364 | 12.1232
164 | 1.3449 | 0.64472 | -1.3449 | -0.64491 | 2.0754e-05 | -0.00018969 | 0.043293 | 0.043295 | 0.043295 | 0.99448 | -0.1173 | 0.99447 | -0.11716 | 19.6797
165 | 0.091271 | 0.041968 | -0.09127 | -0.043808 | 8.912e-07 | -0.0018393 | 0.0029161 | 0.0029388 | 0.0029388 | 0.99448 | -0.1173 | 0.99447 | -0.11722 | 1.3358
166 | -3.4619 | -1.6384 | 3.4629 | 1.6374 | 0.00096006 | -0.0010766 | 0.11144 | 0.11143 | 0.11144 | 0.99212 | -0.16812 | 0.99238 | -0.17041 | 50.6557
167 | -3.4629 | -1.6374 | 3.4629 | 1.6373 | 4.8249e-05 | -5.4136e-05 | 0.11143 | 0.11142 | 0.11143 | 0.99238 | -0.17041 | 0.99239 | -0.17052 | 50.648
168 | -3.7133 | -1.7586 | 3.7137 | 1.7582 | 0.00040145 | -0.00037601 | 0.11952 | 0.11951 | 0.11952 | 0.99239 | -0.17052 | 0.99249 | -0.17142 | 54.3262
169 | -3.7137 | -1.7582 | 3.7175 | 1.7604 | 0.0038018 | 0.0022054 | 0.11951 | 0.11951 | 0.11951 | 0.99249 | -0.17142 | 0.99356 | -0.1641 | 56.9102
170 | 0.27375 | 0.13213 | -0.27375 | -0.13258 | 2.0093e-06 | -0.00045392 | 0.0088317 | 0.0088374 | 0.0088374 | 0.99356 | -0.1641 | 0.99356 | -0.16403 | 4.017
171 | -4.2567 | -2.0146 | 4.259 | 2.017 | 0.0022894 | 0.0024532 | 0.13683 | 0.13683 | 0.13683 | 0.99356 | -0.1641 | 0.99424 | -0.14723 | 39.0941
172 | 4.4642 | 2.1078 | -4.4642 | -2.1098 | 5.2427e-05 | -0.0020242 | 0.14329 | 0.14332 | 0.14332 | 0.99455 | -0.13364 | 0.99454 | -0.13369 | 11.232
173 | 4.4642 | 2.1098 | -4.4636 | -2.1087 | 0.00056195 | 0.0010921 | 0.14332 | 0.14333 | 0.14333 | 0.99454 | -0.13369 | 0.99431 | -0.14676 | 11.1105
174 | 0.426 | 0.20535 | -0.426 | -0.20584 | 5.2002e-06 | -0.00049068 | 0.013697 | 0.013703 | 0.013703 | 0.99669 | -0.085649 | 0.99668 | -0.085543 | 6.2288
175 | 0.071246 | 0.034031 | -0.071246 | -0.034506 | 1.4015e-07 | -0.00047483 | 0.0022869 | 0.0022928 | 0.0022928 | 0.99668 | -0.085543 | 0.99667 | -0.085526 | 1.0422
176 | 0.13529 | 0.064748 | -0.13529 | -0.065524 | 8.3291e-07 | -0.0007752 | 0.0043538 | 0.0043636 | 0.0043636 | 0.99447 | -0.11716 | 0.99446 | -0.11711 | 1.9834
177 | 1.2096 | 0.58016 | -1.2095 | -0.58074 | 5.1064e-05 | -0.00058031 | 0.038941 | 0.038949 | 0.038949 | 0.99447 | -0.11716 | 0.99443 | -0.1168 | 17.7041
178 | 0.09127 | 0.043808 | -0.09127 | -0.044204 | 1.9379e-07 | -0.00039618 | 0.0029388 | 0.0029438 | 0.0029438 | 0.99447 | -0.11722 | 0.99447 | -0.1172 | 1.3381
179 | 1.2095 | 0.58074 | -1.2094 | -0.58153 | 6.9905e-05 | -0.00079399 | 0.038949 | 0.038959 | 0.038959 | 0.99443 | -0.1168 | 0.99437 | -0.11631 | 17.7087
180 | 4.2591 | 2.0167 | -4.259 | -2.017 | 0.00010708 | -0.00032379 | 0.13682 | 0.13683 | 0.13683 | 0.99426 | -0.14693 | 0.99424 | -0.14723 | 37.7976
181 | -4.3509 | -2.0612 | 4.3511 | 2.0542 | 0.00017154 | -0.0069672 | 0.13978 | 0.13969 | 0.13978 | 0.99426 | -0.14693 | 0.99431 | -0.14676 | 10.9547

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 22.0608 | 9.9743

## res_load
| p_mw | q_mvar
0 | 0.34108 | 0.16519
1 | 0.18118 | 0.087749
2 | 0.10879 | 0.05269
3 | 0.33731 | 0.16337
4 | 0.13947 | 0.067548
5 | 0.14297 | 0.069242
6 | 0.15014 | 0.072715
7 | 0.24661 | 0.11944
8 | 0.29106 | 0.14097
9 | 0.20747 | 0.10048
10 | 0.31383 | 0.15199
11 | 0.16966 | 0.082168
12 | 0.080036 | 0.038763
13 | 0.21092 | 0.10215
14 | 0.25425 | 0.12314
15 | 0.27415 | 0.13278
16 | 0.35432 | 0.1716
17 | 0.31973 | 0.15485
18 | 0.30862 | 0.14947
19 | 0.19295 | 0.093451
20 | 0.1838 | 0.089017
21 | 0.075857 | 0.036739
22 | 0.2453 | 0.1188
23 | 0.25929 | 0.12558
24 | 0.41399 | 0.2005
25 | 0.34674 | 0.16794
26 | 0.25249 | 0.12229
27 | 0.25321 | 0.12263
28 | 0.26586 | 0.12876
29 | 0.40665 | 0.19695
30 | 0.3112 | 0.15072
31 | 0.30944 | 0.14987
32 | 0.31768 | 0.15386
33 | 0.40372 | 0.19553
34 | 0.30265 | 0.14658
35 | 0.37575 | 0.18198
36 | 0.40257 | 0.19497
37 | 0.10563 | 0.051158
38 | 1.6619 | 0.80492
39 | 0.32987 | 0.15976
40 | 0.39643 | 0.192
41 | 0.13214 | 0.064001
42 | 0.076338 | 0.036972
43 | 0.11263 | 0.054551
44 | 0.1528 | 0.074002
45 | 0.35722 | 0.17301
46 | 0.081158 | 0.039307
47 | 0.073374 | 0.035536
48 | 0.24958 | 0.12088
49 | 0.22782 | 0.11034
50 | 0.070134 | 0.033968
51 | 0.38458 | 0.18626
52 | 0.33342 | 0.16148
53 | 0.1968 | 0.095313
54 | 0.19461 | 0.094253
55 | 0.40326 | 0.19531
56 | 0.1579 | 0.076474
57 | 0.28391 | 0.1375
58 | 0.3087 | 0.14951
59 | 0.11323 | 0.054839
60 | 0.26734 | 0.12948
61 | 0.074473 | 0.036069
62 | 0.24012 | 0.1163
63 | 0.12291 | 0.059529
64 | 0.17419 | 0.084365
65 | 0.0695 | 0.03366
66 | 0.40451 | 0.19591
67 | 0.10031 | 0.048585
68 | 0.38999 | 0.18888
69 | 0.28231 | 0.13673
70 | 0.28943 | 0.14018
71 | 0.23552 | 0.11407
72 | 0.22841 | 0.11062
73 | 0.32371 | 0.15678
74 | 0.09979 | 0.04833
75 | 0.32736 | 0.15855
76 | 0.2504 | 0.12127
77 | 0.10401 | 0.050372
78 | 0.070575 | 0.034181
79 | 0.40605 | 0.19666
80 | 0.35475 | 0.17181
81 | 0.071246 | 0.034506
82 | 0.13529 | 0.065524
83 | 0.09127 | 0.044204
84 | 0.097792 | 0.047363
85 | 0.091762 | 0.044442
86 | 0.11256 | 0.054513
87 | 0.27375 | 0.13258
88 | 0.068205 | 0.033033

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1