## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_279_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_279_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_279_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_279_0_node_6 | 20 | n |  | TRUE
4 | bus_MV_279_0_node_11 | 20 | n |  | TRUE
5 | bus_MV_279_0_node_1 | 20 | n |  | TRUE
6 | bus_MV_279_0_node_4 | 20 | n |  | TRUE
7 | bus_MV_279_0_node_134 | 20 | n |  | TRUE
8 | bus_MV_279_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_279_0_node_101 | 20 | n |  | TRUE
10 | bus_MV_279_0_node_135 | 20 | n |  | TRUE
11 | bus_MV_279_0_node_136 | 20 | n |  | TRUE
12 | bus_MV_279_0_node_7 | 20 | n |  | TRUE
13 | bus_MV_279_0_node_165 | 20 | n |  | TRUE
14 | bus_MV_279_0_node_9 | 20 | n |  | TRUE
15 | bus_MV_279_0_node_8 | 20 | n |  | TRUE
16 | bus_MV_279_0_node_129 | 20 | n |  | TRUE
17 | bus_MV_279_0_node_112 | 20 | n |  | TRUE
18 | bus_MV_279_0_node_159 | 20 | n |  | TRUE
19 | bus_MV_279_0_node_121 | 20 | n |  | TRUE
20 | bus_MV_279_0_node_102 | 20 | n |  | TRUE
21 | bus_MV_279_0_node_137 | 20 | n |  | TRUE
22 | bus_MV_279_0_node_37 | 20 | n |  | TRUE
23 | bus_MV_279_0_node_111 | 20 | n |  | TRUE
24 | bus_MV_279_0_node_162 | 20 | n |  | TRUE
25 | bus_MV_279_0_node_41 | 20 | n |  | TRUE
26 | bus_MV_279_0_node_12 | 20 | n |  | TRUE
27 | bus_MV_279_0_node_13 | 20 | n |  | TRUE
28 | bus_MV_279_0_node_146 | 20 | n |  | TRUE
29 | bus_MV_279_0_node_14 | 20 | n |  | TRUE
30 | bus_MV_279_0_node_158 | 20 | n |  | TRUE
31 | bus_MV_279_0_node_144 | 20 | n |  | TRUE
32 | bus_MV_279_0_node_23 | 20 | n |  | TRUE
33 | bus_MV_279_0_node_25 | 20 | n |  | TRUE
34 | bus_MV_279_0_node_24 | 20 | n |  | TRUE
35 | bus_MV_279_0_node_26 | 20 | n |  | TRUE
36 | bus_MV_279_0_node_27 | 20 | n |  | TRUE
37 | bus_MV_279_0_node_15 | 20 | n |  | TRUE
38 | bus_MV_279_0_node_17 | 20 | n |  | TRUE
39 | bus_MV_279_0_node_18 | 20 | n |  | TRUE
40 | bus_MV_279_0_node_20 | 20 | n |  | TRUE
41 | bus_MV_279_0_node_21 | 20 | n |  | TRUE
42 | bus_MV_279_0_node_22 | 20 | n |  | TRUE
43 | bus_MV_279_0_node_155 | 20 | n |  | TRUE
44 | bus_MV_279_0_node_156 | 20 | n |  | TRUE
45 | bus_MV_279_0_node_16 | 20 | n |  | TRUE
46 | bus_MV_279_0_node_19 | 20 | n |  | TRUE
47 | bus_MV_279_0_node_69 | 20 | n |  | TRUE
48 | bus_MV_279_0_node_32 | 20 | n |  | TRUE
49 | bus_MV_279_0_node_65 | 20 | n |  | TRUE
50 | bus_MV_279_0_node_68 | 20 | n |  | TRUE
51 | bus_MV_279_0_node_64 | 20 | n |  | TRUE
52 | bus_MV_279_0_node_31 | 20 | n |  | TRUE
53 | bus_MV_279_0_node_28 | 20 | n |  | TRUE
54 | bus_MV_279_0_node_29 | 20 | n |  | TRUE
55 | bus_MV_279_0_node_61 | 20 | n |  | TRUE
56 | bus_MV_279_0_node_62 | 20 | n |  | TRUE
57 | bus_MV_279_0_node_90 | 20 | n |  | TRUE
58 | bus_MV_279_0_node_95 | 20 | n |  | TRUE
59 | bus_MV_279_0_node_63 | 20 | n |  | TRUE
60 | bus_MV_279_0_node_91 | 20 | n |  | TRUE
61 | bus_MV_279_0_node_99 | 20 | n |  | TRUE
62 | bus_MV_279_0_node_98 | 20 | n |  | TRUE
63 | bus_MV_279_0_node_30 | 20 | n |  | TRUE
64 | bus_MV_279_0_node_161 | 20 | n |  | TRUE
65 | bus_MV_279_0_node_128 | 20 | n |  | TRUE
66 | bus_MV_279_0_node_46 | 20 | n |  | TRUE
67 | bus_MV_279_0_node_145 | 20 | n |  | TRUE
68 | bus_MV_279_0_node_66 | 20 | n |  | TRUE
69 | bus_MV_279_0_node_143 | 20 | n |  | TRUE
70 | bus_MV_279_0_node_33 | 20 | n |  | TRUE
71 | bus_MV_279_0_node_35 | 20 | n |  | TRUE
72 | bus_MV_279_0_node_34 | 20 | n |  | TRUE
73 | bus_MV_279_0_node_36 | 20 | n |  | TRUE
74 | bus_MV_279_0_node_139 | 20 | n |  | TRUE
75 | bus_MV_279_0_node_149 | 20 | n |  | TRUE
76 | bus_MV_279_0_node_138 | 20 | n |  | TRUE
77 | bus_MV_279_0_node_49 | 20 | n |  | TRUE
78 | bus_MV_279_0_node_148 | 20 | n |  | TRUE
79 | bus_MV_279_0_node_132 | 20 | n |  | TRUE
80 | bus_MV_279_0_node_120 | 20 | n |  | TRUE
81 | bus_MV_279_0_node_133 | 20 | n |  | TRUE
82 | bus_MV_279_0_node_131 | 20 | n |  | TRUE
83 | bus_MV_279_0_node_75 | 20 | n |  | TRUE
84 | bus_MV_279_0_node_38 | 20 | n |  | TRUE
85 | bus_MV_279_0_node_39 | 20 | n |  | TRUE
86 | bus_MV_279_0_node_43 | 20 | n |  | TRUE
87 | bus_MV_279_0_node_42 | 20 | n |  | TRUE
88 | bus_MV_279_0_node_109 | 20 | n |  | TRUE
89 | bus_MV_279_0_node_106 | 20 | n |  | TRUE
90 | bus_MV_279_0_node_45 | 20 | n |  | TRUE
91 | bus_MV_279_0_node_71 | 20 | n |  | TRUE
92 | bus_MV_279_0_node_107 | 20 | n |  | TRUE
93 | bus_MV_279_0_node_85 | 20 | n |  | TRUE
94 | bus_MV_279_0_node_82 | 20 | n |  | TRUE
95 | bus_MV_279_0_node_127 | 20 | n |  | TRUE
96 | bus_MV_279_0_node_54 | 20 | n |  | TRUE
97 | bus_MV_279_0_node_53 | 20 | n |  | TRUE
98 | bus_MV_279_0_node_52 | 20 | n |  | TRUE
99 | bus_MV_279_0_node_47 | 20 | n |  | TRUE
100 | bus_MV_279_0_node_48 | 20 | n |  | TRUE
101 | bus_MV_279_0_node_51 | 20 | n |  | TRUE
102 | bus_MV_279_0_node_140 | 20 | n |  | TRUE
103 | bus_MV_279_0_node_50 | 20 | n |  | TRUE
104 | bus_MV_279_0_node_166 | 20 | n |  | TRUE
105 | bus_MV_279_0_node_115 | 20 | n |  | TRUE
106 | bus_MV_279_0_node_77 | 20 | n |  | TRUE
107 | bus_MV_279_0_node_119 | 20 | n |  | TRUE
108 | bus_MV_279_0_node_141 | 20 | n |  | TRUE
109 | bus_MV_279_0_node_76 | 20 | n |  | TRUE
110 | bus_MV_279_0_node_154 | 20 | n |  | TRUE
111 | bus_MV_279_0_node_118 | 20 | n |  | TRUE
112 | bus_MV_279_0_node_160 | 20 | n |  | TRUE
113 | bus_MV_279_0_node_117 | 20 | n |  | TRUE
114 | bus_MV_279_0_node_114 | 20 | n |  | TRUE
115 | bus_MV_279_0_node_84 | 20 | n |  | TRUE
116 | bus_MV_279_0_node_116 | 20 | n |  | TRUE
117 | bus_MV_279_0_node_125 | 20 | n |  | TRUE
118 | bus_MV_279_0_node_126 | 20 | n |  | TRUE
119 | bus_MV_279_0_node_55 | 20 | n |  | TRUE
120 | bus_MV_279_0_node_56 | 20 | n |  | TRUE
121 | bus_MV_279_0_node_57 | 20 | n |  | TRUE
122 | bus_MV_279_0_node_58 | 20 | n |  | TRUE
123 | bus_MV_279_0_node_59 | 20 | n |  | TRUE
124 | bus_MV_279_0_node_60 | 20 | n |  | TRUE
125 | bus_MV_279_0_node_142 | 20 | n |  | TRUE
126 | bus_MV_279_0_node_105 | 20 | n |  | TRUE
127 | bus_MV_279_0_node_97 | 20 | n |  | TRUE
128 | bus_MV_279_0_node_89 | 20 | n |  | TRUE
129 | bus_MV_279_0_node_122 | 20 | n |  | TRUE
130 | bus_MV_279_0_node_96 | 20 | n |  | TRUE
131 | bus_MV_279_0_node_87 | 20 | n |  | TRUE
132 | bus_MV_279_0_node_92 | 20 | n |  | TRUE
133 | bus_MV_279_0_node_100 | 20 | n |  | TRUE
134 | bus_MV_279_0_node_157 | 20 | n |  | TRUE
135 | bus_MV_279_0_node_72 | 20 | n |  | TRUE
136 | bus_MV_279_0_node_73 | 20 | n |  | TRUE
137 | bus_MV_279_0_node_164 | 20 | n |  | TRUE
138 | bus_MV_279_0_node_163 | 20 | n |  | TRUE
139 | bus_MV_279_0_node_130 | 20 | n |  | TRUE
140 | bus_MV_279_0_node_151 | 20 | n |  | TRUE
141 | bus_MV_279_0_node_150 | 20 | n |  | TRUE
142 | bus_MV_279_0_node_80 | 20 | n |  | TRUE
143 | bus_MV_279_0_node_81 | 20 | n |  | TRUE
144 | bus_MV_279_0_node_83 | 20 | n |  | TRUE
145 | bus_MV_279_0_node_86 | 20 | n |  | TRUE
146 | bus_MV_279_0_node_88 | 20 | n |  | TRUE
147 | bus_MV_279_0_node_153 | 20 | n |  | TRUE
148 | bus_MV_279_0_node_93 | 20 | n |  | TRUE
149 | bus_MV_279_0_node_94 | 20 | n |  | TRUE
150 | bus_MV_279_0_node_152 | 20 | n |  | TRUE
151 | bus_MV_279_0_node_103 | 20 | n |  | TRUE
152 | bus_MV_279_0_node_123 | 20 | n |  | TRUE
153 | bus_MV_279_0_node_108 | 20 | n |  | TRUE
154 | bus_MV_279_0_node_124 | 20 | n |  | TRUE
155 | bus_MV_279_0_node_110 | 20 | n |  | TRUE
156 | bus_MV_279_0_node_113 | 20 | n |  | TRUE
157 | bus_MV_279_0_node_147 | 20 | n |  | TRUE
158 | bus_HV_279_0_node_88 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_279_0_load_0 | 0 | 0.31137 | 0.1508 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_279_0_load_1 | 5 | 0.19772 | 0.095759 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_279_0_load_4 | 6 | 0.159 | 0.077005 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_279_0_load_134 | 7 | 0.10571 | 0.051197 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_279_0_load_101 | 9 | 0.083379 | 0.040382 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_279_0_load_136 | 11 | 0.14156 | 0.068561 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_279_0_load_165 | 13 | 0.3226 | 0.15624 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_279_0_load_129 | 16 | 0.27406 | 0.13273 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_279_0_load_112 | 17 | 0.077561 | 0.037565 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_279_0_load_159 | 18 | 0.077315 | 0.037445 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_279_0_load_137 | 21 | 0.091075 | 0.04411 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_279_0_load_162 | 24 | 0.30221 | 0.14637 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_279_0_load_12 | 26 | 0.32401 | 0.15693 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_279_0_load_13 | 27 | 0.13159 | 0.06373 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_279_0_load_158 | 30 | 0.15508 | 0.075109 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_279_0_load_23 | 32 | 0.28802 | 0.13949 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_279_0_load_25 | 33 | 0.26812 | 0.12986 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_279_0_load_27 | 36 | 0.32654 | 0.15815 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_279_0_load_15 | 37 | 0.209 | 0.10122 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_279_0_load_22 | 42 | 0.083344 | 0.040366 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_279_0_load_155 | 43 | 0.11991 | 0.058075 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_279_0_load_69 | 47 | 0.2481 | 0.12016 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_279_0_load_32 | 48 | 0.068626 | 0.033237 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_279_0_load_65 | 49 | 0.36467 | 0.17662 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_279_0_load_68 | 50 | 0.24842 | 0.12032 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_279_0_load_64 | 51 | 0.3149 | 0.15251 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_279_0_load_28 | 53 | 0.61395 | 0.29735 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_279_0_load_90 | 57 | 0.14432 | 0.069897 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_279_0_load_95 | 58 | 0.070218 | 0.034008 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_279_0_load_91 | 60 | 0.096041 | 0.046515 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_279_0_load_98 | 62 | 0.13397 | 0.064883 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_279_0_load_30 | 63 | 0.26752 | 0.12956 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_279_0_load_161 | 64 | 0.33823 | 0.16381 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_279_0_load_128 | 65 | 0.099716 | 0.048295 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_279_0_load_145 | 67 | 0.14998 | 0.072638 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_279_0_load_33 | 70 | 0.40135 | 0.19438 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_279_0_load_34 | 72 | 0.06816 | 0.033011 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_279_0_load_138 | 76 | 0.16282 | 0.078857 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_279_0_load_148 | 78 | 0.097693 | 0.047315 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_279_0_load_132 | 79 | 0.16488 | 0.079857 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_279_0_load_120 | 80 | 0.12987 | 0.0629 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_279_0_load_133 | 81 | 0.11732 | 0.05682 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_279_0_load_38 | 84 | 0.37521 | 0.18172 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_279_0_load_109 | 88 | 0.074396 | 0.036032 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_279_0_load_106 | 89 | 0.070371 | 0.034082 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_279_0_load_71 | 91 | 0.39784 | 0.19268 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_279_0_load_85 | 93 | 0.33583 | 0.16265 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_279_0_load_82 | 94 | 0.14619 | 0.070803 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_279_0_load_127 | 95 | 0.097982 | 0.047455 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_279_0_load_52 | 98 | 0.3178 | 0.15392 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_279_0_load_47 | 99 | 0.36911 | 0.17877 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_279_0_load_140 | 102 | 0.17435 | 0.084443 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_279_0_load_166 | 104 | 0.11209 | 0.054289 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_279_0_load_115 | 105 | 0.22793 | 0.11039 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_279_0_load_141 | 108 | 0.079834 | 0.038666 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_279_0_load_154 | 110 | 0.08444 | 0.040896 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_279_0_load_160 | 112 | 0.14355 | 0.069525 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_279_0_load_114 | 114 | 0.14549 | 0.070462 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_279_0_load_84 | 115 | 0.12805 | 0.062016 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_279_0_load_116 | 116 | 0.082046 | 0.039737 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_279_0_load_125 | 117 | 0.1336 | 0.064705 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_279_0_load_56 | 120 | 0.19054 | 0.092281 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_279_0_load_60 | 124 | 0.14381 | 0.069649 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_279_0_load_142 | 125 | 0.27889 | 0.13507 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_279_0_load_105 | 126 | 0.085838 | 0.041573 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_279_0_load_122 | 129 | 0.30468 | 0.14756 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_279_0_load_96 | 130 | 0.41893 | 0.2029 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_279_0_load_100 | 133 | 0.082774 | 0.040089 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_279_0_load_157 | 134 | 0.14595 | 0.070686 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_279_0_load_72 | 135 | 0.39117 | 0.18945 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_279_0_load_164 | 137 | 0.32802 | 0.15887 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_279_0_load_163 | 138 | 0.29685 | 0.14377 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_279_0_load_130 | 139 | 0.083557 | 0.040469 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_279_0_load_151 | 140 | 0.081985 | 0.039707 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_279_0_load_150 | 141 | 0.29336 | 0.14208 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_279_0_load_80 | 142 | 0.074522 | 0.036093 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_279_0_load_83 | 144 | 0.099445 | 0.048163 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_279_0_load_86 | 145 | 0.083239 | 0.040315 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_279_0_load_153 | 147 | 0.48565 | 0.23521 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_279_0_load_152 | 150 | 0.4065 | 0.19688 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_279_0_load_103 | 151 | 0.72307 | 0.3502 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_279_0_load_123 | 152 | 0.19359 | 0.093761 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_279_0_load_124 | 154 | 0.085152 | 0.041241 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_279_0_load_110 | 155 | 0.16536 | 0.080087 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_279_0_load_113 | 156 | 0.13734 | 0.066517 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_279_0_load_147 | 157 | 0.18298 | 0.08862 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 146 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_279_0_line_0 |  | 0 | 1 | 0.007632 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_279_0_line_1 |  | 0 | 2 | 0.014348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_279_0_line_2 |  | 1 | 3 | 0.011548 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_279_0_line_3 |  | 2 | 4 | 0.068662 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_279_0_line_4 |  | 3 | 11 | 0.028713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_279_0_line_5 |  | 4 | 18 | 0.10613 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_279_0_line_6 |  | 4 | 15 | 0.21934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_279_0_line_7 |  | 5 | 6 | 0.047681 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
8 | MV_279_0_line_8 |  | 5 | 7 | 0.014729 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
9 | MV_279_0_line_9 |  | 6 | 8 | 0.0071649 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
10 | MV_279_0_line_10 |  | 6 | 9 | 0.027953 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
11 | MV_279_0_line_11 |  | 7 | 10 | 0.039764 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_279_0_line_12 |  | 8 | 19 | 0.025371 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
13 | MV_279_0_line_13 |  | 9 | 20 | 0.033206 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_279_0_line_14 |  | 10 | 11 | 0.0051566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_279_0_line_15 |  | 12 | 13 | 0.026363 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_279_0_line_16 |  | 12 | 14 | 0.12431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_279_0_line_17 |  | 14 | 17 | 0.018691 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_279_0_line_18 |  | 14 | 15 | 0.19228 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_279_0_line_19 |  | 15 | 16 | 0.052312 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_279_0_line_20 |  | 17 | 23 | 0.015154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_279_0_line_21 |  | 19 | 21 | 0.014538 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_279_0_line_22 |  | 19 | 22 | 0.024838 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
23 | MV_279_0_line_23 |  | 20 | 151 | 0.01127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_279_0_line_24 |  | 22 | 80 | 0.03524 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
25 | MV_279_0_line_25 |  | 23 | 155 | 0.028797 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_279_0_line_26 |  | 24 | 25 | 0.020839 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_279_0_line_27 |  | 25 | 86 | 0.11985 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_279_0_line_28 |  | 26 | 27 | 0.011265 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
29 | MV_279_0_line_29 |  | 26 | 28 | 0.028649 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
30 | MV_279_0_line_30 |  | 27 | 29 | 0.013994 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
31 | MV_279_0_line_31 |  | 28 | 30 | 0.012529 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_279_0_line_32 |  | 28 | 31 | 0.024766 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
33 | MV_279_0_line_33 |  | 29 | 32 | 0.020997 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
34 | MV_279_0_line_34 |  | 30 | 44 | 0.021286 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_279_0_line_35 |  | 31 | 157 | 0.01385 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_279_0_line_36 |  | 31 | 69 | 0.016513 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
37 | MV_279_0_line_37 |  | 32 | 33 | 0.011018 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_279_0_line_38 |  | 32 | 34 | 0.023134 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
39 | MV_279_0_line_39 |  | 34 | 35 | 0.006472 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_279_0_line_40 |  | 34 | 36 | 0.010867 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
41 | MV_279_0_line_41 |  | 35 | 53 | 0.011143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_279_0_line_42 |  | 36 | 54 | 0.021883 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
43 | MV_279_0_line_43 |  | 37 | 38 | 0.0169 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_279_0_line_44 |  | 37 | 39 | 0.023028 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_279_0_line_45 |  | 38 | 40 | 0.019018 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_279_0_line_46 |  | 38 | 41 | 0.009418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_279_0_line_47 |  | 39 | 42 | 0.0088068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_279_0_line_48 |  | 40 | 49 | 0.005712 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_279_0_line_49 |  | 41 | 50 | 0.021111 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_279_0_line_50 |  | 42 | 48 | 0.048063 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_279_0_line_51 |  | 42 | 45 | 0.028608 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_279_0_line_52 |  | 43 | 44 | 0.0038908 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_279_0_line_53 |  | 44 | 134 | 0.013972 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_279_0_line_54 |  | 45 | 46 | 0.052288 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_279_0_line_55 |  | 46 | 47 | 0.044252 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_279_0_line_56 |  | 48 | 52 | 0.013471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_279_0_line_57 |  | 49 | 51 | 0.022434 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_279_0_line_58 |  | 51 | 68 | 0.029998 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_279_0_line_59 |  | 52 | 63 | 0.022598 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_279_0_line_60 |  | 54 | 55 | 0.048381 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_279_0_line_61 |  | 54 | 56 | 0.072999 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
62 | MV_279_0_line_62 |  | 55 | 57 | 0.0066758 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_279_0_line_63 |  | 56 | 58 | 0.006365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_279_0_line_64 |  | 56 | 59 | 0.074367 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_279_0_line_65 |  | 56 | 60 | 0.014261 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
66 | MV_279_0_line_66 |  | 59 | 61 | 0.048957 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_279_0_line_67 |  | 59 | 62 | 0.0093317 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_279_0_line_68 |  | 60 | 132 | 0.0096886 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
69 | MV_279_0_line_69 |  | 61 | 133 | 0.023002 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_279_0_line_70 |  | 63 | 64 | 0.046775 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_279_0_line_71 |  | 63 | 65 | 0.060903 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_279_0_line_72 |  | 64 | 66 | 0.018512 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_279_0_line_73 |  | 66 | 90 | 0.065265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_279_0_line_74 |  | 67 | 68 | 0.042082 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_279_0_line_75 |  | 67 | 69 | 0.022781 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_279_0_line_76 |  | 69 | 125 | 0.0050687 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
77 | MV_279_0_line_77 |  | 70 | 71 | 0.016333 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
78 | MV_279_0_line_78 |  | 70 | 72 | 0.0754 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
79 | MV_279_0_line_79 |  | 71 | 73 | 0.095105 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
80 | MV_279_0_line_80 |  | 71 | 74 | 0.08776 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
81 | MV_279_0_line_81 |  | 72 | 75 | 0.12709 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
82 | MV_279_0_line_82 |  | 73 | 79 | 0.006814 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
83 | MV_279_0_line_83 |  | 74 | 76 | 0.039868 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
84 | MV_279_0_line_84 |  | 74 | 77 | 0.002893 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
85 | MV_279_0_line_85 |  | 75 | 78 | 0.030438 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_279_0_line_86 |  | 76 | 80 | 0.043004 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
87 | MV_279_0_line_87 |  | 77 | 102 | 0.031777 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_279_0_line_88 |  | 77 | 103 | 0.05028 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
89 | MV_279_0_line_89 |  | 77 | 100 | 0.074758 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_279_0_line_90 |  | 78 | 141 | 0.053348 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
91 | MV_279_0_line_91 |  | 79 | 81 | 0.064054 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
92 | MV_279_0_line_92 |  | 79 | 82 | 0.007455 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_279_0_line_93 |  | 81 | 83 | 0.03523 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
94 | MV_279_0_line_94 |  | 82 | 139 | 0.024935 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_279_0_line_95 |  | 83 | 109 | 0.12289 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
96 | MV_279_0_line_96 |  | 83 | 136 | 0.094275 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_279_0_line_97 |  | 84 | 85 | 0.028975 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_279_0_line_98 |  | 85 | 86 | 0.059271 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_279_0_line_99 |  | 86 | 89 | 0.014208 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_279_0_line_100 |  | 86 | 87 | 0.022318 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_279_0_line_101 |  | 87 | 88 | 0.023162 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_279_0_line_102 |  | 89 | 92 | 0.017981 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_279_0_line_103 |  | 90 | 91 | 0.010927 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_279_0_line_104 |  | 92 | 153 | 0.051459 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_279_0_line_105 |  | 93 | 94 | 0.038216 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
106 | MV_279_0_line_106 |  | 94 | 142 | 0.027911 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_279_0_line_107 |  | 95 | 96 | 0.0043336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_279_0_line_108 |  | 96 | 117 | 0.0094292 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_279_0_line_109 |  | 96 | 97 | 0.04101 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_279_0_line_110 |  | 97 | 98 | 0.021552 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_279_0_line_111 |  | 99 | 100 | 0.005605 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_279_0_line_112 |  | 100 | 101 | 0.083659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_279_0_line_113 |  | 101 | 105 | 0.01745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_279_0_line_114 |  | 103 | 104 | 0.005648 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_279_0_line_115 |  | 105 | 114 | 0.047423 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_279_0_line_116 |  | 106 | 107 | 0.037522 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
117 | MV_279_0_line_117 |  | 106 | 108 | 0.013311 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_279_0_line_118 |  | 106 | 109 | 0.031306 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
119 | MV_279_0_line_119 |  | 107 | 110 | 0.018699 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
120 | MV_279_0_line_120 |  | 107 | 111 | 0.083091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_279_0_line_121 |  | 109 | 137 | 0.009175 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_279_0_line_122 |  | 110 | 148 | 0.024038 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
123 | MV_279_0_line_123 |  | 111 | 112 | 0.003684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_279_0_line_124 |  | 111 | 113 | 0.055003 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_279_0_line_125 |  | 113 | 115 | 0.068883 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
126 | MV_279_0_line_126 |  | 113 | 116 | 0.014738 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_279_0_line_127 |  | 114 | 156 | 0.038531 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_279_0_line_128 |  | 115 | 144 | 0.0041828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_279_0_line_129 |  | 117 | 118 | 0.028795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_279_0_line_130 |  | 118 | 154 | 0.013779 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_279_0_line_131 |  | 119 | 120 | 0.013217 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
132 | MV_279_0_line_132 |  | 119 | 121 | 0.014707 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
133 | MV_279_0_line_133 |  | 120 | 122 | 0.026478 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
134 | MV_279_0_line_134 |  | 121 | 123 | 0.029213 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_279_0_line_135 |  | 121 | 124 | 0.014703 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
136 | MV_279_0_line_136 |  | 122 | 125 | 0.018926 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
137 | MV_279_0_line_137 |  | 123 | 126 | 0.016365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_279_0_line_138 |  | 123 | 127 | 0.057978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_279_0_line_139 |  | 124 | 128 | 0.02505 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
140 | MV_279_0_line_140 |  | 126 | 129 | 0.0014385 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_279_0_line_141 |  | 127 | 130 | 0.0016271 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_279_0_line_142 |  | 128 | 131 | 0.057486 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
143 | MV_279_0_line_143 |  | 129 | 152 | 0.0094431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_279_0_line_144 |  | 131 | 146 | 0.012074 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
145 | MV_279_0_line_145 |  | 131 | 145 | 0.0030872 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_279_0_line_146 |  | 132 | 148 | 0.041152 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
147 | MV_279_0_line_147 |  | 135 | 136 | 0.073446 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
148 | MV_279_0_line_148 |  | 138 | 139 | 0.049223 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
149 | MV_279_0_line_149 |  | 140 | 141 | 0.17053 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
150 | MV_279_0_line_150 |  | 142 | 143 | 0.026346 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_279_0_line_151 |  | 143 | 144 | 0.018694 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_279_0_line_152 |  | 146 | 147 | 0.034241 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_279_0_line_153 |  | 148 | 149 | 0.091817 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_279_0_line_154 |  | 149 | 150 | 0.049596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_279_0_line_155 |  | 152 | 153 | 0.030471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_279_0_line_156 |  | 153 | 154 | 0.01251 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_279_0_trafo_88 | 25 MVA 110/20 kV | 158 | 146 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2594150.1508 | 1119718.1095
1 | 2594146.323 | 1119724.7165
2 | 2594144.739 | 1119706.498
3 | 2594149.409 | 1119732.684
4 | 2594107.7081 | 1119699.92
5 | 2594217.0777 | 1119753.7202
6 | 2594258.6635 | 1119777.0464
7 | 2594211.8423 | 1119767.4871
8 | 2594264.9252 | 1119780.5288
9 | 2594273.8711 | 1119753.5921
10 | 2594177.144 | 1119748.0645
11 | 2594172.0217 | 1119748.5141
12 | 2593996.9527 | 1119808.9836
13 | 2593988.476 | 1119833.9488
14 | 2593961.1259 | 1119733.8162
15 | 2594115.1801 | 1119813.5239
16 | 2594161.0758 | 1119838.6258
17 | 2593978.7968 | 1119739.9069
18 | 2594005.1495 | 1119672.6185
19 | 2594263.7653 | 1119801.9071
20 | 2594265.6075 | 1119727.8579
21 | 2594257.5924 | 1119814.9322
22 | 2594285.3299 | 1119811.4355
23 | 2593993.1234 | 1119744.8449
24 | 2593914.3545 | 1119897.4215
25 | 2593933.518 | 1119905.028
26 | 2594071.7932 | 1120165.061
27 | 2594082.7089 | 1120162.2762
28 | 2594043.149 | 1120164.5337
29 | 2594095.414 | 1120156.4446
30 | 2594042.0496 | 1120176.333
31 | 2594028.5796 | 1120144.6163
32 | 2594085.6631 | 1120138.2311
33 | 2594076.9677 | 1120144.9984
34 | 2594070.5997 | 1120120.6738
35 | 2594065.3035 | 1120124.4142
36 | 2594079.3569 | 1120114.2064
37 | 2593954.9317 | 1120268.6732
38 | 2593971.5388 | 1120266.9334
39 | 2593932.8158 | 1120262.0368
40 | 2593972.8774 | 1120247.9672
41 | 2593970.3371 | 1120276.2725
42 | 2593924.3758 | 1120259.5215
43 | 2594025.019 | 1120190.2495
44 | 2594028.8715 | 1120189.7047
45 | 2593913.8245 | 1120286.1123
46 | 2593890.0767 | 1120328.2127
47 | 2593926.6828 | 1120353.0765
48 | 2593922.5018 | 1120211.4948
49 | 2593973.1648 | 1120242.2641
50 | 2593991.4222 | 1120278.1966
51 | 2593975.6495 | 1120219.9729
52 | 2593910.5639 | 1120205.2538
53 | 2594059.3386 | 1120114.9933
54 | 2594100.8606 | 1120109.8275
55 | 2594105.0484 | 1120085.1112
56 | 2594148.2857 | 1120074.5302
57 | 2594102.6235 | 1120078.8914
58 | 2594142.9369 | 1120077.9804
59 | 2594164.3305 | 1120120.4259
60 | 2594160.1622 | 1120066.6384
61 | 2594210.4871 | 1120137.1225
62 | 2594155.5928 | 1120117.1499
63 | 2593890.1185 | 1120195.5033
64 | 2593909.0986 | 1120152.7519
65 | 2593829.27 | 1120198.0781
66 | 2593892.0653 | 1120145.3878
67 | 2594003.6152 | 1120156.0571
68 | 2593978.9675 | 1120190.1661
69 | 2594014.7856 | 1120136.3482
70 | 2594398.7779 | 1119836.8628
71 | 2594385.6796 | 1119846.6688
72 | 2594427.5956 | 1119767.1875
73 | 2594416.1471 | 1119906.1582
74 | 2594306.0668 | 1119883.5955
75 | 2594549.7338 | 1119802.3285
76 | 2594275.9597 | 1119857.4608
77 | 2594303.2671 | 1119884.3541
78 | 2594566.7887 | 1119827.5258
79 | 2594412.0634 | 1119911.6203
80 | 2594312.1222 | 1119834.1878
81 | 2594366.167 | 1119956.3019
82 | 2594417.931 | 1119916.2393
83 | 2594361.5586 | 1119989.0278
84 | 2593916.4534 | 1120019.1234
85 | 2593933.9653 | 1119996.0388
86 | 2593957.8637 | 1119963.9544
87 | 2593945.1372 | 1119966.6464
88 | 2593923.5955 | 1119958.1353
89 | 2593971.2081 | 1119968.8337
90 | 2593862.3029 | 1120107.8221
91 | 2593872.2136 | 1120112.4247
92 | 2593988.4465 | 1119973.3504
93 | 2594022.981 | 1119892.1538
94 | 2594036.371 | 1119927.9469
95 | 2593943.4066 | 1120062.1982
96 | 2593946.8182 | 1120064.8705
97 | 2593973.1847 | 1120093.6802
98 | 2593994.304 | 1120098.2723
99 | 2594239.8847 | 1119926.7801
100 | 2594243.5219 | 1119922.5078
101 | 2594222.1879 | 1119863.7885
102 | 2594318.7215 | 1119910.441
103 | 2594318.7146 | 1119919.4566
104 | 2594314.3747 | 1119923.0847
105 | 2594206.8825 | 1119855.4063
106 | 2594251.3054 | 1120017.9581
107 | 2594219.7729 | 1120015.0649
108 | 2594243.4141 | 1120027.5764
109 | 2594279.0376 | 1120016.0084
110 | 2594210.4334 | 1120030.5198
111 | 2594188.301 | 1119971.3629
112 | 2594185.418 | 1119973.6669
113 | 2594153.6928 | 1119947.5628
114 | 2594165.1157 | 1119832.9467
115 | 2594091.0973 | 1119918.8103
116 | 2594165.253 | 1119938.4205
117 | 2593953.2827 | 1120058.0062
118 | 2593973.8538 | 1120038.0079
119 | 2594041.1267 | 1120078.3713
120 | 2594035.4698 | 1120090.3159
121 | 2594047.972 | 1120065.347
122 | 2594024.8852 | 1120114.583
123 | 2594024.4791 | 1120047.8952
124 | 2594057.6817 | 1120054.3063
125 | 2594016.9191 | 1120131.7504
126 | 2594011.677 | 1120037.7029
127 | 2594051.0046 | 1119996.3547
128 | 2594074.5579 | 1120035.795
129 | 2594010.5435 | 1120036.8173
130 | 2594052.528 | 1119996.9262
131 | 2594113.0286 | 1120033.756
132 | 2594168.1608 | 1120061.171
133 | 2594232.968 | 1120139.9486
134 | 2594038.8382 | 1120199.4429
135 | 2594425.9324 | 1120074.5537
136 | 2594430.9633 | 1120001.2798
137 | 2594284.5528 | 1120023.3511
138 | 2594484.1832 | 1119947.4152
139 | 2594437.5676 | 1119931.6063
140 | 2594775.2118 | 1119894.6543
141 | 2594607.9344 | 1119861.4824
142 | 2594062.707 | 1119933.5456
143 | 2594070.7208 | 1119908.4476
144 | 2594087.3965 | 1119916.861
145 | 2594115.9159 | 1120034.8488
146 | 2594117.3686 | 1120022.4907
147 | 2594149.6369 | 1120033.9439
148 | 2594201.9812 | 1120053.023
149 | 2594250.4534 | 1120078.5775
150 | 2594297.3428 | 1120095.1296
151 | 2594270.7974 | 1119717.8538
152 | 2594003.1018 | 1120031.004
153 | 2593979.0892 | 1120012.2455
154 | 2593976.5978 | 1120024.5051
155 | 2594020.3479 | 1119754.2294
156 | 2594131.1716 | 1119814.7139
157 | 2594041.6075 | 1120140.1339
158 | 2594117.3686 | 1120022.4907

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99794 | -0.033674 | 0.31137 | 0.1508
1 | 0.99795 | -0.033776 | 0 | 0
2 | 0.99792 | -0.033535 | 0 | 0
3 | 0.99797 | -0.033931 | 0 | 0
4 | 0.99784 | -0.032864 | 0 | 0
5 | 0.9981 | -0.034165 | 0.19772 | 0.095759
6 | 0.99813 | -0.034054 | 0.159 | 0.077005
7 | 0.99809 | -0.034991 | 0.10571 | 0.051197
8 | 0.99814 | -0.034029 | 0 | 0
9 | 0.9981 | -0.03471 | 0.083379 | 0.040382
10 | 0.99802 | -0.034393 | 0 | 0
11 | 0.99801 | -0.034316 | 0.14156 | 0.068561
12 | 0.99742 | -0.029157 | 0 | 0
13 | 0.99741 | -0.029056 | 0.3226 | 0.15624
14 | 0.99747 | -0.029623 | 0 | 0
15 | 0.99761 | -0.03084 | 0 | 0
16 | 0.99759 | -0.030669 | 0.27406 | 0.13273
17 | 0.99746 | -0.02957 | 0.077561 | 0.037565
18 | 0.99783 | -0.032773 | 0.077315 | 0.037445
19 | 0.99816 | -0.033941 | 0 | 0
20 | 0.99807 | -0.034423 | 0 | 0
21 | 0.99816 | -0.033925 | 0.091075 | 0.04411
22 | 0.99818 | -0.03385 | 0 | 0
23 | 0.99746 | -0.02954 | 0 | 0
24 | 0.99934 | 0.00198 | 0.30221 | 0.14637
25 | 0.99935 | 0.0019049 | 0 | 0
26 | 0.99934 | -0.0080217 | 0.32401 | 0.15693
27 | 0.99932 | -0.0081004 | 0.13159 | 0.06373
28 | 0.99944 | -0.0022848 | 0 | 0
29 | 0.99929 | -0.008197 | 0 | 0
30 | 0.99943 | -0.0022225 | 0.15508 | 0.075109
31 | 0.99948 | -0.0021006 | 0 | 0
32 | 0.99926 | -0.0083415 | 0.28802 | 0.13949
33 | 0.99926 | -0.0083062 | 0.26812 | 0.12986
34 | 0.99919 | -0.012533 | 0 | 0
35 | 0.99918 | -0.012486 | 0 | 0
36 | 0.99917 | -0.012601 | 0.32654 | 0.15815
37 | 0.99895 | -0.00014188 | 0.209 | 0.10122
38 | 0.99899 | -0.00048285 | 0 | 0
39 | 0.99891 | 0.00026575 | 0 | 0
40 | 0.99904 | -0.00092174 | 0 | 0
41 | 0.99899 | -0.00045517 | 0 | 0
42 | 0.99889 | 0.00042187 | 0.083344 | 0.040366
43 | 0.99942 | -0.0021501 | 0.11991 | 0.058075
44 | 0.99942 | -0.0021557 | 0 | 0
45 | 0.99888 | 0.0003327 | 0 | 0
46 | 0.99886 | 0.000486 | 0 | 0
47 | 0.99884 | 0.00035293 | 0.2481 | 0.12016
48 | 0.99878 | -0.00027388 | 0.068626 | 0.033237
49 | 0.99905 | -0.0010534 | 0.36467 | 0.17662
50 | 0.99898 | -0.00039264 | 0.24842 | 0.12032
51 | 0.99912 | -0.0016683 | 0.3149 | 0.15251
52 | 0.99876 | -9.8268e-05 | 0 | 0
53 | 0.99917 | -0.012404 | 0.61395 | 0.29735
54 | 0.99914 | -0.012732 | 0 | 0
55 | 0.99913 | -0.01265 | 0 | 0
56 | 0.99904 | -0.013159 | 0 | 0
57 | 0.99913 | -0.012639 | 0.14432 | 0.069897
58 | 0.99904 | -0.013153 | 0.070218 | 0.034008
59 | 0.99902 | -0.012979 | 0 | 0
60 | 0.99902 | -0.013239 | 0.096041 | 0.046515
61 | 0.99901 | -0.012934 | 0 | 0
62 | 0.99902 | -0.012964 | 0.13397 | 0.064883
63 | 0.99873 | 0.00019696 | 0.26752 | 0.12956
64 | 0.99866 | -0.00022931 | 0.33823 | 0.16381
65 | 0.99872 | 0.0001232 | 0.099716 | 0.048295
66 | 0.99865 | -0.00014336 | 0 | 0
67 | 0.99943 | -0.0012267 | 0.14998 | 0.072638
68 | 0.99922 | -0.0026022 | 0 | 0
69 | 0.99951 | -0.0019757 | 0 | 0
70 | 0.99845 | -0.021949 | 0.40135 | 0.19438
71 | 0.99846 | -0.02193 | 0 | 0
72 | 0.99843 | -0.023489 | 0.06816 | 0.033011
73 | 0.99854 | -0.021608 | 0 | 0
74 | 0.99833 | -0.028897 | 0 | 0
75 | 0.99835 | -0.025238 | 0 | 0
76 | 0.99829 | -0.029058 | 0.16282 | 0.078857
77 | 0.99833 | -0.028899 | 0 | 0
78 | 0.99834 | -0.025067 | 0.097693 | 0.047315
79 | 0.99854 | -0.021584 | 0.16488 | 0.079857
80 | 0.99821 | -0.033721 | 0.12987 | 0.0629
81 | 0.99867 | -0.014697 | 0.11732 | 0.05682
82 | 0.99854 | -0.021551 | 0 | 0
83 | 0.9987 | -0.014561 | 0 | 0
84 | 0.99935 | 0.0016177 | 0.37521 | 0.18172
85 | 0.99937 | 0.0017493 | 0 | 0
86 | 0.9994 | 0.0014857 | 0 | 0
87 | 0.99939 | 0.0015045 | 0 | 0
88 | 0.99939 | 0.0015247 | 0.074396 | 0.036032
89 | 0.99941 | 0.0013633 | 0.070371 | 0.034082
90 | 0.99862 | 0.0001638 | 0 | 0
91 | 0.99862 | 0.00021587 | 0.39784 | 0.19268
92 | 0.99943 | 0.0011936 | 0 | 0
93 | 0.99855 | -0.012531 | 0.33583 | 0.16265
94 | 0.99857 | -0.012375 | 0.14619 | 0.070803
95 | 0.99944 | 0.0011282 | 0.097982 | 0.047455
96 | 0.99944 | 0.0011231 | 0 | 0
97 | 0.99942 | 0.0012766 | 0 | 0
98 | 0.99941 | 0.0013583 | 0.3178 | 0.15392
99 | 0.99825 | -0.028111 | 0.36911 | 0.17877
100 | 0.99825 | -0.028136 | 0 | 0
101 | 0.9982 | -0.027641 | 0 | 0
102 | 0.99833 | -0.028833 | 0.17435 | 0.084443
103 | 0.99833 | -0.028907 | 0 | 0
104 | 0.99833 | -0.028899 | 0.11209 | 0.054289
105 | 0.99818 | -0.027537 | 0.22793 | 0.11039
106 | 0.99886 | -0.013911 | 0 | 0
107 | 0.9989 | -0.013742 | 0 | 0
108 | 0.99886 | -0.013898 | 0.079834 | 0.038666
109 | 0.99882 | -0.01405 | 0 | 0
110 | 0.99892 | -0.013645 | 0.08444 | 0.040896
111 | 0.99879 | -0.012761 | 0 | 0
112 | 0.99879 | -0.012754 | 0.14355 | 0.069525
113 | 0.99873 | -0.0122 | 0 | 0
114 | 0.99817 | -0.02738 | 0.14549 | 0.070462
115 | 0.99863 | -0.012865 | 0.12805 | 0.062016
116 | 0.99873 | -0.012185 | 0.082046 | 0.039737
117 | 0.99944 | 0.0010772 | 0.1336 | 0.064705
118 | 0.99946 | 0.00089171 | 0 | 0
119 | 0.99966 | -0.001373 | 0 | 0
120 | 0.99963 | -0.0014997 | 0.19054 | 0.092281
121 | 0.9997 | -0.0012319 | 0 | 0
122 | 0.99957 | -0.0017502 | 0 | 0
123 | 0.9996 | -0.00039795 | 0 | 0
124 | 0.99974 | -0.0010679 | 0.14381 | 0.069649
125 | 0.99952 | -0.0019288 | 0.27889 | 0.13507
126 | 0.99956 | -1.0784e-05 | 0.085838 | 0.041573
127 | 0.99957 | -0.00010982 | 0 | 0
128 | 0.99981 | -0.00078607 | 0 | 0
129 | 0.99956 | 2.179e-05 | 0.30468 | 0.14756
130 | 0.99957 | -0.00010166 | 0.41893 | 0.2029
131 | 0.99997 | -0.00013723 | 0 | 0
132 | 0.99901 | -0.013292 | 0 | 0
133 | 0.99901 | -0.012911 | 0.082774 | 0.040089
134 | 0.99942 | -0.0021314 | 0.14595 | 0.070686
135 | 0.9986 | -0.014474 | 0.39117 | 0.18945
136 | 0.99865 | -0.014126 | 0 | 0
137 | 0.99882 | -0.014014 | 0.32802 | 0.15887
138 | 0.9985 | -0.021615 | 0.29685 | 0.14377
139 | 0.99853 | -0.021437 | 0.083557 | 0.040469
140 | 0.99827 | -0.025482 | 0.081985 | 0.039707
141 | 0.9983 | -0.025311 | 0.29336 | 0.14208
142 | 0.99859 | -0.012536 | 0.074522 | 0.036093
143 | 0.99861 | -0.01271 | 0 | 0
144 | 0.99862 | -0.012833 | 0.099445 | 0.048163
145 | 0.99997 | -0.00013416 | 0.083239 | 0.040315
146 | 1 | 0 | -17.6423 | -8.3566
147 | 0.99998 | 0.00019806 | 0.48565 | 0.23521
148 | 0.99895 | -0.01352 | 0 | 0
149 | 0.9989 | -0.013086 | 0 | 0
150 | 0.99888 | -0.012846 | 0.4065 | 0.19688
151 | 0.99806 | -0.034325 | 0.72307 | 0.3502
152 | 0.99954 | 0.00020126 | 0.19359 | 0.093761
153 | 0.99948 | 0.00071071 | 0 | 0
154 | 0.99947 | 0.0008034 | 0.085152 | 0.041241
155 | 0.99745 | -0.029484 | 0.16536 | 0.080087
156 | 0.99816 | -0.027318 | 0.13734 | 0.066517
157 | 0.99948 | -0.0020704 | 0.18298 | 0.08862
158 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -1.2287 | -0.57441 | 1.2287 | 0.57423 | 1.5683e-05 | -0.00017682 | 0.039235 | 0.039232 | 0.039235 | 0.99794 | -0.033674 | 0.99795 | -0.033776 | 17.8339
1 | 0.91731 | 0.42361 | -0.9173 | -0.42394 | 1.6366e-05 | -0.0003363 | 0.029228 | 0.029232 | 0.029232 | 0.99794 | -0.033674 | 0.99792 | -0.033535 | 13.2874
2 | -1.2287 | -0.57423 | 1.2287 | 0.57397 | 2.3726e-05 | -0.00026755 | 0.039232 | 0.039229 | 0.039232 | 0.99795 | -0.033776 | 0.99797 | -0.033931 | 17.8329
3 | 0.9173 | 0.42394 | -0.91722 | -0.42555 | 7.8382e-05 | -0.0016092 | 0.029232 | 0.029252 | 0.029252 | 0.99792 | -0.033535 | 0.99784 | -0.032864 | 13.2964
4 | -1.2287 | -0.57397 | 1.2288 | 0.5733 | 5.8976e-05 | -0.0006653 | 0.039229 | 0.039221 | 0.039229 | 0.99797 | -0.033931 | 0.99801 | -0.034316 | 17.8314
5 | 0.077316 | 0.034922 | -0.077315 | -0.037445 | 8.641e-07 | -0.0025228 | 0.0024543 | 0.0024853 | 0.0024853 | 0.99784 | -0.032864 | 0.99783 | -0.032773 | 1.1297
6 | 0.8399 | 0.39063 | -0.83969 | -0.39578 | 0.00021078 | -0.0051506 | 0.026798 | 0.026862 | 0.026862 | 0.99784 | -0.032864 | 0.99761 | -0.03084 | 12.2099
7 | -1.6739 | -0.7878 | 1.6739 | 0.78483 | 4.2153e-05 | -0.0029609 | 0.053507 | 0.05347 | 0.053507 | 0.9981 | -0.034165 | 0.99813 | -0.034054 | 8.3866
8 | 1.4762 | 0.69204 | -1.4762 | -0.69202 | 1.1691e-05 | 1.1156e-05 | 0.047153 | 0.047154 | 0.047154 | 0.9981 | -0.034165 | 0.99809 | -0.034991 | 7.3106
9 | -2.6394 | -1.2514 | 2.6394 | 1.2509 | 1.58e-05 | -0.0004396 | 0.084481 | 0.084476 | 0.084481 | 0.99813 | -0.034054 | 0.99814 | -0.034029 | 13.2416
10 | 0.8065 | 0.38952 | -0.80648 | -0.38953 | 1.7218e-05 | -1.5301e-05 | 0.025903 | 0.025904 | 0.025904 | 0.99813 | -0.034054 | 0.9981 | -0.03471 | 7.4011
11 | 1.3705 | 0.64083 | -1.3704 | -0.64174 | 0.00010167 | -0.00091557 | 0.043757 | 0.043768 | 0.043768 | 0.99809 | -0.034991 | 0.99802 | -0.034393 | 19.8947
12 | -2.6394 | -1.2509 | 2.6395 | 1.2494 | 5.5931e-05 | -0.0015567 | 0.084476 | 0.084456 | 0.084476 | 0.99814 | -0.034029 | 0.99816 | -0.033941 | 13.2407
13 | 0.7231 | 0.34915 | -0.72308 | -0.34993 | 2.3921e-05 | -0.00078271 | 0.023224 | 0.023234 | 0.023234 | 0.9981 | -0.03471 | 0.99807 | -0.034423 | 10.561
14 | 1.3704 | 0.64174 | -1.3703 | -0.64186 | 1.3188e-05 | -0.00011872 | 0.043768 | 0.04377 | 0.04377 | 0.99802 | -0.034393 | 0.99801 | -0.034316 | 19.8954
15 | 0.3226 | 0.15562 | -0.3226 | -0.15624 | 3.7849e-06 | -0.00062507 | 0.010366 | 0.010374 | 0.010374 | 0.99742 | -0.029157 | 0.99741 | -0.029056 | 4.7155
16 | -0.3226 | -0.15562 | 0.32262 | 0.15267 | 1.777e-05 | -0.0029475 | 0.010366 | 0.010329 | 0.010366 | 0.99742 | -0.029157 | 0.99747 | -0.029623 | 4.712
17 | 0.24292 | 0.11616 | -0.24292 | -0.11661 | 1.5164e-06 | -0.00044356 | 0.0077928 | 0.0077984 | 0.0077984 | 0.99747 | -0.029623 | 0.99746 | -0.02957 | 3.5447
18 | -0.56554 | -0.26883 | 0.56562 | 0.26429 | 8.4042e-05 | -0.0045435 | 0.018122 | 0.018066 | 0.018122 | 0.99747 | -0.029623 | 0.99761 | -0.03084 | 8.2374
19 | 0.27407 | 0.13149 | -0.27406 | -0.13273 | 5.4131e-06 | -0.0012414 | 0.0087962 | 0.0088118 | 0.0088118 | 0.99761 | -0.03084 | 0.99759 | -0.030669 | 4.0054
20 | 0.16536 | 0.079043 | -0.16536 | -0.079403 | 5.6968e-07 | -0.00035981 | 0.0053043 | 0.0053088 | 0.0053088 | 0.99746 | -0.02957 | 0.99746 | -0.02954 | 2.4131
21 | 0.091075 | 0.043764 | -0.091075 | -0.04411 | 1.6598e-07 | -0.00034579 | 0.0029223 | 0.0029266 | 0.0029266 | 0.99816 | -0.033941 | 0.99816 | -0.033925 | 1.3303
22 | -2.7306 | -1.2931 | 2.7306 | 1.2916 | 5.8585e-05 | -0.0015219 | 0.087378 | 0.087359 | 0.087378 | 0.99816 | -0.033941 | 0.99818 | -0.03385 | 13.6957
23 | 0.72308 | 0.34993 | -0.72307 | -0.3502 | 8.1233e-06 | -0.00026564 | 0.023234 | 0.023238 | 0.023238 | 0.99807 | -0.034423 | 0.99806 | -0.034325 | 10.5625
24 | -2.7306 | -1.2916 | 2.7307 | 1.2894 | 8.3075e-05 | -0.0021594 | 0.087359 | 0.087332 | 0.087359 | 0.99818 | -0.03385 | 0.99821 | -0.033721 | 13.6926
25 | 0.16536 | 0.079403 | -0.16536 | -0.080087 | 1.0852e-06 | -0.00068374 | 0.0053088 | 0.0053174 | 0.0053174 | 0.99746 | -0.02954 | 0.99745 | -0.029484 | 2.417
26 | -0.30221 | -0.14637 | 0.30221 | 0.14587 | 2.6158e-06 | -0.00049613 | 0.0096997 | 0.0096935 | 0.0096997 | 0.99934 | 0.00198 | 0.99935 | 0.0019049 | 4.409
27 | -0.30221 | -0.14587 | 0.30223 | 0.14302 | 1.4979e-05 | -0.0028536 | 0.0096935 | 0.0096579 | 0.0096935 | 0.99935 | 0.0019049 | 0.9994 | 0.0014857 | 4.4061
28 | 10.2567 | 4.8289 | -10.2566 | -4.8302 | 0.00018666 | -0.0013086 | 0.32748 | 0.32749 | 0.32749 | 0.99934 | -0.0080217 | 0.99932 | -0.0081004 | 25.6657
29 | -10.5808 | -4.9858 | 10.5813 | 4.9873 | 0.0005838 | 0.0014908 | 0.33788 | 0.33788 | 0.33788 | 0.99934 | -0.0080217 | 0.99944 | -0.0022848 | 26.192
30 | 10.125 | 4.7665 | -10.1247 | -4.7681 | 0.00022596 | -0.0016288 | 0.32327 | 0.32329 | 0.32329 | 0.99932 | -0.0081004 | 0.99929 | -0.008197 | 25.3365
31 | 0.42094 | 0.20264 | -0.42094 | -0.20294 | 3.0464e-06 | -0.0002979 | 0.013494 | 0.013498 | 0.013498 | 0.99944 | -0.0022848 | 0.99943 | -0.0022225 | 6.1353
32 | -11.0023 | -5.19 | 11.0028 | 5.1871 | 0.00047235 | -0.0028428 | 0.35137 | 0.35133 | 0.35137 | 0.99944 | -0.0022848 | 0.99948 | -0.0021006 | 27.5368
33 | 10.1247 | 4.7681 | -10.1244 | -4.7706 | 0.0003391 | -0.0024438 | 0.32329 | 0.32333 | 0.32333 | 0.99929 | -0.008197 | 0.99926 | -0.0083415 | 25.339
34 | 0.26586 | 0.12783 | -0.26586 | -0.12833 | 2.0646e-06 | -0.00050704 | 0.0085206 | 0.0085269 | 0.0085269 | 0.99943 | -0.0022225 | 0.99942 | -0.0021557 | 3.8759
35 | 0.18298 | 0.08829 | -0.18298 | -0.08862 | 6.3709e-07 | -0.00033015 | 0.0058679 | 0.005872 | 0.005872 | 0.99948 | -0.0021006 | 0.99948 | -0.0020704 | 2.6691
36 | -11.1857 | -5.2754 | 11.1861 | 5.2735 | 0.00032549 | -0.0018897 | 0.3572 | 0.35717 | 0.3572 | 0.99948 | -0.0021006 | 0.99951 | -0.0019757 | 27.9936
37 | 0.26812 | 0.1296 | -0.26812 | -0.12986 | 1.0891e-06 | -0.00026237 | 0.0086032 | 0.0086065 | 0.0086065 | 0.99926 | -0.0083415 | 0.99926 | -0.0083062 | 3.912
38 | 9.5683 | 4.5015 | -9.5679 | -4.5005 | 0.00038534 | 0.00097235 | 0.30548 | 0.30548 | 0.30548 | 0.99926 | -0.0083415 | 0.99919 | -0.012533 | 23.6806
39 | 0.61395 | 0.29693 | -0.61395 | -0.29708 | 3.3546e-06 | -0.00015328 | 0.019703 | 0.019705 | 0.019705 | 0.99919 | -0.012533 | 0.99918 | -0.012486 | 8.957
40 | 8.9539 | 4.2036 | -8.9538 | -4.2049 | 0.00013713 | -0.0012861 | 0.28578 | 0.28579 | 0.28579 | 0.99919 | -0.012533 | 0.99917 | -0.012601 | 22.3976
41 | 0.61395 | 0.29708 | -0.61395 | -0.29735 | 5.7773e-06 | -0.0002639 | 0.019705 | 0.019709 | 0.019709 | 0.99918 | -0.012486 | 0.99917 | -0.012404 | 8.9585
42 | 8.6272 | 4.0467 | -8.627 | -4.0493 | 0.00025629 | -0.0026009 | 0.27531 | 0.27535 | 0.27535 | 0.99917 | -0.012601 | 0.99914 | -0.012732 | 21.5788
43 | -1.7127 | -0.82412 | 1.7128 | 0.82373 | 6.8059e-05 | -0.00038249 | 0.054926 | 0.054921 | 0.054926 | 0.99895 | -0.00014188 | 0.99899 | -0.00048285 | 24.9663
44 | 1.5037 | 0.72289 | -1.5037 | -0.72342 | 7.1477e-05 | -0.00052744 | 0.048215 | 0.048222 | 0.048222 | 0.99895 | -0.00014188 | 0.99891 | 0.00026575 | 21.9191
45 | -1.9612 | -0.94332 | 1.9613 | 0.9429 | 0.0001004 | -0.0004234 | 0.062888 | 0.062882 | 0.062888 | 0.99899 | -0.00048285 | 0.99904 | -0.00092174 | 28.5854
46 | 0.24842 | 0.11959 | -0.24842 | -0.11981 | 7.9834e-07 | -0.00022417 | 0.0079671 | 0.0079699 | 0.0079699 | 0.99899 | -0.00048285 | 0.99899 | -0.00045517 | 3.6227
47 | 1.5037 | 0.72342 | -1.5036 | -0.72362 | 2.7341e-05 | -0.0002017 | 0.048222 | 0.048225 | 0.048225 | 0.99891 | 0.00026575 | 0.99889 | 0.00042187 | 21.9203
48 | -1.9613 | -0.9429 | 1.9614 | 0.94277 | 3.0152e-05 | -0.00012718 | 0.062882 | 0.062881 | 0.062882 | 0.99904 | -0.00092174 | 0.99905 | -0.0010534 | 28.5828
49 | 0.24842 | 0.11981 | -0.24842 | -0.12032 | 1.7916e-06 | -0.00050249 | 0.0079699 | 0.0079762 | 0.0079762 | 0.99899 | -0.00045517 | 0.99898 | -0.00039264 | 3.6256
50 | 1.1722 | 0.56442 | -1.1721 | -0.5644 | 0.00012106 | 1.8581e-05 | 0.037598 | 0.037599 | 0.037599 | 0.99889 | 0.00042187 | 0.99878 | -0.00027388 | 17.9042
51 | 0.24811 | 0.11883 | -0.24811 | -0.11887 | 3.2219e-06 | -3.2058e-05 | 0.0079503 | 0.0079507 | 0.0079507 | 0.99889 | 0.00042187 | 0.99888 | 0.0003327 | 3.786
52 | -0.11991 | -0.058075 | 0.11991 | 0.057982 | 7.6876e-08 | -9.2768e-05 | 0.0038483 | 0.0038471 | 0.0038483 | 0.99942 | -0.0021501 | 0.99942 | -0.0021557 | 1.7492
53 | 0.14595 | 0.070353 | -0.14595 | -0.070686 | 4.0887e-07 | -0.00033309 | 0.0046798 | 0.004684 | 0.004684 | 0.99942 | -0.0021557 | 0.99942 | -0.0021314 | 2.1291
54 | 0.24811 | 0.11887 | -0.2481 | -0.12011 | 4.4213e-06 | -0.0012443 | 0.0079507 | 0.0079663 | 0.0079663 | 0.99888 | 0.0003327 | 0.99886 | 0.000486 | 3.6211
55 | 0.2481 | 0.12011 | -0.2481 | -0.12016 | 5.004e-06 | -4.9572e-05 | 0.0079663 | 0.007967 | 0.007967 | 0.99886 | 0.000486 | 0.99884 | 0.00035293 | 3.7938
56 | 1.1034 | 0.53117 | -1.1034 | -0.53148 | 2.2533e-05 | -0.00031416 | 0.035395 | 0.035399 | 0.035399 | 0.99878 | -0.00027388 | 0.99876 | -9.8268e-05 | 16.0905
57 | -2.326 | -1.1194 | 2.3262 | 1.1189 | 0.00016661 | -0.00048523 | 0.074588 | 0.074582 | 0.074588 | 0.99905 | -0.0010534 | 0.99912 | -0.0016683 | 33.9039
58 | -2.6411 | -1.2714 | 2.6414 | 1.2708 | 0.00028721 | -0.00062985 | 0.084691 | 0.084682 | 0.084691 | 0.99912 | -0.0016683 | 0.99922 | -0.0026022 | 38.4959
59 | 1.1034 | 0.53148 | -1.1034 | -0.53201 | 3.7811e-05 | -0.00052698 | 0.035399 | 0.035406 | 0.035406 | 0.99876 | -9.8268e-05 | 0.99873 | 0.00019696 | 16.0935
60 | 0.14432 | 0.068585 | -0.14432 | -0.069738 | 1.3809e-06 | -0.0011527 | 0.0046167 | 0.0046311 | 0.0046311 | 0.99914 | -0.012732 | 0.99913 | -0.01265 | 2.105
61 | 8.4827 | 3.9807 | -8.4818 | -3.9894 | 0.00082698 | -0.0086909 | 0.27073 | 0.27084 | 0.27084 | 0.99914 | -0.012732 | 0.99904 | -0.013159 | 21.2259
62 | 0.14432 | 0.069738 | -0.14432 | -0.069897 | 1.9122e-07 | -0.00015906 | 0.0046311 | 0.0046331 | 0.0046331 | 0.99913 | -0.01265 | 0.99913 | -0.012639 | 2.1059
63 | 0.070218 | 0.033856 | -0.070218 | -0.034008 | 4.3155e-08 | -0.00015167 | 0.0022525 | 0.0022544 | 0.0022544 | 0.99904 | -0.013159 | 0.99904 | -0.013153 | 1.0247
64 | 0.21675 | 0.10126 | -0.21674 | -0.10304 | 4.7592e-06 | -0.0017707 | 0.0069128 | 0.0069346 | 0.0069346 | 0.99904 | -0.013159 | 0.99902 | -0.012979 | 3.1521
65 | 8.1949 | 3.8543 | -8.1947 | -3.856 | 0.00015088 | -0.0017036 | 0.26168 | 0.2617 | 0.2617 | 0.99904 | -0.013159 | 0.99902 | -0.013239 | 20.5093
66 | 0.082775 | 0.038375 | -0.082774 | -0.039541 | 4.5673e-07 | -0.0011665 | 0.0026364 | 0.0026507 | 0.0026507 | 0.99902 | -0.012979 | 0.99901 | -0.012934 | 1.2049
67 | 0.13397 | 0.064661 | -0.13397 | -0.064883 | 2.3033e-07 | -0.0002223 | 0.0042984 | 0.0043012 | 0.0043012 | 0.99902 | -0.012979 | 0.99902 | -0.012964 | 1.9551
68 | 8.0987 | 3.8095 | -8.0986 | -3.8106 | 0.00010012 | -0.0011587 | 0.25862 | 0.25863 | 0.25863 | 0.99902 | -0.013239 | 0.99901 | -0.013292 | 20.2688
69 | 0.082774 | 0.039541 | -0.082774 | -0.040089 | 2.1632e-07 | -0.00054805 | 0.0026507 | 0.0026576 | 0.0026576 | 0.99901 | -0.012934 | 0.99901 | -0.012911 | 1.208
70 | 0.73614 | 0.35422 | -0.73609 | -0.35425 | 4.6468e-05 | -2.6589e-05 | 0.023613 | 0.023613 | 0.023613 | 0.99873 | 0.00019696 | 0.99866 | -0.00022931 | 11.2445
71 | 0.099718 | 0.048223 | -0.099716 | -0.048295 | 1.1126e-06 | -7.1824e-05 | 0.0032016 | 0.0032025 | 0.0032025 | 0.99873 | 0.00019696 | 0.99872 | 0.0001232 | 1.525
72 | 0.39786 | 0.19044 | -0.39786 | -0.19088 | 4.0194e-06 | -0.00043962 | 0.01275 | 0.012756 | 0.012756 | 0.99866 | -0.00022931 | 0.99865 | -0.00014336 | 5.7981
73 | 0.39786 | 0.19088 | -0.39785 | -0.19242 | 1.4198e-05 | -0.0015498 | 0.012756 | 0.012775 | 0.012775 | 0.99865 | -0.00014336 | 0.99862 | 0.0001638 | 5.8069
74 | 2.6419 | 1.2711 | -2.6414 | -1.2708 | 0.00053767 | 0.00028661 | 0.084681 | 0.084682 | 0.084682 | 0.99943 | -0.0012267 | 0.99922 | -0.0026022 | 40.3248
75 | -2.7919 | -1.3437 | 2.7921 | 1.3432 | 0.00024357 | -0.00047111 | 0.089495 | 0.089488 | 0.089495 | 0.99943 | -0.0012267 | 0.99951 | -0.0019757 | 40.6794
76 | -13.9782 | -6.6168 | 13.9784 | 6.6162 | 0.00015623 | -0.00054836 | 0.44666 | 0.44665 | 0.44666 | 0.99951 | -0.0019757 | 0.99952 | -0.0019288 | 35.0046
77 | -0.94261 | -0.45531 | 0.94262 | 0.45429 | 4.6211e-06 | -0.0010205 | 0.030266 | 0.030253 | 0.030266 | 0.99845 | -0.021949 | 0.99846 | -0.02193 | 4.7439
78 | 0.54126 | 0.26093 | -0.54125 | -0.26101 | 8.1245e-06 | -8.2052e-05 | 0.017373 | 0.017374 | 0.017374 | 0.99845 | -0.021949 | 0.99843 | -0.023489 | 2.6936
79 | -5.133 | -2.438 | 5.1334 | 2.4263 | 0.00039627 | -0.011692 | 0.16429 | 0.16415 | 0.16429 | 0.99846 | -0.02193 | 0.99854 | -0.021608 | 12.8757
80 | 4.1904 | 1.9837 | -4.1901 | -1.9832 | 0.00028147 | 0.00051504 | 0.13404 | 0.13405 | 0.13405 | 0.99846 | -0.02193 | 0.99833 | -0.028897 | 10.3911
81 | 0.47309 | 0.228 | -0.47307 | -0.22813 | 2.6903e-05 | -0.00012842 | 0.015184 | 0.015186 | 0.015186 | 0.99843 | -0.023489 | 0.99835 | -0.025238 | 4.3389
82 | -5.1334 | -2.4263 | 5.1334 | 2.4255 | 2.8364e-05 | -0.0008378 | 0.16415 | 0.16414 | 0.16415 | 0.99854 | -0.021608 | 0.99854 | -0.021584 | 12.8642
83 | 3.0237 | 1.4291 | -3.0235 | -1.4315 | 0.00011524 | -0.0024317 | 0.096704 | 0.096735 | 0.096735 | 0.99833 | -0.028897 | 0.99829 | -0.029058 | 15.1623
84 | 1.1664 | 0.55414 | -1.1664 | -0.5545 | 6.2325e-07 | -0.00036198 | 0.037341 | 0.037345 | 0.037345 | 0.99833 | -0.028897 | 0.99833 | -0.028899 | 2.9267
85 | 0.47307 | 0.22813 | -0.47306 | -0.22885 | 9.3769e-06 | -0.00072156 | 0.015186 | 0.015195 | 0.015195 | 0.99835 | -0.025238 | 0.99834 | -0.025067 | 6.907
86 | 2.8607 | 1.3526 | -2.8606 | -1.3523 | 0.00012855 | 0.00028644 | 0.091504 | 0.091505 | 0.091505 | 0.99829 | -0.029058 | 0.99821 | -0.033721 | 14.1868
87 | 0.17435 | 0.083687 | -0.17435 | -0.084443 | 1.3289e-06 | -0.00075578 | 0.0055922 | 0.0056017 | 0.0056017 | 0.99833 | -0.028899 | 0.99833 | -0.028833 | 2.5462
88 | 0.11209 | 0.051006 | -0.11209 | -0.054155 | 1.9914e-07 | -0.0031485 | 0.0035611 | 0.0035997 | 0.0035997 | 0.99833 | -0.028899 | 0.99833 | -0.028907 | 0.56422
89 | 0.87998 | 0.41981 | -0.8799 | -0.42156 | 7.9387e-05 | -0.0017553 | 0.028193 | 0.028215 | 0.028215 | 0.99833 | -0.028899 | 0.99825 | -0.028136 | 12.8249
90 | 0.37537 | 0.18153 | -0.37535 | -0.18159 | 1.3818e-05 | -5.4818e-05 | 0.012057 | 0.012057 | 0.012057 | 0.99834 | -0.025067 | 0.9983 | -0.025311 | 5.7416
91 | -5.6787 | -2.6887 | 5.6791 | 2.6896 | 0.00037723 | 0.00083782 | 0.18164 | 0.18164 | 0.18164 | 0.99854 | -0.021584 | 0.99867 | -0.014697 | 14.0807
92 | 0.38042 | 0.18342 | -0.38042 | -0.1836 | 1.4839e-06 | -0.00017704 | 0.012209 | 0.012212 | 0.012212 | 0.99854 | -0.021584 | 0.99854 | -0.021551 | 5.5508
93 | -5.7964 | -2.7464 | 5.7966 | 2.7421 | 0.00018705 | -0.0043101 | 0.18541 | 0.18535 | 0.18541 | 0.99867 | -0.014697 | 0.9987 | -0.014561 | 14.5304
94 | 0.38042 | 0.1836 | -0.38042 | -0.18419 | 4.9671e-06 | -0.00059213 | 0.012212 | 0.012219 | 0.012219 | 0.99854 | -0.021551 | 0.99853 | -0.021437 | 5.5542
95 | -6.1878 | -2.9292 | 6.1885 | 2.9142 | 0.0007428 | -0.014987 | 0.19789 | 0.1977 | 0.19789 | 0.9987 | -0.014561 | 0.99882 | -0.01405 | 15.5084
96 | 0.39121 | 0.18714 | -0.39119 | -0.18938 | 1.982e-05 | -0.0022391 | 0.012535 | 0.012563 | 0.012563 | 0.9987 | -0.014561 | 0.99865 | -0.014126 | 5.7105
97 | -0.37521 | -0.18172 | 0.37521 | 0.18169 | 7.4867e-06 | -2.9857e-05 | 0.012043 | 0.012042 | 0.012043 | 0.99935 | 0.0016177 | 0.99937 | 0.0017493 | 5.7346
98 | -0.37521 | -0.18169 | 0.37523 | 0.18028 | 1.1458e-05 | -0.00141 | 0.012042 | 0.012024 | 0.012042 | 0.99937 | 0.0017493 | 0.9994 | 0.0014857 | 5.4737
99 | -0.75185 | -0.35824 | 0.75186 | 0.35791 | 1.0975e-05 | -0.00033558 | 0.024056 | 0.024052 | 0.024056 | 0.9994 | 0.0014857 | 0.99941 | 0.0013633 | 10.9347
100 | 0.074396 | 0.034947 | -0.074396 | -0.035479 | 1.6841e-07 | -0.00053217 | 0.0023742 | 0.0023808 | 0.0023808 | 0.9994 | 0.0014857 | 0.99939 | 0.0015045 | 1.0822
101 | 0.074396 | 0.035479 | -0.074396 | -0.036032 | 1.7578e-07 | -0.0005523 | 0.0023808 | 0.0023877 | 0.0023877 | 0.99939 | 0.0015045 | 0.99939 | 0.0015247 | 1.0853
102 | -0.82223 | -0.39199 | 0.82225 | 0.39157 | 1.6614e-05 | -0.0004239 | 0.026311 | 0.026305 | 0.026311 | 0.99941 | 0.0013633 | 0.99943 | 0.0011936 | 11.9594
103 | 0.39785 | 0.19242 | -0.39784 | -0.19268 | 2.3814e-06 | -0.00025947 | 0.012775 | 0.012779 | 0.012779 | 0.99862 | 0.0001638 | 0.99862 | 0.00021587 | 5.8084
104 | -0.82225 | -0.39157 | 0.82229 | 0.39035 | 4.7509e-05 | -0.0012132 | 0.026305 | 0.02629 | 0.026305 | 0.99943 | 0.0011936 | 0.99948 | 0.00071071 | 11.957
105 | -0.33583 | -0.16265 | 0.33584 | 0.16261 | 7.9229e-06 | -4.0528e-05 | 0.010787 | 0.010787 | 0.010787 | 0.99855 | -0.012531 | 0.99857 | -0.012375 | 5.1368
106 | -0.48203 | -0.23341 | 0.48204 | 0.23275 | 8.9271e-06 | -0.00066188 | 0.015483 | 0.015474 | 0.015483 | 0.99857 | -0.012375 | 0.99859 | -0.012536 | 7.0375
107 | -0.097982 | -0.047455 | 0.097983 | 0.047352 | 5.7207e-08 | -0.00010334 | 0.0031446 | 0.0031433 | 0.0031446 | 0.99944 | 0.0011282 | 0.99944 | 0.0011231 | 1.4293
108 | -0.41579 | -0.19978 | 0.4158 | 0.19956 | 2.2343e-06 | -0.00022422 | 0.013324 | 0.013321 | 0.013324 | 0.99944 | 0.0011231 | 0.99944 | 0.0010772 | 6.0564
109 | 0.31781 | 0.15243 | -0.3178 | -0.15341 | 5.6815e-06 | -0.00097637 | 0.010181 | 0.010193 | 0.010193 | 0.99944 | 0.0011231 | 0.99942 | 0.0012766 | 4.6332
110 | 0.3178 | 0.15341 | -0.3178 | -0.15392 | 2.9912e-06 | -0.00051309 | 0.010193 | 0.010199 | 0.010199 | 0.99942 | 0.0012766 | 0.99941 | 0.0013583 | 4.6361
111 | -0.36911 | -0.17877 | 0.36911 | 0.17863 | 1.0523e-06 | -0.00013304 | 0.01186 | 0.011858 | 0.01186 | 0.99825 | -0.028111 | 0.99825 | -0.028136 | 5.3909
112 | 0.51079 | 0.24293 | -0.51076 | -0.24491 | 2.9925e-05 | -0.0019815 | 0.016357 | 0.016381 | 0.016381 | 0.99825 | -0.028136 | 0.9982 | -0.027641 | 7.4461
113 | 0.51076 | 0.24491 | -0.51076 | -0.24533 | 6.2536e-06 | -0.00041329 | 0.016381 | 0.016387 | 0.016387 | 0.9982 | -0.027641 | 0.99818 | -0.027537 | 7.4485
114 | 0.11209 | 0.054155 | -0.11209 | -0.054289 | 9.7765e-08 | -0.00013437 | 0.0035997 | 0.0036014 | 0.0036014 | 0.99833 | -0.028907 | 0.99833 | -0.028899 | 1.637
115 | 0.28283 | 0.13494 | -0.28283 | -0.13606 | 5.2079e-06 | -0.0011266 | 0.0090627 | 0.0090768 | 0.0090768 | 0.99818 | -0.027537 | 0.99817 | -0.02738 | 4.1258
116 | -6.5966 | -3.1074 | 6.5969 | 3.1029 | 0.00025739 | -0.0045596 | 0.21074 | 0.21068 | 0.21074 | 0.99886 | -0.013911 | 0.9989 | -0.013742 | 16.5156
117 | 0.079835 | 0.038349 | -0.079834 | -0.038666 | 1.1661e-07 | -0.00031706 | 0.0025596 | 0.0025636 | 0.0025636 | 0.99886 | -0.013911 | 0.99886 | -0.013898 | 1.1653
118 | 6.5168 | 3.0691 | -6.5166 | -3.0729 | 0.00020967 | -0.0038068 | 0.20818 | 0.20823 | 0.20823 | 0.99886 | -0.013911 | 0.99882 | -0.01405 | 16.3188
119 | -7.6068 | -3.5863 | 7.607 | 3.584 | 0.00017062 | -0.0022485 | 0.24304 | 0.24301 | 0.24304 | 0.9989 | -0.013742 | 0.99892 | -0.013645 | 19.0469
120 | 1.0099 | 0.48341 | -1.0098 | -0.48535 | 0.00011623 | -0.0019448 | 0.032357 | 0.032382 | 0.032382 | 0.9989 | -0.013742 | 0.99879 | -0.012761 | 14.7191
121 | 0.32802 | 0.15865 | -0.32802 | -0.15887 | 1.3588e-06 | -0.00021814 | 0.010531 | 0.010534 | 0.010534 | 0.99882 | -0.01405 | 0.99882 | -0.014014 | 4.7881
122 | -7.6914 | -3.6249 | 7.6916 | 3.622 | 0.0002242 | -0.002888 | 0.24572 | 0.24568 | 0.24572 | 0.99892 | -0.013645 | 0.99895 | -0.01352 | 19.2571
123 | 0.14355 | 0.069437 | -0.14355 | -0.069525 | 1.0449e-07 | -8.7716e-05 | 0.0046089 | 0.00461 | 0.00461 | 0.99879 | -0.012761 | 0.99879 | -0.012754 | 2.0954
124 | 0.86625 | 0.41592 | -0.8662 | -0.41721 | 5.6672e-05 | -0.0012932 | 0.027773 | 0.02779 | 0.02779 | 0.99879 | -0.012761 | 0.99873 | -0.0122 | 12.6316
125 | 0.78415 | 0.37782 | -0.78407 | -0.37786 | 7.7688e-05 | -3.3355e-05 | 0.025159 | 0.02516 | 0.02516 | 0.99873 | -0.0122 | 0.99863 | -0.012865 | 11.9809
126 | 0.082046 | 0.039386 | -0.082046 | -0.039737 | 1.3637e-07 | -0.00035096 | 0.0026306 | 0.002635 | 0.002635 | 0.99873 | -0.0122 | 0.99873 | -0.012185 | 1.1977
127 | 0.13734 | 0.065601 | -0.13734 | -0.066517 | 9.9927e-07 | -0.0009163 | 0.0044018 | 0.0044133 | 0.0044133 | 0.99817 | -0.02738 | 0.99816 | -0.027318 | 2.006
128 | 0.65602 | 0.31584 | -0.65602 | -0.31594 | 2.4738e-06 | -9.8861e-05 | 0.021047 | 0.021048 | 0.021048 | 0.99863 | -0.012865 | 0.99862 | -0.012833 | 9.5675
129 | -0.54939 | -0.26426 | 0.54941 | 0.26358 | 1.1914e-05 | -0.00068323 | 0.017609 | 0.0176 | 0.017609 | 0.99944 | 0.0010772 | 0.99946 | 0.00089171 | 8.004
130 | -0.54941 | -0.26358 | 0.54941 | 0.26325 | 5.6967e-06 | -0.00032694 | 0.0176 | 0.017596 | 0.0176 | 0.99946 | 0.00089171 | 0.99947 | 0.0008034 | 8.0001
131 | 14.4497 | 6.8373 | -14.4492 | -6.8387 | 0.00043515 | -0.0014146 | 0.46162 | 0.46164 | 0.46164 | 0.99966 | -0.001373 | 0.99963 | -0.0014997 | 36.1789
132 | -14.4497 | -6.8373 | 14.4502 | 6.8357 | 0.00048418 | -0.0015743 | 0.46162 | 0.4616 | 0.46162 | 0.99966 | -0.001373 | 0.9997 | -0.0012319 | 36.1773
133 | 14.2587 | 6.7464 | -14.2578 | -6.7493 | 0.00084897 | -0.0028466 | 0.45553 | 0.45557 | 0.45557 | 0.99963 | -0.0014997 | 0.99957 | -0.0017502 | 35.703
134 | 2.4604 | 1.177 | -2.4601 | -1.1776 | 0.00024193 | -0.00062524 | 0.078758 | 0.078766 | 0.078766 | 0.9997 | -0.0012319 | 0.9996 | -0.00039795 | 35.8029
135 | -16.9105 | -8.0127 | 16.9112 | 8.0112 | 0.00066325 | -0.0014731 | 0.54036 | 0.54033 | 0.54036 | 0.9997 | -0.0012319 | 0.99974 | -0.0010679 | 42.3477
136 | 14.2578 | 6.7493 | -14.2572 | -6.7513 | 0.0006069 | -0.0020344 | 0.45557 | 0.4556 | 0.4556 | 0.99957 | -0.0017502 | 0.99952 | -0.0019288 | 35.7053
137 | 2.0412 | 0.97614 | -2.0411 | -0.9765 | 9.3283e-05 | -0.00036274 | 0.065341 | 0.065346 | 0.065346 | 0.9996 | -0.00039795 | 0.99956 | -1.0784e-05 | 29.7028
138 | 0.41895 | 0.20148 | -0.41893 | -0.20286 | 1.3969e-05 | -0.001379 | 0.013425 | 0.013443 | 0.013443 | 0.9996 | -0.00039795 | 0.99957 | -0.00010982 | 6.1103
139 | -17.055 | -8.0809 | 17.0562 | 8.0784 | 0.0011493 | -0.0024993 | 0.54495 | 0.54491 | 0.54495 | 0.99974 | -0.0010679 | 0.99981 | -0.00078607 | 42.7075
140 | 1.9553 | 0.93493 | -1.9553 | -0.93496 | 7.5234e-06 | -3.2083e-05 | 0.062592 | 0.062592 | 0.062592 | 0.99956 | -1.0784e-05 | 0.99956 | 2.179e-05 | 28.451
141 | 0.41893 | 0.20286 | -0.41893 | -0.2029 | 3.9259e-07 | -3.87e-05 | 0.013443 | 0.013443 | 0.013443 | 0.99957 | -0.00010982 | 0.99957 | -0.00010166 | 6.1105
142 | -17.0562 | -8.0784 | 17.0588 | 8.0726 | 0.0026368 | -0.0057375 | 0.54491 | 0.54482 | 0.54491 | 0.99981 | -0.00078607 | 0.99997 | -0.00013723 | 42.7044
143 | 1.6506 | 0.7874 | -1.6505 | -0.78761 | 3.5168e-05 | -0.00021483 | 0.052815 | 0.052818 | 0.052818 | 0.99956 | 2.179e-05 | 0.99954 | 0.00020126 | 24.0083
144 | -17.142 | -8.1129 | 17.1426 | 8.1117 | 0.00055913 | -0.0012024 | 0.54749 | 0.54747 | 0.54749 | 0.99997 | -0.00013723 | 1 | 0 | 42.9066
145 | 0.083239 | 0.040241 | -0.083239 | -0.040315 | 2.9429e-08 | -7.3696e-05 | 0.0026691 | 0.00267 | 0.00267 | 0.99997 | -0.00013723 | 0.99997 | -0.00013416 | 1.2136
146 | 8.0986 | 3.8106 | -8.0982 | -3.8156 | 0.00042539 | -0.0049212 | 0.25863 | 0.25869 | 0.25869 | 0.99901 | -0.013292 | 0.99895 | -0.01352 | 20.2738
147 | -0.39117 | -0.18945 | 0.39119 | 0.18938 | 2.0656e-05 | -7.4502e-05 | 0.012564 | 0.012563 | 0.012564 | 0.9986 | -0.014474 | 0.99865 | -0.014126 | 5.983
148 | -0.29685 | -0.14377 | 0.29686 | 0.14372 | 7.9743e-06 | -5.3594e-05 | 0.0095359 | 0.0095351 | 0.0095359 | 0.9985 | -0.021615 | 0.99853 | -0.021437 | 4.5409
149 | -0.081985 | -0.039707 | 0.081987 | 0.039506 | 2.1064e-06 | -0.00020157 | 0.0026342 | 0.0026317 | 0.0026342 | 0.99827 | -0.025482 | 0.9983 | -0.025311 | 1.2544
150 | -0.55656 | -0.26884 | 0.55657 | 0.26822 | 1.1224e-05 | -0.00062396 | 0.017868 | 0.01786 | 0.017868 | 0.99859 | -0.012536 | 0.99861 | -0.01271 | 8.1217
151 | -0.55657 | -0.26822 | 0.55658 | 0.26778 | 7.9581e-06 | -0.00044275 | 0.01786 | 0.017854 | 0.01786 | 0.99861 | -0.01271 | 0.99862 | -0.012833 | 8.1182
152 | 0.48566 | 0.2344 | -0.48565 | -0.23521 | 1.1085e-05 | -0.00081423 | 0.015567 | 0.015578 | 0.015578 | 1 | 0 | 0.99998 | 0.00019806 | 7.0807
153 | 0.40653 | 0.19352 | -0.40651 | -0.1957 | 2.0794e-05 | -0.0021814 | 0.013011 | 0.013038 | 0.013038 | 0.99895 | -0.01352 | 0.9989 | -0.013086 | 5.9265
154 | 0.40651 | 0.1957 | -0.4065 | -0.19688 | 1.1268e-05 | -0.0011782 | 0.013038 | 0.013053 | 0.013053 | 0.9989 | -0.013086 | 0.99888 | -0.012846 | 5.9332
155 | 1.457 | 0.69385 | -1.4569 | -0.69455 | 8.8377e-05 | -0.0007006 | 0.046606 | 0.046615 | 0.046615 | 0.99954 | 0.00020126 | 0.99948 | 0.00071071 | 21.1886
156 | 0.63457 | 0.3042 | -0.63456 | -0.30449 | 6.9006e-06 | -0.00029633 | 0.020325 | 0.020329 | 0.020329 | 0.99948 | 0.00071071 | 0.99947 | 0.0008034 | 9.2403

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 17.6423 | 8.3566

## res_load
| p_mw | q_mvar
0 | 0.31137 | 0.1508
1 | 0.19772 | 0.095759
2 | 0.159 | 0.077005
3 | 0.10571 | 0.051197
4 | 0.083379 | 0.040382
5 | 0.14156 | 0.068561
6 | 0.3226 | 0.15624
7 | 0.27406 | 0.13273
8 | 0.077561 | 0.037565
9 | 0.077315 | 0.037445
10 | 0.091075 | 0.04411
11 | 0.30221 | 0.14637
12 | 0.32401 | 0.15693
13 | 0.13159 | 0.06373
14 | 0.15508 | 0.075109
15 | 0.28802 | 0.13949
16 | 0.26812 | 0.12986
17 | 0.32654 | 0.15815
18 | 0.209 | 0.10122
19 | 0.083344 | 0.040366
20 | 0.11991 | 0.058075
21 | 0.2481 | 0.12016
22 | 0.068626 | 0.033237
23 | 0.36467 | 0.17662
24 | 0.24842 | 0.12032
25 | 0.3149 | 0.15251
26 | 0.61395 | 0.29735
27 | 0.14432 | 0.069897
28 | 0.070218 | 0.034008
29 | 0.096041 | 0.046515
30 | 0.13397 | 0.064883
31 | 0.26752 | 0.12956
32 | 0.33823 | 0.16381
33 | 0.099716 | 0.048295
34 | 0.14998 | 0.072638
35 | 0.40135 | 0.19438
36 | 0.06816 | 0.033011
37 | 0.16282 | 0.078857
38 | 0.097693 | 0.047315
39 | 0.16488 | 0.079857
40 | 0.12987 | 0.0629
41 | 0.11732 | 0.05682
42 | 0.37521 | 0.18172
43 | 0.074396 | 0.036032
44 | 0.070371 | 0.034082
45 | 0.39784 | 0.19268
46 | 0.33583 | 0.16265
47 | 0.14619 | 0.070803
48 | 0.097982 | 0.047455
49 | 0.3178 | 0.15392
50 | 0.36911 | 0.17877
51 | 0.17435 | 0.084443
52 | 0.11209 | 0.054289
53 | 0.22793 | 0.11039
54 | 0.079834 | 0.038666
55 | 0.08444 | 0.040896
56 | 0.14355 | 0.069525
57 | 0.14549 | 0.070462
58 | 0.12805 | 0.062016
59 | 0.082046 | 0.039737
60 | 0.1336 | 0.064705
61 | 0.19054 | 0.092281
62 | 0.14381 | 0.069649
63 | 0.27889 | 0.13507
64 | 0.085838 | 0.041573
65 | 0.30468 | 0.14756
66 | 0.41893 | 0.2029
67 | 0.082774 | 0.040089
68 | 0.14595 | 0.070686
69 | 0.39117 | 0.18945
70 | 0.32802 | 0.15887
71 | 0.29685 | 0.14377
72 | 0.083557 | 0.040469
73 | 0.081985 | 0.039707
74 | 0.29336 | 0.14208
75 | 0.074522 | 0.036093
76 | 0.099445 | 0.048163
77 | 0.083239 | 0.040315
78 | 0.48565 | 0.23521
79 | 0.4065 | 0.19688
80 | 0.72307 | 0.3502
81 | 0.19359 | 0.093761
82 | 0.085152 | 0.041241
83 | 0.16536 | 0.080087
84 | 0.13734 | 0.066517
85 | 0.18298 | 0.08862

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1