## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_27_2_node_19 | 20 | n |  | TRUE
1 | bus_MV_27_2_node_20 | 20 | n |  | TRUE
2 | bus_MV_27_2_node_21 | 20 | n |  | TRUE
3 | bus_MV_27_2_node_22 | 20 | n |  | TRUE
4 | bus_MV_27_2_node_23 | 20 | n |  | TRUE
5 | bus_MV_27_2_node_232 | 20 | n |  | TRUE
6 | bus_MV_27_2_node_28 | 20 | n |  | TRUE
7 | bus_MV_27_2_node_24 | 20 | n |  | TRUE
8 | bus_MV_27_2_node_25 | 20 | n |  | TRUE
9 | bus_MV_27_2_node_52 | 20 | n |  | TRUE
10 | bus_MV_27_2_node_26 | 20 | n |  | TRUE
11 | bus_MV_27_2_node_166 | 20 | n |  | TRUE
12 | bus_MV_27_2_node_30 | 20 | n |  | TRUE
13 | bus_MV_27_2_node_27 | 20 | n |  | TRUE
14 | bus_MV_27_2_node_29 | 20 | n |  | TRUE
15 | bus_MV_27_2_node_107 | 20 | n |  | TRUE
16 | bus_MV_27_2_node_31 | 20 | n |  | TRUE
17 | bus_MV_27_2_node_32 | 20 | n |  | TRUE
18 | bus_MV_27_2_node_33 | 20 | n |  | TRUE
19 | bus_MV_27_2_node_212 | 20 | n |  | TRUE
20 | bus_MV_27_2_node_37 | 20 | n |  | TRUE
21 | bus_MV_27_2_node_36 | 20 | n |  | TRUE
22 | bus_MV_27_2_node_34 | 20 | n |  | TRUE
23 | bus_MV_27_2_node_35 | 20 | n |  | TRUE
24 | bus_MV_27_2_node_38 | 20 | n |  | TRUE
25 | bus_MV_27_2_node_230 | 20 | n |  | TRUE
26 | bus_MV_27_2_node_50 | 20 | n |  | TRUE
27 | bus_MV_27_2_node_51 | 20 | n |  | TRUE
28 | bus_MV_27_2_node_229 | 20 | n |  | TRUE
29 | bus_MV_27_2_node_53 | 20 | n |  | TRUE
30 | bus_MV_27_2_node_54 | 20 | n |  | TRUE
31 | bus_MV_27_2_node_225 | 20 | n |  | TRUE
32 | bus_MV_27_2_node_234 | 20 | n |  | TRUE
33 | bus_MV_27_2_node_82 | 20 | n |  | TRUE
34 | bus_MV_27_2_node_86 | 20 | n |  | TRUE
35 | bus_MV_27_2_node_84 | 20 | n |  | TRUE
36 | bus_MV_27_2_node_85 | 20 | n |  | TRUE
37 | bus_MV_27_2_node_204 | 20 | n |  | TRUE
38 | bus_MV_27_2_node_195 | 20 | n |  | TRUE
39 | bus_MV_27_2_node_95 | 20 | n |  | TRUE
40 | bus_MV_27_2_node_96 | 20 | n |  | TRUE
41 | bus_MV_27_2_node_208 | 20 | n |  | TRUE
42 | bus_MV_27_2_node_97 | 20 | n |  | TRUE
43 | bus_MV_27_2_node_236 | 20 | n |  | TRUE
44 | bus_MV_27_2_node_98 | 20 | n |  | TRUE
45 | bus_MV_27_2_node_99 | 20 | n |  | TRUE
46 | bus_MV_27_2_node_100 | 20 | n |  | TRUE
47 | bus_MV_27_2_node_101 | 20 | n |  | TRUE
48 | bus_MV_27_2_node_216 | 20 | n |  | TRUE
49 | bus_MV_27_2_node_102 | 20 | n |  | TRUE
50 | bus_MV_27_2_node_103 | 20 | n |  | TRUE
51 | bus_MV_27_2_node_104 | 20 | n |  | TRUE
52 | bus_MV_27_2_node_105 | 20 | n |  | TRUE
53 | bus_MV_27_2_node_185 | 20 | n |  | TRUE
54 | bus_MV_27_2_node_106 | 20 | n |  | TRUE
55 | bus_MV_27_2_node_108 | 20 | n |  | TRUE
56 | bus_MV_27_2_node_109 | 20 | n |  | TRUE
57 | bus_MV_27_2_node_110 | 20 | n |  | TRUE
58 | bus_MV_27_2_node_112 | 20 | n |  | TRUE
59 | bus_MV_27_2_node_111 | 20 | n |  | TRUE
60 | bus_MV_27_2_node_120 | 20 | n |  | TRUE
61 | bus_MV_27_2_node_113 | 20 | n |  | TRUE
62 | bus_MV_27_2_node_115 | 20 | n |  | TRUE
63 | bus_MV_27_2_node_114 | 20 | n |  | TRUE
64 | bus_MV_27_2_node_117 | 20 | n |  | TRUE
65 | bus_MV_27_2_node_118 | 20 | n |  | TRUE
66 | bus_MV_27_2_node_119 | 20 | n |  | TRUE
67 | bus_MV_27_2_node_187 | 20 | n |  | TRUE
68 | bus_MV_27_2_node_235 | 20 | n |  | TRUE
69 | bus_MV_27_2_node_121 | 20 | n |  | TRUE
70 | bus_MV_27_2_node_122 | 20 | n |  | TRUE
71 | bus_MV_27_2_node_126 | 20 | n |  | TRUE
72 | bus_MV_27_2_node_124 | 20 | n |  | TRUE
73 | bus_MV_27_2_node_123 | 20 | n |  | TRUE
74 | bus_MV_27_2_node_223 | 20 | n |  | TRUE
75 | bus_MV_27_2_node_125 | 20 | n |  | TRUE
76 | bus_MV_27_2_node_127 | 20 | n |  | TRUE
77 | bus_MV_27_2_node_128 | 20 | n |  | TRUE
78 | bus_MV_27_2_node_129 | 20 | n |  | TRUE
79 | bus_MV_27_2_node_150 | 20 | n |  | TRUE
80 | bus_MV_27_2_node_130 | 20 | n |  | TRUE
81 | bus_MV_27_2_node_136 | 20 | n |  | TRUE
82 | bus_MV_27_2_node_141 | 20 | n |  | TRUE
83 | bus_MV_27_2_node_131 | 20 | n |  | TRUE
84 | bus_MV_27_2_node_132 | 20 | n |  | TRUE
85 | bus_MV_27_2_node_133 | 20 | n |  | TRUE
86 | bus_MV_27_2_node_139 | 20 | n |  | TRUE
87 | bus_MV_27_2_node_134 | 20 | n |  | TRUE
88 | bus_MV_27_2_node_137 | 20 | n |  | TRUE
89 | bus_MV_27_2_node_138 | 20 | n |  | TRUE
90 | bus_MV_27_2_node_197 | 20 | n |  | TRUE
91 | bus_MV_27_2_node_140 | 20 | n |  | TRUE
92 | bus_MV_27_2_node_143 | 20 | n |  | TRUE
93 | bus_MV_27_2_node_147 | 20 | n |  | TRUE
94 | bus_MV_27_2_node_142 | 20 | n |  | TRUE
95 | bus_MV_27_2_node_144 | 20 | n |  | TRUE
96 | bus_MV_27_2_node_145 | 20 | n |  | TRUE
97 | bus_MV_27_2_node_149 | 20 | n |  | TRUE
98 | bus_MV_27_2_node_146 | 20 | n |  | TRUE
99 | bus_MV_27_2_node_148 | 20 | n |  | TRUE
100 | bus_MV_27_2_node_198 | 20 | n |  | TRUE
101 | bus_MV_27_2_node_189 | 20 | n |  | TRUE
102 | bus_MV_27_2_node_167 | 20 | n |  | TRUE
103 | bus_MV_27_2_node_168 | 20 | n |  | TRUE
104 | bus_MV_27_2_node_186 | 20 | n |  | TRUE
105 | bus_MV_27_2_node_188 | 20 | n |  | TRUE
106 | bus_MV_27_2_node_205 | 20 | n |  | TRUE
107 | bus_MV_27_2_node_206 | 20 | n |  | TRUE
108 | bus_MV_27_2_node_221 | 20 | n |  | TRUE
109 | bus_MV_27_2_node_228 | 20 | n |  | TRUE
110 | bus_HV_27_2_node_30 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_27_2_load_19 | 0 | 0.19268 | 0.093317 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_27_2_load_23 | 4 | 0.12539 | 0.060727 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_27_2_load_232 | 5 | 0.19642 | 0.095131 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_27_2_load_24 | 7 | 0.27759 | 0.13444 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_27_2_load_52 | 9 | 0.27228 | 0.13187 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_27_2_load_166 | 11 | 0.10306 | 0.049914 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_27_2_load_27 | 13 | 0.2096 | 0.10151 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_27_2_load_29 | 14 | 0.077224 | 0.037401 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_27_2_load_31 | 16 | 0.15251 | 0.073865 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_27_2_load_212 | 19 | 0.13092 | 0.063408 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_27_2_load_34 | 22 | 0.41283 | 0.19994 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_27_2_load_38 | 24 | 0.26771 | 0.12966 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_27_2_load_230 | 25 | 0.15693 | 0.076003 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_27_2_load_50 | 26 | 0.14516 | 0.070306 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_27_2_load_225 | 31 | 0.38817 | 0.188 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_27_2_load_82 | 33 | 0.13871 | 0.067182 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_27_2_load_84 | 35 | 0.17774 | 0.086085 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_27_2_load_204 | 37 | 0.21828 | 0.10572 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_27_2_load_195 | 38 | 0.14387 | 0.069678 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_27_2_load_95 | 39 | 0.13662 | 0.06617 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_27_2_load_208 | 41 | 0.10771 | 0.052168 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_27_2_load_97 | 42 | 0.10609 | 0.051382 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_27_2_load_236 | 43 | 0.10149 | 0.049153 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_27_2_load_101 | 47 | 0.13096 | 0.063425 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_27_2_load_216 | 48 | 0.14985 | 0.072573 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_27_2_load_102 | 49 | 0.15189 | 0.073564 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_27_2_load_104 | 51 | 0.24247 | 0.11743 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_27_2_load_185 | 53 | 0.29416 | 0.14247 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_27_2_load_106 | 54 | 0.11758 | 0.056947 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_27_2_load_108 | 55 | 0.14093 | 0.068258 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_27_2_load_111 | 59 | 0.069438 | 0.03363 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_27_2_load_120 | 60 | 0.15826 | 0.076647 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_27_2_load_113 | 61 | 0.11686 | 0.056598 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_27_2_load_119 | 66 | 0.061754 | 0.029909 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_27_2_load_187 | 67 | 0.087573 | 0.042413 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_27_2_load_235 | 68 | 0.27206 | 0.13176 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_27_2_load_121 | 69 | 0.10334 | 0.050048 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_27_2_load_126 | 71 | 0.059534 | 0.028834 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_27_2_load_223 | 74 | 0.073352 | 0.035526 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_27_2_load_125 | 75 | 0.14519 | 0.07032 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_27_2_load_150 | 79 | 0.069641 | 0.033729 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_27_2_load_141 | 82 | 0.072374 | 0.035052 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_27_2_load_131 | 83 | 0.16072 | 0.077839 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_27_2_load_139 | 86 | 0.1075 | 0.052065 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_27_2_load_134 | 87 | 0.055996 | 0.02712 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_27_2_load_197 | 90 | 0.098162 | 0.047542 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_27_2_load_140 | 91 | 0.13464 | 0.065208 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_27_2_load_142 | 94 | 0.16428 | 0.079563 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_27_2_load_145 | 96 | 0.071955 | 0.03485 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_27_2_load_149 | 97 | 0.17908 | 0.086734 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_27_2_load_198 | 100 | 0.10082 | 0.048827 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_27_2_load_168 | 103 | 0.081177 | 0.039316 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_27_2_load_186 | 104 | 0.31677 | 0.15342 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_27_2_load_188 | 105 | 0.078868 | 0.038198 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_27_2_load_221 | 108 | 0.067973 | 0.032921 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_27_2_load_228 | 109 | 0.29394 | 0.14236 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_27_2_line_0 |  | 0 | 1 | 0.094859 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_27_2_line_1 |  | 1 | 2 | 0.3765 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_27_2_line_2 |  | 1 | 3 | 0.38386 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_27_2_line_3 |  | 2 | 4 | 0.024928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_27_2_line_4 |  | 3 | 5 | 0.020781 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_27_2_line_5 |  | 4 | 6 | 1.0725 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_27_2_line_6 |  | 6 | 12 | 0.34532 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_27_2_line_7 |  | 6 | 13 | 0.050752 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_27_2_line_8 |  | 7 | 8 | 0.066752 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
9 | MV_27_2_line_9 |  | 7 | 9 | 1.3399 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
10 | MV_27_2_line_10 |  | 8 | 10 | 0.52959 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
11 | MV_27_2_line_11 |  | 9 | 29 | 0.006146 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
12 | MV_27_2_line_12 |  | 10 | 11 | 0.018579 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_27_2_line_13 |  | 10 | 12 | 0.071517 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
14 | MV_27_2_line_14 |  | 11 | 102 | 0.04608 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_27_2_line_15 |  | 12 | 15 | 1.7592 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
16 | MV_27_2_line_16 |  | 12 | 14 | 0.028182 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_27_2_line_17 |  | 15 | 52 | 1.1943 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
18 | MV_27_2_line_18 |  | 15 | 54 | 0.13034 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_27_2_line_19 |  | 16 | 17 | 0.063138 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_27_2_line_20 |  | 17 | 18 | 0.022083 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_27_2_line_21 |  | 18 | 19 | 0.012177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_27_2_line_22 |  | 18 | 20 | 0.58208 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_27_2_line_23 |  | 18 | 21 | 0.67816 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_27_2_line_24 |  | 20 | 25 | 0.082518 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_27_2_line_25 |  | 20 | 23 | 0.85827 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_27_2_line_26 |  | 21 | 24 | 0.07595 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_27_2_line_27 |  | 22 | 23 | 0.031791 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_27_2_line_28 |  | 24 | 26 | 1.9143 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_27_2_line_29 |  | 26 | 27 | 0.037046 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_27_2_line_30 |  | 27 | 28 | 1.4327 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
31 | MV_27_2_line_31 |  | 28 | 68 | 1.4785 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
32 | MV_27_2_line_32 |  | 28 | 109 | 0.039257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_27_2_line_33 |  | 29 | 30 | 0.60856 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
34 | MV_27_2_line_34 |  | 30 | 31 | 0.037545 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_27_2_line_35 |  | 30 | 32 | 1.5148 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
36 | MV_27_2_line_36 |  | 32 | 68 | 0.082931 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
37 | MV_27_2_line_37 |  | 33 | 34 | 0.94745 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_27_2_line_38 |  | 34 | 38 | 0.04523 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_27_2_line_39 |  | 34 | 36 | 1.1207 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_27_2_line_40 |  | 35 | 36 | 0.097645 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_27_2_line_41 |  | 35 | 37 | 0.85174 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_27_2_line_42 |  | 37 | 106 | 0.17613 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_27_2_line_43 |  | 39 | 40 | 0.017846 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_27_2_line_44 |  | 39 | 41 | 0.45446 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_27_2_line_45 |  | 40 | 42 | 1.9107 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
46 | MV_27_2_line_46 |  | 40 | 43 | 2.0199 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
47 | MV_27_2_line_47 |  | 42 | 44 | 0.018233 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
48 | MV_27_2_line_48 |  | 43 | 99 | 0.061573 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
49 | MV_27_2_line_49 |  | 44 | 45 | 0.32622 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
50 | MV_27_2_line_50 |  | 45 | 46 | 1.3605 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_27_2_line_51 |  | 45 | 47 | 0.068127 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
52 | MV_27_2_line_52 |  | 46 | 48 | 0.026857 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_27_2_line_53 |  | 47 | 49 | 1.2652 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
54 | MV_27_2_line_54 |  | 48 | 107 | 1.3253 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_27_2_line_55 |  | 49 | 50 | 0.035828 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
56 | MV_27_2_line_56 |  | 49 | 51 | 0.040886 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_27_2_line_57 |  | 50 | 52 | 0.23944 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
58 | MV_27_2_line_58 |  | 52 | 53 | 0.035119 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_27_2_line_59 |  | 53 | 104 | 0.01042 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_27_2_line_60 |  | 55 | 56 | 0.19911 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_27_2_line_61 |  | 56 | 57 | 1.2434 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_27_2_line_62 |  | 57 | 58 | 0.46023 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_27_2_line_63 |  | 57 | 59 | 0.055913 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_27_2_line_64 |  | 58 | 60 | 0.023095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_27_2_line_65 |  | 60 | 67 | 0.08234 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_27_2_line_66 |  | 61 | 62 | 0.027605 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_27_2_line_67 |  | 61 | 63 | 0.099159 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
68 | MV_27_2_line_68 |  | 62 | 65 | 0.12632 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_27_2_line_69 |  | 63 | 64 | 0.30724 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_27_2_line_70 |  | 64 | 66 | 0.058579 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_27_2_line_71 |  | 65 | 67 | 0.056155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_27_2_line_72 |  | 66 | 68 | 1.7104 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_27_2_line_73 |  | 69 | 70 | 0.082202 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_27_2_line_74 |  | 69 | 71 | 1.3241 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_27_2_line_75 |  | 70 | 72 | 0.34325 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_27_2_line_76 |  | 71 | 76 | 0.16748 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_27_2_line_77 |  | 72 | 75 | 0.063165 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
78 | MV_27_2_line_78 |  | 72 | 73 | 0.13978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_27_2_line_79 |  | 73 | 74 | 0.23159 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_27_2_line_80 |  | 76 | 77 | 0.60861 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_27_2_line_81 |  | 77 | 78 | 0.43092 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_27_2_line_82 |  | 77 | 79 | 0.14524 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_27_2_line_83 |  | 78 | 80 | 0.25757 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_27_2_line_84 |  | 78 | 81 | 0.095497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_27_2_line_85 |  | 78 | 82 | 0.068432 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
86 | MV_27_2_line_86 |  | 80 | 83 | 0.20469 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
87 | MV_27_2_line_87 |  | 81 | 89 | 0.094564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_27_2_line_88 |  | 81 | 87 | 0.065783 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_27_2_line_89 |  | 82 | 92 | 0.31013 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
90 | MV_27_2_line_90 |  | 82 | 93 | 0.15621 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
91 | MV_27_2_line_91 |  | 83 | 84 | 0.060627 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_27_2_line_92 |  | 84 | 85 | 0.33928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_27_2_line_93 |  | 85 | 86 | 0.029986 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_27_2_line_94 |  | 87 | 88 | 0.19879 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_27_2_line_95 |  | 88 | 90 | 0.066933 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_27_2_line_96 |  | 89 | 91 | 0.016274 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
97 | MV_27_2_line_97 |  | 92 | 98 | 0.015548 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
98 | MV_27_2_line_98 |  | 93 | 100 | 0.032635 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_27_2_line_99 |  | 94 | 95 | 0.027723 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
100 | MV_27_2_line_100 |  | 94 | 96 | 0.047433 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_27_2_line_101 |  | 94 | 97 | 0.017975 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
102 | MV_27_2_line_102 |  | 95 | 99 | 0.028131 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
103 | MV_27_2_line_103 |  | 97 | 98 | 0.051492 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
104 | MV_27_2_line_104 |  | 99 | 101 | 0.041231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_27_2_line_105 |  | 101 | 105 | 0.017643 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_27_2_line_106 |  | 102 | 103 | 0.012261 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_27_2_line_107 |  | 106 | 107 | 1.0346 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_27_2_line_108 |  | 107 | 108 | 0.035887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_27_2_trafo_30 | 25 MVA 110/20 kV | 110 | 12 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2567994.7617 | 1176228.0982
1 | 2568087.6594 | 1176247.2897
2 | 2567909.2107 | 1176494.1172
3 | 2568408.3952 | 1176300.8706
4 | 2567884.578 | 1176489.8583
5 | 2568428.1266 | 1176307.5588
6 | 2566833.9315 | 1176705.3815
7 | 2566392.068 | 1177252.9115
8 | 2566406.726 | 1177187.7951
9 | 2566770.066 | 1178538.3608
10 | 2566593.1622 | 1176734.3697
11 | 2566605.1889 | 1176748.5304
12 | 2566632.2861 | 1176674.4423
13 | 2566786.7327 | 1176686.389
14 | 2566656.2833 | 1176688.3032
15 | 2565846.4896 | 1175100.5
16 | 2569243.5229 | 1177993.2538
17 | 2569181.565 | 1177980.2883
18 | 2569159.8054 | 1177976.1761
19 | 2569152.7994 | 1177967.4188
20 | 2569297.3889 | 1177809.8926
21 | 2569265.6265 | 1178446.1095
22 | 2568901.8659 | 1178007.3505
23 | 2568880.2658 | 1177983.984
24 | 2569276.4649 | 1178521.2819
25 | 2569312.6811 | 1177773.1394
26 | 2568139.472 | 1180061.3826
27 | 2568103.1116 | 1180053.7725
28 | 2567184.5546 | 1181153.2774
29 | 2566770.9861 | 1178544.4367
30 | 2566944.3349 | 1178965.8189
31 | 2566981.4565 | 1178971.439
32 | 2566029.2349 | 1180172.9707
33 | 2568996.012 | 1173808.6933
34 | 2568416.9716 | 1174558.6098
35 | 2567817.0957 | 1173666.655
36 | 2567774.8645 | 1173754.6389
37 | 2567884.1687 | 1172817.5553
38 | 2568414.259 | 1174603.7586
39 | 2564527.5362 | 1172263.7951
40 | 2564526.3951 | 1172281.6
41 | 2564598.5716 | 1171814.9193
42 | 2566421.4542 | 1172525.8643
43 | 2563628.8021 | 1174091.129
44 | 2566425.2023 | 1172543.7081
45 | 2566597.19 | 1172782.5364
46 | 2567225.8801 | 1172095.7391
47 | 2566653.4034 | 1172820.2758
48 | 2567247.1799 | 1172080.1922
49 | 2566112.8573 | 1173964.1388
50 | 2566089.6752 | 1173991.2286
51 | 2566139.5865 | 1173994.3967
52 | 2566084.705 | 1174105.8053
53 | 2566106.6357 | 1174078.487
54 | 2565741.6073 | 1175023.3927
55 | 2562600.029 | 1179962.8697
56 | 2562615.187 | 1179764.3365
57 | 2563630.4356 | 1180072.6054
58 | 2563916.7056 | 1180153.9029
59 | 2563670.1951 | 1180111.9178
60 | 2563930.6567 | 1180135.6052
61 | 2563949.7346 | 1179956.5995
62 | 2563923.1521 | 1179948.8891
63 | 2564031.1951 | 1180013.1388
64 | 2564254.0215 | 1180133.1882
65 | 2563875.584 | 1180054.4654
66 | 2564303.0875 | 1180165.1868
67 | 2563931.5155 | 1180053.2699
68 | 2566011.1718 | 1180253.7381
69 | 2563605.1945 | 1176414.5887
70 | 2563663.4661 | 1176472.7206
71 | 2563372.4712 | 1175111.0811
72 | 2563773.6653 | 1176724.4511
73 | 2563833.0611 | 1176657.1231
74 | 2564057.3486 | 1176674.6918
75 | 2563760.8643 | 1176786.3055
76 | 2563322.0425 | 1174951.9733
77 | 2562990.7428 | 1174653.6677
78 | 2563267.2348 | 1174437.4624
79 | 2562883.7419 | 1174750.0363
80 | 2563070.0502 | 1174337.1789
81 | 2563325.3038 | 1174507.543
82 | 2563331.9474 | 1174415.2095
83 | 2562915.5181 | 1174202.9419
84 | 2562855.9878 | 1174190.6045
85 | 2562540.9162 | 1174075.3409
86 | 2562562.7309 | 1174054.7048
87 | 2563378.0293 | 1174546.7295
88 | 2563567.9982 | 1174605.2786
89 | 2563256.054 | 1174502.932
90 | 2563604.1564 | 1174661.1878
91 | 2563243.3688 | 1174492.7378
92 | 2563580.0893 | 1174229.1751
93 | 2563488.0567 | 1174420.7248
94 | 2563616.821 | 1174181.9408
95 | 2563633.8393 | 1174160.0566
96 | 2563579.3769 | 1174152.8225
97 | 2563624.0182 | 1174198.4125
98 | 2563592.3276 | 1174238.8056
99 | 2563652.9371 | 1174139.6744
100 | 2563506.9853 | 1174394.1399
101 | 2563685.0037 | 1174156.0327
102 | 2566634.9137 | 1176783.7402
103 | 2566623.8811 | 1176785.518
104 | 2566110.5711 | 1174068.839
105 | 2563697.5369 | 1174153.3578
106 | 2568053.5863 | 1172769.3793
107 | 2568566.8704 | 1171957.8983
108 | 2568593.8372 | 1171934.2001
109 | 2567212.4209 | 1181180.9947
110 | 2566632.2861 | 1176674.4423

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9984 | -0.0047991 | 0.19268 | 0.093317
1 | 0.99844 | -0.0045771 | 0 | 0
2 | 0.99862 | -0.0059926 | 0 | 0
3 | 0.99834 | -0.0037964 | 0 | 0
4 | 0.99863 | -0.0060787 | 0.12539 | 0.060727
5 | 0.99834 | -0.0037477 | 0.19642 | 0.095131
6 | 0.99968 | 0.0024256 | 0 | 0
7 | 0.99926 | -0.0042937 | 0.27759 | 0.13444
8 | 0.99933 | -0.0038846 | 0 | 0
9 | 0.99653 | -0.1667 | 0.27228 | 0.13187
10 | 0.99992 | -0.00049465 | 0 | 0
11 | 0.99991 | -0.00045561 | 0.10306 | 0.049914
12 | 1 | 0 | -8.7402 | -3.7586
13 | 0.99967 | 0.002551 | 0.2096 | 0.10151
14 | 1 | 2.5433e-05 | 0.077224 | 0.037401
15 | 0.99518 | -0.29431 | 0 | 0
16 | 0.98507 | -0.50092 | 0.15251 | 0.073865
17 | 0.98509 | -0.50103 | 0 | 0
18 | 0.98509 | -0.50107 | 0 | 0
19 | 0.98509 | -0.50105 | 0.13092 | 0.063408
20 | 0.98467 | -0.4981 | 0 | 0
21 | 0.98583 | -0.50615 | 0 | 0
22 | 0.9842 | -0.49417 | 0.41283 | 0.19994
23 | 0.98421 | -0.49433 | 0 | 0
24 | 0.98595 | -0.50498 | 0.26771 | 0.12966
25 | 0.98465 | -0.49794 | 0.15693 | 0.076003
26 | 0.99007 | -0.46915 | 0.14516 | 0.070306
27 | 0.99013 | -0.46959 | 0 | 0
28 | 0.99192 | -0.40589 | 0 | 0
29 | 0.99652 | -0.16674 | 0 | 0
30 | 0.99596 | -0.16998 | 0 | 0
31 | 0.99593 | -0.17016 | 0.38817 | 0.188
32 | 0.99351 | -0.31562 | 0 | 0
33 | 0.98462 | -0.47633 | 0.13871 | 0.067182
34 | 0.98488 | -0.47465 | 0 | 0
35 | 0.98531 | -0.47767 | 0.17774 | 0.086085
36 | 0.98528 | -0.47751 | 0 | 0
37 | 0.98606 | -0.47056 | 0.21828 | 0.10572
38 | 0.98486 | -0.47473 | 0.14387 | 0.069678
39 | 0.98782 | -0.6185 | 0.13662 | 0.06617
40 | 0.98782 | -0.61856 | 0 | 0
41 | 0.98772 | -0.61912 | 0.10771 | 0.052168
42 | 0.99037 | -0.46702 | 0.10609 | 0.051382
43 | 0.98547 | -0.76036 | 0.10149 | 0.049153
44 | 0.9904 | -0.46551 | 0 | 0
45 | 0.99063 | -0.46423 | 0 | 0
46 | 0.98909 | -0.45579 | 0 | 0
47 | 0.99069 | -0.46378 | 0.13096 | 0.063425
48 | 0.98906 | -0.45559 | 0.14985 | 0.072573
49 | 0.99326 | -0.30649 | 0.15189 | 0.073564
50 | 0.9933 | -0.30624 | 0 | 0
51 | 0.99325 | -0.30637 | 0.24247 | 0.11743
52 | 0.99358 | -0.30452 | 0 | 0
53 | 0.99355 | -0.30426 | 0.29416 | 0.14247
54 | 0.99516 | -0.29414 | 0.11758 | 0.056947
55 | 0.99047 | -0.33663 | 0.14093 | 0.068258
56 | 0.99053 | -0.33628 | 0 | 0
57 | 0.99075 | -0.33722 | 0 | 0
58 | 0.99086 | -0.33736 | 0 | 0
59 | 0.99074 | -0.33727 | 0.069438 | 0.03363
60 | 0.99087 | -0.33736 | 0.15826 | 0.076647
61 | 0.99105 | -0.33727 | 0.11686 | 0.056598
62 | 0.99103 | -0.3372 | 0 | 0
63 | 0.99115 | -0.33618 | 0 | 0
64 | 0.99137 | -0.33733 | 0 | 0
65 | 0.99096 | -0.33685 | 0 | 0
66 | 0.99142 | -0.33754 | 0.061754 | 0.029909
67 | 0.99093 | -0.33669 | 0.087573 | 0.042413
68 | 0.99345 | -0.31601 | 0.27206 | 0.13176
69 | 0.98344 | -0.78124 | 0.10334 | 0.050048
70 | 0.98341 | -0.78111 | 0 | 0
71 | 0.98425 | -0.77368 | 0.059534 | 0.028834
72 | 0.98332 | -0.78047 | 0 | 0
73 | 0.9833 | -0.7804 | 0 | 0
74 | 0.98328 | -0.78023 | 0.073352 | 0.035526
75 | 0.9833 | -0.78058 | 0.14519 | 0.07032
76 | 0.98433 | -0.77422 | 0 | 0
77 | 0.98463 | -0.77586 | 0 | 0
78 | 0.98487 | -0.77694 | 0 | 0
79 | 0.98461 | -0.77575 | 0.069641 | 0.033729
80 | 0.98478 | -0.77631 | 0 | 0
81 | 0.98484 | -0.77665 | 0 | 0
82 | 0.985 | -0.77563 | 0.072374 | 0.035052
83 | 0.98468 | -0.77718 | 0.16072 | 0.077839
84 | 0.98467 | -0.77714 | 0 | 0
85 | 0.98462 | -0.77679 | 0 | 0
86 | 0.98462 | -0.77675 | 0.1075 | 0.052065
87 | 0.98482 | -0.77653 | 0.055996 | 0.02712
88 | 0.98478 | -0.7768 | 0 | 0
89 | 0.98482 | -0.7765 | 0 | 0
90 | 0.98478 | -0.77673 | 0.098162 | 0.047542
91 | 0.98481 | -0.77652 | 0.13464 | 0.065208
92 | 0.98536 | -0.76243 | 0 | 0
93 | 0.98497 | -0.77583 | 0 | 0
94 | 0.98541 | -0.76074 | 0.16428 | 0.079563
95 | 0.98542 | -0.76066 | 0 | 0
96 | 0.9854 | -0.7607 | 0.071955 | 0.03485
97 | 0.98539 | -0.76171 | 0.17908 | 0.086734
98 | 0.98537 | -0.76226 | 0 | 0
99 | 0.98544 | -0.76057 | 0 | 0
100 | 0.98496 | -0.77587 | 0.10082 | 0.048827
101 | 0.98543 | -0.76053 | 0 | 0
102 | 0.99991 | -0.00041332 | 0 | 0
103 | 0.99991 | -0.00040153 | 0.081177 | 0.039316
104 | 0.99355 | -0.30422 | 0.31677 | 0.15342
105 | 0.98543 | -0.76051 | 0.078868 | 0.038198
106 | 0.98629 | -0.46861 | 0 | 0
107 | 0.98718 | -0.47436 | 0 | 0
108 | 0.98718 | -0.47433 | 0.067973 | 0.032921
109 | 0.9919 | -0.40575 | 0.29394 | 0.14236
110 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.19268 | -0.093317 | 0.19268 | 0.093208 | 6.4743e-06 | -0.00010883 | 0.00619 | 0.0061885 | 0.00619 | 0.9984 | -0.0047991 | 0.99844 | -0.0045771 | 2.9476
1 | -0.38912 | -0.17872 | 0.3892 | 0.16977 | 7.6377e-05 | -0.0089403 | 0.01238 | 0.012275 | 0.01238 | 0.99844 | -0.0045771 | 0.99862 | -0.0059926 | 5.6275
2 | 0.19644 | 0.085507 | -0.19642 | -0.094637 | 2.0007e-05 | -0.0091296 | 0.0061944 | 0.0063045 | 0.0063045 | 0.99844 | -0.0045771 | 0.99834 | -0.0037964 | 2.8657
3 | -0.3892 | -0.16977 | 0.38921 | 0.16918 | 5.0112e-06 | -0.00059207 | 0.012275 | 0.012268 | 0.012275 | 0.99862 | -0.0059926 | 0.99863 | -0.0060787 | 5.5794
4 | 0.19642 | 0.094637 | -0.19642 | -0.095131 | 1.1038e-06 | -0.0004942 | 0.0063045 | 0.0063107 | 0.0063107 | 0.99834 | -0.0037964 | 0.99834 | -0.0037477 | 2.8685
5 | -0.51459 | -0.22991 | 0.5151 | 0.22895 | 0.00050677 | -0.00096081 | 0.016292 | 0.016277 | 0.016292 | 0.99863 | -0.0060787 | 0.99968 | 0.0024256 | 7.7583
6 | -0.7247 | -0.32925 | 0.72495 | 0.32108 | 0.00024253 | -0.0081703 | 0.022986 | 0.022888 | 0.022986 | 0.99968 | 0.0024256 | 1 | 0 | 10.448
7 | 0.2096 | 0.1003 | -0.2096 | -0.10151 | 3.0575e-06 | -0.0012101 | 0.00671 | 0.0067252 | 0.0067252 | 0.99968 | 0.0024256 | 0.99967 | 0.002551 | 3.0569
8 | -3.425 | -1.5159 | 3.4252 | 1.5118 | 0.00024138 | -0.0040523 | 0.1082 | 0.10815 | 0.1082 | 0.99926 | -0.0042937 | 0.99933 | -0.0038846 | 16.9595
9 | 3.1474 | 1.3815 | -3.1427 | -1.3706 | 0.0047174 | 0.010841 | 0.099297 | 0.099319 | 0.099319 | 0.99926 | -0.0042937 | 0.99653 | -0.1667 | 15.3982
10 | -3.4252 | -1.5118 | 3.4271 | 1.4797 | 0.0019073 | -0.032176 | 0.10815 | 0.10777 | 0.10815 | 0.99933 | -0.0038846 | 0.99992 | -0.00049465 | 16.9518
11 | 2.8704 | 1.2387 | -2.8704 | -1.2391 | 1.5576e-05 | -0.00037471 | 0.090562 | 0.090567 | 0.090567 | 0.99653 | -0.1667 | 0.99652 | -0.16674 | 14.1954
12 | 0.18424 | 0.087394 | -0.18424 | -0.087837 | 8.6038e-07 | -0.00044325 | 0.005887 | 0.0058925 | 0.0058925 | 0.99992 | -0.00049465 | 0.99991 | -0.00045561 | 2.6784
13 | -3.6114 | -1.5671 | 3.6116 | 1.5627 | 0.00028532 | -0.0043325 | 0.11365 | 0.1136 | 0.11365 | 0.99992 | -0.00049465 | 1 | 0 | 17.8138
14 | 0.081177 | 0.037923 | -0.081177 | -0.039023 | 4.1377e-07 | -0.0010999 | 0.0025867 | 0.0026003 | 0.0026003 | 0.99991 | -0.00045561 | 0.99991 | -0.00041332 | 1.182
15 | 4.3123 | 1.8276 | -4.3009 | -1.7991 | 0.011483 | 0.028459 | 0.1352 | 0.13523 | 0.13523 | 1 | 0 | 0.99518 | -0.29431 | 20.9662
16 | 0.077225 | 0.036729 | -0.077224 | -0.037401 | 2.3005e-07 | -0.0006728 | 0.0024686 | 0.002477 | 0.002477 | 1 | 0 | 1 | 2.5433e-05 | 1.1259
17 | 4.1833 | 1.7453 | -4.1769 | -1.8159 | 0.0064202 | -0.070581 | 0.13148 | 0.13233 | 0.13233 | 0.99518 | -0.29431 | 0.99358 | -0.30452 | 20.7408
18 | 0.11758 | 0.053866 | -0.11758 | -0.056947 | 2.4738e-06 | -0.0030814 | 0.0037516 | 0.0037897 | 0.0037897 | 0.99518 | -0.29431 | 0.99516 | -0.29414 | 1.7226
19 | -0.15251 | -0.073865 | 0.15251 | 0.072403 | 2.0708e-06 | -0.0014622 | 0.0049659 | 0.0049474 | 0.0049659 | 0.98507 | -0.50092 | 0.98509 | -0.50103 | 2.2572
20 | -0.15251 | -0.072403 | 0.15251 | 0.071891 | 7.2065e-07 | -0.00051144 | 0.0049474 | 0.004941 | 0.0049474 | 0.98509 | -0.50103 | 0.98509 | -0.50107 | 2.2488
21 | 0.13092 | 0.063126 | -0.13092 | -0.063408 | 2.9516e-07 | -0.00028205 | 0.0042593 | 0.0042629 | 0.0042629 | 0.98509 | -0.50107 | 0.98509 | -0.50105 | 1.9377
22 | 0.57023 | 0.2401 | -0.56997 | -0.25351 | 0.00025765 | -0.013404 | 0.018131 | 0.018288 | 0.018288 | 0.98509 | -0.50107 | 0.98467 | -0.4981 | 8.3128
23 | -0.85367 | -0.37512 | 0.85434 | 0.35959 | 0.00067144 | -0.015525 | 0.027325 | 0.027143 | 0.027325 | 0.98509 | -0.50107 | 0.98583 | -0.50615 | 12.4204
24 | 0.15693 | 0.074094 | -0.15693 | -0.076003 | 2.865e-06 | -0.0019094 | 0.0050877 | 0.0051119 | 0.0051119 | 0.98467 | -0.4981 | 0.98465 | -0.49794 | 2.3236
25 | 0.41304 | 0.17941 | -0.41284 | -0.19921 | 0.00020332 | -0.019799 | 0.013202 | 0.013445 | 0.013445 | 0.98467 | -0.4981 | 0.98421 | -0.49433 | 6.1113
26 | -0.85434 | -0.35959 | 0.85444 | 0.35957 | 9.9691e-05 | -2.5685e-05 | 0.027143 | 0.027142 | 0.027143 | 0.98583 | -0.50615 | 0.98595 | -0.50498 | 12.9252
27 | -0.41283 | -0.19994 | 0.41284 | 0.19921 | 7.6772e-06 | -0.00073298 | 0.013454 | 0.013445 | 0.013454 | 0.9842 | -0.49417 | 0.98421 | -0.49433 | 6.1156
28 | -1.1222 | -0.48923 | 1.1265 | 0.48974 | 0.0043785 | 0.00051165 | 0.035842 | 0.035816 | 0.035842 | 0.98595 | -0.50498 | 0.99007 | -0.46915 | 17.0676
29 | -1.2717 | -0.56004 | 1.2718 | 0.5592 | 8.1162e-05 | -0.00084301 | 0.040515 | 0.040505 | 0.040515 | 0.99007 | -0.46915 | 0.99013 | -0.46959 | 18.416
30 | -1.2718 | -0.5592 | 1.2734 | 0.5598 | 0.0016746 | 0.00060328 | 0.040505 | 0.040484 | 0.040505 | 0.99013 | -0.46959 | 0.99192 | -0.40589 | 9.8793
31 | -1.5674 | -0.70124 | 1.5687 | 0.70277 | 0.0013175 | 0.0015289 | 0.049973 | 0.049949 | 0.049973 | 0.99192 | -0.40589 | 0.99345 | -0.31601 | 7.7477
32 | 0.29394 | 0.14144 | -0.29394 | -0.14236 | 4.729e-06 | -0.0009208 | 0.0094934 | 0.009505 | 0.009505 | 0.99192 | -0.40589 | 0.9919 | -0.40575 | 4.3205
33 | 2.8704 | 1.2391 | -2.8688 | -1.2762 | 0.0015499 | -0.037077 | 0.090567 | 0.091008 | 0.091008 | 0.99652 | -0.16674 | 0.99596 | -0.16998 | 14.2646
34 | 0.38818 | 0.18796 | -0.38817 | -0.188 | 1.0454e-05 | -3.791e-05 | 0.012501 | 0.012502 | 0.012502 | 0.99596 | -0.16998 | 0.99593 | -0.17016 | 5.9531
35 | 2.4806 | 1.0882 | -2.4773 | -1.0813 | 0.0033347 | 0.0068954 | 0.078515 | 0.078539 | 0.078539 | 0.99596 | -0.16998 | 0.99351 | -0.31562 | 12.1766
36 | 2.4773 | 1.0813 | -2.4771 | -1.0864 | 0.00015819 | -0.0050539 | 0.078539 | 0.078599 | 0.078599 | 0.99351 | -0.31562 | 0.99345 | -0.31601 | 12.3196
37 | -0.13871 | -0.067182 | 0.13875 | 0.066107 | 3.4362e-05 | -0.0010753 | 0.0045187 | 0.0045048 | 0.0045187 | 0.98462 | -0.47633 | 0.98488 | -0.47465 | 2.1518
38 | 0.14387 | 0.069627 | -0.14387 | -0.069678 | 1.7689e-06 | -5.1266e-05 | 0.0046848 | 0.0046855 | 0.0046855 | 0.98488 | -0.47465 | 0.98486 | -0.47473 | 2.2312
39 | -0.28262 | -0.13573 | 0.28274 | 0.1098 | 0.00012204 | -0.02593 | 0.0091896 | 0.0088867 | 0.0091896 | 0.98488 | -0.47465 | 0.98528 | -0.47751 | 4.1771
40 | 0.28275 | 0.10754 | -0.28274 | -0.1098 | 1.0267e-05 | -0.0022603 | 0.0088629 | 0.0088867 | 0.0088867 | 0.98531 | -0.47767 | 0.98528 | -0.47751 | 4.0394
41 | -0.46049 | -0.19363 | 0.46082 | 0.19284 | 0.00032481 | -0.00078447 | 0.014636 | 0.014624 | 0.014636 | 0.98531 | -0.47767 | 0.98606 | -0.47056 | 6.9693
42 | -0.6791 | -0.29856 | 0.67925 | 0.29845 | 0.000148 | -0.0001118 | 0.021718 | 0.021715 | 0.021718 | 0.98606 | -0.47056 | 0.98629 | -0.46861 | 10.3417
43 | -0.24435 | -0.11781 | 0.24435 | 0.1174 | 1.4962e-06 | -0.00041533 | 0.0079273 | 0.0079221 | 0.0079273 | 0.98782 | -0.6185 | 0.98782 | -0.61856 | 3.6033
44 | 0.10772 | 0.051645 | -0.10771 | -0.052168 | 9.8877e-06 | -0.00052316 | 0.0034911 | 0.0034978 | 0.0034978 | 0.98782 | -0.6185 | 0.98772 | -0.61912 | 1.6656
45 | -2.0248 | -0.89447 | 2.0277 | 0.89956 | 0.0028531 | 0.0050883 | 0.064689 | 0.064658 | 0.064689 | 0.98782 | -0.61856 | 0.99037 | -0.46702 | 10.0292
46 | 1.7805 | 0.77707 | -1.7781 | -0.77354 | 0.0023254 | 0.0035351 | 0.056771 | 0.056803 | 0.056803 | 0.98782 | -0.61856 | 0.98547 | -0.76036 | 8.8066
47 | -2.1338 | -0.95094 | 2.1338 | 0.951 | 3.018e-05 | 5.6435e-05 | 0.068092 | 0.068092 | 0.068092 | 0.99037 | -0.46702 | 0.9904 | -0.46551 | 10.5569
48 | 1.6767 | 0.72439 | -1.6766 | -0.72811 | 5.4507e-05 | -0.0037263 | 0.053502 | 0.053546 | 0.053546 | 0.98547 | -0.76036 | 0.98544 | -0.76057 | 8.3928
49 | -2.1338 | -0.951 | 2.1343 | 0.93115 | 0.00046574 | -0.019848 | 0.068092 | 0.067855 | 0.068092 | 0.9904 | -0.46551 | 0.99063 | -0.46423 | 10.6727
50 | 0.90051 | 0.34652 | -0.89906 | -0.37791 | 0.0014534 | -0.031397 | 0.028117 | 0.028464 | 0.028464 | 0.99063 | -0.46423 | 0.98909 | -0.45579 | 12.9381
51 | -3.0348 | -1.2777 | 3.035 | 1.2736 | 0.00019372 | -0.0040919 | 0.095953 | 0.095906 | 0.095953 | 0.99063 | -0.46423 | 0.99069 | -0.46378 | 15.0397
52 | 0.89906 | 0.37791 | -0.89903 | -0.37853 | 2.9056e-05 | -0.00061868 | 0.028464 | 0.028471 | 0.028471 | 0.98909 | -0.45579 | 0.98906 | -0.45559 | 12.9414
53 | -3.1659 | -1.337 | 3.1705 | 1.3475 | 0.0045284 | 0.010456 | 0.10014 | 0.10012 | 0.10014 | 0.99069 | -0.46378 | 0.99326 | -0.30649 | 15.5256
54 | 0.74918 | 0.30596 | -0.74787 | -0.30668 | 0.0013183 | -0.00071908 | 0.02362 | 0.023637 | 0.023637 | 0.98906 | -0.45559 | 0.98718 | -0.47436 | 11.2556
55 | -3.5648 | -1.5375 | 3.565 | 1.5354 | 0.00014091 | -0.0021417 | 0.11283 | 0.11281 | 0.11283 | 0.99326 | -0.30649 | 0.9933 | -0.30624 | 17.6851
56 | 0.24247 | 0.11647 | -0.24247 | -0.11743 | 3.3413e-06 | -0.00096209 | 0.0078179 | 0.0078301 | 0.0078301 | 0.99326 | -0.30649 | 0.99325 | -0.30637 | 3.5591
57 | -3.565 | -1.5354 | 3.5659 | 1.521 | 0.00094008 | -0.014319 | 0.11281 | 0.11264 | 0.11281 | 0.9933 | -0.30624 | 0.99358 | -0.30452 | 17.6811
58 | 0.61096 | 0.29482 | -0.61094 | -0.29564 | 1.8222e-05 | -0.00082235 | 0.019709 | 0.01972 | 0.01972 | 0.99358 | -0.30452 | 0.99355 | -0.30426 | 8.9636
59 | 0.31678 | 0.15318 | -0.31677 | -0.15342 | 1.4543e-06 | -0.00024515 | 0.010223 | 0.010227 | 0.010227 | 0.99355 | -0.30426 | 0.99355 | -0.30422 | 4.6484
60 | -0.14093 | -0.068258 | 0.14094 | 0.068029 | 7.3847e-06 | -0.00022858 | 0.004564 | 0.004561 | 0.004564 | 0.99047 | -0.33663 | 0.99053 | -0.33628 | 2.1733
61 | -0.14094 | -0.068029 | 0.14097 | 0.038905 | 3.2036e-05 | -0.029124 | 0.004561 | 0.0042611 | 0.004561 | 0.99053 | -0.33628 | 0.99075 | -0.33722 | 2.0732
62 | -0.21041 | -0.072471 | 0.21044 | 0.061691 | 2.544e-05 | -0.01078 | 0.0064843 | 0.0063888 | 0.0064843 | 0.99075 | -0.33722 | 0.99086 | -0.33736 | 2.9474
63 | 0.069439 | 0.033565 | -0.069438 | -0.03363 | 5.0327e-07 | -6.5204e-05 | 0.0022472 | 0.0022481 | 0.0022481 | 0.99075 | -0.33722 | 0.99074 | -0.33727 | 1.0705
64 | -0.21044 | -0.061691 | 0.21044 | 0.06115 | 1.2576e-06 | -0.00054101 | 0.0063888 | 0.0063844 | 0.0063888 | 0.99086 | -0.33736 | 0.99087 | -0.33736 | 2.904
65 | -0.36869 | -0.1378 | 0.36871 | 0.13771 | 1.9289e-05 | -8.4434e-05 | 0.011467 | 0.011466 | 0.011467 | 0.99087 | -0.33736 | 0.99093 | -0.33669 | 5.4605
66 | 0.45634 | 0.17522 | -0.45634 | -0.17586 | 7.475e-06 | -0.00064512 | 0.014239 | 0.014245 | 0.014245 | 0.99105 | -0.33727 | 0.99103 | -0.3372 | 6.4752
67 | -0.5732 | -0.23181 | 0.57326 | 0.23173 | 5.7302e-05 | -8.0386e-05 | 0.01801 | 0.018009 | 0.01801 | 0.99105 | -0.33727 | 0.99115 | -0.33618 | 8.5763
68 | 0.45634 | 0.17586 | -0.4563 | -0.17881 | 3.4298e-05 | -0.0029519 | 0.014245 | 0.014277 | 0.014277 | 0.99103 | -0.3372 | 0.99096 | -0.33685 | 6.4894
69 | -0.57326 | -0.23173 | 0.57339 | 0.22457 | 0.00013245 | -0.0071687 | 0.018009 | 0.017931 | 0.018009 | 0.99115 | -0.33618 | 0.99137 | -0.33733 | 8.1859
70 | -0.57339 | -0.22457 | 0.57342 | 0.2232 | 2.5124e-05 | -0.0013672 | 0.017931 | 0.017917 | 0.017931 | 0.99137 | -0.33733 | 0.99142 | -0.33754 | 8.1506
71 | 0.4563 | 0.17881 | -0.45629 | -0.18013 | 1.5295e-05 | -0.0013121 | 0.014277 | 0.014291 | 0.014291 | 0.99096 | -0.33685 | 0.99093 | -0.33669 | 6.4958
72 | -0.63517 | -0.25311 | 0.63638 | 0.25185 | 0.0012066 | -0.0012553 | 0.019909 | 0.019887 | 0.019909 | 0.99142 | -0.33754 | 0.99345 | -0.31601 | 9.4804
73 | 0.21858 | 0.087387 | -0.21857 | -0.089284 | 5.2554e-06 | -0.0018966 | 0.0069098 | 0.0069307 | 0.0069307 | 0.98344 | -0.78124 | 0.98341 | -0.78111 | 3.1503
74 | -0.32191 | -0.13744 | 0.32216 | 0.13606 | 0.00024862 | -0.0013743 | 0.010275 | 0.010257 | 0.010275 | 0.98344 | -0.78124 | 0.98425 | -0.77368 | 4.8926
75 | 0.21857 | 0.089284 | -0.21855 | -0.097202 | 2.2297e-05 | -0.0079185 | 0.0069307 | 0.007022 | 0.007022 | 0.98341 | -0.78111 | 0.98332 | -0.78047 | 3.1918
76 | -0.3817 | -0.16489 | 0.38173 | 0.16103 | 3.3128e-05 | -0.0038642 | 0.012195 | 0.01215 | 0.012195 | 0.98425 | -0.77368 | 0.98433 | -0.77422 | 5.5432
77 | 0.1452 | 0.070249 | -0.14519 | -0.07032 | 2.5239e-06 | -7.133e-05 | 0.0047352 | 0.0047362 | 0.0047362 | 0.98332 | -0.78047 | 0.9833 | -0.78058 | 2.2553
78 | 0.073355 | 0.026954 | -0.073354 | -0.03018 | 9.9665e-07 | -0.0032267 | 0.0022943 | 0.0023286 | 0.0023286 | 0.98332 | -0.78047 | 0.9833 | -0.7804 | 1.0585
79 | 0.073354 | 0.03018 | -0.073352 | -0.035526 | 1.7214e-06 | -0.0053458 | 0.0023286 | 0.0023928 | 0.0023928 | 0.9833 | -0.7804 | 0.98328 | -0.78023 | 1.0876
80 | -0.38173 | -0.16103 | 0.38185 | 0.14698 | 0.0001184 | -0.014049 | 0.01215 | 0.011996 | 0.01215 | 0.98433 | -0.77422 | 0.98463 | -0.77586 | 5.5229
81 | -0.45149 | -0.17735 | 0.45161 | 0.16741 | 0.00011549 | -0.0099429 | 0.014222 | 0.014117 | 0.014222 | 0.98463 | -0.77586 | 0.98487 | -0.77694 | 6.4643
82 | 0.069642 | 0.030367 | -0.069641 | -0.033729 | 9.7951e-07 | -0.0033617 | 0.0022274 | 0.0022686 | 0.0022686 | 0.98463 | -0.77586 | 0.98461 | -0.77575 | 1.0312
83 | 0.26828 | 0.11378 | -0.26825 | -0.11973 | 2.529e-05 | -0.0059571 | 0.0085414 | 0.0086112 | 0.0086112 | 0.98487 | -0.77694 | 0.98478 | -0.77631 | 3.9142
84 | 0.28882 | 0.13215 | -0.28881 | -0.13436 | 1.1081e-05 | -0.0022083 | 0.0093096 | 0.0093368 | 0.0093368 | 0.98487 | -0.77694 | 0.98484 | -0.77665 | 4.244
85 | -1.0087 | -0.41334 | 1.0088 | 0.41334 | 0.00012447 | -1.2856e-06 | 0.031952 | 0.031951 | 0.031952 | 0.98487 | -0.77694 | 0.985 | -0.77563 | 15.2152
86 | 0.26825 | 0.11973 | -0.26823 | -0.11995 | 2.7053e-05 | -0.00022001 | 0.0086112 | 0.008614 | 0.008614 | 0.98478 | -0.77631 | 0.98468 | -0.77718 | 4.1019
87 | 0.13464 | 0.063001 | -0.13464 | -0.06519 | 2.4119e-06 | -0.0021891 | 0.0043573 | 0.0043849 | 0.0043849 | 0.98484 | -0.77665 | 0.98482 | -0.7765 | 1.9931
88 | 0.15416 | 0.071362 | -0.15416 | -0.072884 | 2.1858e-06 | -0.0015227 | 0.0049795 | 0.0049984 | 0.0049984 | 0.98484 | -0.77665 | 0.98482 | -0.77653 | 2.272
89 | -1.182 | -0.497 | 1.1823 | 0.49706 | 0.00031215 | 6.2322e-05 | 0.037579 | 0.037575 | 0.037579 | 0.985 | -0.77563 | 0.98536 | -0.76243 | 9.1656
90 | 0.10082 | 0.048611 | -0.10082 | -0.04879 | 2.9968e-06 | -0.00017905 | 0.0032802 | 0.0032825 | 0.0032825 | 0.985 | -0.77563 | 0.98497 | -0.77583 | 1.5631
91 | 0.10751 | 0.042115 | -0.10751 | -0.043519 | 9.3153e-07 | -0.0014032 | 0.003385 | 0.0034002 | 0.0034002 | 0.98468 | -0.77718 | 0.98467 | -0.77714 | 1.5455
92 | 0.10751 | 0.043519 | -0.1075 | -0.051371 | 5.3756e-06 | -0.0078522 | 0.0034002 | 0.0034931 | 0.0034931 | 0.98467 | -0.77714 | 0.98462 | -0.77679 | 1.5878
93 | 0.1075 | 0.051371 | -0.1075 | -0.052065 | 4.8969e-07 | -0.00069395 | 0.0034931 | 0.0035019 | 0.0035019 | 0.98462 | -0.77679 | 0.98462 | -0.77675 | 1.5918
94 | 0.098167 | 0.045765 | -0.098163 | -0.045993 | 3.5732e-06 | -0.00022792 | 0.0031748 | 0.0031777 | 0.0031777 | 0.98482 | -0.77653 | 0.98478 | -0.7768 | 1.5132
95 | 0.098163 | 0.045993 | -0.098162 | -0.047542 | 9.0781e-07 | -0.0015496 | 0.0031777 | 0.0031972 | 0.0031972 | 0.98478 | -0.7768 | 0.98478 | -0.77673 | 1.4533
96 | 0.13464 | 0.06519 | -0.13464 | -0.065208 | 5.5751e-07 | -1.8493e-05 | 0.0043849 | 0.0043851 | 0.0043851 | 0.98482 | -0.7765 | 0.98481 | -0.77652 | 2.0881
97 | -1.1823 | -0.49706 | 1.1823 | 0.49649 | 8.0329e-06 | -0.00056932 | 0.037575 | 0.037568 | 0.037575 | 0.98536 | -0.76243 | 0.98537 | -0.76226 | 8.9251
98 | 0.10082 | 0.04879 | -0.10082 | -0.048827 | 6.2662e-07 | -3.7405e-05 | 0.0032825 | 0.003283 | 0.003283 | 0.98497 | -0.77583 | 0.98496 | -0.77587 | 1.5633
99 | -1.5977 | -0.69466 | 1.5977 | 0.69298 | 2.2305e-05 | -0.0016789 | 0.051037 | 0.051017 | 0.051037 | 0.98541 | -0.76074 | 0.98542 | -0.76066 | 7.9995
100 | 0.071956 | 0.03375 | -0.071955 | -0.03485 | 3.4531e-07 | -0.0010996 | 0.0023283 | 0.0023422 | 0.0023422 | 0.98541 | -0.76074 | 0.9854 | -0.7607 | 1.0646
101 | 1.3615 | 0.58135 | -1.3614 | -0.58134 | 1.2069e-05 | 8.3285e-06 | 0.043368 | 0.043368 | 0.043368 | 0.98541 | -0.76074 | 0.98539 | -0.76171 | 6.7237
102 | -1.5977 | -0.69298 | 1.5977 | 0.69128 | 2.2616e-05 | -0.0017037 | 0.051017 | 0.050997 | 0.051017 | 0.98542 | -0.76066 | 0.98544 | -0.76057 | 7.9964
103 | 1.1824 | 0.49461 | -1.1823 | -0.49649 | 2.6583e-05 | -0.0018856 | 0.037546 | 0.037568 | 0.037568 | 0.98539 | -0.76171 | 0.98537 | -0.76226 | 8.9235
104 | 0.078869 | 0.036833 | -0.078868 | -0.037789 | 3.5957e-07 | -0.00095586 | 0.0025499 | 0.0025619 | 0.0025619 | 0.98544 | -0.76057 | 0.98543 | -0.76053 | 1.1645
105 | 0.078868 | 0.037789 | -0.078868 | -0.038198 | 1.5489e-07 | -0.00040901 | 0.0025619 | 0.0025671 | 0.0025671 | 0.98543 | -0.76053 | 0.98543 | -0.76051 | 1.1669
106 | 0.081177 | 0.039023 | -0.081177 | -0.039316 | 1.1083e-07 | -0.00029266 | 0.0026003 | 0.002604 | 0.002604 | 0.99991 | -0.00041332 | 0.99991 | -0.00040153 | 1.1836
107 | -0.67925 | -0.29845 | 0.67989 | 0.27459 | 0.00064299 | -0.023861 | 0.021715 | 0.021442 | 0.021715 | 0.98629 | -0.46861 | 0.98718 | -0.47436 | 9.8706
108 | 0.067973 | 0.032086 | -0.067973 | -0.032921 | 2.3257e-07 | -0.00083495 | 0.002198 | 0.0022086 | 0.0022086 | 0.98718 | -0.47436 | 0.98718 | -0.47433 | 1.0039

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 8.7402 | 3.7586

## res_load
| p_mw | q_mvar
0 | 0.19268 | 0.093317
1 | 0.12539 | 0.060727
2 | 0.19642 | 0.095131
3 | 0.27759 | 0.13444
4 | 0.27228 | 0.13187
5 | 0.10306 | 0.049914
6 | 0.2096 | 0.10151
7 | 0.077224 | 0.037401
8 | 0.15251 | 0.073865
9 | 0.13092 | 0.063408
10 | 0.41283 | 0.19994
11 | 0.26771 | 0.12966
12 | 0.15693 | 0.076003
13 | 0.14516 | 0.070306
14 | 0.38817 | 0.188
15 | 0.13871 | 0.067182
16 | 0.17774 | 0.086085
17 | 0.21828 | 0.10572
18 | 0.14387 | 0.069678
19 | 0.13662 | 0.06617
20 | 0.10771 | 0.052168
21 | 0.10609 | 0.051382
22 | 0.10149 | 0.049153
23 | 0.13096 | 0.063425
24 | 0.14985 | 0.072573
25 | 0.15189 | 0.073564
26 | 0.24247 | 0.11743
27 | 0.29416 | 0.14247
28 | 0.11758 | 0.056947
29 | 0.14093 | 0.068258
30 | 0.069438 | 0.03363
31 | 0.15826 | 0.076647
32 | 0.11686 | 0.056598
33 | 0.061754 | 0.029909
34 | 0.087573 | 0.042413
35 | 0.27206 | 0.13176
36 | 0.10334 | 0.050048
37 | 0.059534 | 0.028834
38 | 0.073352 | 0.035526
39 | 0.14519 | 0.07032
40 | 0.069641 | 0.033729
41 | 0.072374 | 0.035052
42 | 0.16072 | 0.077839
43 | 0.1075 | 0.052065
44 | 0.055996 | 0.02712
45 | 0.098162 | 0.047542
46 | 0.13464 | 0.065208
47 | 0.16428 | 0.079563
48 | 0.071955 | 0.03485
49 | 0.17908 | 0.086734
50 | 0.10082 | 0.048827
51 | 0.081177 | 0.039316
52 | 0.31677 | 0.15342
53 | 0.078868 | 0.038198
54 | 0.067973 | 0.032921
55 | 0.29394 | 0.14236

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1