## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_281_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_281_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_281_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_281_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_281_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_281_0_node_6 | 20 | n |  | TRUE
6 | bus_MV_281_0_node_5 | 20 | n |  | TRUE
7 | bus_MV_281_0_node_10 | 20 | n |  | TRUE
8 | bus_MV_281_0_node_7 | 20 | n |  | TRUE
9 | bus_MV_281_0_node_8 | 20 | n |  | TRUE
10 | bus_MV_281_0_node_9 | 20 | n |  | TRUE
11 | bus_MV_281_0_node_31 | 20 | n |  | TRUE
12 | bus_MV_281_0_node_11 | 20 | n |  | TRUE
13 | bus_MV_281_0_node_13 | 20 | n |  | TRUE
14 | bus_MV_281_0_node_32 | 20 | n |  | TRUE
15 | bus_MV_281_0_node_33 | 20 | n |  | TRUE
16 | bus_MV_281_0_node_14 | 20 | n |  | TRUE
17 | bus_MV_281_0_node_12 | 20 | n |  | TRUE
18 | bus_MV_281_0_node_15 | 20 | n |  | TRUE
19 | bus_MV_281_0_node_18 | 20 | n |  | TRUE
20 | bus_MV_281_0_node_23 | 20 | n |  | TRUE
21 | bus_MV_281_0_node_16 | 20 | n |  | TRUE
22 | bus_MV_281_0_node_22 | 20 | n |  | TRUE
23 | bus_MV_281_0_node_27 | 20 | n |  | TRUE
24 | bus_MV_281_0_node_17 | 20 | n |  | TRUE
25 | bus_MV_281_0_node_19 | 20 | n |  | TRUE
26 | bus_MV_281_0_node_20 | 20 | n |  | TRUE
27 | bus_MV_281_0_node_21 | 20 | n |  | TRUE
28 | bus_MV_281_0_node_28 | 20 | n |  | TRUE
29 | bus_MV_281_0_node_26 | 20 | n |  | TRUE
30 | bus_MV_281_0_node_25 | 20 | n |  | TRUE
31 | bus_MV_281_0_node_30 | 20 | n |  | TRUE
32 | bus_MV_281_0_node_29 | 20 | n |  | TRUE
33 | bus_MV_281_0_node_24 | 20 | n |  | TRUE
34 | bus_HV_281_0_node_2 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_281_0_load_0 | 0 | 1.8312 | 0.88689 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_281_0_load_1 | 1 | 3.204 | 1.5517 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_281_0_load_2 | 2 | 1.013 | 0.49063 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_281_0_load_4 | 4 | 0.095346 | 0.046178 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_281_0_load_6 | 5 | 3.6315 | 1.7588 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_281_0_load_10 | 7 | 0.65808 | 0.31872 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_281_0_load_9 | 10 | 1.7059 | 0.82618 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_281_0_load_31 | 11 | 0.16455 | 0.079697 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_281_0_load_11 | 12 | 1.457 | 0.70567 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_281_0_load_32 | 14 | 0.11796 | 0.057129 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_281_0_load_33 | 15 | 0.11796 | 0.057132 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_281_0_load_12 | 17 | 0.43122 | 0.20885 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_281_0_load_18 | 19 | 0.37426 | 0.18126 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_281_0_load_23 | 20 | 0.083719 | 0.040547 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_281_0_load_16 | 21 | 0.10617 | 0.051421 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_281_0_load_22 | 22 | 0.074065 | 0.035871 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_281_0_load_27 | 23 | 0.1642 | 0.079526 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_281_0_load_17 | 24 | 0.12404 | 0.060073 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_281_0_load_20 | 26 | 0.071139 | 0.034454 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_281_0_load_26 | 29 | 0.17745 | 0.085942 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_281_0_load_25 | 30 | 0.094769 | 0.045899 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_281_0_load_30 | 31 | 0.085543 | 0.04143 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_281_0_load_29 | 32 | 0.21825 | 0.1057 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_281_0_load_24 | 33 | 0.30451 | 0.14748 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_281_0_line_0 |  | 0 | 1 | 0.0012997 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
1 | MV_281_0_line_1 |  | 0 | 2 | 0.03881 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
2 | MV_281_0_line_2 |  | 1 | 3 | 0.037135 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
3 | MV_281_0_line_3 |  | 2 | 4 | 0.028387 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
4 | MV_281_0_line_4 |  | 3 | 5 | 0.055079 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
5 | MV_281_0_line_5 |  | 4 | 6 | 0.020886 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
6 | MV_281_0_line_6 |  | 5 | 7 | 0.0029745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_281_0_line_7 |  | 6 | 8 | 0.052762 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_281_0_line_8 |  | 6 | 9 | 0.60612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_281_0_line_9 |  | 7 | 12 | 0.022375 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_281_0_line_10 |  | 8 | 10 | 0.014389 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_281_0_line_11 |  | 9 | 11 | 0.064442 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_281_0_line_12 |  | 10 | 13 | 0.053159 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_281_0_line_13 |  | 11 | 14 | 0.032547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_281_0_line_14 |  | 11 | 15 | 0.037725 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_281_0_line_15 |  | 12 | 17 | 0.0087461 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_281_0_line_16 |  | 13 | 16 | 0.85382 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_281_0_line_17 |  | 16 | 18 | 0.043159 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_281_0_line_18 |  | 18 | 19 | 0.016547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_281_0_line_19 |  | 19 | 22 | 0.11744 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_281_0_line_20 |  | 19 | 23 | 0.097018 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_281_0_line_21 |  | 20 | 21 | 0.073171 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_281_0_line_22 |  | 21 | 24 | 0.074123 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_281_0_line_23 |  | 22 | 28 | 0.030465 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_281_0_line_24 |  | 23 | 29 | 0.029469 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_281_0_line_25 |  | 24 | 25 | 0.016446 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_281_0_line_26 |  | 25 | 26 | 0.017417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_281_0_line_27 |  | 25 | 27 | 0.039693 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_281_0_line_28 |  | 26 | 30 | 0.032989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_281_0_line_29 |  | 27 | 29 | 0.048469 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_281_0_line_30 |  | 28 | 32 | 0.089049 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_281_0_line_31 |  | 30 | 31 | 0.04303 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_281_0_line_32 |  | 31 | 33 | 0.085918 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_281_0_trafo_2 | 25 MVA 110/20 kV | 34 | 2 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2634503.1706 | 1127261.9353
1 | 2634502.9447 | 1127263.2152
2 | 2634509.9148 | 1127223.7154
3 | 2634496.4916 | 1127299.7853
4 | 2634514.8478 | 1127195.7602
5 | 2634442.2473 | 1127290.2325
6 | 2634518.4772 | 1127175.1923
7 | 2634439.3179 | 1127289.7166
8 | 2634466.3455 | 1127166.1353
9 | 2634414.9084 | 1127469.9623
10 | 2634452.1692 | 1127163.6724
11 | 2634387.7632 | 1127411.5009
12 | 2634417.2815 | 1127285.8358
13 | 2634399.803 | 1127154.5289
14 | 2634366.2986 | 1127387.035
15 | 2634355.3884 | 1127392.1342
16 | 2634560.5455 | 1126827.813
17 | 2634408.6679 | 1127284.3189
18 | 2634542.7676 | 1126838.5726
19 | 2634533.2349 | 1126852.1139
20 | 2634658.404 | 1126835.5939
21 | 2634607.6081 | 1126888.2606
22 | 2634493.7246 | 1126962.7082
23 | 2634602.8529 | 1126919.6852
24 | 2634675.7211 | 1126917.2689
25 | 2634691.2457 | 1126922.6969
26 | 2634707.7722 | 1126928.1949
27 | 2634671.2523 | 1126957.0108
28 | 2634483.5151 | 1126991.4118
29 | 2634628.5078 | 1126934.1601
30 | 2634739.0748 | 1126938.6088
31 | 2634779.9046 | 1126952.1922
32 | 2634409.84 | 1126972.1498
33 | 2634820.9182 | 1126876.6956
34 | 2634509.9148 | 1127223.7154

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99986 | -0.00050946 | 1.8312 | 0.88689
1 | 0.99985 | -0.00052373 | 3.204 | 1.5517
2 | 1 | 0 | -15.3168 | -7.3567
3 | 0.99978 | -0.00079253 | 0 | 0
4 | 0.99994 | -0.00068621 | 0.095346 | 0.046178
5 | 0.99959 | -0.0026981 | 3.6315 | 1.7588
6 | 0.99989 | -0.0011796 | 0 | 0
7 | 0.99958 | -0.0026075 | 0.65808 | 0.31872
8 | 0.99965 | 0.00095933 | 0 | 0
9 | 0.99959 | 0.0013223 | 0 | 0
10 | 0.99959 | 0.0015436 | 1.7059 | 0.82618
11 | 0.99955 | 0.0016212 | 0.16455 | 0.079697
12 | 0.99953 | -0.0021023 | 1.457 | 0.70567
13 | 0.99946 | 0.0026192 | 0 | 0
14 | 0.99955 | 0.0016664 | 0.11796 | 0.057129
15 | 0.99955 | 0.0016734 | 0.11796 | 0.057132
16 | 0.99742 | 0.020523 | 0 | 0
17 | 0.99952 | -0.0020572 | 0.43122 | 0.20885
18 | 0.99732 | 0.02146 | 0 | 0
19 | 0.99728 | 0.021819 | 0.37426 | 0.18126
20 | 0.99688 | 0.021729 | 0.083719 | 0.040547
21 | 0.99689 | 0.021804 | 0.10617 | 0.051421
22 | 0.99723 | 0.022201 | 0.074065 | 0.035871
23 | 0.99705 | 0.020329 | 0.1642 | 0.079526
24 | 0.99691 | 0.021639 | 0.12404 | 0.060073
25 | 0.99691 | 0.021579 | 0 | 0
26 | 0.9969 | 0.021693 | 0.071139 | 0.034454
27 | 0.99696 | 0.021176 | 0 | 0
28 | 0.99723 | 0.022276 | 0 | 0
29 | 0.99701 | 0.020687 | 0.17745 | 0.085942
30 | 0.99688 | 0.021882 | 0.094769 | 0.045899
31 | 0.99686 | 0.022083 | 0.085543 | 0.04143
32 | 0.9972 | 0.022504 | 0.21825 | 0.1057
33 | 0.99681 | 0.021764 | 0.30451 | 0.14748
34 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 9.3834 | 4.5397 | -9.3834 | -4.5398 | 3.6375e-05 | -6.1155e-05 | 0.30095 | 0.30096 | 0.30096 | 0.99986 | -0.00050946 | 0.99985 | -0.00052373 | 47.1718
1 | -11.2146 | -5.4266 | 11.2162 | 5.4251 | 0.0015515 | -0.0015645 | 0.3597 | 0.35967 | 0.3597 | 0.99986 | -0.00050946 | 1 | 0 | 56.3791
2 | 6.1794 | 2.9881 | -6.179 | -2.9901 | 0.00045071 | -0.0020786 | 0.19817 | 0.1982 | 0.1982 | 0.99985 | -0.00052373 | 0.99978 | -0.00079253 | 31.0663
3 | 4.0866 | 1.9212 | -4.0864 | -1.922 | 0.00023301 | -0.00080446 | 0.13036 | 0.13037 | 0.13037 | 1 | 0 | 0.99994 | -0.00068621 | 36.0134
4 | 6.179 | 2.9901 | -6.1779 | -2.9913 | 0.0010452 | -0.0011288 | 0.1982 | 0.19823 | 0.19823 | 0.99978 | -0.00079253 | 0.99959 | -0.0026981 | 54.7588
5 | 3.991 | 1.8758 | -3.9909 | -1.8764 | 0.00016351 | -0.00059756 | 0.12731 | 0.12732 | 0.12732 | 0.99994 | -0.00068621 | 0.99989 | -0.0011796 | 35.171
6 | 2.5465 | 1.2325 | -2.5464 | -1.2325 | 2.6507e-05 | -6.31e-05 | 0.0817 | 0.081701 | 0.081701 | 0.99959 | -0.0026981 | 0.99958 | -0.0026075 | 37.1369
7 | 3.5903 | 1.7001 | -3.5893 | -1.701 | 0.00092659 | -0.00098432 | 0.11469 | 0.1147 | 0.1147 | 0.99989 | -0.0011796 | 0.99965 | 0.00095933 | 52.1373
8 | 0.40062 | 0.17632 | -0.40049 | -0.19075 | 0.00013097 | -0.014425 | 0.012637 | 0.012811 | 0.012811 | 0.99989 | -0.0011796 | 0.99959 | 0.0013223 | 5.8231
9 | 1.8883 | 0.9138 | -1.8882 | -0.9143 | 0.00010965 | -0.00050124 | 0.060584 | 0.060591 | 0.060591 | 0.99958 | -0.0026075 | 0.99953 | -0.0021023 | 27.5414
10 | 3.5893 | 1.701 | -3.5891 | -1.7013 | 0.00025273 | -0.00026832 | 0.1147 | 0.11471 | 0.11471 | 0.99965 | 0.00095933 | 0.99959 | 0.0015436 | 52.1392
11 | 0.40049 | 0.19075 | -0.40047 | -0.19228 | 1.414e-05 | -0.0015331 | 0.012811 | 0.01283 | 0.01283 | 0.99959 | 0.0013223 | 0.99955 | 0.0016212 | 5.8318
12 | 1.8832 | 0.87512 | -1.883 | -0.87631 | 0.00025531 | -0.0011923 | 0.059972 | 0.059987 | 0.059987 | 0.99959 | 0.0015436 | 0.99946 | 0.0026192 | 27.267
13 | 0.11796 | 0.056353 | -0.11796 | -0.057129 | 6.2093e-07 | -0.00077621 | 0.0037755 | 0.0037852 | 0.0037852 | 0.99955 | 0.0016212 | 0.99955 | 0.0016664 | 1.7205
14 | 0.11796 | 0.056232 | -0.11796 | -0.057132 | 7.195e-07 | -0.00089971 | 0.0037741 | 0.0037854 | 0.0037854 | 0.99955 | 0.0016212 | 0.99955 | 0.0016734 | 1.7206
15 | 0.43122 | 0.20864 | -0.43122 | -0.20885 | 2.2354e-06 | -0.00020796 | 0.013835 | 0.013838 | 0.013838 | 0.99953 | -0.0021023 | 0.99952 | -0.0020572 | 6.2899
16 | 1.883 | 0.87631 | -1.8789 | -0.89541 | 0.0041188 | -0.019101 | 0.059987 | 0.060238 | 0.060238 | 0.99946 | 0.0026192 | 0.99742 | 0.020523 | 27.3808
17 | 1.8789 | 0.89541 | -1.8786 | -0.89638 | 0.00020911 | -0.00096302 | 0.060238 | 0.06025 | 0.06025 | 0.99742 | 0.020523 | 0.99732 | 0.02146 | 27.3866
18 | 1.8786 | 0.89638 | -1.8786 | -0.89675 | 8.0197e-05 | -0.00036916 | 0.06025 | 0.060255 | 0.060255 | 0.99732 | 0.02146 | 0.99728 | 0.021819 | 27.3888
19 | 0.29233 | 0.13595 | -0.29232 | -0.13874 | 1.3705e-05 | -0.0027846 | 0.0093323 | 0.0093666 | 0.0093666 | 0.99728 | 0.021819 | 0.99723 | 0.022201 | 4.2575
20 | 1.212 | 0.57953 | -1.2117 | -0.57948 | 0.0002614 | 4.8568e-05 | 0.038887 | 0.038888 | 0.038888 | 0.99728 | 0.021819 | 0.99705 | 0.020329 | 18.5181
21 | -0.083719 | -0.040547 | 0.08372 | 0.040461 | 9.4557e-07 | -8.6216e-05 | 0.0026937 | 0.0026926 | 0.0026937 | 0.99688 | 0.021729 | 0.99689 | 0.021804 | 1.2827
22 | -0.18989 | -0.091881 | 0.18989 | 0.090124 | 3.6792e-06 | -0.0017577 | 0.0061086 | 0.0060866 | 0.0061086 | 0.99689 | 0.021804 | 0.99691 | 0.021639 | 2.7767
23 | 0.21825 | 0.10287 | -0.21825 | -0.10359 | 1.9866e-06 | -0.00072278 | 0.0069845 | 0.0069934 | 0.0069934 | 0.99723 | 0.022201 | 0.99723 | 0.022276 | 3.1788
24 | 1.0475 | 0.49996 | -1.0475 | -0.50064 | 4.4442e-05 | -0.00068625 | 0.033606 | 0.033615 | 0.033615 | 0.99705 | 0.020329 | 0.99701 | 0.020687 | 15.2794
25 | -0.31393 | -0.1502 | 0.31393 | 0.14981 | 2.2286e-06 | -0.00038959 | 0.010077 | 0.010072 | 0.010077 | 0.99691 | 0.021639 | 0.99691 | 0.021579 | 4.5806
26 | 0.556 | 0.26696 | -0.55599 | -0.26737 | 7.4187e-06 | -0.00041108 | 0.01786 | 0.017865 | 0.017865 | 0.99691 | 0.021579 | 0.9969 | 0.021693 | 8.1204
27 | -0.86993 | -0.41677 | 0.86997 | 0.41584 | 4.1326e-05 | -0.00092965 | 0.027932 | 0.02792 | 0.027932 | 0.99691 | 0.021579 | 0.99696 | 0.021176 | 12.6964
28 | 0.48485 | 0.23292 | -0.48484 | -0.2337 | 1.0692e-05 | -0.0007796 | 0.015576 | 0.015586 | 0.015586 | 0.9969 | 0.021693 | 0.99688 | 0.021882 | 7.0845
29 | -0.86997 | -0.41584 | 0.87002 | 0.4147 | 5.0415e-05 | -0.0011353 | 0.02792 | 0.027906 | 0.02792 | 0.99696 | 0.021176 | 0.99701 | 0.020687 | 12.6911
30 | 0.21825 | 0.10359 | -0.21825 | -0.1057 | 5.8361e-06 | -0.0021126 | 0.0069934 | 0.0070199 | 0.0070199 | 0.99723 | 0.022276 | 0.9972 | 0.022504 | 3.1909
31 | 0.39007 | 0.1878 | -0.39006 | -0.18882 | 9.0376e-06 | -0.0010183 | 0.012537 | 0.012549 | 0.012549 | 0.99688 | 0.021882 | 0.99686 | 0.022083 | 5.7043
32 | 0.30452 | 0.14739 | -0.30451 | -0.14748 | 1.4695e-05 | -9.2716e-05 | 0.009797 | 0.0097983 | 0.0097983 | 0.99686 | 0.022083 | 0.99681 | 0.021764 | 4.6659

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 16.3298 | 7.8473

## res_load
| p_mw | q_mvar
0 | 1.8312 | 0.88689
1 | 3.204 | 1.5517
2 | 1.013 | 0.49063
3 | 0.095346 | 0.046178
4 | 3.6315 | 1.7588
5 | 0.65808 | 0.31872
6 | 1.7059 | 0.82618
7 | 0.16455 | 0.079697
8 | 1.457 | 0.70567
9 | 0.11796 | 0.057129
10 | 0.11796 | 0.057132
11 | 0.43122 | 0.20885
12 | 0.37426 | 0.18126
13 | 0.083719 | 0.040547
14 | 0.10617 | 0.051421
15 | 0.074065 | 0.035871
16 | 0.1642 | 0.079526
17 | 0.12404 | 0.060073
18 | 0.071139 | 0.034454
19 | 0.17745 | 0.085942
20 | 0.094769 | 0.045899
21 | 0.085543 | 0.04143
22 | 0.21825 | 0.1057
23 | 0.30451 | 0.14748

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1