## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_288_1_node_34 | 20 | n |  | TRUE
1 | bus_MV_288_1_node_106 | 20 | n |  | TRUE
2 | bus_MV_288_1_node_45 | 20 | n |  | TRUE
3 | bus_MV_288_1_node_39 | 20 | n |  | TRUE
4 | bus_MV_288_1_node_107 | 20 | n |  | TRUE
5 | bus_MV_288_1_node_36 | 20 | n |  | TRUE
6 | bus_MV_288_1_node_37 | 20 | n |  | TRUE
7 | bus_MV_288_1_node_38 | 20 | n |  | TRUE
8 | bus_MV_288_1_node_158 | 20 | n |  | TRUE
9 | bus_MV_288_1_node_156 | 20 | n |  | TRUE
10 | bus_MV_288_1_node_95 | 20 | n |  | TRUE
11 | bus_MV_288_1_node_96 | 20 | n |  | TRUE
12 | bus_MV_288_1_node_157 | 20 | n |  | TRUE
13 | bus_MV_288_1_node_105 | 20 | n |  | TRUE
14 | bus_MV_288_1_node_40 | 20 | n |  | TRUE
15 | bus_MV_288_1_node_41 | 20 | n |  | TRUE
16 | bus_MV_288_1_node_42 | 20 | n |  | TRUE
17 | bus_MV_288_1_node_43 | 20 | n |  | TRUE
18 | bus_MV_288_1_node_155 | 20 | n |  | TRUE
19 | bus_MV_288_1_node_174 | 20 | n |  | TRUE
20 | bus_MV_288_1_node_44 | 20 | n |  | TRUE
21 | bus_MV_288_1_node_88 | 20 | n |  | TRUE
22 | bus_MV_288_1_node_52 | 20 | n |  | TRUE
23 | bus_MV_288_1_node_46 | 20 | n |  | TRUE
24 | bus_MV_288_1_node_47 | 20 | n |  | TRUE
25 | bus_MV_288_1_node_48 | 20 | n |  | TRUE
26 | bus_MV_288_1_node_49 | 20 | n |  | TRUE
27 | bus_MV_288_1_node_50 | 20 | n |  | TRUE
28 | bus_MV_288_1_node_53 | 20 | n |  | TRUE
29 | bus_MV_288_1_node_54 | 20 | n |  | TRUE
30 | bus_MV_288_1_node_91 | 20 | n |  | TRUE
31 | bus_MV_288_1_node_51 | 20 | n |  | TRUE
32 | bus_MV_288_1_node_139 | 20 | n |  | TRUE
33 | bus_MV_288_1_node_142 | 20 | n |  | TRUE
34 | bus_MV_288_1_node_141 | 20 | n |  | TRUE
35 | bus_MV_288_1_node_67 | 20 | n |  | TRUE
36 | bus_MV_288_1_node_56 | 20 | n |  | TRUE
37 | bus_MV_288_1_node_140 | 20 | n |  | TRUE
38 | bus_MV_288_1_node_143 | 20 | n |  | TRUE
39 | bus_MV_288_1_node_144 | 20 | n |  | TRUE
40 | bus_MV_288_1_node_68 | 20 | n |  | TRUE
41 | bus_MV_288_1_node_55 | 20 | n |  | TRUE
42 | bus_MV_288_1_node_57 | 20 | n |  | TRUE
43 | bus_MV_288_1_node_58 | 20 | n |  | TRUE
44 | bus_MV_288_1_node_59 | 20 | n |  | TRUE
45 | bus_MV_288_1_node_90 | 20 | n |  | TRUE
46 | bus_MV_288_1_node_63 | 20 | n |  | TRUE
47 | bus_MV_288_1_node_89 | 20 | n |  | TRUE
48 | bus_MV_288_1_node_61 | 20 | n |  | TRUE
49 | bus_MV_288_1_node_60 | 20 | n |  | TRUE
50 | bus_MV_288_1_node_66 | 20 | n |  | TRUE
51 | bus_MV_288_1_node_168 | 20 | n |  | TRUE
52 | bus_MV_288_1_node_70 | 20 | n |  | TRUE
53 | bus_MV_288_1_node_62 | 20 | n |  | TRUE
54 | bus_MV_288_1_node_80 | 20 | n |  | TRUE
55 | bus_MV_288_1_node_83 | 20 | n |  | TRUE
56 | bus_MV_288_1_node_171 | 20 | n |  | TRUE
57 | bus_MV_288_1_node_64 | 20 | n |  | TRUE
58 | bus_MV_288_1_node_138 | 20 | n |  | TRUE
59 | bus_MV_288_1_node_65 | 20 | n |  | TRUE
60 | bus_MV_288_1_node_81 | 20 | n |  | TRUE
61 | bus_MV_288_1_node_136 | 20 | n |  | TRUE
62 | bus_MV_288_1_node_137 | 20 | n |  | TRUE
63 | bus_MV_288_1_node_84 | 20 | n |  | TRUE
64 | bus_MV_288_1_node_85 | 20 | n |  | TRUE
65 | bus_MV_288_1_node_148 | 20 | n |  | TRUE
66 | bus_MV_288_1_node_165 | 20 | n |  | TRUE
67 | bus_MV_288_1_node_82 | 20 | n |  | TRUE
68 | bus_MV_288_1_node_135 | 20 | n |  | TRUE
69 | bus_MV_288_1_node_133 | 20 | n |  | TRUE
70 | bus_MV_288_1_node_134 | 20 | n |  | TRUE
71 | bus_MV_288_1_node_170 | 20 | n |  | TRUE
72 | bus_MV_288_1_node_149 | 20 | n |  | TRUE
73 | bus_MV_288_1_node_150 | 20 | n |  | TRUE
74 | bus_MV_288_1_node_151 | 20 | n |  | TRUE
75 | bus_MV_288_1_node_152 | 20 | n |  | TRUE
76 | bus_MV_288_1_node_153 | 20 | n |  | TRUE
77 | bus_MV_288_1_node_154 | 20 | n |  | TRUE
78 | bus_MV_288_1_node_86 | 20 | n |  | TRUE
79 | bus_MV_288_1_node_77 | 20 | n |  | TRUE
80 | bus_MV_288_1_node_69 | 20 | n |  | TRUE
81 | bus_MV_288_1_node_71 | 20 | n |  | TRUE
82 | bus_MV_288_1_node_72 | 20 | n |  | TRUE
83 | bus_MV_288_1_node_74 | 20 | n |  | TRUE
84 | bus_MV_288_1_node_73 | 20 | n |  | TRUE
85 | bus_MV_288_1_node_76 | 20 | n |  | TRUE
86 | bus_MV_288_1_node_172 | 20 | n |  | TRUE
87 | bus_MV_288_1_node_94 | 20 | n |  | TRUE
88 | bus_MV_288_1_node_75 | 20 | n |  | TRUE
89 | bus_MV_288_1_node_93 | 20 | n |  | TRUE
90 | bus_MV_288_1_node_92 | 20 | n |  | TRUE
91 | bus_MV_288_1_node_97 | 20 | n |  | TRUE
92 | bus_MV_288_1_node_111 | 20 | n |  | TRUE
93 | bus_MV_288_1_node_108 | 20 | n |  | TRUE
94 | bus_MV_288_1_node_99 | 20 | n |  | TRUE
95 | bus_MV_288_1_node_100 | 20 | n |  | TRUE
96 | bus_MV_288_1_node_101 | 20 | n |  | TRUE
97 | bus_MV_288_1_node_102 | 20 | n |  | TRUE
98 | bus_MV_288_1_node_103 | 20 | n |  | TRUE
99 | bus_MV_288_1_node_112 | 20 | n |  | TRUE
100 | bus_MV_288_1_node_109 | 20 | n |  | TRUE
101 | bus_MV_288_1_node_110 | 20 | n |  | TRUE
102 | bus_MV_288_1_node_104 | 20 | n |  | TRUE
103 | bus_MV_288_1_node_146 | 20 | n |  | TRUE
104 | bus_MV_288_1_node_147 | 20 | n |  | TRUE
105 | bus_MV_288_1_node_145 | 20 | n |  | TRUE
106 | bus_MV_288_1_node_173 | 20 | n |  | TRUE
107 | bus_HV_288_1_node_52 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_288_1_load_34 | 0 | 0.3632 | 0.17591 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_288_1_load_106 | 1 | 0.16958 | 0.082134 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_288_1_load_45 | 2 | 0.33089 | 0.16026 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_288_1_load_39 | 3 | 0.10514 | 0.05092 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_288_1_load_36 | 5 | 0.097314 | 0.047132 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_288_1_load_158 | 8 | 0.15779 | 0.076421 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_288_1_load_95 | 10 | 0.12923 | 0.062589 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_288_1_load_157 | 12 | 0.25167 | 0.12189 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_288_1_load_155 | 18 | 0.10105 | 0.048942 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_288_1_load_174 | 19 | 0.11756 | 0.056937 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_288_1_load_88 | 21 | 0.32117 | 0.15555 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_288_1_load_46 | 23 | 0.39159 | 0.18966 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_288_1_load_91 | 30 | 0.34635 | 0.16775 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_288_1_load_139 | 32 | 0.35072 | 0.16986 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_288_1_load_141 | 34 | 0.70418 | 0.34105 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_288_1_load_67 | 35 | 0.21943 | 0.10628 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_288_1_load_56 | 36 | 0.36526 | 0.17691 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_288_1_load_140 | 37 | 0.37008 | 0.17924 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_288_1_load_144 | 39 | 0.35355 | 0.17123 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_288_1_load_90 | 45 | 0.40365 | 0.1955 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_288_1_load_89 | 47 | 0.32225 | 0.15607 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_288_1_load_66 | 50 | 0.37639 | 0.18229 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_288_1_load_168 | 51 | 0.2574 | 0.12466 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_288_1_load_70 | 52 | 0.13912 | 0.067378 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_288_1_load_80 | 54 | 0.3559 | 0.17237 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_288_1_load_171 | 56 | 0.11963 | 0.057937 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_288_1_load_138 | 58 | 0.07499 | 0.036319 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_288_1_load_81 | 60 | 0.29006 | 0.14048 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_288_1_load_136 | 61 | 0.096332 | 0.046656 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_288_1_load_137 | 62 | 0.16213 | 0.078524 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_288_1_load_148 | 65 | 0.81859 | 0.39646 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_288_1_load_165 | 66 | 0.2365 | 0.11454 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_288_1_load_133 | 69 | 0.080999 | 0.039229 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_288_1_load_134 | 70 | 0.13067 | 0.063284 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_288_1_load_170 | 71 | 0.093959 | 0.045506 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_288_1_load_151 | 74 | 0.67709 | 0.32793 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_288_1_load_152 | 75 | 0.14481 | 0.070135 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_288_1_load_154 | 77 | 0.675 | 0.32692 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_288_1_load_86 | 78 | 0.09179 | 0.044456 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_288_1_load_77 | 79 | 0.33897 | 0.16417 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_288_1_load_71 | 81 | 0.11887 | 0.057571 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_288_1_load_172 | 86 | 0.29053 | 0.14071 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_288_1_load_94 | 87 | 0.27987 | 0.13555 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_288_1_load_93 | 89 | 0.11628 | 0.056319 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_288_1_load_92 | 90 | 0.22471 | 0.10883 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_288_1_load_111 | 92 | 0.33093 | 0.16028 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_288_1_load_99 | 94 | 0.21907 | 0.1061 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_288_1_load_102 | 97 | 0.076224 | 0.036917 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_288_1_load_103 | 98 | 0.19907 | 0.096414 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_288_1_load_112 | 99 | 0.37698 | 0.18258 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_288_1_load_104 | 102 | 0.11153 | 0.054018 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_288_1_load_146 | 103 | 1.0146 | 0.49138 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_288_1_load_145 | 105 | 0.41151 | 0.19931 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_288_1_load_173 | 106 | 0.22049 | 0.10679 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_288_1_line_0 |  | 0 | 1 | 1.4878 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_288_1_line_1 |  | 1 | 4 | 0.10077 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_288_1_line_2 |  | 2 | 3 | 1.3527 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_288_1_line_3 |  | 3 | 14 | 0.037897 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_288_1_line_4 |  | 3 | 15 | 0.29592 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_288_1_line_5 |  | 4 | 93 | 0.2587 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_288_1_line_6 |  | 4 | 99 | 0.56901 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_288_1_line_7 |  | 5 | 6 | 0.29504 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_288_1_line_8 |  | 6 | 7 | 0.75666 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_288_1_line_9 |  | 7 | 10 | 0.028756 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_288_1_line_10 |  | 8 | 9 | 0.037881 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_288_1_line_11 |  | 9 | 12 | 0.018555 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_288_1_line_12 |  | 9 | 18 | 0.058795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_288_1_line_13 |  | 10 | 11 | 0.01246 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_288_1_line_14 |  | 11 | 91 | 0.3631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_288_1_line_15 |  | 12 | 13 | 0.78388 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_288_1_line_16 |  | 13 | 93 | 1.0362 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_288_1_line_17 |  | 13 | 102 | 0.073646 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_288_1_line_18 |  | 14 | 16 | 0.48234 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_288_1_line_19 |  | 15 | 17 | 0.2095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_288_1_line_20 |  | 16 | 18 | 0.0058734 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_288_1_line_21 |  | 17 | 19 | 0.026569 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_288_1_line_22 |  | 17 | 20 | 0.57203 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_288_1_line_23 |  | 20 | 21 | 0.044294 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_288_1_line_24 |  | 21 | 22 | 0.023906 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_288_1_line_25 |  | 22 | 31 | 0.22644 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
26 | MV_288_1_line_26 |  | 23 | 24 | 0.004097 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
27 | MV_288_1_line_27 |  | 23 | 25 | 0.034805 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
28 | MV_288_1_line_28 |  | 24 | 26 | 0.050847 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
29 | MV_288_1_line_29 |  | 24 | 27 | 0.21336 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
30 | MV_288_1_line_30 |  | 25 | 28 | 0.58473 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
31 | MV_288_1_line_31 |  | 25 | 29 | 0.082833 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
32 | MV_288_1_line_32 |  | 26 | 30 | 0.048674 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_288_1_line_33 |  | 27 | 31 | 0.24481 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
34 | MV_288_1_line_34 |  | 27 | 32 | 0.023654 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
35 | MV_288_1_line_35 |  | 28 | 35 | 0.089623 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
36 | MV_288_1_line_36 |  | 29 | 36 | 0.019003 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
37 | MV_288_1_line_37 |  | 31 | 33 | 0.031018 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
38 | MV_288_1_line_38 |  | 31 | 34 | 0.024729 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
39 | MV_288_1_line_39 |  | 32 | 37 | 0.019497 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
40 | MV_288_1_line_40 |  | 33 | 38 | 0.037165 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
41 | MV_288_1_line_41 |  | 33 | 39 | 0.020647 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
42 | MV_288_1_line_42 |  | 35 | 40 | 0.08282 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
43 | MV_288_1_line_43 |  | 36 | 41 | 0.019584 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
44 | MV_288_1_line_44 |  | 38 | 103 | 0.02522 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
45 | MV_288_1_line_45 |  | 38 | 104 | 0.11233 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
46 | MV_288_1_line_46 |  | 39 | 105 | 0.00022089 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_288_1_line_47 |  | 40 | 80 | 0.28423 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
48 | MV_288_1_line_48 |  | 41 | 42 | 0.2351 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
49 | MV_288_1_line_49 |  | 42 | 43 | 0.21385 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
50 | MV_288_1_line_50 |  | 42 | 44 | 0.5522 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
51 | MV_288_1_line_51 |  | 42 | 45 | 0.015558 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_288_1_line_52 |  | 43 | 46 | 0.23842 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
53 | MV_288_1_line_53 |  | 43 | 47 | 0.005881 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_288_1_line_54 |  | 44 | 48 | 0.84188 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
55 | MV_288_1_line_55 |  | 44 | 49 | 0.38647 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
56 | MV_288_1_line_56 |  | 44 | 50 | 0.025064 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_288_1_line_57 |  | 46 | 57 | 0.20746 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
58 | MV_288_1_line_58 |  | 46 | 58 | 0.0030259 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
59 | MV_288_1_line_59 |  | 48 | 52 | 0.034517 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_288_1_line_60 |  | 49 | 51 | 0.10043 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_288_1_line_61 |  | 53 | 54 | 0.070794 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_288_1_line_62 |  | 53 | 55 | 0.3621 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
63 | MV_288_1_line_63 |  | 53 | 56 | 0.56127 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
64 | MV_288_1_line_64 |  | 55 | 63 | 0.18107 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
65 | MV_288_1_line_65 |  | 55 | 64 | 0.3349 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
66 | MV_288_1_line_66 |  | 55 | 65 | 0.003476 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
67 | MV_288_1_line_67 |  | 57 | 59 | 0.22733 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
68 | MV_288_1_line_68 |  | 57 | 60 | 0.022806 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
69 | MV_288_1_line_69 |  | 59 | 61 | 0.097178 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_288_1_line_70 |  | 59 | 62 | 0.04199 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_288_1_line_71 |  | 60 | 67 | 0.055607 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
72 | MV_288_1_line_72 |  | 61 | 79 | 0.42565 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_288_1_line_73 |  | 63 | 66 | 0.047282 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
74 | MV_288_1_line_74 |  | 63 | 67 | 0.57942 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
75 | MV_288_1_line_75 |  | 64 | 68 | 0.17993 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
76 | MV_288_1_line_76 |  | 64 | 69 | 0.075321 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
77 | MV_288_1_line_77 |  | 65 | 72 | 0.008864 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
78 | MV_288_1_line_78 |  | 68 | 71 | 0.18427 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
79 | MV_288_1_line_79 |  | 69 | 70 | 0.019455 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
80 | MV_288_1_line_80 |  | 71 | 78 | 2.091 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
81 | MV_288_1_line_81 |  | 72 | 73 | 0.019998 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
82 | MV_288_1_line_82 |  | 72 | 74 | 0.031223 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
83 | MV_288_1_line_83 |  | 73 | 75 | 0.021468 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
84 | MV_288_1_line_84 |  | 73 | 76 | 0.010832 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
85 | MV_288_1_line_85 |  | 76 | 77 | 0.02639 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
86 | MV_288_1_line_86 |  | 80 | 81 | 0.16905 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
87 | MV_288_1_line_87 |  | 81 | 82 | 0.2261 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
88 | MV_288_1_line_88 |  | 82 | 83 | 0.59297 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
89 | MV_288_1_line_89 |  | 83 | 87 | 0.071508 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
90 | MV_288_1_line_90 |  | 83 | 84 | 0.7293 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
91 | MV_288_1_line_91 |  | 84 | 85 | 0.46531 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
92 | MV_288_1_line_92 |  | 84 | 86 | 0.004436 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
93 | MV_288_1_line_93 |  | 85 | 90 | 0.10505 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
94 | MV_288_1_line_94 |  | 85 | 88 | 0.42442 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
95 | MV_288_1_line_95 |  | 88 | 89 | 0.031435 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
96 | MV_288_1_line_96 |  | 91 | 92 | 0.020954 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_288_1_line_97 |  | 92 | 93 | 0.057071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_288_1_line_98 |  | 94 | 95 | 0.015268 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_288_1_line_99 |  | 94 | 96 | 0.02388 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_288_1_line_100 |  | 95 | 97 | 0.099336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_288_1_line_101 |  | 96 | 98 | 0.12042 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_288_1_line_102 |  | 98 | 100 | 0.14947 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
103 | MV_288_1_line_103 |  | 99 | 101 | 0.01593 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_288_1_line_104 |  | 100 | 101 | 0.16992 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_288_1_line_105 |  | 104 | 106 | 0.043666 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_288_1_trafo_52 | 25 MVA 110/20 kV | 107 | 22 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2606041.5811 | 1255494.0751
1 | 2606821.9311 | 1254227.3995
2 | 2604591.6999 | 1254274.8076
3 | 2605357.979 | 1253160.0212
4 | 2606918.4991 | 1254256.1849
5 | 2607519.6359 | 1252761.952
6 | 2607335.9334 | 1252992.8193
7 | 2606927.1997 | 1253589.6567
8 | 2605668.3081 | 1253254.0288
9 | 2605655.0163 | 1253289.5009
10 | 2606932.1611 | 1253617.981
11 | 2606934.2215 | 1253630.2692
12 | 2605666.0551 | 1253304.3878
13 | 2606196.5987 | 1253881.4362
14 | 2605394.8136 | 1253150.6703
15 | 2605317.3983 | 1252867.5714
16 | 2605610.9845 | 1253242.5399
17 | 2605362.7468 | 1252764.0551
18 | 2605614.5242 | 1253247.2269
19 | 2605367.652 | 1252737.9424
20 | 2605164.7908 | 1252559.47
21 | 2605120.4401 | 1252556.9081
22 | 2605096.4915 | 1252555.7314
23 | 2604667.8813 | 1252467.2921
24 | 2604667.6819 | 1252471.3835
25 | 2604635.7665 | 1252458.0613
26 | 2604661.991 | 1252521.901
27 | 2604846.8516 | 1252511.7294
28 | 2604317.2957 | 1252517.3964
29 | 2604631.8762 | 1252375.471
30 | 2604708.4682 | 1252536.3578
31 | 2604870.3523 | 1252544.5254
32 | 2604824.2159 | 1252513.9714
33 | 2604863.3784 | 1252574.7506
34 | 2604845.64 | 1252543.6471
35 | 2604236.6473 | 1252480.1259
36 | 2604650.857 | 1252376.3836
37 | 2604804.7836 | 1252512.3809
38 | 2604852.3332 | 1252610.2427
39 | 2604883.9966 | 1252575.8402
40 | 2604156.302 | 1252463.2367
41 | 2604670.4187 | 1252377.3242
42 | 2604672.3516 | 1252249.6424
43 | 2604791.5715 | 1252191.1647
44 | 2604397.529 | 1252175.6981
45 | 2604668.8922 | 1252234.4743
46 | 2604799.8019 | 1252033.5129
47 | 2604797.3736 | 1252192.2256
48 | 2603967.941 | 1252254.0065
49 | 2604313.9096 | 1251935.7145
50 | 2604405.2312 | 1252158.1479
51 | 2604414.3227 | 1251933.9751
52 | 2603965.1641 | 1252219.6045
53 | 2604603.9486 | 1251706.2133
54 | 2604533.2935 | 1251710.6514
55 | 2604922.0459 | 1251533.2082
56 | 2604982.7568 | 1251292.057
57 | 2604923.8193 | 1252030.3668
58 | 2604798.9782 | 1252030.6013
59 | 2605080.4765 | 1252095.9844
60 | 2604902.6668 | 1252021.6883
61 | 2605164.739 | 1252128.6999
62 | 2605073.1973 | 1252137.3386
63 | 2604950.343 | 1251592.6368
64 | 2604778.2499 | 1251293.3363
65 | 2604925.3695 | 1251532.19
66 | 2604994.1964 | 1251575.6954
67 | 2604901.3991 | 1251966.0954
68 | 2604759.5386 | 1251114.6387
69 | 2604840.9296 | 1251252.4459
70 | 2604855.3374 | 1251239.3722
71 | 2604800.5211 | 1250934.988
72 | 2604933.8446 | 1251529.5933
73 | 2604953.6803 | 1251526.63
74 | 2604937.3586 | 1251560.6164
75 | 2604950.5583 | 1251505.3913
76 | 2604964.4284 | 1251525.0489
77 | 2604971.7496 | 1251550.2329
78 | 2602932.3391 | 1249995.8055
79 | 2605590.3914 | 1252130.0266
80 | 2603887.5767 | 1252441.1986
81 | 2603718.5309 | 1252439.8468
82 | 2603494.2163 | 1252445.2608
83 | 2603125.2666 | 1252698.3467
84 | 2602821.6088 | 1252506.4836
85 | 2602672.8553 | 1252813.1835
86 | 2602825.164 | 1252503.8169
87 | 2603196.3943 | 1252689.1667
88 | 2602363.5307 | 1252910.8974
89 | 2602389.6587 | 1252893.4184
90 | 2602740.1432 | 1252881.3136
91 | 2606953.5819 | 1253952.8482
92 | 2606955.1568 | 1253973.7415
93 | 2606960.0771 | 1254030.5958
94 | 2607882.3816 | 1254392.4682
95 | 2607889.6786 | 1254379.0468
96 | 2607870.4587 | 1254413.1773
97 | 2607849.1505 | 1254293.4524
98 | 2607766.1468 | 1254352.7676
99 | 2607487.4957 | 1254252.1789
100 | 2607623.6211 | 1254307.7321
101 | 2607503.4725 | 1254252.3324
102 | 2606241.6502 | 1253939.7769
103 | 2604829.7288 | 1252599.0572
104 | 2604936.8155 | 1252670.8956
105 | 2604884.2172 | 1252575.8518
106 | 2604968.0161 | 1252698.0057
107 | 2605096.4915 | 1252555.7314

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98614 | 0.04295 | 0.3632 | 0.17591
1 | 0.9872 | 0.049769 | 0.16958 | 0.082134
2 | 0.99461 | 0.029448 | 0.33089 | 0.16026
3 | 0.99548 | 0.035004 | 0.10514 | 0.05092
4 | 0.98731 | 0.050451 | 0 | 0
5 | 0.98747 | 0.047132 | 0.097314 | 0.047132
6 | 0.98753 | 0.047492 | 0 | 0
7 | 0.98762 | 0.047041 | 0 | 0
8 | 0.99355 | 0.050235 | 0.15779 | 0.076421
9 | 0.99356 | 0.050164 | 0 | 0
10 | 0.98762 | 0.047041 | 0.12923 | 0.062589
11 | 0.98763 | 0.047022 | 0 | 0
12 | 0.99351 | 0.050599 | 0.25167 | 0.12189
13 | 0.99038 | 0.025443 | 0 | 0
14 | 0.99536 | 0.035973 | 0 | 0
15 | 0.99662 | 0.025992 | 0 | 0
16 | 0.99377 | 0.048523 | 0 | 0
17 | 0.99743 | 0.019705 | 0 | 0
18 | 0.99375 | 0.048679 | 0.10105 | 0.048942
19 | 0.99743 | 0.019742 | 0.11756 | 0.056937
20 | 0.99972 | 0.0021466 | 0 | 0
21 | 0.99989 | 0.00081118 | 0.32117 | 0.15555
22 | 1 | 0 | -15.2042 | -6.6766
23 | 0.99787 | -0.013166 | 0.39159 | 0.18966
24 | 0.99789 | -0.013097 | 0 | 0
25 | 0.99779 | -0.013729 | 0 | 0
26 | 0.99788 | -0.013119 | 0 | 0
27 | 0.99845 | -0.0094273 | 0 | 0
28 | 0.99757 | -0.016407 | 0 | 0
29 | 0.99762 | -0.014663 | 0 | 0
30 | 0.99785 | -0.013324 | 0.34635 | 0.16775
31 | 0.99915 | -0.0049544 | 0 | 0
32 | 0.99844 | -0.0094479 | 0.35072 | 0.16986
33 | 0.99913 | -0.005034 | 0 | 0
34 | 0.99914 | -0.004975 | 0.70418 | 0.34105
35 | 0.99754 | -0.01679 | 0.21943 | 0.10628
36 | 0.99759 | -0.014877 | 0.36526 | 0.17691
37 | 0.99844 | -0.0094565 | 0.37008 | 0.17924
38 | 0.99912 | -0.0050943 | 0 | 0
39 | 0.99912 | -0.0050526 | 0.35355 | 0.17123
40 | 0.99751 | -0.017115 | 0 | 0
41 | 0.99755 | -0.015088 | 0 | 0
42 | 0.9971 | -0.017599 | 0 | 0
43 | 0.99678 | -0.019263 | 0 | 0
44 | 0.99697 | -0.018685 | 0 | 0
45 | 0.99709 | -0.017524 | 0.40365 | 0.1955
46 | 0.99644 | -0.020979 | 0 | 0
47 | 0.99677 | -0.01924 | 0.32225 | 0.15607
48 | 0.99691 | -0.01964 | 0 | 0
49 | 0.99694 | -0.018872 | 0 | 0
50 | 0.99696 | -0.018572 | 0.37639 | 0.18229
51 | 0.99689 | -0.019186 | 0.2574 | 0.12466
52 | 0.9969 | -0.019583 | 0.13912 | 0.067378
53 | 0.99504 | -0.040265 | 0 | 0
54 | 0.99499 | -0.040572 | 0.3559 | 0.17237
55 | 0.99516 | -0.033722 | 0 | 0
56 | 0.99499 | -0.042817 | 0.11963 | 0.057937
57 | 0.99614 | -0.022411 | 0 | 0
58 | 0.99644 | -0.020979 | 0.07499 | 0.036319
59 | 0.9961 | -0.022604 | 0 | 0
60 | 0.99612 | -0.022544 | 0.29006 | 0.14048
61 | 0.99605 | -0.022104 | 0.096332 | 0.046656
62 | 0.99609 | -0.022687 | 0.16213 | 0.078524
63 | 0.99534 | -0.032895 | 0 | 0
64 | 0.99511 | -0.034031 | 0 | 0
65 | 0.99515 | -0.033732 | 0.81859 | 0.39646
66 | 0.99534 | -0.032909 | 0.2365 | 0.11454
67 | 0.99599 | -0.02986 | 0 | 0
68 | 0.9951 | -0.034094 | 0 | 0
69 | 0.99511 | -0.034054 | 0.080999 | 0.039229
70 | 0.99511 | -0.034057 | 0.13067 | 0.063284
71 | 0.99508 | -0.035402 | 0.093959 | 0.045506
72 | 0.99515 | -0.033749 | 0 | 0
73 | 0.99514 | -0.033769 | 0 | 0
74 | 0.99514 | -0.033774 | 0.67709 | 0.32793
75 | 0.99514 | -0.033773 | 0.14481 | 0.070135
76 | 0.99514 | -0.033778 | 0 | 0
77 | 0.99513 | -0.033799 | 0.675 | 0.32692
78 | 0.99495 | -0.042739 | 0.09179 | 0.044456
79 | 0.99577 | -0.023871 | 0.33897 | 0.16417
80 | 0.99742 | -0.018185 | 0 | 0
81 | 0.99732 | -0.025241 | 0.11887 | 0.057571
82 | 0.99726 | -0.026007 | 0 | 0
83 | 0.99709 | -0.027791 | 0 | 0
84 | 0.99695 | -0.029252 | 0 | 0
85 | 0.9969 | -0.029766 | 0 | 0
86 | 0.99695 | -0.029253 | 0.29053 | 0.14071
87 | 0.99709 | -0.027817 | 0.27987 | 0.13555
88 | 0.99689 | -0.029908 | 0 | 0
89 | 0.99688 | -0.029952 | 0.11628 | 0.056319
90 | 0.99689 | -0.029799 | 0.22471 | 0.10883
91 | 0.98773 | 0.046562 | 0 | 0
92 | 0.98774 | 0.046542 | 0.33093 | 0.16028
93 | 0.98778 | 0.046258 | 0 | 0
94 | 0.98602 | 0.044273 | 0.21907 | 0.1061
95 | 0.98602 | 0.044285 | 0 | 0
96 | 0.98603 | 0.04419 | 0 | 0
97 | 0.98601 | 0.04437 | 0.076224 | 0.036917
98 | 0.98608 | 0.043789 | 0.19907 | 0.096414
99 | 0.98634 | 0.043759 | 0.37698 | 0.18258
100 | 0.98622 | 0.044787 | 0 | 0
101 | 0.98633 | 0.043845 | 0 | 0
102 | 0.99037 | 0.025539 | 0.11153 | 0.054018
103 | 0.99911 | -0.0051244 | 1.0146 | 0.49138
104 | 0.99911 | -0.0051336 | 0 | 0
105 | 0.99912 | -0.0050515 | 0.41151 | 0.19931
106 | 0.9991 | -0.0051457 | 0.22049 | 0.10679
107 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.3632 | -0.17591 | 0.36357 | 0.17441 | 0.00036923 | -0.0014978 | 0.011813 | 0.011791 | 0.011813 | 0.98614 | 0.04295 | 0.9872 | 0.049769 | 5.6254
1 | -0.53315 | -0.25654 | 0.53321 | 0.25646 | 5.3737e-05 | -8.3591e-05 | 0.017301 | 0.0173 | 0.017301 | 0.9872 | 0.049769 | 0.98731 | 0.050451 | 8.2387
2 | -0.33089 | -0.16026 | 0.33116 | 0.15883 | 0.00027392 | -0.0014274 | 0.010671 | 0.010651 | 0.010671 | 0.99461 | 0.029448 | 0.99548 | 0.035004 | 5.0813
3 | 2.6029 | 1.1693 | -2.6026 | -1.1701 | 0.00034646 | -0.0007938 | 0.082747 | 0.082758 | 0.082758 | 0.99548 | 0.035004 | 0.99536 | 0.035973 | 37.6172
4 | -3.0392 | -1.379 | 3.0429 | 1.3731 | 0.0036971 | -0.0059131 | 0.096781 | 0.096698 | 0.096781 | 0.99548 | 0.035004 | 0.99662 | 0.025992 | 43.9916
5 | -1.4055 | -0.66788 | 1.4062 | 0.66207 | 0.00071376 | -0.005812 | 0.045499 | 0.045424 | 0.045499 | 0.98731 | 0.050451 | 0.98778 | 0.046258 | 20.6813
6 | 0.87231 | 0.41142 | -0.8715 | -0.41158 | 0.00080643 | -0.00015639 | 0.0282 | 0.028208 | 0.028208 | 0.98731 | 0.050451 | 0.98634 | 0.043759 | 13.4323
7 | -0.097314 | -0.047132 | 0.09732 | 0.046791 | 5.245e-06 | -0.00034018 | 0.003161 | 0.0031566 | 0.003161 | 0.98747 | 0.047132 | 0.98753 | 0.047492 | 1.5052
8 | -0.09732 | -0.046791 | 0.097329 | 0.029174 | 9.4206e-06 | -0.017617 | 0.0031566 | 0.0029699 | 0.0031566 | 0.98753 | 0.047492 | 0.98762 | 0.047041 | 1.4348
9 | -0.097329 | -0.029174 | 0.097329 | 0.028505 | 3.3798e-07 | -0.00066959 | 0.0029699 | 0.0029644 | 0.0029699 | 0.98762 | 0.047041 | 0.98762 | 0.047041 | 1.35
10 | -0.15779 | -0.076421 | 0.15779 | 0.075529 | 1.3093e-06 | -0.00089244 | 0.005094 | 0.0050827 | 0.005094 | 0.99355 | 0.050235 | 0.99356 | 0.050164 | 2.3154
11 | 2.3388 | 1.057 | -2.3386 | -1.0574 | 0.00013775 | -0.00039645 | 0.07457 | 0.074575 | 0.074575 | 0.99356 | 0.050164 | 0.99351 | 0.050599 | 33.8979
12 | -2.4966 | -1.1326 | 2.4971 | 1.1313 | 0.00049788 | -0.0012384 | 0.079652 | 0.079635 | 0.079652 | 0.99356 | 0.050164 | 0.99375 | 0.048679 | 36.2053
13 | -0.22656 | -0.091093 | 0.22656 | 0.090804 | 8.4701e-07 | -0.00028993 | 0.0071374 | 0.0071342 | 0.0071374 | 0.98762 | 0.047041 | 0.98763 | 0.047022 | 3.2443
14 | -0.22656 | -0.090804 | 0.22658 | 0.082354 | 2.4361e-05 | -0.0084499 | 0.0071342 | 0.007046 | 0.0071342 | 0.98763 | 0.047022 | 0.98773 | 0.046562 | 3.2428
15 | 2.087 | 0.93556 | -2.0808 | -0.93261 | 0.0061686 | 0.0029431 | 0.066454 | 0.066464 | 0.066464 | 0.99351 | 0.050599 | 0.99038 | 0.025443 | 31.6497
16 | 1.9693 | 0.88032 | -1.9638 | -0.90289 | 0.0054936 | -0.022572 | 0.062874 | 0.063166 | 0.063166 | 0.99038 | 0.025443 | 0.98778 | 0.046258 | 28.7119
17 | 0.11153 | 0.052294 | -0.11153 | -0.054018 | 1.2751e-06 | -0.0017243 | 0.0035906 | 0.0036122 | 0.0036122 | 0.99038 | 0.025443 | 0.99037 | 0.025539 | 1.6419
18 | 2.6026 | 1.1701 | -2.5982 | -1.1802 | 0.0044174 | -0.010081 | 0.082758 | 0.082894 | 0.082894 | 0.99536 | 0.035973 | 0.99377 | 0.048523 | 37.6791
19 | -3.0429 | -1.3731 | 3.0455 | 1.3689 | 0.0026135 | -0.0041971 | 0.096698 | 0.096639 | 0.096698 | 0.99662 | 0.025992 | 0.99743 | 0.019705 | 43.9535
20 | 2.5982 | 1.1802 | -2.5981 | -1.1803 | 5.388e-05 | -0.00012251 | 0.082894 | 0.082896 | 0.082896 | 0.99377 | 0.048523 | 0.99375 | 0.048679 | 37.6799
21 | 0.11756 | 0.056306 | -0.11756 | -0.056937 | 5.0586e-07 | -0.00063096 | 0.0037725 | 0.0037805 | 0.0037805 | 0.99743 | 0.019705 | 0.99743 | 0.019742 | 1.7184
22 | -3.1631 | -1.4252 | 3.1708 | 1.4139 | 0.0076871 | -0.011339 | 0.10041 | 0.10025 | 0.10041 | 0.99743 | 0.019705 | 0.99972 | 0.0021466 | 45.6409
23 | -3.1708 | -1.4139 | 3.1714 | 1.413 | 0.0005942 | -0.0008809 | 0.10025 | 0.10024 | 0.10025 | 0.99972 | 0.0021466 | 0.99989 | 0.00081118 | 45.5677
24 | -3.4926 | -1.5686 | 3.4929 | 1.5681 | 0.0003899 | -0.00045507 | 0.11053 | 0.11053 | 0.11053 | 0.99989 | 0.00081118 | 1 | 0 | 50.2429
25 | 11.6973 | 5.0979 | -11.6878 | -5.1068 | 0.0094977 | -0.0088673 | 0.36835 | 0.36851 | 0.36851 | 1 | 0 | 0.99915 | -0.0049544 | 57.7603
26 | -7.9057 | -3.3276 | 7.9058 | 3.3274 | 7.7948e-05 | -0.00021244 | 0.24814 | 0.24813 | 0.24814 | 0.99787 | -0.013166 | 0.99789 | -0.013097 | 38.893
27 | 7.5141 | 3.138 | -7.5135 | -3.1398 | 0.00059687 | -0.0018413 | 0.23557 | 0.23559 | 0.23559 | 0.99787 | -0.013166 | 0.99779 | -0.013729 | 36.9268
28 | 0.34636 | 0.16451 | -0.34636 | -0.16769 | 1.9402e-06 | -0.0031802 | 0.011093 | 0.011132 | 0.011132 | 0.99789 | -0.013097 | 0.99788 | -0.013119 | 1.7449
29 | -8.2521 | -3.4919 | 8.2565 | 3.4811 | 0.0044275 | -0.010864 | 0.25922 | 0.25907 | 0.25922 | 0.99789 | -0.013097 | 0.99845 | -0.0094273 | 40.6295
30 | 1.2505 | 0.37684 | -1.2502 | -0.41326 | 0.00026009 | -0.036423 | 0.037785 | 0.038104 | 0.038104 | 0.99779 | -0.013729 | 0.99757 | -0.016407 | 5.9723
31 | 6.263 | 2.763 | -6.262 | -2.7676 | 0.0010042 | -0.0046153 | 0.19805 | 0.19811 | 0.19811 | 0.99779 | -0.013729 | 0.99762 | -0.014663 | 31.0513
32 | 0.34636 | 0.16769 | -0.34635 | -0.16775 | 1.0748e-05 | -5.1126e-05 | 0.011132 | 0.011133 | 0.011133 | 0.99788 | -0.013119 | 0.99785 | -0.013324 | 5.3015
33 | -8.9773 | -3.8275 | 8.9834 | 3.8155 | 0.006019 | -0.011956 | 0.28216 | 0.28199 | 0.28216 | 0.99845 | -0.0094273 | 0.99915 | -0.0049544 | 44.2261
34 | 0.7208 | 0.3464 | -0.7208 | -0.34788 | 3.9106e-06 | -0.0014794 | 0.023122 | 0.02314 | 0.02314 | 0.99845 | -0.0094273 | 0.99844 | -0.0094479 | 3.627
35 | 1.2502 | 0.41326 | -1.2502 | -0.41884 | 4.0262e-05 | -0.005581 | 0.038104 | 0.038155 | 0.038155 | 0.99757 | -0.016407 | 0.99754 | -0.01679 | 5.9804
36 | 6.262 | 2.7676 | -6.2618 | -2.7686 | 0.00023047 | -0.0010585 | 0.19811 | 0.19812 | 0.19812 | 0.99762 | -0.014663 | 0.99759 | -0.014877 | 31.0535
37 | 2.0002 | 0.9518 | -2.0002 | -0.95373 | 3.9272e-05 | -0.0019235 | 0.063999 | 0.064023 | 0.064023 | 0.99915 | -0.0049544 | 0.99913 | -0.005034 | 10.035
38 | 0.70419 | 0.3395 | -0.70418 | -0.34105 | 3.9015e-06 | -0.0015489 | 0.022587 | 0.022606 | 0.022606 | 0.99915 | -0.0049544 | 0.99914 | -0.004975 | 3.5433
39 | 0.37008 | 0.17802 | -0.37008 | -0.17924 | 8.5045e-07 | -0.0012208 | 0.011874 | 0.011889 | 0.011889 | 0.99844 | -0.0094479 | 0.99844 | -0.0094565 | 1.8635
40 | 1.2351 | 0.58449 | -1.2351 | -0.58681 | 1.7912e-05 | -0.002321 | 0.039479 | 0.039508 | 0.039508 | 0.99913 | -0.005034 | 0.99912 | -0.0050943 | 6.1925
41 | 0.76507 | 0.36924 | -0.76507 | -0.37053 | 3.846e-06 | -0.0012929 | 0.024545 | 0.024561 | 0.024561 | 0.99913 | -0.005034 | 0.99912 | -0.0050526 | 3.8497
42 | 1.0307 | 0.31257 | -1.0307 | -0.31773 | 2.4898e-05 | -0.0051639 | 0.03117 | 0.031213 | 0.031213 | 0.99754 | -0.01679 | 0.99751 | -0.017115 | 4.8924
43 | 5.8965 | 2.5917 | -5.8963 | -2.5928 | 0.00021024 | -0.0011061 | 0.18638 | 0.1864 | 0.1864 | 0.99759 | -0.014877 | 0.99755 | -0.015088 | 29.2162
44 | 1.0146 | 0.4898 | -1.0146 | -0.49138 | 8.2627e-06 | -0.0015772 | 0.032552 | 0.032572 | 0.032572 | 0.99912 | -0.0050943 | 0.99911 | -0.0051244 | 5.1053
45 | 0.22049 | 0.097006 | -0.22049 | -0.10405 | 1.7017e-06 | -0.0070446 | 0.0069601 | 0.0070445 | 0.0070445 | 0.99912 | -0.0050943 | 0.99911 | -0.0051336 | 1.1042
46 | 0.41151 | 0.1993 | -0.41151 | -0.19931 | 5.1933e-08 | -5.2495e-06 | 0.013211 | 0.013211 | 0.013211 | 0.99912 | -0.0050526 | 0.99912 | -0.0050515 | 6.005
47 | 1.0307 | 0.31773 | -1.0306 | -0.33545 | 8.5988e-05 | -0.01772 | 0.031213 | 0.031369 | 0.031369 | 0.99751 | -0.017115 | 0.99742 | -0.018185 | 4.9167
48 | 5.8963 | 2.5928 | -5.8938 | -2.6061 | 0.0025264 | -0.013271 | 0.1864 | 0.18657 | 0.18657 | 0.99755 | -0.015088 | 0.9971 | -0.017599 | 29.2431
49 | 4.7171 | 2.1254 | -4.7156 | -2.138 | 0.0014842 | -0.012519 | 0.14979 | 0.14995 | 0.14995 | 0.9971 | -0.017599 | 0.99678 | -0.019263 | 23.503
50 | 0.77303 | 0.28554 | -0.77293 | -0.31998 | 9.8577e-05 | -0.034435 | 0.023858 | 0.024223 | 0.024223 | 0.9971 | -0.017599 | 0.99697 | -0.018685 | 3.7966
51 | 0.40366 | 0.19513 | -0.40365 | -0.1955 | 3.5007e-06 | -0.00036827 | 0.01298 | 0.012985 | 0.012985 | 0.9971 | -0.017599 | 0.99709 | -0.017524 | 5.9022
52 | 4.3934 | 1.982 | -4.3919 | -1.9961 | 0.0014372 | -0.01407 | 0.13958 | 0.13976 | 0.13976 | 0.99678 | -0.019263 | 0.99644 | -0.020979 | 21.9063
53 | 0.32225 | 0.15593 | -0.32225 | -0.15607 | 8.4407e-07 | -0.00013926 | 0.010368 | 0.01037 | 0.01037 | 0.99678 | -0.019263 | 0.99677 | -0.01924 | 4.7135
54 | 0.13913 | 0.03786 | -0.13912 | -0.066559 | 7.5284e-06 | -0.0287 | 0.004175 | 0.0044658 | 0.0044658 | 0.99697 | -0.018685 | 0.99691 | -0.01964 | 1.2336
55 | 0.25742 | 0.10042 | -0.25741 | -0.12455 | 7.9014e-06 | -0.02413 | 0.0080007 | 0.0082803 | 0.0082803 | 0.99697 | -0.018685 | 0.99694 | -0.018872 | 1.2978
56 | 0.37639 | 0.1817 | -0.37639 | -0.18229 | 4.9035e-06 | -0.00059335 | 0.012102 | 0.012109 | 0.012109 | 0.99697 | -0.018685 | 0.99696 | -0.018572 | 5.5043
57 | 4.3169 | 1.96 | -4.3157 | -1.9722 | 0.0012107 | -0.012257 | 0.13735 | 0.13751 | 0.13751 | 0.99644 | -0.020979 | 0.99614 | -0.022411 | 21.5528
58 | 0.07499 | 0.036131 | -0.07499 | -0.036319 | 5.4602e-09 | -0.00018877 | 0.0024115 | 0.0024139 | 0.0024139 | 0.99644 | -0.020979 | 0.99644 | -0.020979 | 0.37836
59 | 0.13912 | 0.066559 | -0.13912 | -0.067378 | 9.2111e-07 | -0.00081876 | 0.0044658 | 0.0044761 | 0.0044761 | 0.99691 | -0.01964 | 0.9969 | -0.019583 | 2.0346
60 | 0.25741 | 0.12455 | -0.2574 | -0.12466 | 1.227e-05 | -0.00011147 | 0.0082803 | 0.0082818 | 0.0082818 | 0.99694 | -0.018872 | 0.99689 | -0.019186 | 3.9437
61 | 0.35592 | 0.1723 | -0.3559 | -0.17237 | 1.6602e-05 | -7.3275e-05 | 0.011472 | 0.011473 | 0.011473 | 0.99504 | -0.040265 | 0.99499 | -0.040572 | 5.4634
62 | -0.47555 | -0.22948 | 0.47558 | 0.22906 | 3.0322e-05 | -0.0004141 | 0.015319 | 0.015312 | 0.015319 | 0.99504 | -0.040265 | 0.99516 | -0.033722 | 2.375
63 | 0.11963 | 0.057177 | -0.11963 | -0.057937 | 2.9723e-06 | -0.00076013 | 0.0038466 | 0.0038563 | 0.0038563 | 0.99504 | -0.040265 | 0.99499 | -0.042817 | 0.59788
64 | -3.1885 | -1.4944 | 3.1891 | 1.4834 | 0.00058299 | -0.010941 | 0.10215 | 0.10201 | 0.10215 | 0.99516 | -0.033722 | 0.99534 | -0.032895 | 16.0106
65 | 0.39744 | 0.15147 | -0.39742 | -0.1723 | 1.6037e-05 | -0.020829 | 0.012338 | 0.012566 | 0.012566 | 0.99516 | -0.033722 | 0.99511 | -0.034031 | 1.9696
66 | 2.3155 | 1.1138 | -2.3155 | -1.1141 | 5.9673e-06 | -0.00021293 | 0.074536 | 0.074538 | 0.074538 | 0.99516 | -0.033722 | 0.99515 | -0.033732 | 11.6832
67 | 0.59758 | 0.2724 | -0.59755 | -0.28656 | 2.5673e-05 | -0.014158 | 0.019032 | 0.019206 | 0.019206 | 0.99614 | -0.022411 | 0.9961 | -0.022604 | 3.0103
68 | 3.7181 | 1.6998 | -3.7181 | -1.7012 | 9.8929e-05 | -0.0013662 | 0.11848 | 0.11849 | 0.11849 | 0.99614 | -0.022411 | 0.99612 | -0.022544 | 18.5725
69 | 0.43542 | 0.20808 | -0.43539 | -0.21038 | 2.5428e-05 | -0.0022945 | 0.013986 | 0.014014 | 0.014014 | 0.9961 | -0.022604 | 0.99605 | -0.022104 | 6.3702
70 | 0.16213 | 0.078475 | -0.16213 | -0.078524 | 2.0389e-06 | -4.846e-05 | 0.0052201 | 0.0052208 | 0.0052208 | 0.9961 | -0.022604 | 0.99609 | -0.022687 | 2.4861
71 | 3.428 | 1.5607 | -3.4278 | -1.5601 | 0.00023653 | 0.00055979 | 0.10915 | 0.10916 | 0.10916 | 0.99612 | -0.022544 | 0.99599 | -0.02986 | 16.9234
72 | 0.33906 | 0.16372 | -0.33897 | -0.16417 | 9.036e-05 | -0.0004474 | 0.010912 | 0.010919 | 0.010919 | 0.99605 | -0.022104 | 0.99577 | -0.023871 | 5.1994
73 | 0.2365 | 0.1116 | -0.2365 | -0.11454 | 8.4446e-07 | -0.0029427 | 0.0075843 | 0.0076211 | 0.0076211 | 0.99534 | -0.032895 | 0.99534 | -0.032909 | 1.1945
74 | -3.4256 | -1.595 | 3.4278 | 1.5601 | 0.0021418 | -0.034885 | 0.10959 | 0.10916 | 0.10959 | 0.99534 | -0.032895 | 0.99599 | -0.02986 | 17.1776
75 | 0.18576 | 0.075678 | -0.18576 | -0.086872 | 1.9236e-06 | -0.011194 | 0.0058188 | 0.0059489 | 0.0059489 | 0.99511 | -0.034031 | 0.9951 | -0.034094 | 0.93243
76 | 0.21167 | 0.096617 | -0.21166 | -0.1013 | 1.0693e-06 | -0.0046858 | 0.0067497 | 0.0068073 | 0.0068073 | 0.99511 | -0.034031 | 0.99511 | -0.034054 | 1.067
77 | 1.4969 | 0.7176 | -1.4969 | -0.71815 | 6.3523e-06 | -0.00054798 | 0.048154 | 0.048161 | 0.048161 | 0.99515 | -0.033732 | 0.99515 | -0.033749 | 7.5488
78 | 0.18576 | 0.086872 | -0.18575 | -0.087118 | 2.3292e-06 | -0.00024595 | 0.0059489 | 0.005952 | 0.005952 | 0.9951 | -0.034094 | 0.99508 | -0.035402 | 0.92279
79 | 0.13067 | 0.062074 | -0.13067 | -0.063284 | 1.0625e-07 | -0.0012104 | 0.0041965 | 0.0042117 | 0.0042117 | 0.99511 | -0.034054 | 0.99511 | -0.034057 | 0.66014
80 | 0.091796 | 0.041612 | -0.09179 | -0.044456 | 6.4577e-06 | -0.0028442 | 0.0029239 | 0.0029591 | 0.0029591 | 0.99508 | -0.035402 | 0.99495 | -0.042739 | 0.45878
81 | 0.81982 | 0.39216 | -0.81982 | -0.3934 | 4.297e-06 | -0.0012419 | 0.026362 | 0.026378 | 0.026378 | 0.99515 | -0.033749 | 0.99514 | -0.033769 | 4.1345
82 | 0.67709 | 0.32599 | -0.67709 | -0.32793 | 4.5898e-06 | -0.0019402 | 0.021799 | 0.021824 | 0.021824 | 0.99515 | -0.033749 | 0.99514 | -0.033774 | 3.4206
83 | 0.14481 | 0.068799 | -0.14481 | -0.070135 | 1.4402e-07 | -0.0013357 | 0.0046507 | 0.0046675 | 0.0046675 | 0.99514 | -0.033769 | 0.99514 | -0.033773 | 0.73158
84 | 0.675 | 0.3246 | -0.675 | -0.32528 | 1.5807e-06 | -0.00067311 | 0.021727 | 0.021736 | 0.021736 | 0.99514 | -0.033769 | 0.99514 | -0.033778 | 3.4069
85 | 0.675 | 0.32528 | -0.675 | -0.32692 | 3.8563e-06 | -0.0016399 | 0.021736 | 0.021756 | 0.021756 | 0.99514 | -0.033778 | 0.99513 | -0.033799 | 3.4101
86 | 1.0306 | 0.33545 | -1.0306 | -0.33552 | 5.9389e-05 | -7.275e-05 | 0.031369 | 0.031371 | 0.031371 | 0.99742 | -0.018185 | 0.99732 | -0.025241 | 4.8637
87 | 0.91169 | 0.27795 | -0.91164 | -0.29205 | 5.3407e-05 | -0.014099 | 0.027588 | 0.02771 | 0.02771 | 0.99732 | -0.025241 | 0.99726 | -0.026007 | 4.3433
88 | 0.91164 | 0.29205 | -0.9115 | -0.32902 | 0.00014241 | -0.036967 | 0.02771 | 0.028056 | 0.028056 | 0.99726 | -0.026007 | 0.99709 | -0.027791 | 4.3975
89 | 0.27987 | 0.13108 | -0.27987 | -0.13555 | 1.7798e-06 | -0.0044659 | 0.0089473 | 0.0090029 | 0.0090029 | 0.99709 | -0.027791 | 0.99709 | -0.027817 | 1.4111
90 | 0.63163 | 0.19794 | -0.63155 | -0.24344 | 8.4562e-05 | -0.045503 | 0.019164 | 0.019598 | 0.019598 | 0.99709 | -0.027791 | 0.99695 | -0.029252 | 3.0719
91 | 0.34101 | 0.10301 | -0.341 | -0.13205 | 1.5684e-05 | -0.029048 | 0.010315 | 0.010589 | 0.010589 | 0.99695 | -0.029252 | 0.9969 | -0.029766 | 1.6597
92 | 0.29053 | 0.14043 | -0.29053 | -0.14071 | 1.1976e-07 | -0.00027696 | 0.0093439 | 0.0093474 | 0.0093474 | 0.99695 | -0.029252 | 0.99695 | -0.029253 | 1.4651
93 | 0.22471 | 0.10227 | -0.22471 | -0.10883 | 1.6776e-06 | -0.0065584 | 0.0071492 | 0.00723 | 0.00723 | 0.9969 | -0.029766 | 0.99689 | -0.029799 | 1.1332
94 | 0.11629 | 0.029782 | -0.11629 | -0.056282 | 1.6907e-06 | -0.026501 | 0.003476 | 0.003741 | 0.003741 | 0.9969 | -0.029766 | 0.99689 | -0.029908 | 0.58637
95 | 0.11629 | 0.056282 | -0.11628 | -0.056319 | 7.8396e-07 | -3.6803e-05 | 0.003741 | 0.0037415 | 0.0037415 | 0.99689 | -0.029908 | 0.99688 | -0.029952 | 1.7817
96 | -0.22658 | -0.082354 | 0.22659 | 0.081866 | 1.3878e-06 | -0.00048769 | 0.007046 | 0.0070412 | 0.007046 | 0.98773 | 0.046562 | 0.98774 | 0.046542 | 3.2027
97 | -0.55752 | -0.24214 | 0.55754 | 0.24082 | 2.4023e-05 | -0.0013223 | 0.017765 | 0.017749 | 0.017765 | 0.98774 | 0.046542 | 0.98778 | 0.046258 | 8.0748
98 | 0.076225 | 0.034257 | -0.076225 | -0.034611 | 1.2222e-07 | -0.00035439 | 0.0024466 | 0.0024509 | 0.0024509 | 0.98602 | 0.044273 | 0.98602 | 0.044285 | 1.114
99 | -0.2953 | -0.14036 | 0.2953 | 0.1398 | 2.9189e-06 | -0.00055348 | 0.0095722 | 0.0095652 | 0.0095722 | 0.98602 | 0.044273 | 0.98603 | 0.04419 | 4.351
100 | 0.076225 | 0.034611 | -0.076224 | -0.036917 | 8.0582e-07 | -0.0023057 | 0.0024509 | 0.0024796 | 0.0024796 | 0.98602 | 0.044285 | 0.98601 | 0.04437 | 1.1271
101 | -0.2953 | -0.1398 | 0.29531 | 0.13701 | 1.4655e-05 | -0.0027912 | 0.0095652 | 0.0095305 | 0.0095652 | 0.98603 | 0.04419 | 0.98608 | 0.043789 | 4.3478
102 | -0.49439 | -0.23343 | 0.49445 | 0.2333 | 6.8212e-05 | -0.00013081 | 0.016005 | 0.016003 | 0.016005 | 0.98608 | 0.043789 | 0.98622 | 0.044787 | 7.6216
103 | 0.49452 | 0.229 | -0.49451 | -0.22937 | 5.4116e-06 | -0.00036842 | 0.01595 | 0.015954 | 0.015954 | 0.98634 | 0.043759 | 0.98633 | 0.043845 | 7.2519
104 | -0.49445 | -0.2333 | 0.49451 | 0.22937 | 5.7918e-05 | -0.0039294 | 0.016003 | 0.015954 | 0.016003 | 0.98622 | 0.044787 | 0.98633 | 0.043845 | 7.2742
105 | 0.22049 | 0.10405 | -0.22049 | -0.10679 | 6.7282e-07 | -0.0027383 | 0.0070445 | 0.0070786 | 0.0070786 | 0.99911 | -0.0051336 | 0.9991 | -0.0051457 | 1.1095

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 15.2042 | 6.6766

## res_load
| p_mw | q_mvar
0 | 0.3632 | 0.17591
1 | 0.16958 | 0.082134
2 | 0.33089 | 0.16026
3 | 0.10514 | 0.05092
4 | 0.097314 | 0.047132
5 | 0.15779 | 0.076421
6 | 0.12923 | 0.062589
7 | 0.25167 | 0.12189
8 | 0.10105 | 0.048942
9 | 0.11756 | 0.056937
10 | 0.32117 | 0.15555
11 | 0.39159 | 0.18966
12 | 0.34635 | 0.16775
13 | 0.35072 | 0.16986
14 | 0.70418 | 0.34105
15 | 0.21943 | 0.10628
16 | 0.36526 | 0.17691
17 | 0.37008 | 0.17924
18 | 0.35355 | 0.17123
19 | 0.40365 | 0.1955
20 | 0.32225 | 0.15607
21 | 0.37639 | 0.18229
22 | 0.2574 | 0.12466
23 | 0.13912 | 0.067378
24 | 0.3559 | 0.17237
25 | 0.11963 | 0.057937
26 | 0.07499 | 0.036319
27 | 0.29006 | 0.14048
28 | 0.096332 | 0.046656
29 | 0.16213 | 0.078524
30 | 0.81859 | 0.39646
31 | 0.2365 | 0.11454
32 | 0.080999 | 0.039229
33 | 0.13067 | 0.063284
34 | 0.093959 | 0.045506
35 | 0.67709 | 0.32793
36 | 0.14481 | 0.070135
37 | 0.675 | 0.32692
38 | 0.09179 | 0.044456
39 | 0.33897 | 0.16417
40 | 0.11887 | 0.057571
41 | 0.29053 | 0.14071
42 | 0.27987 | 0.13555
43 | 0.11628 | 0.056319
44 | 0.22471 | 0.10883
45 | 0.33093 | 0.16028
46 | 0.21907 | 0.1061
47 | 0.076224 | 0.036917
48 | 0.19907 | 0.096414
49 | 0.37698 | 0.18258
50 | 0.11153 | 0.054018
51 | 1.0146 | 0.49138
52 | 0.41151 | 0.19931
53 | 0.22049 | 0.10679

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1