## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_294_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_294_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_294_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_294_0_node_50 | 20 | n |  | TRUE
4 | bus_MV_294_0_node_3 | 20 | n |  | TRUE
5 | bus_MV_294_0_node_51 | 20 | n |  | TRUE
6 | bus_MV_294_0_node_25 | 20 | n |  | TRUE
7 | bus_MV_294_0_node_4 | 20 | n |  | TRUE
8 | bus_MV_294_0_node_8 | 20 | n |  | TRUE
9 | bus_MV_294_0_node_9 | 20 | n |  | TRUE
10 | bus_MV_294_0_node_10 | 20 | n |  | TRUE
11 | bus_MV_294_0_node_6 | 20 | n |  | TRUE
12 | bus_MV_294_0_node_7 | 20 | n |  | TRUE
13 | bus_MV_294_0_node_13 | 20 | n |  | TRUE
14 | bus_MV_294_0_node_14 | 20 | n |  | TRUE
15 | bus_MV_294_0_node_12 | 20 | n |  | TRUE
16 | bus_MV_294_0_node_26 | 20 | n |  | TRUE
17 | bus_MV_294_0_node_11 | 20 | n |  | TRUE
18 | bus_MV_294_0_node_77 | 20 | n |  | TRUE
19 | bus_MV_294_0_node_83 | 20 | n |  | TRUE
20 | bus_MV_294_0_node_15 | 20 | n |  | TRUE
21 | bus_MV_294_0_node_27 | 20 | n |  | TRUE
22 | bus_MV_294_0_node_49 | 20 | n |  | TRUE
23 | bus_MV_294_0_node_16 | 20 | n |  | TRUE
24 | bus_MV_294_0_node_78 | 20 | n |  | TRUE
25 | bus_MV_294_0_node_17 | 20 | n |  | TRUE
26 | bus_MV_294_0_node_19 | 20 | n |  | TRUE
27 | bus_MV_294_0_node_20 | 20 | n |  | TRUE
28 | bus_MV_294_0_node_18 | 20 | n |  | TRUE
29 | bus_MV_294_0_node_22 | 20 | n |  | TRUE
30 | bus_MV_294_0_node_21 | 20 | n |  | TRUE
31 | bus_MV_294_0_node_23 | 20 | n |  | TRUE
32 | bus_MV_294_0_node_24 | 20 | n |  | TRUE
33 | bus_MV_294_0_node_43 | 20 | n |  | TRUE
34 | bus_MV_294_0_node_72 | 20 | n |  | TRUE
35 | bus_MV_294_0_node_74 | 20 | n |  | TRUE
36 | bus_MV_294_0_node_44 | 20 | n |  | TRUE
37 | bus_MV_294_0_node_42 | 20 | n |  | TRUE
38 | bus_MV_294_0_node_71 | 20 | n |  | TRUE
39 | bus_MV_294_0_node_75 | 20 | n |  | TRUE
40 | bus_MV_294_0_node_28 | 20 | n |  | TRUE
41 | bus_MV_294_0_node_73 | 20 | n |  | TRUE
42 | bus_MV_294_0_node_29 | 20 | n |  | TRUE
43 | bus_MV_294_0_node_30 | 20 | n |  | TRUE
44 | bus_MV_294_0_node_38 | 20 | n |  | TRUE
45 | bus_MV_294_0_node_45 | 20 | n |  | TRUE
46 | bus_MV_294_0_node_81 | 20 | n |  | TRUE
47 | bus_MV_294_0_node_35 | 20 | n |  | TRUE
48 | bus_MV_294_0_node_32 | 20 | n |  | TRUE
49 | bus_MV_294_0_node_33 | 20 | n |  | TRUE
50 | bus_MV_294_0_node_82 | 20 | n |  | TRUE
51 | bus_MV_294_0_node_40 | 20 | n |  | TRUE
52 | bus_MV_294_0_node_41 | 20 | n |  | TRUE
53 | bus_MV_294_0_node_39 | 20 | n |  | TRUE
54 | bus_MV_294_0_node_34 | 20 | n |  | TRUE
55 | bus_MV_294_0_node_37 | 20 | n |  | TRUE
56 | bus_MV_294_0_node_52 | 20 | n |  | TRUE
57 | bus_MV_294_0_node_53 | 20 | n |  | TRUE
58 | bus_MV_294_0_node_67 | 20 | n |  | TRUE
59 | bus_MV_294_0_node_46 | 20 | n |  | TRUE
60 | bus_MV_294_0_node_47 | 20 | n |  | TRUE
61 | bus_MV_294_0_node_48 | 20 | n |  | TRUE
62 | bus_MV_294_0_node_84 | 20 | n |  | TRUE
63 | bus_MV_294_0_node_65 | 20 | n |  | TRUE
64 | bus_MV_294_0_node_66 | 20 | n |  | TRUE
65 | bus_MV_294_0_node_68 | 20 | n |  | TRUE
66 | bus_MV_294_0_node_69 | 20 | n |  | TRUE
67 | bus_MV_294_0_node_70 | 20 | n |  | TRUE
68 | bus_MV_294_0_node_54 | 20 | n |  | TRUE
69 | bus_MV_294_0_node_58 | 20 | n |  | TRUE
70 | bus_MV_294_0_node_59 | 20 | n |  | TRUE
71 | bus_MV_294_0_node_61 | 20 | n |  | TRUE
72 | bus_MV_294_0_node_56 | 20 | n |  | TRUE
73 | bus_MV_294_0_node_55 | 20 | n |  | TRUE
74 | bus_MV_294_0_node_57 | 20 | n |  | TRUE
75 | bus_MV_294_0_node_60 | 20 | n |  | TRUE
76 | bus_MV_294_0_node_63 | 20 | n |  | TRUE
77 | bus_MV_294_0_node_62 | 20 | n |  | TRUE
78 | bus_MV_294_0_node_64 | 20 | n |  | TRUE
79 | bus_MV_294_0_node_80 | 20 | n |  | TRUE
80 | bus_MV_294_0_node_79 | 20 | n |  | TRUE
81 | bus_MV_294_0_node_85 | 20 | n |  | TRUE
82 | bus_MV_294_0_node_76 | 20 | n |  | TRUE
83 | bus_HV_294_0_node_42 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_294_0_load_0 | 0 | 0.35986 | 0.17429 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_294_0_load_50 | 3 | 0.26181 | 0.1268 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_294_0_load_25 | 6 | 0.40908 | 0.19813 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_294_0_load_4 | 7 | 0.30292 | 0.14671 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_294_0_load_7 | 12 | 0.16297 | 0.078932 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_294_0_load_14 | 14 | 0.24779 | 0.12001 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_294_0_load_26 | 16 | 0.22885 | 0.11084 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_294_0_load_77 | 18 | 0.069422 | 0.033623 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_294_0_load_83 | 19 | 0.40111 | 0.19426 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_294_0_load_78 | 24 | 0.17451 | 0.084517 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_294_0_load_17 | 25 | 0.40044 | 0.19394 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_294_0_load_19 | 26 | 0.38534 | 0.18663 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_294_0_load_20 | 27 | 0.086089 | 0.041695 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_294_0_load_18 | 28 | 0.11179 | 0.054141 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_294_0_load_23 | 31 | 0.19189 | 0.092938 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_294_0_load_24 | 32 | 0.37664 | 0.18242 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_294_0_load_74 | 35 | 0.14697 | 0.071182 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_294_0_load_42 | 37 | 0.13575 | 0.065745 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_294_0_load_75 | 39 | 0.093215 | 0.045146 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_294_0_load_28 | 40 | 0.070926 | 0.034351 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_294_0_load_29 | 42 | 0.27725 | 0.13428 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_294_0_load_45 | 45 | 0.2656 | 0.12864 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_294_0_load_81 | 46 | 0.075886 | 0.036753 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_294_0_load_82 | 50 | 0.16447 | 0.079658 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_294_0_load_41 | 52 | 0.081164 | 0.039309 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_294_0_load_39 | 53 | 0.23414 | 0.1134 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_294_0_load_34 | 54 | 0.24948 | 0.12083 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_294_0_load_53 | 57 | 0.36719 | 0.17784 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_294_0_load_46 | 59 | 0.34123 | 0.16526 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_294_0_load_84 | 62 | 0.39925 | 0.19337 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_294_0_load_65 | 63 | 0.124 | 0.060054 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_294_0_load_69 | 66 | 0.094903 | 0.045964 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_294_0_load_54 | 68 | 0.32347 | 0.15666 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_294_0_load_61 | 71 | 0.1172 | 0.056762 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_294_0_load_55 | 73 | 0.071456 | 0.034608 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_294_0_load_60 | 75 | 0.15771 | 0.076383 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_294_0_load_62 | 77 | 0.1533 | 0.074246 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_294_0_load_64 | 78 | 0.22656 | 0.10973 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_294_0_load_79 | 80 | 0.075375 | 0.036506 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_294_0_load_85 | 81 | 0.31989 | 0.15493 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_294_0_load_76 | 82 | 0.083103 | 0.040249 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 37 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_294_0_line_0 |  | 0 | 1 | 0.033021 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_294_0_line_1 |  | 0 | 2 | 0.09945 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_294_0_line_2 |  | 1 | 3 | 1.7769 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_294_0_line_3 |  | 2 | 4 | 0.33682 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_294_0_line_4 |  | 3 | 5 | 0.083079 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_294_0_line_5 |  | 4 | 6 | 0.049221 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_294_0_line_6 |  | 5 | 56 | 0.5681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_294_0_line_7 |  | 7 | 8 | 0.36942 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_294_0_line_8 |  | 8 | 9 | 0.43458 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_294_0_line_9 |  | 8 | 10 | 0.4541 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_294_0_line_10 |  | 8 | 11 | 0.088227 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_294_0_line_11 |  | 9 | 13 | 0.50495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_294_0_line_12 |  | 9 | 14 | 0.038725 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_294_0_line_13 |  | 10 | 15 | 0.1357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_294_0_line_14 |  | 10 | 16 | 0.12287 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_294_0_line_15 |  | 11 | 12 | 0.010476 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_294_0_line_16 |  | 13 | 19 | 0.025134 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_294_0_line_17 |  | 14 | 20 | 0.047595 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_294_0_line_18 |  | 15 | 17 | 0.13151 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_294_0_line_19 |  | 16 | 21 | 0.073481 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_294_0_line_20 |  | 17 | 18 | 0.019371 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_294_0_line_21 |  | 19 | 22 | 0.10272 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_294_0_line_22 |  | 20 | 23 | 0.48796 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_294_0_line_23 |  | 21 | 40 | 0.076395 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_294_0_line_24 |  | 22 | 60 | 0.84077 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_294_0_line_25 |  | 23 | 24 | 0.030036 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_294_0_line_26 |  | 25 | 26 | 0.038498 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_294_0_line_27 |  | 25 | 27 | 0.041571 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
28 | MV_294_0_line_28 |  | 25 | 28 | 0.039794 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_294_0_line_29 |  | 27 | 29 | 0.015764 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
30 | MV_294_0_line_30 |  | 28 | 30 | 0.017291 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_294_0_line_31 |  | 29 | 33 | 0.57016 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
32 | MV_294_0_line_32 |  | 30 | 31 | 0.057771 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_294_0_line_33 |  | 30 | 32 | 0.071076 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_294_0_line_34 |  | 31 | 34 | 0.024133 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_294_0_line_35 |  | 32 | 35 | 0.0025425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_294_0_line_36 |  | 33 | 36 | 0.1526 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
37 | MV_294_0_line_37 |  | 33 | 37 | 0.045076 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
38 | MV_294_0_line_38 |  | 34 | 38 | 0.13419 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_294_0_line_39 |  | 35 | 39 | 0.030866 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_294_0_line_40 |  | 36 | 50 | 0.05323 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
41 | MV_294_0_line_41 |  | 38 | 41 | 0.057197 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_294_0_line_42 |  | 38 | 40 | 0.048176 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_294_0_line_43 |  | 39 | 82 | 0.0093561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_294_0_line_44 |  | 41 | 79 | 0.39934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_294_0_line_45 |  | 41 | 80 | 0.089629 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_294_0_line_46 |  | 42 | 43 | 0.12596 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_294_0_line_47 |  | 43 | 44 | 0.40878 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_294_0_line_48 |  | 44 | 45 | 0.06848 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_294_0_line_49 |  | 44 | 46 | 0.12519 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_294_0_line_50 |  | 44 | 47 | 0.41401 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_294_0_line_51 |  | 46 | 48 | 0.070793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_294_0_line_52 |  | 47 | 54 | 0.060193 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_294_0_line_53 |  | 48 | 49 | 0.3833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_294_0_line_54 |  | 49 | 50 | 0.011019 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
55 | MV_294_0_line_55 |  | 49 | 51 | 0.31616 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
56 | MV_294_0_line_56 |  | 51 | 52 | 0.18635 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_294_0_line_57 |  | 51 | 53 | 0.18628 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
58 | MV_294_0_line_58 |  | 53 | 55 | 0.12242 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
59 | MV_294_0_line_59 |  | 55 | 56 | 1.6429 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
60 | MV_294_0_line_60 |  | 56 | 57 | 0.057569 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_294_0_line_61 |  | 56 | 58 | 2.1312 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_294_0_line_62 |  | 58 | 63 | 0.013721 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_294_0_line_63 |  | 59 | 60 | 0.020213 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_294_0_line_64 |  | 60 | 61 | 0.39221 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_294_0_line_65 |  | 61 | 62 | 0.063171 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_294_0_line_66 |  | 63 | 64 | 0.06199 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_294_0_line_67 |  | 64 | 65 | 0.24984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_294_0_line_68 |  | 65 | 66 | 0.018539 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_294_0_line_69 |  | 66 | 67 | 0.048412 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_294_0_line_70 |  | 67 | 68 | 2.0899 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_294_0_line_71 |  | 68 | 69 | 2.903 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_294_0_line_72 |  | 69 | 70 | 0.54057 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_294_0_line_73 |  | 69 | 71 | 0.086063 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
74 | MV_294_0_line_74 |  | 69 | 72 | 0.42362 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_294_0_line_75 |  | 70 | 76 | 0.07121 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_294_0_line_76 |  | 70 | 77 | 0.080084 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
77 | MV_294_0_line_77 |  | 72 | 74 | 0.42819 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_294_0_line_78 |  | 72 | 73 | 0.16091 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
79 | MV_294_0_line_79 |  | 74 | 75 | 0.086585 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_294_0_line_80 |  | 76 | 78 | 0.2566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_294_0_line_81 |  | 79 | 81 | 0.028466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_294_0_trafo_42 | 25 MVA 110/20 kV | 83 | 37 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2607573.5977 | 1250718.8042
1 | 2607541.0255 | 1250724.229
2 | 2607670.5825 | 1250697.0874
3 | 2605813.3797 | 1250308.9554
4 | 2607854.371 | 1250711.6243
5 | 2605861.3712 | 1250241.0471
6 | 2607902.0658 | 1250706.4061
7 | 2608591.4361 | 1250458.4746
8 | 2608334.0556 | 1250723.4818
9 | 2608346.4156 | 1250904.1497
10 | 2608064.9685 | 1250793.4357
11 | 2608329.2724 | 1250635.3847
12 | 2608318.7873 | 1250636.0483
13 | 2608096.0619 | 1251119.0559
14 | 2608371.2586 | 1250933.9149
15 | 2607939.0384 | 1250800.7607
16 | 2608048.58 | 1250671.8569
17 | 2607883.8312 | 1250865.5519
18 | 2607864.8436 | 1250869.3849
19 | 2608101.4249 | 1251143.6124
20 | 2608402.6291 | 1250969.6599
21 | 2608034.8794 | 1250599.6695
22 | 2608115.2814 | 1251243.9409
23 | 2608368.6098 | 1251272.787
24 | 2608398.3453 | 1251268.5476
25 | 2607855.7954 | 1250360.4962
26 | 2607819.2264 | 1250372.5288
27 | 2607846.7327 | 1250319.9331
28 | 2607868.2792 | 1250398.2808
29 | 2607843.3572 | 1250304.5349
30 | 2607874.2364 | 1250414.5134
31 | 2607896.9925 | 1250467.578
32 | 2607808.3939 | 1250436.5413
33 | 2607812.4492 | 1249736.6717
34 | 2607902.8037 | 1250490.934
35 | 2607806.8304 | 1250438.5463
36 | 2607812.6335 | 1249584.1178
37 | 2607767.9525 | 1249743.8739
38 | 2608015.457 | 1250476.8749
39 | 2607792.6757 | 1250465.0259
40 | 2608021.5079 | 1250524.4535
41 | 2608003.7461 | 1250423.2022
42 | 2608216.7141 | 1249270.9132
43 | 2608102.4144 | 1249217.9897
44 | 2607772.2263 | 1248976.996
45 | 2607781.4548 | 1249044.8517
46 | 2607703.1574 | 1249081.4103
47 | 2607654.8747 | 1248752.8559
48 | 2607722.263 | 1249149.5424
49 | 2607813.8348 | 1249519.8891
50 | 2607813.8204 | 1249530.9073
51 | 2607506.856 | 1249444.2692
52 | 2607470.4039 | 1249588.3294
53 | 2607480.3463 | 1249259.8838
54 | 2607707.8948 | 1248781.3535
55 | 2607358.855 | 1249272.3522
56 | 2605806.9623 | 1249811.5721
57 | 2605816.5399 | 1249868.3291
58 | 2604825.2824 | 1247919.8978
59 | 2607824.6964 | 1251843.6104
60 | 2607823.1984 | 1251863.766
61 | 2607822.7697 | 1252179.5604
62 | 2607809.552 | 1252240.683
63 | 2604811.8634 | 1247919.9092
64 | 2604772.2257 | 1247872.2471
65 | 2604960.8995 | 1247727.6962
66 | 2604976.3589 | 1247717.4135
67 | 2604993.9465 | 1247672.4771
68 | 2605052.4547 | 1245583.351
69 | 2607613.5895 | 1246950.0038
70 | 2607677.3765 | 1247358.335
71 | 2607656.9392 | 1246875.6561
72 | 2607824.3993 | 1247009.1691
73 | 2607966.0987 | 1247085.4049
74 | 2607817.9712 | 1246697.9511
75 | 2607878.3716 | 1246635.913
76 | 2607631.7974 | 1247412.8004
77 | 2607719.1001 | 1247289.9783
78 | 2607559.1558 | 1247618.9901
79 | 2608114.2198 | 1250131.1176
80 | 2607989.3932 | 1250334.7299
81 | 2608109.1097 | 1250103.1148
82 | 2607792.527 | 1250474.3807
83 | 2607767.9525 | 1249743.8739

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9919 | -0.25438 | 0.35986 | 0.17429
1 | 0.99194 | -0.25466 | 0 | 0
2 | 0.99185 | -0.25395 | 0 | 0
3 | 0.99458 | -0.23589 | 0.26181 | 0.1268
4 | 0.99168 | -0.25239 | 0 | 0
5 | 0.99469 | -0.23685 | 0 | 0
6 | 0.99165 | -0.25214 | 0.40908 | 0.19813
7 | 0.99471 | -0.014797 | 0.30292 | 0.14671
8 | 0.99493 | -0.013424 | 0 | 0
9 | 0.99407 | -0.007031 | 0 | 0
10 | 0.9961 | -0.022316 | 0 | 0
11 | 0.9949 | -0.013602 | 0 | 0
12 | 0.9949 | -0.013581 | 0.16297 | 0.078932
13 | 0.99334 | -0.0013483 | 0 | 0
14 | 0.99405 | -0.0068674 | 0.24779 | 0.12001
15 | 0.99609 | -0.022247 | 0 | 0
16 | 0.99643 | -0.024713 | 0.22885 | 0.11084
17 | 0.99608 | -0.022154 | 0 | 0
18 | 0.99608 | -0.022138 | 0.069422 | 0.033623
19 | 0.9933 | -0.0010551 | 0.40111 | 0.19426
20 | 0.99404 | -0.0068061 | 0 | 0
21 | 0.99664 | -0.026338 | 0 | 0
22 | 0.9932 | -0.0003462 | 0 | 0
23 | 0.99393 | -0.0059785 | 0 | 0
24 | 0.99392 | -0.0059157 | 0.17451 | 0.084517
25 | 0.99816 | -0.033338 | 0.40044 | 0.19394
26 | 0.99815 | -0.033161 | 0.38534 | 0.18663
27 | 0.99827 | -0.032149 | 0.086089 | 0.041695
28 | 0.99788 | -0.035585 | 0.11179 | 0.054141
29 | 0.99831 | -0.03169 | 0 | 0
30 | 0.99779 | -0.03495 | 0 | 0
31 | 0.99758 | -0.0333 | 0.19189 | 0.092938
32 | 0.99773 | -0.034361 | 0.37664 | 0.18242
33 | 0.99974 | -0.014992 | 0 | 0
34 | 0.99749 | -0.032664 | 0 | 0
35 | 0.99773 | -0.034351 | 0.14697 | 0.071182
36 | 0.99954 | -0.015974 | 0 | 0
37 | 1 | 0 | -8.7433 | -3.9775
38 | 0.99702 | -0.029113 | 0 | 0
39 | 0.99772 | -0.034287 | 0.093215 | 0.045146
40 | 0.99687 | -0.028018 | 0.070926 | 0.034351
41 | 0.99699 | -0.028888 | 0 | 0
42 | 0.99848 | -0.01525 | 0.27725 | 0.13428
43 | 0.99855 | -0.014826 | 0 | 0
44 | 0.99877 | -0.013439 | 0 | 0
45 | 0.99873 | -0.013659 | 0.2656 | 0.12864
46 | 0.99896 | -0.012123 | 0.075886 | 0.036753
47 | 0.99864 | -0.012332 | 0 | 0
48 | 0.99904 | -0.012807 | 0 | 0
49 | 0.99946 | -0.016379 | 0 | 0
50 | 0.99947 | -0.016312 | 0.16447 | 0.079658
51 | 0.99883 | -0.052618 | 0 | 0
52 | 0.99881 | -0.052463 | 0.081164 | 0.039309
53 | 0.99847 | -0.073406 | 0.23414 | 0.1134
54 | 0.99861 | -0.012514 | 0.24948 | 0.12083
55 | 0.99836 | -0.073939 | 0 | 0
56 | 0.99544 | -0.24311 | 0 | 0
57 | 0.99541 | -0.24286 | 0.36719 | 0.17784
58 | 0.99023 | -0.28639 | 0 | 0
59 | 0.9924 | 0.0061485 | 0.34123 | 0.16526
60 | 0.99241 | 0.006065 | 0 | 0
61 | 0.99221 | 0.0078129 | 0 | 0
62 | 0.99218 | 0.0081163 | 0.39925 | 0.19337
63 | 0.99021 | -0.28622 | 0.124 | 0.060054
64 | 0.99007 | -0.28739 | 0 | 0
65 | 0.9897 | -0.28467 | 0 | 0
66 | 0.98968 | -0.28447 | 0.094903 | 0.045964
67 | 0.98961 | -0.28399 | 0 | 0
68 | 0.98538 | -0.31931 | 0.32347 | 0.15666
69 | 0.98133 | -0.35632 | 0 | 0
70 | 0.98107 | -0.35426 | 0 | 0
71 | 0.98131 | -0.35644 | 0.1172 | 0.056762
72 | 0.98121 | -0.35553 | 0 | 0
73 | 0.98119 | -0.35568 | 0.071456 | 0.034608
74 | 0.98112 | -0.35483 | 0 | 0
75 | 0.9811 | -0.355 | 0.15771 | 0.076383
76 | 0.98105 | -0.35409 | 0 | 0
77 | 0.98105 | -0.35441 | 0.1533 | 0.074246
78 | 0.98097 | -0.35342 | 0.22656 | 0.10973
79 | 0.99682 | -0.027489 | 0 | 0
80 | 0.99698 | -0.028813 | 0.075375 | 0.036506
81 | 0.99681 | -0.02738 | 0.31989 | 0.15493
82 | 0.99772 | -0.034278 | 0.083103 | 0.040249
83 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.76906 | -0.36105 | 0.76909 | 0.36028 | 2.694e-05 | -0.00076773 | 0.024726 | 0.024716 | 0.024726 | 0.9919 | -0.25438 | 0.99194 | -0.25466 | 11.239
1 | 0.4092 | 0.18676 | -0.40917 | -0.18909 | 2.2801e-05 | -0.0023293 | 0.013091 | 0.013119 | 0.013119 | 0.9919 | -0.25438 | 0.99185 | -0.25395 | 5.9632
2 | -0.76909 | -0.36028 | 0.77102 | 0.3594 | 0.001932 | -0.0008826 | 0.024716 | 0.02469 | 0.024716 | 0.99194 | -0.25466 | 0.99458 | -0.23589 | 11.7696
3 | 0.40917 | 0.18909 | -0.4091 | -0.19698 | 7.7965e-05 | -0.0078869 | 0.013119 | 0.013217 | 0.013217 | 0.99185 | -0.25395 | 0.99168 | -0.25239 | 6.0078
4 | -1.0328 | -0.4862 | 1.0329 | 0.48427 | 0.00012167 | -0.0019263 | 0.033133 | 0.033109 | 0.033133 | 0.99458 | -0.23589 | 0.99469 | -0.23685 | 15.0605
5 | 0.4091 | 0.19698 | -0.40908 | -0.19813 | 1.1492e-05 | -0.0011523 | 0.013217 | 0.013232 | 0.013232 | 0.99168 | -0.25239 | 0.99165 | -0.25214 | 6.0145
6 | -1.0329 | -0.48427 | 1.0338 | 0.47109 | 0.00082725 | -0.013185 | 0.033109 | 0.032945 | 0.033109 | 0.99469 | -0.23685 | 0.99544 | -0.24311 | 15.0495
7 | -0.30292 | -0.14671 | 0.30299 | 0.14632 | 6.2765e-05 | -0.00039715 | 0.0097679 | 0.0097624 | 0.0097679 | 0.99471 | -0.014797 | 0.99493 | -0.013424 | 4.6514
8 | 1.5671 | 0.68797 | -1.5657 | -0.69781 | 0.0014341 | -0.0098368 | 0.049657 | 0.049778 | 0.049778 | 0.99493 | -0.013424 | 0.99407 | -0.007031 | 22.6263
9 | -2.0331 | -0.91287 | 2.0356 | 0.90288 | 0.0025297 | -0.0099947 | 0.064662 | 0.064535 | 0.064662 | 0.99493 | -0.013424 | 0.9961 | -0.022316 | 29.3919
10 | 0.16298 | 0.078583 | -0.16298 | -0.078685 | 4.3334e-06 | -0.00010154 | 0.0052498 | 0.0052511 | 0.0052511 | 0.99493 | -0.013424 | 0.9949 | -0.013602 | 2.5005
11 | 1.1433 | 0.50753 | -1.1424 | -0.51917 | 0.00089301 | -0.01164 | 0.036326 | 0.036468 | 0.036468 | 0.99407 | -0.007031 | 0.99334 | -0.0013483 | 16.5764
12 | 0.42233 | 0.19028 | -0.42232 | -0.19119 | 9.3623e-06 | -0.00091087 | 0.013452 | 0.013463 | 0.013463 | 0.99407 | -0.007031 | 0.99405 | -0.0068674 | 6.1194
13 | 0.069424 | 0.026834 | -0.069423 | -0.030049 | 8.5638e-07 | -0.0032144 | 0.002157 | 0.0021923 | 0.0021923 | 0.9961 | -0.022316 | 0.99609 | -0.022247 | 0.99651
14 | -2.105 | -0.92971 | 2.1057 | 0.92702 | 0.00072915 | -0.0026954 | 0.06669 | 0.066656 | 0.06669 | 0.9961 | -0.022316 | 0.99643 | -0.024713 | 30.3135
15 | 0.16298 | 0.078685 | -0.16297 | -0.078932 | 3.8587e-07 | -0.00024747 | 0.0052511 | 0.0052542 | 0.0052542 | 0.9949 | -0.013602 | 0.9949 | -0.013581 | 2.3883
16 | 1.1424 | 0.51917 | -1.1424 | -0.51975 | 4.4633e-05 | -0.00057887 | 0.036468 | 0.036475 | 0.036475 | 0.99334 | -0.0013483 | 0.9933 | -0.0010551 | 16.5796
17 | 0.17453 | 0.071182 | -0.17453 | -0.072304 | 1.908e-06 | -0.0011223 | 0.0054737 | 0.0054861 | 0.0054861 | 0.99405 | -0.0068674 | 0.99404 | -0.0068061 | 2.4937
18 | 0.069423 | 0.030049 | -0.069422 | -0.033164 | 8.5799e-07 | -0.0031152 | 0.0021923 | 0.0022297 | 0.0022297 | 0.99609 | -0.022247 | 0.99608 | -0.022154 | 1.0135
19 | -2.3346 | -1.0379 | 2.3351 | 1.0363 | 0.00053729 | -0.0015829 | 0.074018 | 0.073997 | 0.074018 | 0.99643 | -0.024713 | 0.99664 | -0.026338 | 33.6445
20 | 0.069422 | 0.033164 | -0.069422 | -0.033623 | 1.289e-07 | -0.00045884 | 0.0022297 | 0.0022355 | 0.0022355 | 0.99608 | -0.022154 | 0.99608 | -0.022138 | 1.0161
21 | 0.74129 | 0.32548 | -0.74121 | -0.32788 | 7.601e-05 | -0.0023971 | 0.023529 | 0.023557 | 0.023557 | 0.9933 | -0.0010551 | 0.9932 | -0.0003462 | 10.7077
22 | 0.17453 | 0.072304 | -0.17451 | -0.083809 | 2.0082e-05 | -0.011505 | 0.0054861 | 0.0056226 | 0.0056226 | 0.99404 | -0.0068061 | 0.99393 | -0.0059785 | 2.5557
23 | -2.3351 | -1.0363 | 2.3357 | 1.0346 | 0.00055828 | -0.0016466 | 0.073997 | 0.073976 | 0.073997 | 0.99664 | -0.026338 | 0.99687 | -0.028018 | 33.6352
24 | 0.74121 | 0.32788 | -0.74058 | -0.34748 | 0.00062912 | -0.0196 | 0.023557 | 0.023796 | 0.023796 | 0.9932 | -0.0003462 | 0.99241 | 0.006065 | 10.8162
25 | 0.17451 | 0.083809 | -0.17451 | -0.084517 | 1.2696e-06 | -0.00070809 | 0.0056226 | 0.0056315 | 0.0056315 | 0.99393 | -0.0059785 | 0.99392 | -0.0059157 | 2.5598
26 | 0.38535 | 0.18572 | -0.38534 | -0.18663 | 7.8732e-06 | -0.00091345 | 0.012371 | 0.012383 | 0.012383 | 0.99816 | -0.033338 | 0.99815 | -0.033161 | 5.6285
27 | -4.5955 | -2.1047 | 4.5959 | 2.1036 | 0.00042901 | -0.0011093 | 0.14618 | 0.14616 | 0.14618 | 0.99816 | -0.033338 | 0.99827 | -0.032149 | 40.3812
28 | 3.8097 | 1.725 | -3.8087 | -1.7244 | 0.0010372 | 0.00060232 | 0.12095 | 0.12095 | 0.12095 | 0.99816 | -0.033338 | 0.99788 | -0.035585 | 57.5942
29 | -4.682 | -2.1452 | 4.6822 | 2.1448 | 0.00016887 | -0.00041623 | 0.14893 | 0.14892 | 0.14893 | 0.99827 | -0.032149 | 0.99831 | -0.03169 | 41.1404
30 | 3.6969 | 1.6703 | -3.6966 | -1.6706 | 0.00031793 | -0.00031675 | 0.11736 | 0.11736 | 0.11736 | 0.99788 | -0.035585 | 0.99779 | -0.03495 | 53.3458
31 | -4.6822 | -2.1448 | 4.6883 | 2.1297 | 0.0060979 | -0.015091 | 0.14892 | 0.14869 | 0.14892 | 0.99831 | -0.03169 | 0.99974 | -0.014992 | 41.1386
32 | 2.9966 | 1.3343 | -2.9959 | -1.3354 | 0.00069471 | -0.0011669 | 0.094901 | 0.094917 | 0.094917 | 0.99779 | -0.03495 | 0.99758 | -0.0333 | 43.1442
33 | 0.69998 | 0.3363 | -0.69994 | -0.33798 | 4.7943e-05 | -0.0016752 | 0.022467 | 0.022489 | 0.022489 | 0.99779 | -0.03495 | 0.99773 | -0.034361 | 10.2221
34 | 2.804 | 1.2425 | -2.8037 | -1.243 | 0.00025378 | -0.00049807 | 0.088751 | 0.088757 | 0.088757 | 0.99758 | -0.0333 | 0.99749 | -0.032664 | 40.3442
35 | 0.32329 | 0.15556 | -0.32329 | -0.15562 | 3.6577e-07 | -6.0322e-05 | 0.01038 | 0.010381 | 0.010381 | 0.99773 | -0.034361 | 0.99773 | -0.034351 | 4.7187
36 | 4.0398 | 1.834 | -4.039 | -1.8431 | 0.00077451 | -0.0091448 | 0.12811 | 0.12822 | 0.12822 | 0.99974 | -0.014992 | 0.99954 | -0.015974 | 20.0973
37 | -8.7281 | -3.9637 | 8.7293 | 3.967 | 0.0012329 | 0.003253 | 0.27679 | 0.27679 | 0.27679 | 0.99974 | -0.014992 | 1 | 0 | 42.9138
38 | 2.8037 | 1.243 | -2.8023 | -1.2458 | 0.0014119 | -0.0027676 | 0.088757 | 0.088795 | 0.088795 | 0.99749 | -0.032664 | 0.99702 | -0.029113 | 40.3612
39 | 0.17632 | 0.084439 | -0.17632 | -0.085172 | 1.3205e-06 | -0.00073321 | 0.0056563 | 0.0056655 | 0.0056655 | 0.99773 | -0.034351 | 0.99772 | -0.034287 | 2.5752
40 | 4.039 | 1.8431 | -4.0387 | -1.8463 | 0.0002705 | -0.0031889 | 0.12822 | 0.12826 | 0.12826 | 0.99954 | -0.015974 | 0.99947 | -0.016312 | 20.1036
41 | 0.39534 | 0.17782 | -0.39533 | -0.17918 | 1.2045e-05 | -0.0013539 | 0.012551 | 0.012568 | 0.012568 | 0.99702 | -0.029113 | 0.99699 | -0.028888 | 5.7125
42 | 2.407 | 1.0679 | -2.4066 | -1.069 | 0.00037394 | -0.0010323 | 0.076244 | 0.076257 | 0.076257 | 0.99702 | -0.029113 | 0.99687 | -0.028018 | 34.6623
43 | 0.083103 | 0.040026 | -0.083103 | -0.040249 | 8.9054e-08 | -0.00022234 | 0.0026688 | 0.0026716 | 0.0026716 | 0.99772 | -0.034287 | 0.99772 | -0.034278 | 1.2144
44 | 0.31995 | 0.1448 | -0.3199 | -0.15426 | 5.5749e-05 | -0.0094592 | 0.010169 | 0.010285 | 0.010285 | 0.99699 | -0.028888 | 0.99682 | -0.027489 | 4.675
45 | 0.075376 | 0.034379 | -0.075375 | -0.036506 | 6.9597e-07 | -0.0021269 | 0.0023988 | 0.002425 | 0.002425 | 0.99699 | -0.028888 | 0.99698 | -0.028813 | 1.1023
46 | -0.27725 | -0.13428 | 0.27726 | 0.13414 | 1.7797e-05 | -0.00013877 | 0.0089062 | 0.0089043 | 0.0089062 | 0.99848 | -0.01525 | 0.99855 | -0.014826 | 4.241
47 | -0.27726 | -0.13414 | 0.27732 | 0.13369 | 5.7707e-05 | -0.00045055 | 0.0089043 | 0.0088982 | 0.0089043 | 0.99855 | -0.014826 | 0.99877 | -0.013439 | 4.2401
48 | 0.26561 | 0.12856 | -0.2656 | -0.12864 | 8.8765e-06 | -7.5988e-05 | 0.0085289 | 0.00853 | 0.00853 | 0.99877 | -0.013439 | 0.99873 | -0.013659 | 4.0619
49 | -0.79245 | -0.37316 | 0.7926 | 0.3731 | 0.00014295 | -5.9572e-05 | 0.025317 | 0.025315 | 0.025317 | 0.99877 | -0.013439 | 0.99896 | -0.012123 | 12.0556
50 | 0.24952 | 0.11091 | -0.24949 | -0.12076 | 3.4944e-05 | -0.0098489 | 0.0078924 | 0.0080124 | 0.0080124 | 0.99877 | -0.013439 | 0.99864 | -0.012332 | 3.642
51 | -0.86848 | -0.40985 | 0.86856 | 0.40819 | 7.273e-05 | -0.0016653 | 0.027751 | 0.027731 | 0.027751 | 0.99896 | -0.012123 | 0.99904 | -0.012807 | 12.6143
52 | 0.24949 | 0.12076 | -0.24948 | -0.12083 | 6.8859e-06 | -6.7348e-05 | 0.0080124 | 0.0080133 | 0.0080133 | 0.99864 | -0.012332 | 0.99861 | -0.012514 | 3.8159
53 | -0.86856 | -0.40819 | 0.86895 | 0.39917 | 0.00039192 | -0.0090218 | 0.027731 | 0.027619 | 0.027731 | 0.99904 | -0.012807 | 0.99946 | -0.016379 | 12.6048
54 | -3.8742 | -1.7673 | 3.8743 | 1.7666 | 5.1503e-05 | -0.0006626 | 0.12299 | 0.12298 | 0.12299 | 0.99946 | -0.016379 | 0.99947 | -0.016312 | 19.2778
55 | 3.0053 | 1.3681 | -3.0042 | -1.3658 | 0.0010267 | 0.0023246 | 0.095373 | 0.095378 | 0.095378 | 0.99946 | -0.016379 | 0.99883 | -0.052618 | 14.7874
56 | 0.081165 | 0.034871 | -0.081164 | -0.039309 | 1.6548e-06 | -0.0044383 | 0.0025531 | 0.0026064 | 0.0026064 | 0.99883 | -0.052618 | 0.99881 | -0.052463 | 1.1847
57 | 2.9231 | 1.3309 | -2.9225 | -1.3297 | 0.00057305 | 0.0012842 | 0.092826 | 0.092829 | 0.092829 | 0.99883 | -0.052618 | 0.99847 | -0.073406 | 14.3921
58 | 2.6884 | 1.2163 | -2.6881 | -1.2238 | 0.0002756 | -0.0075125 | 0.08531 | 0.085402 | 0.085402 | 0.99847 | -0.073406 | 0.99836 | -0.073939 | 13.3858
59 | 2.6881 | 1.2238 | -2.6838 | -1.2145 | 0.0042791 | 0.0092498 | 0.085402 | 0.085429 | 0.085429 | 0.99836 | -0.073939 | 0.99544 | -0.24311 | 13.2447
60 | 0.3672 | 0.17648 | -0.36719 | -0.17784 | 1.0744e-05 | -0.0013588 | 0.011815 | 0.011832 | 0.011832 | 0.99544 | -0.24311 | 0.99541 | -0.24286 | 5.3782
61 | 1.2828 | 0.56696 | -1.2765 | -0.56553 | 0.0062863 | 0.0014296 | 0.040673 | 0.040703 | 0.040703 | 0.99544 | -0.24311 | 0.99023 | -0.28639 | 19.3822
62 | 1.2765 | 0.56553 | -1.2765 | -0.56584 | 3.035e-05 | -0.00031222 | 0.040703 | 0.040706 | 0.040706 | 0.99023 | -0.28639 | 0.99021 | -0.28622 | 18.5029
63 | -0.34123 | -0.16526 | 0.34123 | 0.16479 | 3.2804e-06 | -0.00047433 | 0.011029 | 0.011023 | 0.011029 | 0.9924 | 0.0061485 | 0.99241 | 0.006065 | 5.013
64 | 0.39935 | 0.18269 | -0.39927 | -0.19189 | 8.6198e-05 | -0.0091955 | 0.012774 | 0.012888 | 0.012888 | 0.99241 | 0.006065 | 0.99221 | 0.0078129 | 5.8582
65 | 0.39927 | 0.19189 | -0.39925 | -0.19337 | 1.4028e-05 | -0.0014807 | 0.012888 | 0.012907 | 0.012907 | 0.99221 | 0.0078129 | 0.99218 | 0.0081163 | 5.8668
66 | 1.1525 | 0.50579 | -1.1524 | -0.50577 | 0.0001487 | 2.0592e-05 | 0.036693 | 0.036693 | 0.036693 | 0.99021 | -0.28622 | 0.99007 | -0.28739 | 17.473
67 | 1.1524 | 0.50577 | -1.1519 | -0.51148 | 0.00044991 | -0.0057116 | 0.036693 | 0.036762 | 0.036762 | 0.99007 | -0.28739 | 0.9897 | -0.28467 | 16.7101
68 | 1.1519 | 0.51148 | -1.1519 | -0.5119 | 3.3453e-05 | -0.00042364 | 0.036762 | 0.036767 | 0.036767 | 0.9897 | -0.28467 | 0.98968 | -0.28447 | 16.7124
69 | 1.057 | 0.46594 | -1.0569 | -0.46705 | 7.34e-05 | -0.0011103 | 0.033693 | 0.033707 | 0.033707 | 0.98968 | -0.28447 | 0.98961 | -0.28399 | 15.3212
70 | 1.0569 | 0.46705 | -1.0527 | -0.46683 | 0.0042342 | 0.0002192 | 0.033707 | 0.033736 | 0.033736 | 0.98961 | -0.28399 | 0.98538 | -0.31931 | 16.0645
71 | 0.72921 | 0.31017 | -0.72641 | -0.31177 | 0.0027921 | -0.0016023 | 0.023215 | 0.023254 | 0.023254 | 0.98538 | -0.31931 | 0.98133 | -0.35632 | 11.0731
72 | 0.38 | 0.16397 | -0.37989 | -0.17636 | 0.00010826 | -0.012394 | 0.012174 | 0.012324 | 0.012324 | 0.98133 | -0.35632 | 0.98107 | -0.35426 | 5.6017
73 | 0.1172 | 0.056664 | -0.1172 | -0.056762 | 2.2494e-06 | -9.7531e-05 | 0.0038294 | 0.0038307 | 0.0038307 | 0.98133 | -0.35632 | 0.98131 | -0.35644 | 1.8241
74 | 0.22922 | 0.091142 | -0.22919 | -0.10087 | 3.0223e-05 | -0.0097301 | 0.0072563 | 0.0073669 | 0.0073669 | 0.98133 | -0.35632 | 0.98121 | -0.35553 | 3.3486
75 | 0.22659 | 0.1022 | -0.22658 | -0.10384 | 5.0994e-06 | -0.0016349 | 0.007314 | 0.007334 | 0.007334 | 0.98107 | -0.35426 | 0.98105 | -0.35409 | 3.3336
76 | 0.1533 | 0.074156 | -0.1533 | -0.074246 | 3.5835e-06 | -8.9773e-05 | 0.0050109 | 0.005012 | 0.005012 | 0.98107 | -0.35426 | 0.98105 | -0.35441 | 2.3867
77 | 0.15773 | 0.066448 | -0.15771 | -0.076286 | 1.483e-05 | -0.0098377 | 0.0050354 | 0.0051548 | 0.0051548 | 0.98121 | -0.35553 | 0.98112 | -0.35483 | 2.3431
78 | 0.071458 | 0.034424 | -0.071456 | -0.034608 | 1.5627e-06 | -0.00018396 | 0.0023335 | 0.0023359 | 0.0023359 | 0.98121 | -0.35553 | 0.98119 | -0.35568 | 1.1123
79 | 0.15771 | 0.076286 | -0.15771 | -0.076383 | 4.1002e-06 | -9.6929e-05 | 0.0051548 | 0.005156 | 0.005156 | 0.98112 | -0.35483 | 0.9811 | -0.355 | 2.4553
80 | 0.22658 | 0.10384 | -0.22656 | -0.10973 | 1.861e-05 | -0.0058906 | 0.007334 | 0.0074079 | 0.0074079 | 0.98105 | -0.35409 | 0.98097 | -0.35342 | 3.3672
81 | 0.3199 | 0.15426 | -0.31989 | -0.15493 | 4.0232e-06 | -0.00067415 | 0.010285 | 0.010293 | 0.010293 | 0.99682 | -0.027489 | 0.99681 | -0.02738 | 4.6788

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 8.879 | 4.0432

## res_load
| p_mw | q_mvar
0 | 0.35986 | 0.17429
1 | 0.26181 | 0.1268
2 | 0.40908 | 0.19813
3 | 0.30292 | 0.14671
4 | 0.16297 | 0.078932
5 | 0.24779 | 0.12001
6 | 0.22885 | 0.11084
7 | 0.069422 | 0.033623
8 | 0.40111 | 0.19426
9 | 0.17451 | 0.084517
10 | 0.40044 | 0.19394
11 | 0.38534 | 0.18663
12 | 0.086089 | 0.041695
13 | 0.11179 | 0.054141
14 | 0.19189 | 0.092938
15 | 0.37664 | 0.18242
16 | 0.14697 | 0.071182
17 | 0.13575 | 0.065745
18 | 0.093215 | 0.045146
19 | 0.070926 | 0.034351
20 | 0.27725 | 0.13428
21 | 0.2656 | 0.12864
22 | 0.075886 | 0.036753
23 | 0.16447 | 0.079658
24 | 0.081164 | 0.039309
25 | 0.23414 | 0.1134
26 | 0.24948 | 0.12083
27 | 0.36719 | 0.17784
28 | 0.34123 | 0.16526
29 | 0.39925 | 0.19337
30 | 0.124 | 0.060054
31 | 0.094903 | 0.045964
32 | 0.32347 | 0.15666
33 | 0.1172 | 0.056762
34 | 0.071456 | 0.034608
35 | 0.15771 | 0.076383
36 | 0.1533 | 0.074246
37 | 0.22656 | 0.10973
38 | 0.075375 | 0.036506
39 | 0.31989 | 0.15493
40 | 0.083103 | 0.040249

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1