## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_2_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_2_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_2_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_2_0_node_31 | 20 | n |  | TRUE
4 | bus_MV_2_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_2_0_node_6 | 20 | n |  | TRUE
6 | bus_MV_2_0_node_3 | 20 | n |  | TRUE
7 | bus_MV_2_0_node_257 | 20 | n |  | TRUE
8 | bus_MV_2_0_node_258 | 20 | n |  | TRUE
9 | bus_MV_2_0_node_259 | 20 | n |  | TRUE
10 | bus_MV_2_0_node_5 | 20 | n |  | TRUE
11 | bus_MV_2_0_node_22 | 20 | n |  | TRUE
12 | bus_MV_2_0_node_27 | 20 | n |  | TRUE
13 | bus_MV_2_0_node_7 | 20 | n |  | TRUE
14 | bus_MV_2_0_node_8 | 20 | n |  | TRUE
15 | bus_MV_2_0_node_10 | 20 | n |  | TRUE
16 | bus_MV_2_0_node_11 | 20 | n |  | TRUE
17 | bus_MV_2_0_node_9 | 20 | n |  | TRUE
18 | bus_MV_2_0_node_13 | 20 | n |  | TRUE
19 | bus_MV_2_0_node_313 | 20 | n |  | TRUE
20 | bus_MV_2_0_node_16 | 20 | n |  | TRUE
21 | bus_MV_2_0_node_317 | 20 | n |  | TRUE
22 | bus_MV_2_0_node_12 | 20 | n |  | TRUE
23 | bus_MV_2_0_node_318 | 20 | n |  | TRUE
24 | bus_MV_2_0_node_326 | 20 | n |  | TRUE
25 | bus_MV_2_0_node_14 | 20 | n |  | TRUE
26 | bus_MV_2_0_node_15 | 20 | n |  | TRUE
27 | bus_MV_2_0_node_40 | 20 | n |  | TRUE
28 | bus_MV_2_0_node_38 | 20 | n |  | TRUE
29 | bus_MV_2_0_node_37 | 20 | n |  | TRUE
30 | bus_MV_2_0_node_17 | 20 | n |  | TRUE
31 | bus_MV_2_0_node_19 | 20 | n |  | TRUE
32 | bus_MV_2_0_node_20 | 20 | n |  | TRUE
33 | bus_MV_2_0_node_29 | 20 | n |  | TRUE
34 | bus_MV_2_0_node_23 | 20 | n |  | TRUE
35 | bus_MV_2_0_node_24 | 20 | n |  | TRUE
36 | bus_MV_2_0_node_41 | 20 | n |  | TRUE
37 | bus_MV_2_0_node_39 | 20 | n |  | TRUE
38 | bus_MV_2_0_node_25 | 20 | n |  | TRUE
39 | bus_MV_2_0_node_26 | 20 | n |  | TRUE
40 | bus_MV_2_0_node_36 | 20 | n |  | TRUE
41 | bus_MV_2_0_node_297 | 20 | n |  | TRUE
42 | bus_MV_2_0_node_30 | 20 | n |  | TRUE
43 | bus_MV_2_0_node_298 | 20 | n |  | TRUE
44 | bus_MV_2_0_node_32 | 20 | n |  | TRUE
45 | bus_MV_2_0_node_33 | 20 | n |  | TRUE
46 | bus_MV_2_0_node_34 | 20 | n |  | TRUE
47 | bus_MV_2_0_node_253 | 20 | n |  | TRUE
48 | bus_MV_2_0_node_261 | 20 | n |  | TRUE
49 | bus_MV_2_0_node_42 | 20 | n |  | TRUE
50 | bus_MV_2_0_node_43 | 20 | n |  | TRUE
51 | bus_MV_2_0_node_46 | 20 | n |  | TRUE
52 | bus_MV_2_0_node_310 | 20 | n |  | TRUE
53 | bus_MV_2_0_node_44 | 20 | n |  | TRUE
54 | bus_MV_2_0_node_45 | 20 | n |  | TRUE
55 | bus_MV_2_0_node_47 | 20 | n |  | TRUE
56 | bus_MV_2_0_node_48 | 20 | n |  | TRUE
57 | bus_MV_2_0_node_49 | 20 | n |  | TRUE
58 | bus_MV_2_0_node_50 | 20 | n |  | TRUE
59 | bus_MV_2_0_node_300 | 20 | n |  | TRUE
60 | bus_MV_2_0_node_51 | 20 | n |  | TRUE
61 | bus_MV_2_0_node_320 | 20 | n |  | TRUE
62 | bus_MV_2_0_node_53 | 20 | n |  | TRUE
63 | bus_MV_2_0_node_54 | 20 | n |  | TRUE
64 | bus_MV_2_0_node_58 | 20 | n |  | TRUE
65 | bus_MV_2_0_node_55 | 20 | n |  | TRUE
66 | bus_MV_2_0_node_65 | 20 | n |  | TRUE
67 | bus_MV_2_0_node_64 | 20 | n |  | TRUE
68 | bus_MV_2_0_node_56 | 20 | n |  | TRUE
69 | bus_MV_2_0_node_63 | 20 | n |  | TRUE
70 | bus_MV_2_0_node_57 | 20 | n |  | TRUE
71 | bus_MV_2_0_node_71 | 20 | n |  | TRUE
72 | bus_MV_2_0_node_67 | 20 | n |  | TRUE
73 | bus_MV_2_0_node_66 | 20 | n |  | TRUE
74 | bus_MV_2_0_node_59 | 20 | n |  | TRUE
75 | bus_MV_2_0_node_60 | 20 | n |  | TRUE
76 | bus_MV_2_0_node_62 | 20 | n |  | TRUE
77 | bus_MV_2_0_node_61 | 20 | n |  | TRUE
78 | bus_MV_2_0_node_268 | 20 | n |  | TRUE
79 | bus_MV_2_0_node_219 | 20 | n |  | TRUE
80 | bus_MV_2_0_node_271 | 20 | n |  | TRUE
81 | bus_MV_2_0_node_272 | 20 | n |  | TRUE
82 | bus_MV_2_0_node_69 | 20 | n |  | TRUE
83 | bus_MV_2_0_node_70 | 20 | n |  | TRUE
84 | bus_MV_2_0_node_68 | 20 | n |  | TRUE
85 | bus_MV_2_0_node_270 | 20 | n |  | TRUE
86 | bus_MV_2_0_node_252 | 20 | n |  | TRUE
87 | bus_MV_2_0_node_254 | 20 | n |  | TRUE
88 | bus_MV_2_0_node_255 | 20 | n |  | TRUE
89 | bus_MV_2_0_node_260 | 20 | n |  | TRUE
90 | bus_MV_2_0_node_256 | 20 | n |  | TRUE
91 | bus_MV_2_0_node_319 | 20 | n |  | TRUE
92 | bus_MV_2_0_node_262 | 20 | n |  | TRUE
93 | bus_MV_2_0_node_263 | 20 | n |  | TRUE
94 | bus_MV_2_0_node_264 | 20 | n |  | TRUE
95 | bus_MV_2_0_node_265 | 20 | n |  | TRUE
96 | bus_MV_2_0_node_267 | 20 | n |  | TRUE
97 | bus_MV_2_0_node_266 | 20 | n |  | TRUE
98 | bus_MV_2_0_node_269 | 20 | n |  | TRUE
99 | bus_MV_2_0_node_301 | 20 | n |  | TRUE
100 | bus_MV_2_0_node_302 | 20 | n |  | TRUE
101 | bus_MV_2_0_node_303 | 20 | n |  | TRUE
102 | bus_MV_2_0_node_304 | 20 | n |  | TRUE
103 | bus_HV_2_0_node_5 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_2_0_load_0 | 0 | 0.17322 | 0.083896 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_2_0_load_6 | 5 | 0.17878 | 0.086585 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_2_0_load_258 | 8 | 0.091659 | 0.044393 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_2_0_load_259 | 9 | 0.071202 | 0.034485 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_2_0_load_22 | 11 | 0.28236 | 0.13676 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_2_0_load_27 | 12 | 0.34356 | 0.1664 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_2_0_load_7 | 13 | 0.14065 | 0.068121 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_2_0_load_313 | 19 | 0.28521 | 0.13813 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_2_0_load_16 | 20 | 0.1796 | 0.086982 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_2_0_load_317 | 21 | 0.069695 | 0.033755 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_2_0_load_318 | 23 | 0.32504 | 0.15743 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_2_0_load_326 | 24 | 0.092495 | 0.044797 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_2_0_load_40 | 27 | 0.29513 | 0.14294 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_2_0_load_37 | 29 | 0.40451 | 0.19591 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_2_0_load_17 | 30 | 0.22382 | 0.1084 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_2_0_load_29 | 33 | 0.27286 | 0.13215 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_2_0_load_41 | 36 | 0.14526 | 0.070355 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_2_0_load_39 | 37 | 0.19465 | 0.094274 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_2_0_load_25 | 38 | 0.11355 | 0.054993 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_2_0_load_36 | 40 | 0.18474 | 0.089472 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_2_0_load_297 | 41 | 0.28784 | 0.13941 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_2_0_load_298 | 43 | 0.22063 | 0.10686 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_2_0_load_32 | 44 | 0.061928 | 0.029993 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_2_0_load_34 | 46 | 0.074916 | 0.036284 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_2_0_load_261 | 48 | 0.12358 | 0.059851 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_2_0_load_310 | 52 | 0.25486 | 0.12344 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_2_0_load_44 | 53 | 0.22287 | 0.10794 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_2_0_load_49 | 57 | 0.18074 | 0.087537 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_2_0_load_50 | 58 | 0.09185 | 0.044485 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_2_0_load_51 | 60 | 0.052474 | 0.025414 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_2_0_load_320 | 61 | 0.051322 | 0.024856 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_2_0_load_55 | 65 | 0.12653 | 0.061281 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_2_0_load_64 | 67 | 0.07727 | 0.037424 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_2_0_load_63 | 69 | 0.14053 | 0.068061 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_2_0_load_71 | 71 | 0.087949 | 0.042596 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_2_0_load_67 | 72 | 0.085215 | 0.041271 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_2_0_load_66 | 73 | 0.13753 | 0.066608 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_2_0_load_59 | 74 | 0.13721 | 0.066453 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_2_0_load_268 | 78 | 0.17341 | 0.083987 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_2_0_load_219 | 79 | 0.1266 | 0.061314 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_2_0_load_272 | 81 | 0.074206 | 0.035939 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_2_0_load_68 | 84 | 0.0947 | 0.045865 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_2_0_load_252 | 86 | 0.38837 | 0.1881 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_2_0_load_254 | 87 | 1.5077 | 0.73024 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_2_0_load_256 | 90 | 0.27735 | 0.13433 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_2_0_load_319 | 91 | 0.32856 | 0.15913 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_2_0_load_262 | 92 | 0.19318 | 0.093559 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_2_0_load_263 | 93 | 0.14114 | 0.068358 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_2_0_load_267 | 96 | 0.11481 | 0.055605 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_2_0_load_266 | 97 | 0.073898 | 0.03579 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_2_0_load_269 | 98 | 0.11662 | 0.056481 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_2_0_load_301 | 99 | 0.062181 | 0.030115 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_2_0_load_304 | 102 | 0.067409 | 0.032647 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_2_0_line_0 |  | 0 | 1 | 0.010673 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_2_0_line_1 |  | 1 | 2 | 0.47686 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
2 | MV_2_0_line_2 |  | 1 | 3 | 0.22302 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
3 | MV_2_0_line_3 |  | 2 | 4 | 0.84925 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
4 | MV_2_0_line_4 |  | 2 | 5 | 0.034091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_2_0_line_5 |  | 3 | 43 | 0.005706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_2_0_line_6 |  | 3 | 37 | 0.23522 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
7 | MV_2_0_line_7 |  | 3 | 42 | 0.25918 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_2_0_line_8 |  | 4 | 9 | 0.042651 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
9 | MV_2_0_line_9 |  | 4 | 6 | 0.058553 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_2_0_line_10 |  | 6 | 7 | 0.02004 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_2_0_line_11 |  | 6 | 8 | 0.030348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_2_0_line_12 |  | 7 | 90 | 0.034243 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_2_0_line_13 |  | 9 | 88 | 0.025734 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
14 | MV_2_0_line_14 |  | 10 | 11 | 0.36999 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
15 | MV_2_0_line_15 |  | 10 | 12 | 0.043416 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_2_0_line_16 |  | 11 | 34 | 0.068337 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
17 | MV_2_0_line_17 |  | 12 | 41 | 1.5648 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_2_0_line_18 |  | 13 | 14 | 0.12753 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_2_0_line_19 |  | 14 | 15 | 0.56073 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_2_0_line_20 |  | 14 | 16 | 0.73036 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_2_0_line_21 |  | 15 | 20 | 0.099847 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_2_0_line_22 |  | 15 | 17 | 0.47404 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_2_0_line_23 |  | 16 | 21 | 0.35423 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_2_0_line_24 |  | 17 | 18 | 0.74745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_2_0_line_25 |  | 17 | 19 | 0.039985 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_2_0_line_26 |  | 18 | 24 | 0.016624 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_2_0_line_27 |  | 18 | 25 | 0.17682 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_2_0_line_28 |  | 18 | 26 | 0.29635 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_2_0_line_29 |  | 18 | 22 | 0.67896 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_2_0_line_30 |  | 19 | 45 | 0.48741 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_2_0_line_31 |  | 22 | 23 | 0.030373 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_2_0_line_32 |  | 25 | 27 | 0.040315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_2_0_line_33 |  | 26 | 28 | 0.025559 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_2_0_line_34 |  | 26 | 29 | 0.063249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_2_0_line_35 |  | 28 | 47 | 0.18649 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_2_0_line_36 |  | 28 | 48 | 0.056709 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_2_0_line_37 |  | 30 | 31 | 0.065328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_2_0_line_38 |  | 31 | 32 | 0.36583 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_2_0_line_39 |  | 32 | 33 | 0.033484 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_2_0_line_40 |  | 33 | 42 | 0.014095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_2_0_line_41 |  | 34 | 35 | 0.41667 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
42 | MV_2_0_line_42 |  | 34 | 36 | 1.5813 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_2_0_line_43 |  | 35 | 37 | 0.098126 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
44 | MV_2_0_line_44 |  | 36 | 49 | 0.036123 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_2_0_line_45 |  | 38 | 39 | 0.20318 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_2_0_line_46 |  | 39 | 40 | 1.6926 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_2_0_line_47 |  | 40 | 46 | 0.012411 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_2_0_line_48 |  | 41 | 66 | 0.14238 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_2_0_line_49 |  | 44 | 45 | 0.035008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_2_0_line_50 |  | 44 | 46 | 0.038266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_2_0_line_51 |  | 47 | 87 | 0.10388 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_2_0_line_52 |  | 47 | 88 | 0.17376 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
53 | MV_2_0_line_53 |  | 47 | 86 | 0.019798 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_2_0_line_54 |  | 49 | 50 | 0.22805 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_2_0_line_55 |  | 50 | 51 | 0.41084 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_2_0_line_56 |  | 50 | 52 | 0.035182 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_2_0_line_57 |  | 51 | 56 | 1.0995 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_2_0_line_58 |  | 51 | 53 | 0.040224 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_2_0_line_59 |  | 53 | 54 | 0.0023288 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_2_0_line_60 |  | 54 | 55 | 1.1272 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_2_0_line_61 |  | 55 | 57 | 0.003712 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_2_0_line_62 |  | 56 | 58 | 0.24096 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_2_0_line_63 |  | 57 | 59 | 1.983 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_2_0_line_64 |  | 59 | 99 | 0.00663 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_2_0_line_65 |  | 60 | 61 | 0.83726 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_2_0_line_66 |  | 61 | 83 | 0.053599 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_2_0_line_67 |  | 62 | 63 | 0.33204 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_2_0_line_68 |  | 62 | 64 | 0.34419 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_2_0_line_69 |  | 62 | 65 | 0.02684 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
70 | MV_2_0_line_70 |  | 63 | 66 | 0.47662 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_2_0_line_71 |  | 63 | 67 | 0.004348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_2_0_line_72 |  | 64 | 73 | 0.12262 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_2_0_line_73 |  | 64 | 68 | 0.038396 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_2_0_line_74 |  | 68 | 69 | 0.087995 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_2_0_line_75 |  | 70 | 71 | 0.064967 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
76 | MV_2_0_line_76 |  | 70 | 72 | 0.59367 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
77 | MV_2_0_line_77 |  | 72 | 82 | 0.031312 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_2_0_line_78 |  | 72 | 83 | 0.006435 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_2_0_line_79 |  | 72 | 73 | 0.053516 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_2_0_line_80 |  | 74 | 75 | 0.041054 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
81 | MV_2_0_line_81 |  | 75 | 76 | 0.16394 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_2_0_line_82 |  | 76 | 80 | 0.061359 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_2_0_line_83 |  | 76 | 81 | 0.054293 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_2_0_line_84 |  | 76 | 77 | 0.11886 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_2_0_line_85 |  | 77 | 78 | 0.071914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_2_0_line_86 |  | 77 | 79 | 2.3209 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
87 | MV_2_0_line_87 |  | 78 | 96 | 0.066798 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_2_0_line_88 |  | 80 | 98 | 0.18196 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_2_0_line_89 |  | 82 | 85 | 0.14876 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_2_0_line_90 |  | 82 | 84 | 0.024071 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
91 | MV_2_0_line_91 |  | 85 | 98 | 0.18124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_2_0_line_92 |  | 88 | 89 | 0.021729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_2_0_line_93 |  | 89 | 91 | 0.013057 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_2_0_line_94 |  | 92 | 93 | 0.045118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_2_0_line_95 |  | 93 | 94 | 0.057081 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_2_0_line_96 |  | 94 | 95 | 0.073483 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_2_0_line_97 |  | 95 | 96 | 0.15047 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_2_0_line_98 |  | 95 | 97 | 0.054604 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_2_0_line_99 |  | 99 | 100 | 0.31896 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_2_0_line_100 |  | 100 | 101 | 0.47883 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_2_0_line_101 |  | 101 | 102 | 0.022446 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_2_0_trafo_5 | 25 MVA 110/20 kV | 103 | 10 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2656194.4461 | 1209757.2876
1 | 2656205.1089 | 1209758.2219
2 | 2656144.2234 | 1209837.6853
3 | 2656426.8336 | 1209782.2389
4 | 2656218.3744 | 1210328.2762
5 | 2656178.2175 | 1209841.3406
6 | 2656267.2916 | 1210339.2436
7 | 2656283.5546 | 1210343.3994
8 | 2656268.6528 | 1210308.9258
9 | 2656220.577 | 1210285.6826
10 | 2655907.6373 | 1209651.7653
11 | 2656091.9285 | 1209330.936
12 | 2655901.0922 | 1209608.8451
13 | 2656478.4466 | 1210782.1696
14 | 2656603.8415 | 1210763.4684
15 | 2656456.5698 | 1210655.8647
16 | 2656991.6817 | 1211127.3106
17 | 2656808.1492 | 1210700.2936
18 | 2656612.9609 | 1210129.9867
19 | 2656839.643 | 1210724.9305
20 | 2656532.9393 | 1210711.9767
21 | 2657073.752 | 1211421.1492
22 | 2656828.6264 | 1210321.7395
23 | 2656814.3273 | 1210294.9429
24 | 2656616.394 | 1210146.2512
25 | 2656608.2516 | 1209975.8832
26 | 2656413.2277 | 1210188.2196
27 | 2656640.4753 | 1209972.1644
28 | 2656387.6452 | 1210186.6102
29 | 2656414.2132 | 1210124.9911
30 | 2656979.5838 | 1209799.288
31 | 2656916.2106 | 1209814.9929
32 | 2656665.7849 | 1209787.3274
33 | 2656638.6385 | 1209767.7248
34 | 2656057.2111 | 1209272.0748
35 | 2656319.969 | 1209533.9371
36 | 2656082.8995 | 1207690.9986
37 | 2656416.1719 | 1209547.2645
38 | 2659228.8122 | 1210418.475
39 | 2659032.5789 | 1210465.3148
40 | 2657341.1799 | 1210529.5981
41 | 2654338.3637 | 1209689.2876
42 | 2656624.5235 | 1209766.9571
43 | 2656426.3921 | 1209787.927
44 | 2657340.1609 | 1210580.2641
45 | 2657305.0509 | 1210580.1491
46 | 2657341.0045 | 1210542.0073
47 | 2656216.9131 | 1210182.5086
48 | 2656392.2578 | 1210130.3949
49 | 2656079.0694 | 1207655.1747
50 | 2655853.8905 | 1207625.2357
51 | 2655860.6179 | 1207247.6194
52 | 2655825.8934 | 1207646.4643
53 | 2655896.9871 | 1207264.3663
54 | 2655899.0566 | 1207265.4341
55 | 2656834.5298 | 1207448.5604
56 | 2655083.3933 | 1207387.25
57 | 2656836.7062 | 1207451.5717
58 | 2654855.4489 | 1207383.4562
59 | 2658734.0014 | 1206874.9636
60 | 2653014.5755 | 1209097.2918
61 | 2653209.3797 | 1209911.5731
62 | 2653523.2183 | 1209639.1502
63 | 2653730.2059 | 1209681.4233
64 | 2653397.3315 | 1209866.8357
65 | 2653544.15 | 1209622.3502
66 | 2654195.695 | 1209695.1943
67 | 2653730.2048 | 1209685.7703
68 | 2653378.2478 | 1209833.5342
69 | 2653326.3791 | 1209772.5012
70 | 2653838.7179 | 1209909.4806
71 | 2653883.4321 | 1209956.612
72 | 2653247.0571 | 1209958.2589
73 | 2653294.8256 | 1209934.1326
74 | 2652697.8029 | 1210358.0334
75 | 2652715.2433 | 1210395.1983
76 | 2652816.495 | 1210308.742
77 | 2652867.2841 | 1210416.1775
78 | 2652934.0127 | 1210412.543
79 | 2652937.6862 | 1212736.0378
80 | 2652789.8213 | 1210253.4844
81 | 2652865.6838 | 1210285.7585
82 | 2653220.7587 | 1209975.3679
83 | 2653243.6017 | 1209952.8248
84 | 2653203.9429 | 1209992.5913
85 | 2653096.4509 | 1210057.5875
86 | 2656236.7085 | 1210182.8455
87 | 2656113.1589 | 1210177.4336
88 | 2656218.1203 | 1210260.0664
89 | 2656196.395 | 1210259.6838
90 | 2656270.8664 | 1210370.1033
91 | 2656195.9985 | 1210272.7323
92 | 2653145.6127 | 1210207.4694
93 | 2653169.2763 | 1210245.8834
94 | 2653198.3909 | 1210294.9802
95 | 2653135.4713 | 1210333.2315
96 | 2652997.6458 | 1210392.228
97 | 2653106.257 | 1210287.0997
98 | 2652944.6011 | 1210157.1758
99 | 2658740.5458 | 1206876.0619
100 | 2659023.022 | 1206727.9362
101 | 2659369.6399 | 1206494.6881
102 | 2659391.3807 | 1206496.4275
103 | 2655907.6373 | 1209651.7653

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99441 | -0.22488 | 0.17322 | 0.083896
1 | 0.99441 | -0.2249 | 0 | 0
2 | 0.99307 | -0.24084 | 0 | 0
3 | 0.99581 | -0.18807 | 0 | 0
4 | 0.99077 | -0.26801 | 0 | 0
5 | 0.99306 | -0.24077 | 0.17878 | 0.086585
6 | 0.99074 | -0.26775 | 0 | 0
7 | 0.99073 | -0.26769 | 0 | 0
8 | 0.99073 | -0.26772 | 0.091659 | 0.044393
9 | 0.99066 | -0.26926 | 0.071202 | 0.034485
10 | 1 | 0 | -10.3144 | -4.6369
11 | 0.99815 | -0.10824 | 0.28236 | 0.13676
12 | 0.99978 | -0.0016783 | 0.34356 | 0.1664
13 | 0.98743 | -0.25796 | 0.14065 | 0.068121
14 | 0.98745 | -0.25816 | 0 | 0
15 | 0.9876 | -0.25834 | 0 | 0
16 | 0.98739 | -0.25834 | 0 | 0
17 | 0.98783 | -0.25908 | 0 | 0
18 | 0.98888 | -0.26571 | 0 | 0
19 | 0.98777 | -0.25947 | 0.28521 | 0.13813
20 | 0.98758 | -0.25813 | 0.1796 | 0.086982
21 | 0.98736 | -0.25813 | 0.069695 | 0.033755
22 | 0.9886 | -0.26336 | 0 | 0
23 | 0.98858 | -0.26348 | 0.32504 | 0.15743
24 | 0.98888 | -0.26569 | 0.092495 | 0.044797
25 | 0.98881 | -0.2651 | 0 | 0
26 | 0.98956 | -0.27027 | 0 | 0
27 | 0.9888 | -0.26496 | 0.29513 | 0.14294
28 | 0.98964 | -0.27078 | 0 | 0
29 | 0.98953 | -0.26996 | 0.40451 | 0.19591
30 | 0.9955 | -0.18577 | 0.22382 | 0.1084
31 | 0.99552 | -0.18594 | 0 | 0
32 | 0.99563 | -0.18679 | 0 | 0
33 | 0.99564 | -0.18667 | 0.27286 | 0.13215
34 | 0.99782 | -0.12754 | 0 | 0
35 | 0.99697 | -0.13185 | 0 | 0
36 | 0.9948 | -0.15973 | 0.14526 | 0.070355
37 | 0.99677 | -0.13285 | 0.19465 | 0.094274
38 | 0.98692 | -0.26509 | 0.11355 | 0.054993
39 | 0.98695 | -0.26534 | 0 | 0
40 | 0.98732 | -0.26212 | 0.18474 | 0.089472
41 | 0.99287 | -0.055929 | 0.28784 | 0.13941
42 | 0.99565 | -0.18674 | 0 | 0
43 | 0.99581 | -0.18805 | 0.22063 | 0.10686
44 | 0.98734 | -0.26231 | 0.061928 | 0.029993
45 | 0.98736 | -0.26248 | 0 | 0
46 | 0.98732 | -0.26216 | 0.074916 | 0.036284
47 | 0.99019 | -0.27473 | 0 | 0
48 | 0.98963 | -0.27069 | 0.12358 | 0.059851
49 | 0.99476 | -0.15956 | 0 | 0
50 | 0.99451 | -0.15841 | 0 | 0
51 | 0.99419 | -0.15739 | 0 | 0
52 | 0.9945 | -0.1583 | 0.25486 | 0.12344
53 | 0.99417 | -0.15724 | 0.22287 | 0.10794
54 | 0.99417 | -0.15724 | 0 | 0
55 | 0.99373 | -0.15504 | 0 | 0
56 | 0.99407 | -0.15749 | 0 | 0
57 | 0.99373 | -0.15503 | 0.18074 | 0.087537
58 | 0.99404 | -0.15727 | 0.09185 | 0.044485
59 | 0.99325 | -0.16048 | 0 | 0
60 | 0.98917 | -0.030178 | 0.052474 | 0.025414
61 | 0.98925 | -0.0296 | 0.051322 | 0.024856
62 | 0.99047 | -0.036988 | 0 | 0
63 | 0.99129 | -0.043566 | 0 | 0
64 | 0.98968 | -0.030512 | 0 | 0
65 | 0.99047 | -0.03703 | 0.12653 | 0.061281
66 | 0.99251 | -0.05314 | 0 | 0
67 | 0.99129 | -0.043562 | 0.07727 | 0.037424
68 | 0.98968 | -0.030452 | 0 | 0
69 | 0.98966 | -0.030307 | 0.14053 | 0.068061
70 | 0.98916 | -0.030201 | 0 | 0
71 | 0.98915 | -0.030271 | 0.087949 | 0.042596
72 | 0.98926 | -0.029534 | 0.085215 | 0.041271
73 | 0.98942 | -0.028345 | 0.13753 | 0.066608
74 | 0.98837 | -0.022318 | 0.13721 | 0.066453
75 | 0.98838 | -0.022248 | 0 | 0
76 | 0.98841 | -0.022502 | 0 | 0
77 | 0.98828 | -0.02143 | 0 | 0
78 | 0.98822 | -0.020869 | 0.17341 | 0.083987
79 | 0.98771 | -0.02534 | 0.1266 | 0.061314
80 | 0.98849 | -0.023186 | 0 | 0
81 | 0.9884 | -0.022455 | 0.074206 | 0.035939
82 | 0.98922 | -0.029132 | 0 | 0
83 | 0.98926 | -0.029526 | 0 | 0
84 | 0.98921 | -0.02916 | 0.0947 | 0.045865
85 | 0.989 | -0.02737 | 0 | 0
86 | 0.99018 | -0.27464 | 0.38837 | 0.1881
87 | 0.98999 | -0.27283 | 1.5077 | 0.73024
88 | 0.99059 | -0.27001 | 0 | 0
89 | 0.99059 | -0.26993 | 0 | 0
90 | 0.99072 | -0.26757 | 0.27735 | 0.13433
91 | 0.99058 | -0.26988 | 0.32856 | 0.15913
92 | 0.98803 | -0.019182 | 0.19318 | 0.093559
93 | 0.98804 | -0.019287 | 0.14114 | 0.068358
94 | 0.98806 | -0.019515 | 0 | 0
95 | 0.98809 | -0.0198 | 0 | 0
96 | 0.98817 | -0.020483 | 0.11481 | 0.055605
97 | 0.98809 | -0.019753 | 0.073898 | 0.03579
98 | 0.98873 | -0.025178 | 0.11662 | 0.056481
99 | 0.99325 | -0.16048 | 0.062181 | 0.030115
100 | 0.99321 | -0.16107 | 0 | 0
101 | 0.99317 | -0.16087 | 0 | 0
102 | 0.99317 | -0.16085 | 0.067409 | 0.032647
103 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.17322 | -0.083896 | 0.17322 | 0.083644 | 4.4455e-07 | -0.00025186 | 0.0055874 | 0.0055842 | 0.0055874 | 0.99441 | -0.22488 | 0.99441 | -0.2249 | 2.5397
1 | 5.219 | 2.3532 | -5.2126 | -2.3648 | 0.0063692 | -0.011527 | 0.1662 | 0.16639 | 0.16639 | 0.99441 | -0.2249 | 0.99307 | -0.24084 | 45.9638
2 | -5.3922 | -2.4369 | 5.3983 | 2.4435 | 0.0060411 | 0.0066322 | 0.17178 | 0.17177 | 0.17178 | 0.99441 | -0.2249 | 0.99581 | -0.18807 | 49.0794
3 | 5.0339 | 2.279 | -5.0232 | -2.2999 | 0.010606 | -0.020958 | 0.16063 | 0.16097 | 0.16097 | 0.99307 | -0.24084 | 0.99077 | -0.26801 | 44.4674
4 | 0.17878 | 0.085783 | -0.17878 | -0.086585 | 1.5148e-06 | -0.00080227 | 0.0057642 | 0.0057743 | 0.0057743 | 0.99307 | -0.24084 | 0.99306 | -0.24077 | 2.6247
5 | 0.22064 | 0.10672 | -0.22063 | -0.10686 | 3.8462e-07 | -0.00013498 | 0.0071049 | 0.0071066 | 0.0071066 | 0.99581 | -0.18807 | 0.99581 | -0.18805 | 3.2303
6 | -6.1157 | -2.7741 | 6.1189 | 2.7824 | 0.0031823 | 0.0082347 | 0.19467 | 0.19467 | 0.19467 | 0.99581 | -0.18807 | 0.99677 | -0.13285 | 30.182
7 | 0.4968 | 0.22388 | -0.49672 | -0.22999 | 8.6741e-05 | -0.0061098 | 0.015797 | 0.01587 | 0.01587 | 0.99581 | -0.18807 | 0.99565 | -0.18674 | 7.2138
8 | 4.6542 | 2.1246 | -4.6538 | -2.1257 | 0.00045782 | -0.0011034 | 0.14907 | 0.14909 | 0.14909 | 0.99077 | -0.26801 | 0.99066 | -0.26926 | 41.184
9 | 0.36903 | 0.17537 | -0.36902 | -0.17674 | 1.1094e-05 | -0.001369 | 0.011905 | 0.011922 | 0.011922 | 0.99077 | -0.26801 | 0.99074 | -0.26775 | 5.419
10 | 0.27736 | 0.13306 | -0.27735 | -0.13353 | 2.1508e-06 | -0.00046901 | 0.0089633 | 0.0089692 | 0.0089692 | 0.99074 | -0.26775 | 0.99073 | -0.26769 | 4.0769
11 | 0.09166 | 0.043682 | -0.091659 | -0.044393 | 3.5569e-07 | -0.00071113 | 0.0029585 | 0.0029675 | 0.0029675 | 0.99074 | -0.26775 | 0.99073 | -0.26772 | 1.3489
12 | 0.27735 | 0.13353 | -0.27735 | -0.13433 | 3.6817e-06 | -0.0008014 | 0.0089692 | 0.0089794 | 0.0089794 | 0.99073 | -0.26769 | 0.99072 | -0.26757 | 4.0815
13 | 4.5826 | 2.0912 | -4.5823 | -2.0919 | 0.00026781 | -0.00067174 | 0.14678 | 0.14679 | 0.14679 | 0.99066 | -0.26926 | 0.99059 | -0.27001 | 40.5502
14 | 7.6401 | 3.4144 | -7.6324 | -3.3942 | 0.0077085 | 0.020218 | 0.24157 | 0.24158 | 0.24158 | 1 | 0 | 0.99815 | -0.10824 | 37.4542
15 | 2.6602 | 1.212 | -2.6597 | -1.2117 | 0.00055089 | 0.00029324 | 0.084389 | 0.084389 | 0.084389 | 1 | 0 | 0.99978 | -0.0016783 | 40.1854
16 | 7.35 | 3.2574 | -7.3487 | -3.254 | 0.0013189 | 0.0034526 | 0.23251 | 0.23251 | 0.23251 | 0.99815 | -0.10824 | 0.99782 | -0.12754 | 36.0484
17 | 2.3161 | 1.0453 | -2.3011 | -1.0377 | 0.015013 | 0.0075493 | 0.073371 | 0.073393 | 0.073393 | 0.99978 | -0.0016783 | 0.99287 | -0.055929 | 34.9489
18 | -0.14065 | -0.068121 | 0.14066 | 0.065153 | 3.5248e-06 | -0.0029679 | 0.0045689 | 0.0045317 | 0.0045689 | 0.98743 | -0.25796 | 0.98745 | -0.25816 | 2.0768
19 | -0.21036 | -0.073662 | 0.21039 | 0.060615 | 3.1193e-05 | -0.013047 | 0.0065158 | 0.0063998 | 0.0065158 | 0.98745 | -0.25816 | 0.9876 | -0.25834 | 2.9617
20 | 0.069701 | 0.0085088 | -0.069697 | -0.02551 | 4.2895e-06 | -0.017001 | 0.0020528 | 0.0021699 | 0.0021699 | 0.98745 | -0.25816 | 0.98739 | -0.25834 | 0.9863
21 | 0.1796 | 0.084659 | -0.1796 | -0.086982 | 4.5124e-06 | -0.0023238 | 0.0058037 | 0.005833 | 0.005833 | 0.9876 | -0.25834 | 0.98758 | -0.25813 | 2.6514
22 | -0.38999 | -0.14527 | 0.39008 | 0.13426 | 9.2795e-05 | -0.011014 | 0.012165 | 0.012056 | 0.012165 | 0.9876 | -0.25834 | 0.98783 | -0.25908 | 5.5294
23 | 0.069697 | 0.02551 | -0.069695 | -0.033755 | 2.3185e-06 | -0.0082448 | 0.0021699 | 0.0022641 | 0.0022641 | 0.98739 | -0.25834 | 0.98736 | -0.25813 | 1.0291
24 | -1.1107 | -0.47399 | 1.1119 | 0.45693 | 0.0012357 | -0.017066 | 0.03529 | 0.035093 | 0.03529 | 0.98783 | -0.25908 | 0.98888 | -0.26571 | 16.0408
25 | 0.7206 | 0.33973 | -0.72057 | -0.33976 | 3.8616e-05 | -2.239e-05 | 0.023281 | 0.023282 | 0.023282 | 0.98783 | -0.25908 | 0.98777 | -0.25947 | 11.0866
26 | 0.092495 | 0.044409 | -0.092495 | -0.044797 | 1.9943e-07 | -0.00038808 | 0.0029952 | 0.0030001 | 0.0030001 | 0.98888 | -0.26571 | 0.98888 | -0.26569 | 1.3637
27 | 0.29516 | 0.13788 | -0.29514 | -0.142 | 2.1464e-05 | -0.0041217 | 0.0095101 | 0.0095617 | 0.0095617 | 0.98888 | -0.26571 | 0.98881 | -0.2651 | 4.3462
28 | -1.8247 | -0.78079 | 1.8261 | 0.77426 | 0.0013263 | -0.0065305 | 0.057939 | 0.05786 | 0.057939 | 0.98888 | -0.26571 | 0.98956 | -0.27027 | 26.336
29 | 0.32515 | 0.14158 | -0.32505 | -0.15739 | 9.8927e-05 | -0.015819 | 0.010353 | 0.010546 | 0.010546 | 0.98888 | -0.26571 | 0.9886 | -0.26336 | 4.7935
30 | 0.43536 | 0.20162 | -0.43519 | -0.20208 | 0.00017082 | -0.0004605 | 0.014022 | 0.014028 | 0.014028 | 0.98777 | -0.25947 | 0.98736 | -0.26248 | 6.6802
31 | 0.32505 | 0.15739 | -0.32504 | -0.15743 | 6.0186e-06 | -3.1667e-05 | 0.010546 | 0.010546 | 0.010546 | 0.9886 | -0.26336 | 0.98858 | -0.26348 | 5.022
32 | 0.29514 | 0.142 | -0.29513 | -0.14294 | 4.9268e-06 | -0.00093967 | 0.0095617 | 0.0095737 | 0.0095737 | 0.98881 | -0.2651 | 0.9888 | -0.26496 | 4.3517
33 | -2.2306 | -0.9687 | 2.2307 | 0.96815 | 0.0001717 | -0.00054669 | 0.070941 | 0.070934 | 0.070941 | 0.98956 | -0.27027 | 0.98964 | -0.27078 | 32.2461
34 | 0.40452 | 0.19444 | -0.40451 | -0.19591 | 1.4496e-05 | -0.0014744 | 0.013093 | 0.013112 | 0.013112 | 0.98956 | -0.27027 | 0.98953 | -0.26996 | 5.9599
35 | -2.3543 | -1.0267 | 2.3557 | 1.0227 | 0.0013965 | -0.003949 | 0.074921 | 0.07487 | 0.074921 | 0.98964 | -0.27078 | 0.99019 | -0.27473 | 34.055
36 | 0.12358 | 0.058525 | -0.12358 | -0.059851 | 1.2094e-06 | -0.0013257 | 0.0039885 | 0.0040053 | 0.0040053 | 0.98964 | -0.27078 | 0.98963 | -0.27069 | 1.8206
37 | -0.22382 | -0.1084 | 0.22382 | 0.10686 | 4.5232e-06 | -0.0015445 | 0.0072114 | 0.007192 | 0.0072114 | 0.9955 | -0.18577 | 0.99552 | -0.18594 | 3.2779
38 | -0.22382 | -0.10686 | 0.22385 | 0.098206 | 2.4889e-05 | -0.0086501 | 0.007192 | 0.0070874 | 0.007192 | 0.99552 | -0.18594 | 0.99563 | -0.18679 | 3.2691
39 | -0.22385 | -0.098206 | 0.22385 | 0.098168 | 2.9966e-06 | -3.7748e-05 | 0.0070874 | 0.007087 | 0.0070874 | 0.99563 | -0.18679 | 0.99564 | -0.18667 | 3.375
40 | -0.49671 | -0.23032 | 0.49672 | 0.22999 | 4.7406e-06 | -0.0003322 | 0.015874 | 0.01587 | 0.015874 | 0.99564 | -0.18667 | 0.99565 | -0.18674 | 7.2157
41 | 6.3199 | 2.8481 | -6.3148 | -2.8712 | 0.0051862 | -0.023123 | 0.20055 | 0.20086 | 0.20086 | 0.99782 | -0.12754 | 0.99697 | -0.13185 | 31.4825
42 | 1.0288 | 0.40593 | -1.0259 | -0.40599 | 0.0028861 | -6.6116e-05 | 0.031996 | 0.032016 | 0.032016 | 0.99782 | -0.12754 | 0.9948 | -0.15973 | 15.2457
43 | 6.3148 | 2.8712 | -6.3135 | -2.8766 | 0.0012237 | -0.0054378 | 0.20086 | 0.20093 | 0.20093 | 0.99697 | -0.13185 | 0.99677 | -0.13285 | 31.494
44 | 0.88062 | 0.33564 | -0.88058 | -0.33648 | 3.6077e-05 | -0.0008428 | 0.027347 | 0.027356 | 0.027356 | 0.9948 | -0.15973 | 0.99476 | -0.15956 | 12.4346
45 | -0.11355 | -0.054993 | 0.11355 | 0.050269 | 3.6349e-06 | -0.0047242 | 0.0036903 | 0.0036321 | 0.0036903 | 0.98692 | -0.26509 | 0.98695 | -0.26534 | 1.6774
46 | -0.11355 | -0.050269 | 0.11359 | 0.048324 | 3.9532e-05 | -0.0019442 | 0.0036321 | 0.0036092 | 0.0036321 | 0.98695 | -0.26534 | 0.98732 | -0.26212 | 1.7296
47 | -0.29833 | -0.1378 | 0.29833 | 0.13751 | 1.5289e-06 | -0.0002884 | 0.0096081 | 0.0096045 | 0.0096081 | 0.98732 | -0.26212 | 0.98732 | -0.26216 | 4.3673
48 | 2.0133 | 0.89831 | -2.0125 | -0.90143 | 0.0007814 | -0.0031181 | 0.064098 | 0.064138 | 0.064138 | 0.99287 | -0.055929 | 0.99251 | -0.05314 | 29.1536
49 | -0.43518 | -0.2029 | 0.43519 | 0.20208 | 9.2041e-06 | -0.00081211 | 0.014039 | 0.014028 | 0.014039 | 0.98734 | -0.26231 | 0.98736 | -0.26248 | 6.3812
50 | 0.37325 | 0.1729 | -0.37324 | -0.17379 | 7.3961e-06 | -0.00088845 | 0.012027 | 0.012038 | 0.012038 | 0.98734 | -0.26231 | 0.98732 | -0.26216 | 5.4718
51 | 1.5081 | 0.7279 | -1.5077 | -0.73024 | 0.00033072 | -0.0023332 | 0.048819 | 0.04885 | 0.04885 | 0.99019 | -0.27473 | 0.98999 | -0.27283 | 22.2045
52 | -4.2522 | -1.9383 | 4.2537 | 1.9335 | 0.0015569 | -0.0047157 | 0.13624 | 0.13617 | 0.13624 | 0.99019 | -0.27473 | 0.99059 | -0.27001 | 37.6344
53 | 0.38837 | 0.18763 | -0.38837 | -0.1881 | 4.1812e-06 | -0.00046224 | 0.012575 | 0.01258 | 0.01258 | 0.99019 | -0.27473 | 0.99018 | -0.27464 | 5.7184
54 | 0.88058 | 0.33648 | -0.88035 | -0.3418 | 0.0002283 | -0.005319 | 0.027356 | 0.027412 | 0.027412 | 0.99476 | -0.15956 | 0.99451 | -0.15841 | 12.4601
55 | 0.62549 | 0.21919 | -0.62528 | -0.22883 | 0.00020399 | -0.0096382 | 0.019238 | 0.019333 | 0.019333 | 0.99451 | -0.15841 | 0.99419 | -0.15739 | 8.7879
56 | 0.25487 | 0.12261 | -0.25486 | -0.12344 | 3.1694e-06 | -0.00082986 | 0.0082094 | 0.0082199 | 0.0082199 | 0.99451 | -0.15841 | 0.9945 | -0.1583 | 3.7363
57 | 0.091864 | 0.01286 | -0.091853 | -0.038801 | 1.1269e-05 | -0.025941 | 0.0026934 | 0.0028956 | 0.0028956 | 0.99419 | -0.15739 | 0.99407 | -0.15749 | 1.3162
58 | 0.53342 | 0.21597 | -0.53341 | -0.21692 | 1.5003e-05 | -0.00094479 | 0.01671 | 0.01672 | 0.01672 | 0.99419 | -0.15739 | 0.99417 | -0.15724 | 7.6001
59 | 0.31054 | 0.10897 | -0.31054 | -0.10903 | 2.8402e-07 | -5.4871e-05 | 0.0095561 | 0.0095566 | 0.0095566 | 0.99417 | -0.15724 | 0.99417 | -0.15724 | 4.3439
60 | 0.31054 | 0.10903 | -0.31039 | -0.13558 | 0.00014134 | -0.026547 | 0.0095566 | 0.0098395 | 0.0098395 | 0.99417 | -0.15724 | 0.99373 | -0.15504 | 4.4725
61 | 0.31039 | 0.13558 | -0.31039 | -0.13566 | 4.7981e-07 | -8.7377e-05 | 0.0098395 | 0.0098405 | 0.0098405 | 0.99373 | -0.15504 | 0.99373 | -0.15503 | 4.4729
62 | 0.091853 | 0.038801 | -0.09185 | -0.044485 | 2.7592e-06 | -0.0056842 | 0.0028956 | 0.0029637 | 0.0029637 | 0.99407 | -0.15749 | 0.99404 | -0.15727 | 1.3472
63 | 0.12965 | 0.048127 | -0.12959 | -0.050427 | 5.7363e-05 | -0.0023006 | 0.0040175 | 0.0040416 | 0.0040416 | 0.99373 | -0.15503 | 0.99325 | -0.16048 | 1.9246
64 | 0.12959 | 0.050427 | -0.12959 | -0.050583 | 1.4465e-07 | -0.00015613 | 0.0040416 | 0.0040432 | 0.0040432 | 0.99325 | -0.16048 | 0.99325 | -0.16048 | 1.8378
65 | -0.052474 | -0.025414 | 0.052478 | 0.024439 | 4.2876e-06 | -0.00097539 | 0.0017015 | 0.0016893 | 0.0017015 | 0.98917 | -0.030178 | 0.98925 | -0.0296 | 0.81025
66 | -0.1038 | -0.049295 | 0.1038 | 0.049233 | 1.0735e-06 | -6.1947e-05 | 0.0033532 | 0.0033524 | 0.0033532 | 0.98925 | -0.0296 | 0.98926 | -0.029526 | 1.5968
67 | -1.9309 | -0.88181 | 1.9326 | 0.87453 | 0.0016941 | -0.0072814 | 0.061867 | 0.061774 | 0.061867 | 0.99047 | -0.036988 | 0.99129 | -0.043566 | 28.1216
68 | 1.8044 | 0.82056 | -1.8028 | -0.82816 | 0.0015362 | -0.0076 | 0.057771 | 0.057869 | 0.057869 | 0.99047 | -0.036988 | 0.98968 | -0.030512 | 26.3041
69 | 0.12653 | 0.06125 | -0.12653 | -0.061281 | 8.0279e-07 | -3.0931e-05 | 0.0040971 | 0.0040975 | 0.0040975 | 0.99047 | -0.036988 | 0.99047 | -0.03703 | 1.9512
70 | -2.0099 | -0.91185 | 2.0125 | 0.90143 | 0.0026229 | -0.010418 | 0.064272 | 0.064138 | 0.064272 | 0.99129 | -0.043566 | 0.99251 | -0.05314 | 29.2144
71 | 0.07727 | 0.037322 | -0.07727 | -0.037424 | 3.6281e-08 | -0.000102 | 0.0024989 | 0.0025002 | 0.0025002 | 0.99129 | -0.043566 | 0.99129 | -0.043562 | 1.1365
72 | 1.6623 | 0.76305 | -1.6618 | -0.76578 | 0.00046626 | -0.0027286 | 0.053351 | 0.053386 | 0.053386 | 0.98968 | -0.030512 | 0.98942 | -0.028345 | 24.2665
73 | 0.14053 | 0.065107 | -0.14053 | -0.066004 | 1.0487e-06 | -0.00089762 | 0.0045177 | 0.0045287 | 0.0045287 | 0.98968 | -0.030512 | 0.98968 | -0.030452 | 2.0585
74 | 0.14053 | 0.066004 | -0.14053 | -0.068061 | 2.423e-06 | -0.0020571 | 0.0045287 | 0.0045546 | 0.0045546 | 0.98968 | -0.030452 | 0.98966 | -0.030307 | 2.0703
75 | 0.08795 | 0.04252 | -0.087949 | -0.042596 | 9.4113e-07 | -7.5296e-05 | 0.0028509 | 0.0028519 | 0.0028519 | 0.98916 | -0.030201 | 0.98915 | -0.030271 | 1.358
76 | -0.08795 | -0.04252 | 0.087958 | 0.041832 | 8.5707e-06 | -0.00068815 | 0.0028509 | 0.0028422 | 0.0028509 | 0.98916 | -0.030201 | 0.98926 | -0.029534 | 1.3576
77 | 1.2471 | 0.56691 | -1.247 | -0.56762 | 6.6815e-05 | -0.00071179 | 0.039975 | 0.039984 | 0.039984 | 0.98926 | -0.029534 | 0.98922 | -0.029132 | 18.1746
78 | 0.1038 | 0.049083 | -0.1038 | -0.049233 | 9.6492e-08 | -0.00015033 | 0.0033506 | 0.0033524 | 0.0033524 | 0.98926 | -0.029534 | 0.98926 | -0.029526 | 1.5238
79 | -1.5241 | -0.69909 | 1.5243 | 0.69918 | 0.00022827 | 8.045e-05 | 0.04893 | 0.048929 | 0.04893 | 0.98926 | -0.029534 | 0.98942 | -0.028345 | 23.2999
80 | -0.13721 | -0.066453 | 0.13721 | 0.066406 | 1.4501e-06 | -4.6969e-05 | 0.0044528 | 0.0044522 | 0.0044528 | 0.98837 | -0.022318 | 0.98838 | -0.022248 | 2.1204
81 | -0.13721 | -0.066406 | 0.13721 | 0.062584 | 4.2915e-06 | -0.0038227 | 0.0044522 | 0.0044047 | 0.0044522 | 0.98838 | -0.022248 | 0.98841 | -0.022502 | 2.0237
82 | -1.0348 | -0.4784 | 1.0349 | 0.477 | 9.076e-05 | -0.0014045 | 0.033295 | 0.033278 | 0.033295 | 0.98841 | -0.022502 | 0.98849 | -0.023186 | 15.1341
83 | 0.074206 | 0.034673 | -0.074206 | -0.035939 | 4.1752e-07 | -0.0012663 | 0.0023922 | 0.0024081 | 0.0024081 | 0.98841 | -0.022502 | 0.9884 | -0.022455 | 1.0946
84 | 0.82335 | 0.38114 | -0.82324 | -0.38388 | 0.00011156 | -0.0027391 | 0.026498 | 0.026532 | 0.026532 | 0.98841 | -0.022502 | 0.98828 | -0.02143 | 12.0602
85 | 0.69657 | 0.32523 | -0.69652 | -0.32689 | 4.8454e-05 | -0.0016625 | 0.022455 | 0.022476 | 0.022476 | 0.98828 | -0.02143 | 0.98822 | -0.020869 | 10.2163
86 | 0.12667 | 0.058653 | -0.1266 | -0.061314 | 6.9313e-05 | -0.0026612 | 0.0040773 | 0.0041112 | 0.0041112 | 0.98828 | -0.02143 | 0.98771 | -0.02534 | 1.9577
87 | 0.52311 | 0.2429 | -0.52308 | -0.24445 | 2.5342e-05 | -0.0015499 | 0.016848 | 0.016867 | 0.016867 | 0.98822 | -0.020869 | 0.98817 | -0.020483 | 7.6669
88 | -1.0349 | -0.477 | 1.0351 | 0.47283 | 0.00026858 | -0.0041663 | 0.033278 | 0.033226 | 0.033278 | 0.98849 | -0.023186 | 0.98873 | -0.025178 | 15.1262
89 | 1.1523 | 0.52178 | -1.1521 | -0.52518 | 0.00027093 | -0.0033944 | 0.036915 | 0.036957 | 0.036957 | 0.98922 | -0.029132 | 0.989 | -0.02737 | 16.7986
90 | 0.0947 | 0.045837 | -0.0947 | -0.045865 | 4.0433e-07 | -2.7866e-05 | 0.0030703 | 0.0030706 | 0.0030706 | 0.98922 | -0.029132 | 0.98921 | -0.02916 | 1.4622
91 | 1.1521 | 0.52518 | -1.1517 | -0.52931 | 0.00033092 | -0.0041333 | 0.036957 | 0.037008 | 0.037008 | 0.989 | -0.02737 | 0.98873 | -0.025178 | 16.8219
92 | 0.32856 | 0.15832 | -0.32856 | -0.15882 | 3.2788e-06 | -0.00050811 | 0.010628 | 0.010635 | 0.010635 | 0.99059 | -0.27001 | 0.99059 | -0.26993 | 4.834
93 | 0.32856 | 0.15882 | -0.32856 | -0.15913 | 1.9722e-06 | -0.00030532 | 0.010635 | 0.010639 | 0.010639 | 0.99059 | -0.26993 | 0.99058 | -0.26988 | 4.8358
94 | -0.19318 | -0.093559 | 0.19318 | 0.092508 | 2.3638e-06 | -0.0010509 | 0.0062712 | 0.0062579 | 0.0062712 | 0.98803 | -0.019182 | 0.98804 | -0.019287 | 2.8505
95 | -0.33432 | -0.16087 | 0.33433 | 0.15954 | 8.94e-06 | -0.0013278 | 0.01084 | 0.010823 | 0.01084 | 0.98804 | -0.019287 | 0.98806 | -0.019515 | 4.9272
96 | -0.33433 | -0.15954 | 0.33434 | 0.15783 | 1.1468e-05 | -0.0017095 | 0.010823 | 0.010802 | 0.010823 | 0.98806 | -0.019515 | 0.98809 | -0.0198 | 4.9195
97 | -0.40824 | -0.19235 | 0.40827 | 0.18885 | 3.4802e-05 | -0.0034975 | 0.013184 | 0.013141 | 0.013184 | 0.98809 | -0.0198 | 0.98817 | -0.020483 | 5.9929
98 | 0.073898 | 0.034518 | -0.073898 | -0.03579 | 4.1667e-07 | -0.0012727 | 0.0023829 | 0.0023988 | 0.0023988 | 0.98809 | -0.0198 | 0.98809 | -0.019753 | 1.0904
99 | 0.067414 | 0.020468 | -0.067411 | -0.020842 | 2.3864e-06 | -0.00037414 | 0.0020476 | 0.0020508 | 0.0020508 | 0.99325 | -0.16048 | 0.99321 | -0.16107 | 0.97658
100 | 0.067411 | 0.020842 | -0.067409 | -0.032119 | 2.8326e-06 | -0.011277 | 0.0020508 | 0.0021703 | 0.0021703 | 0.99321 | -0.16107 | 0.99317 | -0.16087 | 0.98652
101 | 0.067409 | 0.032119 | -0.067409 | -0.032647 | 1.4158e-07 | -0.00052859 | 0.0021703 | 0.002177 | 0.002177 | 0.99317 | -0.16087 | 0.99317 | -0.16085 | 0.98954

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 10.3144 | 4.6369

## res_load
| p_mw | q_mvar
0 | 0.17322 | 0.083896
1 | 0.17878 | 0.086585
2 | 0.091659 | 0.044393
3 | 0.071202 | 0.034485
4 | 0.28236 | 0.13676
5 | 0.34356 | 0.1664
6 | 0.14065 | 0.068121
7 | 0.28521 | 0.13813
8 | 0.1796 | 0.086982
9 | 0.069695 | 0.033755
10 | 0.32504 | 0.15743
11 | 0.092495 | 0.044797
12 | 0.29513 | 0.14294
13 | 0.40451 | 0.19591
14 | 0.22382 | 0.1084
15 | 0.27286 | 0.13215
16 | 0.14526 | 0.070355
17 | 0.19465 | 0.094274
18 | 0.11355 | 0.054993
19 | 0.18474 | 0.089472
20 | 0.28784 | 0.13941
21 | 0.22063 | 0.10686
22 | 0.061928 | 0.029993
23 | 0.074916 | 0.036284
24 | 0.12358 | 0.059851
25 | 0.25486 | 0.12344
26 | 0.22287 | 0.10794
27 | 0.18074 | 0.087537
28 | 0.09185 | 0.044485
29 | 0.052474 | 0.025414
30 | 0.051322 | 0.024856
31 | 0.12653 | 0.061281
32 | 0.07727 | 0.037424
33 | 0.14053 | 0.068061
34 | 0.087949 | 0.042596
35 | 0.085215 | 0.041271
36 | 0.13753 | 0.066608
37 | 0.13721 | 0.066453
38 | 0.17341 | 0.083987
39 | 0.1266 | 0.061314
40 | 0.074206 | 0.035939
41 | 0.0947 | 0.045865
42 | 0.38837 | 0.1881
43 | 1.5077 | 0.73024
44 | 0.27735 | 0.13433
45 | 0.32856 | 0.15913
46 | 0.19318 | 0.093559
47 | 0.14114 | 0.068358
48 | 0.11481 | 0.055605
49 | 0.073898 | 0.03579
50 | 0.11662 | 0.056481
51 | 0.062181 | 0.030115
52 | 0.067409 | 0.032647

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1