## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_301_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_301_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_301_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_301_0_node_4 | 20 | n |  | TRUE
4 | bus_MV_301_0_node_179 | 20 | n |  | TRUE
5 | bus_MV_301_0_node_3 | 20 | n |  | TRUE
6 | bus_MV_301_0_node_5 | 20 | n |  | TRUE
7 | bus_MV_301_0_node_6 | 20 | n |  | TRUE
8 | bus_MV_301_0_node_172 | 20 | n |  | TRUE
9 | bus_MV_301_0_node_7 | 20 | n |  | TRUE
10 | bus_MV_301_0_node_8 | 20 | n |  | TRUE
11 | bus_MV_301_0_node_9 | 20 | n |  | TRUE
12 | bus_MV_301_0_node_11 | 20 | n |  | TRUE
13 | bus_MV_301_0_node_170 | 20 | n |  | TRUE
14 | bus_MV_301_0_node_10 | 20 | n |  | TRUE
15 | bus_MV_301_0_node_13 | 20 | n |  | TRUE
16 | bus_MV_301_0_node_12 | 20 | n |  | TRUE
17 | bus_MV_301_0_node_163 | 20 | n |  | TRUE
18 | bus_MV_301_0_node_81 | 20 | n |  | TRUE
19 | bus_MV_301_0_node_169 | 20 | n |  | TRUE
20 | bus_MV_301_0_node_147 | 20 | n |  | TRUE
21 | bus_MV_301_0_node_148 | 20 | n |  | TRUE
22 | bus_MV_301_0_node_63 | 20 | n |  | TRUE
23 | bus_MV_301_0_node_149 | 20 | n |  | TRUE
24 | bus_MV_301_0_node_181 | 20 | n |  | TRUE
25 | bus_MV_301_0_node_174 | 20 | n |  | TRUE
26 | bus_MV_301_0_node_182 | 20 | n |  | TRUE
27 | bus_MV_301_0_node_173 | 20 | n |  | TRUE
28 | bus_MV_301_0_node_176 | 20 | n |  | TRUE
29 | bus_MV_301_0_node_177 | 20 | n |  | TRUE
30 | bus_MV_301_0_node_178 | 20 | n |  | TRUE
31 | bus_MV_301_0_node_70 | 20 | n |  | TRUE
32 | bus_MV_301_0_node_77 | 20 | n |  | TRUE
33 | bus_MV_301_0_node_59 | 20 | n |  | TRUE
34 | bus_MV_301_0_node_61 | 20 | n |  | TRUE
35 | bus_MV_301_0_node_62 | 20 | n |  | TRUE
36 | bus_MV_301_0_node_66 | 20 | n |  | TRUE
37 | bus_MV_301_0_node_64 | 20 | n |  | TRUE
38 | bus_MV_301_0_node_72 | 20 | n |  | TRUE
39 | bus_MV_301_0_node_65 | 20 | n |  | TRUE
40 | bus_MV_301_0_node_79 | 20 | n |  | TRUE
41 | bus_MV_301_0_node_75 | 20 | n |  | TRUE
42 | bus_MV_301_0_node_67 | 20 | n |  | TRUE
43 | bus_MV_301_0_node_68 | 20 | n |  | TRUE
44 | bus_MV_301_0_node_69 | 20 | n |  | TRUE
45 | bus_MV_301_0_node_71 | 20 | n |  | TRUE
46 | bus_MV_301_0_node_83 | 20 | n |  | TRUE
47 | bus_MV_301_0_node_84 | 20 | n |  | TRUE
48 | bus_MV_301_0_node_73 | 20 | n |  | TRUE
49 | bus_MV_301_0_node_74 | 20 | n |  | TRUE
50 | bus_MV_301_0_node_78 | 20 | n |  | TRUE
51 | bus_MV_301_0_node_76 | 20 | n |  | TRUE
52 | bus_MV_301_0_node_80 | 20 | n |  | TRUE
53 | bus_MV_301_0_node_85 | 20 | n |  | TRUE
54 | bus_HV_301_0_node_73 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_301_0_load_0 | 0 | 0.14655 | 0.070979 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_301_0_load_4 | 3 | 0.15033 | 0.072808 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_301_0_load_179 | 4 | 0.070901 | 0.034339 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_301_0_load_3 | 5 | 0.3263 | 0.15803 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_301_0_load_172 | 8 | 0.1043 | 0.050512 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_301_0_load_7 | 9 | 0.34824 | 0.16866 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_301_0_load_170 | 13 | 0.087525 | 0.04239 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_301_0_load_12 | 16 | 0.26682 | 0.12923 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_301_0_load_163 | 17 | 0.22515 | 0.10905 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_301_0_load_169 | 19 | 0.15492 | 0.07503 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_301_0_load_147 | 20 | 0.35244 | 0.1707 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_301_0_load_181 | 24 | 0.17378 | 0.084165 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_301_0_load_174 | 25 | 0.16365 | 0.07926 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_301_0_load_182 | 26 | 0.41044 | 0.19879 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_301_0_load_173 | 27 | 0.097226 | 0.047089 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_301_0_load_178 | 30 | 0.25127 | 0.1217 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_301_0_load_59 | 33 | 0.12536 | 0.060712 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_301_0_load_61 | 34 | 0.21973 | 0.10642 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_301_0_load_72 | 38 | 0.13987 | 0.067743 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_301_0_load_79 | 40 | 0.14191 | 0.06873 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_301_0_load_75 | 41 | 0.13908 | 0.06736 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_301_0_load_67 | 42 | 0.2072 | 0.10035 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_301_0_load_84 | 47 | 0.26626 | 0.12895 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_301_0_load_78 | 50 | 0.091557 | 0.044343 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_301_0_load_80 | 52 | 0.28425 | 0.13767 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_301_0_load_85 | 53 | 0.18685 | 0.090493 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 48 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_301_0_line_0 |  | 0 | 1 | 0.041712 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_301_0_line_1 |  | 0 | 2 | 0.061854 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_301_0_line_2 |  | 1 | 3 | 3.094 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_301_0_line_3 |  | 1 | 4 | 2.4819 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_301_0_line_4 |  | 2 | 5 | 1.2328 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_301_0_line_5 |  | 3 | 6 | 0.085837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_301_0_line_6 |  | 4 | 29 | 0.069567 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_301_0_line_7 |  | 6 | 7 | 0.40121 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_301_0_line_8 |  | 7 | 8 | 0.048561 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_301_0_line_9 |  | 9 | 10 | 0.014906 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_301_0_line_10 |  | 10 | 11 | 0.29778 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_301_0_line_11 |  | 10 | 12 | 1.3484 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_301_0_line_12 |  | 11 | 13 | 0.003672 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_301_0_line_13 |  | 11 | 14 | 0.41137 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_301_0_line_14 |  | 12 | 17 | 0.028699 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_301_0_line_15 |  | 12 | 18 | 0.98971 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_301_0_line_16 |  | 14 | 15 | 0.25171 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_301_0_line_17 |  | 14 | 16 | 0.1548 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_301_0_line_18 |  | 15 | 19 | 0.089819 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_301_0_line_19 |  | 18 | 46 | 1.3046 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_301_0_line_20 |  | 18 | 52 | 0.090409 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_301_0_line_21 |  | 20 | 21 | 0.025681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_301_0_line_22 |  | 21 | 22 | 0.64691 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_301_0_line_23 |  | 22 | 23 | 0.59022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_301_0_line_24 |  | 22 | 27 | 0.030444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_301_0_line_25 |  | 22 | 35 | 0.25615 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_301_0_line_26 |  | 23 | 24 | 2.2451 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_301_0_line_27 |  | 23 | 25 | 0.052113 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_301_0_line_28 |  | 23 | 26 | 0.27509 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_301_0_line_29 |  | 24 | 33 | 0.31996 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_301_0_line_30 |  | 26 | 28 | 0.040339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_301_0_line_31 |  | 28 | 29 | 0.086022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_301_0_line_32 |  | 30 | 31 | 0.032251 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_301_0_line_33 |  | 30 | 32 | 0.046605 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_301_0_line_34 |  | 31 | 43 | 0.27528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_301_0_line_35 |  | 32 | 51 | 0.77896 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_301_0_line_36 |  | 34 | 35 | 0.015234 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_301_0_line_37 |  | 35 | 36 | 0.38388 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_301_0_line_38 |  | 36 | 41 | 0.057132 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_301_0_line_39 |  | 36 | 37 | 0.17071 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
40 | MV_301_0_line_40 |  | 36 | 39 | 0.28109 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_301_0_line_41 |  | 37 | 38 | 0.086288 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
42 | MV_301_0_line_42 |  | 38 | 48 | 0.036749 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
43 | MV_301_0_line_43 |  | 39 | 40 | 0.027568 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_301_0_line_44 |  | 41 | 51 | 0.018016 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_301_0_line_45 |  | 42 | 43 | 0.075432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_301_0_line_46 |  | 42 | 44 | 0.075892 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_301_0_line_47 |  | 44 | 45 | 0.82504 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_301_0_line_48 |  | 45 | 46 | 0.46936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_301_0_line_49 |  | 45 | 47 | 0.040025 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_301_0_line_50 |  | 46 | 53 | 0.10754 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_301_0_line_51 |  | 48 | 49 | 0.18942 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_301_0_line_52 |  | 49 | 50 | 0.066303 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_301_0_trafo_73 | 25 MVA 110/20 kV | 54 | 48 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2646059.8332 | 1254946.6413
1 | 2646042.3792 | 1254908.7351
2 | 2646077.974 | 1255003.8552
3 | 2643011.8965 | 1255532.4197
4 | 2645367.9775 | 1252520.1753
5 | 2646301.8645 | 1256216.1391
6 | 2642997.1638 | 1255616.9599
7 | 2642753.6124 | 1255737.581
8 | 2642708.7548 | 1255756.1814
9 | 2648502.893 | 1251624.9453
10 | 2648517.6234 | 1251622.3974
11 | 2648694.442 | 1251560.7046
12 | 2647771.8623 | 1251476.5874
13 | 2648690.7926 | 1251561.1972
14 | 2648851.9254 | 1251676.9128
15 | 2648947.5433 | 1251874.8702
16 | 2649006.6595 | 1251681.3037
17 | 2647767.5579 | 1251504.961
18 | 2646819.7847 | 1251206.2768
19 | 2649033.8171 | 1251899.8557
20 | 2645916.7445 | 1252065.0559
21 | 2645925.7575 | 1252042.3658
22 | 2645829.1834 | 1251726.1033
23 | 2645488.3807 | 1252136.036
24 | 2643504.4843 | 1251084.9379
25 | 2645539.0138 | 1252148.3664
26 | 2645430.4443 | 1252404.9528
27 | 2645800.9143 | 1251715.0774
28 | 2645462.3403 | 1252429.7698
29 | 2645419.6078 | 1252474.8619
30 | 2645825.1266 | 1251340.1096
31 | 2645821.5015 | 1251308.1933
32 | 2645833.9975 | 1251385.6647
33 | 2643308.4348 | 1250832.077
34 | 2645993.9004 | 1251777.5099
35 | 2646008.9218 | 1251777.986
36 | 2646224.6495 | 1251638.1685
37 | 2646345.4033 | 1251730.9742
38 | 2646347.88 | 1251810.9035
39 | 2646435.8058 | 1251546.567
40 | 2646462.4609 | 1251551.0674
41 | 2646171.0698 | 1251618.394
42 | 2645909.2469 | 1251076.6925
43 | 2645900.6959 | 1251151.6327
44 | 2645915.0638 | 1251001.0306
45 | 2646167.5813 | 1250950.768
46 | 2646471.3253 | 1250814.7702
47 | 2646160.5364 | 1250989.8619
48 | 2646359.0751 | 1251845.27
49 | 2646441.7642 | 1251735.8202
50 | 2646508.1306 | 1251739.9988
51 | 2646153.8792 | 1251613.0112
52 | 2646817.3423 | 1251296.6523
53 | 2646371.8188 | 1250773.997
54 | 2646359.0751 | 1251845.27

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9918 | -0.014017 | 0.14655 | 0.070979
1 | 0.99182 | -0.014248 | 0 | 0
2 | 0.99177 | -0.01378 | 0 | 0
3 | 0.99032 | -0.027497 | 0.15033 | 0.072808
4 | 0.9953 | 0.012224 | 0.070901 | 0.034339
5 | 0.99099 | -0.018803 | 0.3263 | 0.15803
6 | 0.99031 | -0.027447 | 0 | 0
7 | 0.99026 | -0.02706 | 0 | 0
8 | 0.99025 | -0.027123 | 0.1043 | 0.050512
9 | 0.98685 | 0.041261 | 0.34824 | 0.16866
10 | 0.98685 | 0.041197 | 0 | 0
11 | 0.98666 | 0.042686 | 0 | 0
12 | 0.98833 | 0.030426 | 0 | 0
13 | 0.98666 | 0.04269 | 0.087525 | 0.04239
14 | 0.98644 | 0.044525 | 0 | 0
15 | 0.98639 | 0.044954 | 0 | 0
16 | 0.98636 | 0.044011 | 0.26682 | 0.12923
17 | 0.98832 | 0.030505 | 0.22515 | 0.10905
18 | 0.99038 | 0.04849 | 0 | 0
19 | 0.98636 | 0.044781 | 0.15492 | 0.07503
20 | 0.9971 | 0.0072862 | 0.35244 | 0.1707
21 | 0.99711 | 0.0071778 | 0 | 0
22 | 0.9974 | 0.0047787 | 0 | 0
23 | 0.99614 | 0.015312 | 0 | 0
24 | 0.99484 | 0.006794 | 0.17378 | 0.084165
25 | 0.99613 | 0.015208 | 0.16365 | 0.07926
26 | 0.9955 | 0.010628 | 0.41044 | 0.19879
27 | 0.99739 | 0.0048136 | 0.097226 | 0.047089
28 | 0.99546 | 0.010952 | 0 | 0
29 | 0.99537 | 0.011651 | 0 | 0
30 | 0.99662 | 0.006926 | 0.25127 | 0.1217
31 | 0.99654 | 0.0074479 | 0 | 0
32 | 0.99676 | 0.0060339 | 0 | 0
33 | 0.99476 | 0.006299 | 0.12536 | 0.060712
34 | 0.99808 | -0.00068927 | 0.21973 | 0.10642
35 | 0.99809 | -0.0007293 | 0 | 0
36 | 0.99923 | -0.0097849 | 0 | 0
37 | 0.99968 | -0.0041216 | 0 | 0
38 | 0.9999 | -0.0012522 | 0.13987 | 0.067743
39 | 0.99918 | -0.0093788 | 0 | 0
40 | 0.99917 | -0.0093325 | 0.14191 | 0.06873
41 | 0.99905 | -0.008675 | 0.13908 | 0.06736
42 | 0.99564 | 0.01323 | 0.2072 | 0.10035
43 | 0.99584 | 0.01197 | 0 | 0
44 | 0.99547 | 0.014318 | 0 | 0
45 | 0.99357 | 0.026731 | 0 | 0
46 | 0.99264 | 0.032789 | 0 | 0
47 | 0.99355 | 0.026859 | 0.26626 | 0.12895
48 | 1 | 0 | -5.1814 | -2.2594
49 | 0.99998 | 0.00016108 | 0 | 0
50 | 0.99997 | 0.00023036 | 0.091557 | 0.044343
51 | 0.999 | -0.0083539 | 0 | 0
52 | 0.99033 | 0.048172 | 0.28425 | 0.13767
53 | 0.9926 | 0.032542 | 0.18685 | 0.090493
54 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.47311 | -0.22627 | 0.47312 | 0.22529 | 1.2964e-05 | -0.00097583 | 0.015264 | 0.015252 | 0.015264 | 0.9918 | -0.014017 | 0.99182 | -0.014248 | 6.9383
1 | 0.32655 | 0.15529 | -0.32654 | -0.15674 | 9.1626e-06 | -0.0014499 | 0.010525 | 0.010543 | 0.010543 | 0.9918 | -0.014017 | 0.99177 | -0.01378 | 4.7922
2 | 0.25499 | 0.10846 | -0.25463 | -0.11186 | 0.00036043 | -0.0034022 | 0.0080652 | 0.0081071 | 0.0081071 | 0.99182 | -0.014248 | 0.99032 | -0.027497 | 3.8605
3 | -0.72811 | -0.33375 | 0.73051 | 0.33233 | 0.0023996 | -0.0014219 | 0.023312 | 0.023277 | 0.023312 | 0.99182 | -0.014248 | 0.9953 | 0.012224 | 11.1011
4 | 0.32654 | 0.15674 | -0.3263 | -0.15803 | 0.00024457 | -0.0012933 | 0.010543 | 0.010561 | 0.010561 | 0.99177 | -0.01378 | 0.99099 | -0.018803 | 5.0292
5 | 0.1043 | 0.039054 | -0.1043 | -0.041064 | 1.2155e-06 | -0.0020096 | 0.0032465 | 0.0032675 | 0.0032675 | 0.99032 | -0.027497 | 0.99031 | -0.027447 | 1.4852
6 | -0.80141 | -0.36667 | 0.80147 | 0.36504 | 6.0634e-05 | -0.0016275 | 0.025561 | 0.025542 | 0.025561 | 0.9953 | 0.012224 | 0.99537 | 0.011651 | 11.6188
7 | 0.1043 | 0.041064 | -0.1043 | -0.050456 | 5.9044e-06 | -0.0093924 | 0.0032675 | 0.0033775 | 0.0033775 | 0.99031 | -0.027447 | 0.99026 | -0.02706 | 1.5352
8 | 0.1043 | 0.050456 | -0.1043 | -0.050512 | 9.872e-07 | -5.623e-05 | 0.0033775 | 0.0033782 | 0.0033782 | 0.99026 | -0.02706 | 0.99025 | -0.027123 | 1.6087
9 | -0.34824 | -0.16866 | 0.34824 | 0.16832 | 2.5484e-06 | -0.00034584 | 0.011319 | 0.011314 | 0.011319 | 0.98685 | 0.041261 | 0.98685 | 0.041197 | 5.1449
10 | 0.5095 | 0.22403 | -0.5094 | -0.23092 | 0.00010591 | -0.0068914 | 0.016281 | 0.016364 | 0.016364 | 0.98685 | 0.041197 | 0.98666 | 0.042686 | 7.438
11 | -0.85775 | -0.39234 | 0.8591 | 0.36134 | 0.0013518 | -0.030998 | 0.027591 | 0.027222 | 0.027591 | 0.98685 | 0.041197 | 0.98833 | 0.030426 | 12.5414
12 | 0.087525 | 0.042305 | -0.087525 | -0.04239 | 3.9685e-08 | -8.5338e-05 | 0.0028442 | 0.0028453 | 0.0028453 | 0.98666 | 0.042686 | 0.98666 | 0.04269 | 1.2933
13 | 0.42187 | 0.18861 | -0.42177 | -0.19814 | 0.00010125 | -0.0095293 | 0.013521 | 0.013637 | 0.013637 | 0.98666 | 0.042686 | 0.98644 | 0.044525 | 6.1987
14 | 0.22516 | 0.10838 | -0.22515 | -0.10905 | 2.0433e-06 | -0.0006687 | 0.0072987 | 0.0073072 | 0.0073072 | 0.98833 | 0.030426 | 0.98832 | 0.030505 | 3.3214
15 | -1.0843 | -0.46972 | 1.0864 | 0.46988 | 0.0020997 | 0.00015868 | 0.034514 | 0.0345 | 0.034514 | 0.98833 | 0.030426 | 0.99038 | 0.04849 | 16.435
16 | 0.15493 | 0.069083 | -0.15492 | -0.074929 | 8.4e-06 | -0.0058452 | 0.0049643 | 0.0050364 | 0.0050364 | 0.98644 | 0.044525 | 0.98639 | 0.044954 | 2.2893
17 | 0.26684 | 0.12906 | -0.26682 | -0.12923 | 2.0758e-05 | -0.0001668 | 0.0086743 | 0.0086766 | 0.0086766 | 0.98644 | 0.044525 | 0.98636 | 0.044011 | 4.1317
18 | 0.15492 | 0.074929 | -0.15492 | -0.07503 | 4.0603e-06 | -0.00010178 | 0.0050364 | 0.0050377 | 0.0050377 | 0.98639 | 0.044954 | 0.98636 | 0.044781 | 2.3989
19 | -1.3706 | -0.60745 | 1.3739 | 0.57781 | 0.0032988 | -0.029644 | 0.043699 | 0.043345 | 0.043699 | 0.99038 | 0.04849 | 0.99264 | 0.032789 | 19.863
20 | 0.28426 | 0.13757 | -0.28425 | -0.13767 | 1.3651e-05 | -9.7307e-05 | 0.009205 | 0.0092064 | 0.0092064 | 0.99038 | 0.04849 | 0.99033 | 0.048172 | 4.384
21 | -0.35244 | -0.1707 | 0.35245 | 0.17009 | 4.4039e-06 | -0.00060831 | 0.011338 | 0.01133 | 0.011338 | 0.9971 | 0.0072862 | 0.99711 | 0.0071778 | 5.1534
22 | -0.35245 | -0.17009 | 0.35256 | 0.15476 | 0.00010901 | -0.015329 | 0.01133 | 0.011144 | 0.01133 | 0.99711 | 0.0071778 | 0.9974 | 0.0047787 | 5.1499
23 | 1.6782 | 0.76896 | -1.6759 | -0.78229 | 0.0022563 | -0.013332 | 0.053428 | 0.053598 | 0.053598 | 0.9974 | 0.0047787 | 0.99614 | 0.015312 | 24.3626
24 | 0.097226 | 0.046366 | -0.097226 | -0.047089 | 3.9617e-07 | -0.00072299 | 0.0031176 | 0.0031267 | 0.0031267 | 0.9974 | 0.0047787 | 0.99739 | 0.0048136 | 1.4212
25 | -2.128 | -0.97008 | 2.1295 | 0.96446 | 0.001565 | -0.0056241 | 0.067687 | 0.067614 | 0.067687 | 0.9974 | 0.0047787 | 0.99809 | -0.0007293 | 30.7669
26 | 0.29951 | 0.14208 | -0.29914 | -0.1445 | 0.00037045 | -0.0024241 | 0.0096068 | 0.00964 | 0.00964 | 0.99614 | 0.015312 | 0.99484 | 0.006794 | 4.5905
27 | 0.16365 | 0.0792 | -0.16365 | -0.07926 | 2.5779e-06 | -6.0118e-05 | 0.0052687 | 0.0052695 | 0.0052695 | 0.99614 | 0.015312 | 0.99613 | 0.015208 | 2.5093
28 | 1.2128 | 0.56101 | -1.212 | -0.56087 | 0.000735 | 0.00013472 | 0.038723 | 0.038727 | 0.038727 | 0.99614 | 0.015312 | 0.9955 | 0.010628 | 18.4415
29 | 0.12536 | 0.06034 | -0.12536 | -0.060712 | 9.3024e-06 | -0.00037218 | 0.0040372 | 0.0040419 | 0.0040419 | 0.99484 | 0.006794 | 0.99476 | 0.006299 | 1.9247
30 | 0.80158 | 0.36209 | -0.80155 | -0.36303 | 3.5049e-05 | -0.00094406 | 0.025506 | 0.025517 | 0.025517 | 0.9955 | 0.010628 | 0.99546 | 0.010952 | 11.5987
31 | 0.80155 | 0.36303 | -0.80147 | -0.36504 | 7.4846e-05 | -0.0020129 | 0.025517 | 0.025542 | 0.025542 | 0.99546 | 0.010952 | 0.99537 | 0.011651 | 11.6098
32 | 2.0419 | 0.8574 | -2.0417 | -0.85811 | 0.00017718 | -0.00071222 | 0.064146 | 0.064154 | 0.064154 | 0.99662 | 0.006926 | 0.99654 | 0.0074479 | 29.1611
33 | -2.2931 | -0.9791 | 2.2935 | 0.97809 | 0.00032448 | -0.0010091 | 0.072222 | 0.07221 | 0.072222 | 0.99662 | 0.006926 | 0.99676 | 0.0060339 | 32.8284
34 | 2.0417 | 0.85811 | -2.0402 | -0.86419 | 0.0015143 | -0.0060734 | 0.064154 | 0.064228 | 0.064228 | 0.99654 | 0.0074479 | 0.99584 | 0.01197 | 29.1945
35 | -2.2935 | -0.97809 | 2.2989 | 0.96117 | 0.0054067 | -0.016916 | 0.07221 | 0.072002 | 0.07221 | 0.99676 | 0.0060339 | 0.999 | -0.0083539 | 32.8227
36 | -0.21973 | -0.10642 | 0.21973 | 0.10606 | 1.0134e-06 | -0.00036203 | 0.0070613 | 0.0070568 | 0.0070613 | 0.99808 | -0.00068927 | 0.99809 | -0.0007293 | 3.2097
37 | -2.3493 | -1.0705 | 2.3521 | 1.0622 | 0.0028532 | -0.0082947 | 0.074669 | 0.07456 | 0.074669 | 0.99809 | -0.0007293 | 0.99923 | -0.0097849 | 33.9406
38 | 2.4385 | 1.0269 | -2.4381 | -1.0281 | 0.00044575 | -0.0012295 | 0.07644 | 0.076456 | 0.076456 | 0.99923 | -0.0097849 | 0.99905 | -0.008675 | 34.7525
39 | -4.9326 | -2.1505 | 4.9345 | 2.1461 | 0.0019917 | -0.0044027 | 0.15545 | 0.15539 | 0.15545 | 0.99923 | -0.0097849 | 0.99968 | -0.0041216 | 42.9434
40 | 0.14192 | 0.061375 | -0.14191 | -0.068073 | 7.6202e-06 | -0.0066985 | 0.004467 | 0.0045473 | 0.0045473 | 0.99923 | -0.0097849 | 0.99918 | -0.0093788 | 2.0669
41 | -4.9345 | -2.1461 | 4.9356 | 2.1439 | 0.0010061 | -0.0022278 | 0.15539 | 0.15535 | 0.15539 | 0.99968 | -0.0041216 | 0.9999 | -0.0012522 | 42.9247
42 | -5.0754 | -2.2116 | 5.0759 | 2.2107 | 0.00045342 | -0.00093109 | 0.15984 | 0.15982 | 0.15984 | 0.9999 | -0.0012522 | 1 | 0 | 44.1537
43 | 0.14191 | 0.068073 | -0.14191 | -0.06873 | 7.6239e-07 | -0.00065691 | 0.0045473 | 0.0045555 | 0.0045555 | 0.99918 | -0.0093788 | 0.99917 | -0.0093325 | 2.0707
44 | 2.299 | 0.96078 | -2.2989 | -0.96117 | 0.00012468 | -0.00039233 | 0.071997 | 0.072002 | 0.072002 | 0.99905 | -0.008675 | 0.999 | -0.0083539 | 32.728
45 | -2.0398 | -0.86585 | 2.0402 | 0.86419 | 0.00041555 | -0.0016624 | 0.064248 | 0.064228 | 0.064248 | 0.99564 | 0.01323 | 0.99584 | 0.01197 | 29.2037
46 | 1.8326 | 0.7655 | -1.8322 | -0.76719 | 0.00033605 | -0.0016962 | 0.057582 | 0.057602 | 0.057602 | 0.99564 | 0.01323 | 0.99547 | 0.014318 | 26.1829
47 | 1.8322 | 0.76719 | -1.8286 | -0.78559 | 0.0036685 | -0.018395 | 0.057602 | 0.057823 | 0.057823 | 0.99547 | 0.014318 | 0.99357 | 0.026731 | 26.2832
48 | 1.5623 | 0.65758 | -1.5608 | -0.66818 | 0.0015236 | -0.0106 | 0.049248 | 0.049374 | 0.049374 | 0.99357 | 0.026731 | 0.99264 | 0.032789 | 22.4427
49 | 0.26626 | 0.12801 | -0.26626 | -0.12895 | 3.9424e-06 | -0.0009422 | 0.0085837 | 0.0085956 | 0.0085956 | 0.99357 | 0.026731 | 0.99355 | 0.026859 | 3.9071
50 | 0.18685 | 0.090371 | -0.18685 | -0.090493 | 6.9827e-06 | -0.00012212 | 0.0060361 | 0.0060377 | 0.0060377 | 0.99264 | 0.032789 | 0.9926 | 0.032542 | 2.8751
51 | 0.09156 | 0.038239 | -0.091558 | -0.042761 | 2.1122e-06 | -0.0045219 | 0.0028644 | 0.0029172 | 0.0029172 | 1 | 0 | 0.99998 | 0.00016108 | 1.326
52 | 0.091558 | 0.042761 | -0.091557 | -0.044343 | 7.5828e-07 | -0.0015828 | 0.0029172 | 0.0029368 | 0.0029368 | 0.99998 | 0.00016108 | 0.99997 | 0.00023036 | 1.3349

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 5.1814 | 2.2594

## res_load
| p_mw | q_mvar
0 | 0.14655 | 0.070979
1 | 0.15033 | 0.072808
2 | 0.070901 | 0.034339
3 | 0.3263 | 0.15803
4 | 0.1043 | 0.050512
5 | 0.34824 | 0.16866
6 | 0.087525 | 0.04239
7 | 0.26682 | 0.12923
8 | 0.22515 | 0.10905
9 | 0.15492 | 0.07503
10 | 0.35244 | 0.1707
11 | 0.17378 | 0.084165
12 | 0.16365 | 0.07926
13 | 0.41044 | 0.19879
14 | 0.097226 | 0.047089
15 | 0.25127 | 0.1217
16 | 0.12536 | 0.060712
17 | 0.21973 | 0.10642
18 | 0.13987 | 0.067743
19 | 0.14191 | 0.06873
20 | 0.13908 | 0.06736
21 | 0.2072 | 0.10035
22 | 0.26626 | 0.12895
23 | 0.091557 | 0.044343
24 | 0.28425 | 0.13767
25 | 0.18685 | 0.090493

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1