## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_301_1_node_24 | 20 | n |  | TRUE
1 | bus_MV_301_1_node_25 | 20 | n |  | TRUE
2 | bus_MV_301_1_node_27 | 20 | n |  | TRUE
3 | bus_MV_301_1_node_28 | 20 | n |  | TRUE
4 | bus_MV_301_1_node_154 | 20 | n |  | TRUE
5 | bus_MV_301_1_node_14 | 20 | n |  | TRUE
6 | bus_MV_301_1_node_15 | 20 | n |  | TRUE
7 | bus_MV_301_1_node_16 | 20 | n |  | TRUE
8 | bus_MV_301_1_node_109 | 20 | n |  | TRUE
9 | bus_MV_301_1_node_17 | 20 | n |  | TRUE
10 | bus_MV_301_1_node_19 | 20 | n |  | TRUE
11 | bus_MV_301_1_node_123 | 20 | n |  | TRUE
12 | bus_MV_301_1_node_18 | 20 | n |  | TRUE
13 | bus_MV_301_1_node_29 | 20 | n |  | TRUE
14 | bus_MV_301_1_node_31 | 20 | n |  | TRUE
15 | bus_MV_301_1_node_30 | 20 | n |  | TRUE
16 | bus_MV_301_1_node_171 | 20 | n |  | TRUE
17 | bus_MV_301_1_node_20 | 20 | n |  | TRUE
18 | bus_MV_301_1_node_23 | 20 | n |  | TRUE
19 | bus_MV_301_1_node_130 | 20 | n |  | TRUE
20 | bus_MV_301_1_node_22 | 20 | n |  | TRUE
21 | bus_MV_301_1_node_161 | 20 | n |  | TRUE
22 | bus_MV_301_1_node_108 | 20 | n |  | TRUE
23 | bus_MV_301_1_node_126 | 20 | n |  | TRUE
24 | bus_MV_301_1_node_26 | 20 | n |  | TRUE
25 | bus_MV_301_1_node_159 | 20 | n |  | TRUE
26 | bus_MV_301_1_node_91 | 20 | n |  | TRUE
27 | bus_MV_301_1_node_122 | 20 | n |  | TRUE
28 | bus_MV_301_1_node_158 | 20 | n |  | TRUE
29 | bus_MV_301_1_node_32 | 20 | n |  | TRUE
30 | bus_MV_301_1_node_120 | 20 | n |  | TRUE
31 | bus_MV_301_1_node_38 | 20 | n |  | TRUE
32 | bus_MV_301_1_node_39 | 20 | n |  | TRUE
33 | bus_MV_301_1_node_117 | 20 | n |  | TRUE
34 | bus_MV_301_1_node_40 | 20 | n |  | TRUE
35 | bus_MV_301_1_node_116 | 20 | n |  | TRUE
36 | bus_MV_301_1_node_128 | 20 | n |  | TRUE
37 | bus_MV_301_1_node_37 | 20 | n |  | TRUE
38 | bus_MV_301_1_node_35 | 20 | n |  | TRUE
39 | bus_MV_301_1_node_127 | 20 | n |  | TRUE
40 | bus_MV_301_1_node_34 | 20 | n |  | TRUE
41 | bus_MV_301_1_node_42 | 20 | n |  | TRUE
42 | bus_MV_301_1_node_112 | 20 | n |  | TRUE
43 | bus_MV_301_1_node_41 | 20 | n |  | TRUE
44 | bus_MV_301_1_node_54 | 20 | n |  | TRUE
45 | bus_MV_301_1_node_49 | 20 | n |  | TRUE
46 | bus_MV_301_1_node_119 | 20 | n |  | TRUE
47 | bus_MV_301_1_node_115 | 20 | n |  | TRUE
48 | bus_MV_301_1_node_53 | 20 | n |  | TRUE
49 | bus_MV_301_1_node_156 | 20 | n |  | TRUE
50 | bus_MV_301_1_node_33 | 20 | n |  | TRUE
51 | bus_MV_301_1_node_36 | 20 | n |  | TRUE
52 | bus_MV_301_1_node_43 | 20 | n |  | TRUE
53 | bus_MV_301_1_node_44 | 20 | n |  | TRUE
54 | bus_MV_301_1_node_134 | 20 | n |  | TRUE
55 | bus_MV_301_1_node_162 | 20 | n |  | TRUE
56 | bus_MV_301_1_node_118 | 20 | n |  | TRUE
57 | bus_MV_301_1_node_113 | 20 | n |  | TRUE
58 | bus_MV_301_1_node_121 | 20 | n |  | TRUE
59 | bus_MV_301_1_node_52 | 20 | n |  | TRUE
60 | bus_MV_301_1_node_151 | 20 | n |  | TRUE
61 | bus_MV_301_1_node_45 | 20 | n |  | TRUE
62 | bus_MV_301_1_node_46 | 20 | n |  | TRUE
63 | bus_MV_301_1_node_56 | 20 | n |  | TRUE
64 | bus_MV_301_1_node_150 | 20 | n |  | TRUE
65 | bus_MV_301_1_node_47 | 20 | n |  | TRUE
66 | bus_MV_301_1_node_55 | 20 | n |  | TRUE
67 | bus_MV_301_1_node_166 | 20 | n |  | TRUE
68 | bus_MV_301_1_node_57 | 20 | n |  | TRUE
69 | bus_MV_301_1_node_165 | 20 | n |  | TRUE
70 | bus_MV_301_1_node_48 | 20 | n |  | TRUE
71 | bus_MV_301_1_node_95 | 20 | n |  | TRUE
72 | bus_MV_301_1_node_132 | 20 | n |  | TRUE
73 | bus_MV_301_1_node_131 | 20 | n |  | TRUE
74 | bus_MV_301_1_node_133 | 20 | n |  | TRUE
75 | bus_MV_301_1_node_99 | 20 | n |  | TRUE
76 | bus_MV_301_1_node_51 | 20 | n |  | TRUE
77 | bus_MV_301_1_node_125 | 20 | n |  | TRUE
78 | bus_MV_301_1_node_86 | 20 | n |  | TRUE
79 | bus_MV_301_1_node_87 | 20 | n |  | TRUE
80 | bus_MV_301_1_node_88 | 20 | n |  | TRUE
81 | bus_MV_301_1_node_160 | 20 | n |  | TRUE
82 | bus_MV_301_1_node_107 | 20 | n |  | TRUE
83 | bus_MV_301_1_node_106 | 20 | n |  | TRUE
84 | bus_MV_301_1_node_155 | 20 | n |  | TRUE
85 | bus_MV_301_1_node_104 | 20 | n |  | TRUE
86 | bus_MV_301_1_node_89 | 20 | n |  | TRUE
87 | bus_MV_301_1_node_90 | 20 | n |  | TRUE
88 | bus_MV_301_1_node_144 | 20 | n |  | TRUE
89 | bus_MV_301_1_node_138 | 20 | n |  | TRUE
90 | bus_MV_301_1_node_135 | 20 | n |  | TRUE
91 | bus_MV_301_1_node_139 | 20 | n |  | TRUE
92 | bus_MV_301_1_node_92 | 20 | n |  | TRUE
93 | bus_MV_301_1_node_93 | 20 | n |  | TRUE
94 | bus_MV_301_1_node_94 | 20 | n |  | TRUE
95 | bus_MV_301_1_node_146 | 20 | n |  | TRUE
96 | bus_MV_301_1_node_145 | 20 | n |  | TRUE
97 | bus_MV_301_1_node_96 | 20 | n |  | TRUE
98 | bus_MV_301_1_node_97 | 20 | n |  | TRUE
99 | bus_MV_301_1_node_98 | 20 | n |  | TRUE
100 | bus_MV_301_1_node_101 | 20 | n |  | TRUE
101 | bus_MV_301_1_node_100 | 20 | n |  | TRUE
102 | bus_MV_301_1_node_111 | 20 | n |  | TRUE
103 | bus_MV_301_1_node_102 | 20 | n |  | TRUE
104 | bus_MV_301_1_node_110 | 20 | n |  | TRUE
105 | bus_MV_301_1_node_129 | 20 | n |  | TRUE
106 | bus_MV_301_1_node_180 | 20 | n |  | TRUE
107 | bus_MV_301_1_node_164 | 20 | n |  | TRUE
108 | bus_MV_301_1_node_103 | 20 | n |  | TRUE
109 | bus_MV_301_1_node_105 | 20 | n |  | TRUE
110 | bus_MV_301_1_node_168 | 20 | n |  | TRUE
111 | bus_MV_301_1_node_157 | 20 | n |  | TRUE
112 | bus_MV_301_1_node_114 | 20 | n |  | TRUE
113 | bus_MV_301_1_node_124 | 20 | n |  | TRUE
114 | bus_MV_301_1_node_152 | 20 | n |  | TRUE
115 | bus_MV_301_1_node_141 | 20 | n |  | TRUE
116 | bus_MV_301_1_node_140 | 20 | n |  | TRUE
117 | bus_MV_301_1_node_142 | 20 | n |  | TRUE
118 | bus_MV_301_1_node_143 | 20 | n |  | TRUE
119 | bus_MV_301_1_node_167 | 20 | n |  | TRUE
120 | bus_HV_301_1_node_39 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_301_1_load_24 | 0 | 0.30859 | 0.14946 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_301_1_load_154 | 4 | 0.36918 | 0.1788 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_301_1_load_14 | 5 | 0.09338 | 0.045226 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_301_1_load_109 | 8 | 0.093503 | 0.045286 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_301_1_load_30 | 15 | 0.26699 | 0.12931 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_301_1_load_171 | 16 | 0.32596 | 0.15787 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_301_1_load_130 | 19 | 0.1802 | 0.087276 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_301_1_load_161 | 21 | 0.33301 | 0.16129 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_301_1_load_108 | 22 | 0.23936 | 0.11593 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_301_1_load_159 | 25 | 0.37413 | 0.1812 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_301_1_load_91 | 26 | 0.083292 | 0.04034 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_301_1_load_122 | 27 | 0.074418 | 0.036042 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_301_1_load_158 | 28 | 0.40333 | 0.19534 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_301_1_load_32 | 29 | 0.14194 | 0.068744 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_301_1_load_116 | 35 | 0.10666 | 0.051659 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_301_1_load_128 | 36 | 0.35475 | 0.17182 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_301_1_load_127 | 39 | 0.2984 | 0.14452 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_301_1_load_34 | 40 | 0.23998 | 0.11623 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_301_1_load_112 | 42 | 0.08298 | 0.040189 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_301_1_load_54 | 44 | 0.28127 | 0.13623 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_301_1_load_49 | 45 | 0.22496 | 0.10895 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_301_1_load_119 | 46 | 0.11449 | 0.055451 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_301_1_load_115 | 47 | 0.088238 | 0.042736 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_301_1_load_53 | 48 | 0.33857 | 0.16398 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_301_1_load_33 | 50 | 0.74924 | 0.36287 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_301_1_load_134 | 54 | 0.54842 | 0.26561 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_301_1_load_162 | 55 | 0.40894 | 0.19806 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_301_1_load_118 | 56 | 0.33922 | 0.16429 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_301_1_load_121 | 58 | 0.12263 | 0.059393 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_301_1_load_45 | 61 | 0.33819 | 0.16379 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_301_1_load_150 | 64 | 0.41416 | 0.20059 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_301_1_load_55 | 66 | 0.19642 | 0.095133 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_301_1_load_165 | 69 | 0.33849 | 0.16394 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_301_1_load_95 | 71 | 0.3313 | 0.16046 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_301_1_load_131 | 73 | 0.21646 | 0.10484 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_301_1_load_133 | 74 | 0.23847 | 0.11549 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_301_1_load_125 | 77 | 0.16406 | 0.079459 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_301_1_load_86 | 78 | 0.38324 | 0.18561 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_301_1_load_87 | 79 | 0.32572 | 0.15775 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_301_1_load_160 | 81 | 0.2559 | 0.12394 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_301_1_load_155 | 84 | 0.13298 | 0.064405 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_301_1_load_144 | 88 | 0.082788 | 0.040096 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_301_1_load_135 | 90 | 0.11297 | 0.054716 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_301_1_load_139 | 91 | 0.48085 | 0.23289 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_301_1_load_92 | 92 | 0.093184 | 0.045131 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_301_1_load_146 | 95 | 0.38221 | 0.18511 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_301_1_load_96 | 97 | 0.41935 | 0.2031 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_301_1_load_98 | 99 | 0.30955 | 0.14992 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_301_1_load_110 | 104 | 0.33217 | 0.16088 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_301_1_load_129 | 105 | 0.3593 | 0.17401 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_301_1_load_180 | 106 | 0.14116 | 0.068369 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_301_1_load_164 | 107 | 0.40008 | 0.19377 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_301_1_load_103 | 108 | 0.11076 | 0.053643 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_301_1_load_168 | 110 | 0.21921 | 0.10617 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_301_1_load_157 | 111 | 0.12672 | 0.061373 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_301_1_load_124 | 113 | 0.32877 | 0.15923 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_301_1_load_152 | 114 | 0.27151 | 0.1315 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_301_1_load_140 | 116 | 0.099519 | 0.048199 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_301_1_load_167 | 119 | 1.8582 | 0.89998 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_301_1_line_0 |  | 0 | 1 | 0.007792 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_301_1_line_1 |  | 1 | 2 | 0.75725 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_301_1_line_2 |  | 1 | 3 | 0.79687 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_301_1_line_3 |  | 2 | 4 | 0.01794 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_301_1_line_4 |  | 3 | 28 | 0.06542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_301_1_line_5 |  | 3 | 24 | 0.30485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_301_1_line_6 |  | 5 | 6 | 0.031021 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_301_1_line_7 |  | 6 | 7 | 0.33218 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_301_1_line_8 |  | 7 | 8 | 0.0011917 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
9 | MV_301_1_line_9 |  | 7 | 9 | 0.39631 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
10 | MV_301_1_line_10 |  | 8 | 23 | 0.12286 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
11 | MV_301_1_line_11 |  | 9 | 10 | 0.66465 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
12 | MV_301_1_line_12 |  | 9 | 11 | 0.059217 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_301_1_line_13 |  | 10 | 16 | 0.049406 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_301_1_line_14 |  | 10 | 12 | 0.43273 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
15 | MV_301_1_line_15 |  | 11 | 27 | 0.031421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_301_1_line_16 |  | 12 | 13 | 0.49886 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_301_1_line_17 |  | 12 | 14 | 0.21575 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_301_1_line_18 |  | 12 | 15 | 0.033406 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_301_1_line_19 |  | 13 | 26 | 0.026836 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_301_1_line_20 |  | 13 | 24 | 0.1497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_301_1_line_21 |  | 14 | 29 | 0.014208 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_301_1_line_22 |  | 17 | 18 | 0.38487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_301_1_line_23 |  | 17 | 19 | 0.022198 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_301_1_line_24 |  | 18 | 22 | 0.036967 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_301_1_line_25 |  | 18 | 20 | 0.47348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_301_1_line_26 |  | 19 | 30 | 0.13626 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_301_1_line_27 |  | 20 | 21 | 0.008474 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_301_1_line_28 |  | 23 | 77 | 0.053912 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_301_1_line_29 |  | 23 | 59 | 0.17924 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
30 | MV_301_1_line_30 |  | 24 | 25 | 0.044853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_301_1_line_31 |  | 27 | 113 | 0.047249 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_301_1_line_32 |  | 28 | 49 | 0.00974 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_301_1_line_33 |  | 29 | 50 | 0.085377 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_301_1_line_34 |  | 30 | 46 | 0.069854 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
35 | MV_301_1_line_35 |  | 30 | 58 | 0.034215 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
36 | MV_301_1_line_36 |  | 31 | 32 | 0.19881 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
37 | MV_301_1_line_37 |  | 31 | 33 | 0.12062 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_301_1_line_38 |  | 31 | 34 | 0.20149 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
39 | MV_301_1_line_39 |  | 31 | 35 | 0.039525 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_301_1_line_40 |  | 32 | 36 | 0.017285 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_301_1_line_41 |  | 32 | 37 | 0.043443 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_301_1_line_42 |  | 32 | 38 | 0.46933 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_301_1_line_43 |  | 33 | 56 | 0.028688 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_301_1_line_44 |  | 34 | 41 | 0.38796 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
45 | MV_301_1_line_45 |  | 34 | 42 | 0.020274 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
46 | MV_301_1_line_46 |  | 37 | 39 | 0.005272 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_301_1_line_47 |  | 38 | 40 | 0.006313 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_301_1_line_48 |  | 40 | 51 | 0.056505 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_301_1_line_49 |  | 41 | 45 | 0.045813 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_301_1_line_50 |  | 41 | 46 | 0.12103 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
51 | MV_301_1_line_51 |  | 41 | 43 | 0.27836 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_301_1_line_52 |  | 42 | 57 | 0.005751 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
53 | MV_301_1_line_53 |  | 43 | 44 | 0.046514 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_301_1_line_54 |  | 47 | 48 | 0.1071 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_301_1_line_55 |  | 48 | 76 | 0.004361 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_301_1_line_56 |  | 49 | 83 | 0.4562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_301_1_line_57 |  | 51 | 52 | 0.38942 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_301_1_line_58 |  | 52 | 53 | 0.23493 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_301_1_line_59 |  | 52 | 54 | 0.074037 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_301_1_line_60 |  | 53 | 55 | 0.037756 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_301_1_line_61 |  | 54 | 60 | 0.11732 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_301_1_line_62 |  | 57 | 112 | 0.10369 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
63 | MV_301_1_line_63 |  | 58 | 59 | 0.041976 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
64 | MV_301_1_line_64 |  | 59 | 76 | 0.11415 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_301_1_line_65 |  | 60 | 114 | 0.015897 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_301_1_line_66 |  | 61 | 62 | 0.063555 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
67 | MV_301_1_line_67 |  | 61 | 63 | 0.45728 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
68 | MV_301_1_line_68 |  | 61 | 64 | 0.39443 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
69 | MV_301_1_line_69 |  | 62 | 65 | 0.26032 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
70 | MV_301_1_line_70 |  | 63 | 68 | 0.97109 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_301_1_line_71 |  | 63 | 66 | 0.001941 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_301_1_line_72 |  | 65 | 70 | 0.23531 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
73 | MV_301_1_line_73 |  | 65 | 71 | 0.038421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_301_1_line_74 |  | 66 | 67 | 0.45528 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_301_1_line_75 |  | 67 | 69 | 0.01854 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_301_1_line_76 |  | 68 | 78 | 0.03643 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_301_1_line_77 |  | 70 | 72 | 0.011062 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_301_1_line_78 |  | 70 | 73 | 0.027005 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
79 | MV_301_1_line_79 |  | 72 | 74 | 0.007572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_301_1_line_80 |  | 73 | 75 | 0.027554 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
81 | MV_301_1_line_81 |  | 75 | 98 | 0.039962 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
82 | MV_301_1_line_82 |  | 78 | 79 | 0.34445 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_301_1_line_83 |  | 79 | 80 | 0.018629 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_301_1_line_84 |  | 80 | 86 | 0.026682 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_301_1_line_85 |  | 81 | 82 | 0.021514 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
86 | MV_301_1_line_86 |  | 82 | 96 | 0.57837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_301_1_line_87 |  | 82 | 83 | 0.19324 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_301_1_line_88 |  | 83 | 84 | 0.022992 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_301_1_line_89 |  | 83 | 85 | 0.2319 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_301_1_line_90 |  | 84 | 111 | 0.040834 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_301_1_line_91 |  | 85 | 109 | 0.11444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_301_1_line_92 |  | 85 | 108 | 0.037234 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_301_1_line_93 |  | 86 | 87 | 0.083421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_301_1_line_94 |  | 86 | 88 | 0.028372 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_301_1_line_95 |  | 87 | 89 | 0.01712 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_301_1_line_96 |  | 87 | 90 | 0.034431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_301_1_line_97 |  | 89 | 91 | 0.054064 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_301_1_line_98 |  | 91 | 115 | 0.00282 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_301_1_line_99 |  | 92 | 93 | 0.052832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_301_1_line_100 |  | 93 | 94 | 0.091093 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_301_1_line_101 |  | 94 | 95 | 0.058239 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
102 | MV_301_1_line_102 |  | 95 | 96 | 0.020033 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_301_1_line_103 |  | 97 | 98 | 0.0045988 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_301_1_line_104 |  | 97 | 99 | 0.027944 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_301_1_line_105 |  | 98 | 100 | 0.088148 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
106 | MV_301_1_line_106 |  | 100 | 105 | 0.0085735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_301_1_line_107 |  | 100 | 101 | 0.10416 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
108 | MV_301_1_line_108 |  | 101 | 102 | 0.35939 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
109 | MV_301_1_line_109 |  | 101 | 103 | 0.076144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_301_1_line_110 |  | 101 | 104 | 0.060214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_301_1_line_111 |  | 102 | 107 | 0.022977 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
112 | MV_301_1_line_112 |  | 103 | 106 | 0.00276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_301_1_line_113 |  | 107 | 112 | 0.018505 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
114 | MV_301_1_line_114 |  | 109 | 110 | 0.022563 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
115 | MV_301_1_line_115 |  | 115 | 116 | 0.0020273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_301_1_line_116 |  | 116 | 117 | 0.042289 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_301_1_line_117 |  | 117 | 118 | 0.16527 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_301_1_line_118 |  | 118 | 119 | 0.065276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_301_1_trafo_39 | 25 MVA 110/20 kV | 120 | 32 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2647011.508 | 1250480.823
1 | 2647019.2442 | 1250481.9295
2 | 2647355.6474 | 1250027.9647
3 | 2646831.1659 | 1250097.2364
4 | 2647372.7471 | 1250033.5495
5 | 2646555.4686 | 1249523.5673
6 | 2646524.3591 | 1249523.1118
7 | 2646477.6232 | 1249257.5664
8 | 2646478.0644 | 1249256.4594
9 | 2646727.7799 | 1249396.1806
10 | 2647128.2962 | 1249571.8454
11 | 2646766.1579 | 1249351.0748
12 | 2647104.0621 | 1249825.4022
13 | 2646987.6688 | 1249978.0712
14 | 2647245.2022 | 1249757.9345
15 | 2647135.2965 | 1249837.4918
16 | 2647133.8883 | 1249522.7567
17 | 2646394.5222 | 1249217.4444
18 | 2646333.2532 | 1249239.4693
19 | 2646414.937 | 1249220.7806
20 | 2646436.266 | 1249369.9627
21 | 2646439.1145 | 1249361.9797
22 | 2646367.3091 | 1249253.8452
23 | 2646557.8321 | 1249163.0094
24 | 2647029.3464 | 1250090.6333
25 | 2647070.1064 | 1250108.4464
26 | 2646961.0331 | 1249975.3805
27 | 2646792.279 | 1249363.6124
28 | 2646816.7714 | 1250161.0549
29 | 2647258.4863 | 1249763.0772
30 | 2646494.4763 | 1249110.1435
31 | 2646833.3978 | 1249238.4849
32 | 2646869.1817 | 1249198.9297
33 | 2646925.7111 | 1249304.7813
34 | 2646767.1754 | 1249143.6096
35 | 2646799.5295 | 1249218.1089
36 | 2646853.3482 | 1249205.8641
37 | 2646889.7752 | 1249229.9578
38 | 2647117.3758 | 1249022.2321
39 | 2646884.8941 | 1249231.9503
40 | 2647123.2685 | 1249019.9218
41 | 2646605.8042 | 1249002.0109
42 | 2646760.4503 | 1249124.4837
43 | 2646538.5358 | 1248743.3087
44 | 2646496.9242 | 1248764.3188
45 | 2646560.3857 | 1249008.0139
46 | 2646555.2844 | 1249111.9891
47 | 2646406.5442 | 1248914.8503
48 | 2646399.5423 | 1249021.7185
49 | 2646815.1555 | 1250170.6597
50 | 2647338.0971 | 1249793.9206
51 | 2647176.3101 | 1249000.13
52 | 2647270.3411 | 1249241.1411
53 | 2647360.9934 | 1249030.8556
54 | 2647337.4727 | 1249272.3639
55 | 2647374.4042 | 1248995.7612
56 | 2646938.8715 | 1249279.291
57 | 2646758.5426 | 1249119.0583
58 | 2646489.5774 | 1249076.2823
59 | 2646448.3113 | 1249084.3423
60 | 2647440.4282 | 1249328.6246
61 | 2646700.645 | 1248650.4423
62 | 2646764.162 | 1248652.6329
63 | 2646715.6251 | 1248193.4086
64 | 2646430.8045 | 1248362.7644
65 | 2646893.8305 | 1248779.2861
66 | 2646714.0712 | 1248192.24
67 | 2646599.2148 | 1247751.6858
68 | 2647034.0185 | 1248267.318
69 | 2646599.7153 | 1247733.1551
70 | 2646838.9976 | 1248880.4211
71 | 2646929.2018 | 1248765.072
72 | 2646836.549 | 1248891.209
73 | 2646865.6068 | 1248885.0292
74 | 2646829.0532 | 1248889.9934
75 | 2646892.7529 | 1248889.752
76 | 2646395.2182 | 1249022.374
77 | 2646600.5897 | 1249193.9085
78 | 2647050.0398 | 1248300.056
79 | 2647196.7449 | 1248611.6969
80 | 2647181.416 | 1248622.2827
81 | 2646577.6109 | 1249929.2374
82 | 2646586.3496 | 1249948.8971
83 | 2646685.2149 | 1250077.4836
84 | 2646706.6866 | 1250085.8694
85 | 2646725.0647 | 1249862.2963
86 | 2647201.951 | 1248629.4064
87 | 2647242.9819 | 1248689.2955
88 | 2647225.9576 | 1248644.28
89 | 2647226.1903 | 1248692.8642
90 | 2647265.4236 | 1248667.8445
91 | 2647192.7741 | 1248733.1032
92 | 2646659.6519 | 1249752.3281
93 | 2646670.0946 | 1249700.5431
94 | 2646613.1878 | 1249752.0527
95 | 2646554.9582 | 1249751.028
96 | 2646547.226 | 1249769.4687
97 | 2646885.1471 | 1248860.7192
98 | 2646889.7004 | 1248861.3643
99 | 2646857.4794 | 1248856.7993
100 | 2646945.4858 | 1248839.3795
101 | 2646942.994 | 1248928.064
102 | 2646811.5307 | 1249063.6944
103 | 2646914.8171 | 1248919.2018
104 | 2647001.1755 | 1248936.1857
105 | 2646944.7832 | 1248830.8349
106 | 2646914.2898 | 1248921.9106
107 | 2646789.8152 | 1249071.3838
108 | 2646723.2297 | 1249899.3892
109 | 2646782.4327 | 1249849.9067
110 | 2646793.4444 | 1249830.2136
111 | 2646743.1902 | 1250067.5681
112 | 2646772.3248 | 1249077.5723
113 | 2646789.9148 | 1249410.8024
114 | 2647435.8194 | 1249343.1754
115 | 2647191.1699 | 1248735.4253
116 | 2647189.9429 | 1248737.0392
117 | 2647164.3478 | 1248770.7025
118 | 2647128.8609 | 1248859.7249
119 | 2647083.789 | 1248819.9625
120 | 2646869.1817 | 1249198.9297

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99018 | -0.073424 | 0.30859 | 0.14946
1 | 0.99019 | -0.073453 | 0 | 0
2 | 0.98983 | -0.070498 | 0 | 0
3 | 0.99087 | -0.078608 | 0 | 0
4 | 0.98982 | -0.070417 | 0.36918 | 0.1788
5 | 0.99701 | -0.066338 | 0.09338 | 0.045226
6 | 0.99702 | -0.066373 | 0 | 0
7 | 0.99705 | -0.066646 | 0 | 0
8 | 0.99706 | -0.066622 | 0.093503 | 0.045286
9 | 0.99665 | -0.074442 | 0 | 0
10 | 0.99509 | -0.092963 | 0 | 0
11 | 0.99662 | -0.07416 | 0 | 0
12 | 0.99415 | -0.10407 | 0 | 0
13 | 0.99233 | -0.089994 | 0 | 0
14 | 0.9939 | -0.10181 | 0 | 0
15 | 0.99414 | -0.10396 | 0.26699 | 0.12931
16 | 0.99506 | -0.09316 | 0.32596 | 0.15787
17 | 0.99743 | -0.051979 | 0 | 0
18 | 0.99715 | -0.049746 | 0 | 0
19 | 0.99745 | -0.052101 | 0.1802 | 0.087276
20 | 0.99695 | -0.048025 | 0 | 0
21 | 0.99695 | -0.047991 | 0.33301 | 0.16129
22 | 0.99714 | -0.04964 | 0.23936 | 0.11593
23 | 0.99735 | -0.056176 | 0 | 0
24 | 0.9918 | -0.085832 | 0 | 0
25 | 0.99178 | -0.08563 | 0.37413 | 0.1812
26 | 0.99233 | -0.089967 | 0.083292 | 0.04034
27 | 0.9966 | -0.074008 | 0.074418 | 0.036042
28 | 0.99073 | -0.077421 | 0.40333 | 0.19534
29 | 0.99389 | -0.10165 | 0.14194 | 0.068744
30 | 0.99764 | -0.050598 | 0 | 0
31 | 0.99935 | -0.012058 | 0 | 0
32 | 1 | 0 | -17.1585 | -7.8507
33 | 0.9993 | -0.011585 | 0 | 0
34 | 0.99872 | -0.02392 | 0 | 0
35 | 0.99935 | -0.012009 | 0.10666 | 0.051659
36 | 0.99999 | 7.3136e-05 | 0.35475 | 0.17182
37 | 0.99998 | 0.00015331 | 0 | 0
38 | 0.99913 | 0.0075023 | 0 | 0
39 | 0.99998 | 0.00017211 | 0.2984 | 0.14452
40 | 0.99911 | 0.0076056 | 0.23998 | 0.11623
41 | 0.99813 | -0.035209 | 0 | 0
42 | 0.99869 | -0.02452 | 0.08298 | 0.040189
43 | 0.99803 | -0.034347 | 0 | 0
44 | 0.99801 | -0.034192 | 0.28127 | 0.13623
45 | 0.99811 | -0.035334 | 0.22496 | 0.10895
46 | 0.99774 | -0.048742 | 0.11449 | 0.055451
47 | 0.99747 | -0.051884 | 0.088238 | 0.042736
48 | 0.99749 | -0.051769 | 0.33857 | 0.16398
49 | 0.99071 | -0.077291 | 0 | 0
50 | 0.99381 | -0.10089 | 0.74924 | 0.36287
51 | 0.99903 | 0.0083704 | 0 | 0
52 | 0.99842 | 0.013777 | 0 | 0
53 | 0.9983 | 0.014875 | 0 | 0
54 | 0.99834 | 0.014499 | 0.54842 | 0.26561
55 | 0.99828 | 0.015059 | 0.40894 | 0.19806
56 | 0.99929 | -0.011469 | 0.33922 | 0.16429
57 | 0.99868 | -0.024689 | 0 | 0
58 | 0.9976 | -0.051401 | 0.12263 | 0.059393
59 | 0.99755 | -0.052366 | 0 | 0
60 | 0.99828 | 0.014108 | 0 | 0
61 | 0.99624 | -0.066007 | 0.33819 | 0.16379
62 | 0.99659 | -0.057277 | 0 | 0
63 | 0.99412 | -0.11892 | 0 | 0
64 | 0.99592 | -0.068005 | 0.41416 | 0.20059
65 | 0.99725 | -0.050203 | 0 | 0
66 | 0.99412 | -0.11891 | 0.19642 | 0.095133
67 | 0.99382 | -0.12082 | 0 | 0
68 | 0.98995 | -0.080918 | 0 | 0
69 | 0.99381 | -0.12074 | 0.33849 | 0.16394
70 | 0.99751 | -0.045611 | 0 | 0
71 | 0.99724 | -0.050051 | 0.3313 | 0.16046
72 | 0.99751 | -0.04558 | 0 | 0
73 | 0.99754 | -0.045058 | 0.21646 | 0.10484
74 | 0.99751 | -0.045558 | 0.23847 | 0.11549
75 | 0.99757 | -0.044469 | 0 | 0
76 | 0.99749 | -0.051791 | 0 | 0
77 | 0.99734 | -0.056072 | 0.16406 | 0.079459
78 | 0.98979 | -0.079458 | 0.38324 | 0.18561
79 | 0.98779 | -0.092473 | 0.32572 | 0.15775
80 | 0.98773 | -0.091886 | 0 | 0
81 | 0.98975 | -0.069651 | 0.2559 | 0.12394
82 | 0.98976 | -0.069583 | 0 | 0
83 | 0.98994 | -0.071061 | 0 | 0
84 | 0.98994 | -0.07099 | 0.13298 | 0.064405
85 | 0.98984 | -0.070221 | 0 | 0
86 | 0.98764 | -0.091045 | 0 | 0
87 | 0.98737 | -0.088488 | 0 | 0
88 | 0.98764 | -0.091017 | 0.082788 | 0.040096
89 | 0.98731 | -0.087984 | 0 | 0
90 | 0.98736 | -0.088441 | 0.11297 | 0.054716
91 | 0.98714 | -0.086391 | 0.48085 | 0.23289
92 | 0.98937 | -0.066449 | 0.093184 | 0.045131
93 | 0.98938 | -0.066507 | 0 | 0
94 | 0.98939 | -0.066598 | 0 | 0
95 | 0.9894 | -0.066513 | 0.38221 | 0.18511
96 | 0.98941 | -0.066625 | 0 | 0
97 | 0.99762 | -0.043575 | 0.41935 | 0.2031
98 | 0.99762 | -0.043615 | 0 | 0
99 | 0.99761 | -0.043472 | 0.30955 | 0.14992
100 | 0.99774 | -0.041483 | 0 | 0
101 | 0.99789 | -0.038814 | 0 | 0
102 | 0.99844 | -0.0289 | 0 | 0
103 | 0.99788 | -0.03869 | 0 | 0
104 | 0.99787 | -0.038577 | 0.33217 | 0.16088
105 | 0.99774 | -0.041446 | 0.3593 | 0.17401
106 | 0.99788 | -0.038685 | 0.14116 | 0.068369
107 | 0.99848 | -0.028264 | 0.40008 | 0.19377
108 | 0.98984 | -0.070172 | 0.11076 | 0.053643
109 | 0.98981 | -0.069925 | 0 | 0
110 | 0.9898 | -0.069986 | 0.21921 | 0.10617
111 | 0.98993 | -0.070928 | 0.12672 | 0.061373
112 | 0.99851 | -0.027723 | 0 | 0
113 | 0.99657 | -0.074197 | 0.32877 | 0.15923
114 | 0.99827 | 0.01416 | 0.27151 | 0.1315
115 | 0.98714 | -0.086324 | 0 | 0
116 | 0.98713 | -0.086276 | 0.099519 | 0.048199
117 | 0.98703 | -0.085328 | 0 | 0
118 | 0.98663 | -0.081592 | 0 | 0
119 | 0.98648 | -0.080104 | 1.8582 | 0.89998
120 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.30859 | -0.14946 | 0.30859 | 0.14928 | 1.0392e-06 | -0.0001821 | 0.0099962 | 0.0099939 | 0.0099962 | 0.99018 | -0.073424 | 0.99019 | -0.073453 | 4.5437
1 | 0.36932 | 0.1607 | -0.36918 | -0.17838 | 0.0001419 | -0.017678 | 0.011742 | 0.011958 | 0.011958 | 0.99019 | -0.073453 | 0.98983 | -0.070498 | 5.4354
2 | -0.67791 | -0.30998 | 0.67841 | 0.29146 | 0.00049726 | -0.01852 | 0.021732 | 0.021511 | 0.021732 | 0.99019 | -0.073453 | 0.99087 | -0.078608 | 9.8781
3 | 0.36918 | 0.17838 | -0.36918 | -0.1788 | 3.4261e-06 | -0.00041865 | 0.011958 | 0.011963 | 0.011963 | 0.98983 | -0.070498 | 0.98982 | -0.070417 | 5.4378
4 | 1.7261 | 0.79073 | -1.7258 | -0.79219 | 0.00026728 | -0.0014541 | 0.055312 | 0.05533 | 0.05533 | 0.99087 | -0.078608 | 0.99073 | -0.077421 | 25.1501
5 | -2.4045 | -1.0822 | 2.4069 | 1.0757 | 0.0023989 | -0.0064415 | 0.076818 | 0.076733 | 0.076818 | 0.99087 | -0.078608 | 0.9918 | -0.085832 | 34.9175
6 | -0.09338 | -0.045226 | 0.09338 | 0.04449 | 3.726e-07 | -0.00073613 | 0.0030041 | 0.0029949 | 0.0030041 | 0.99701 | -0.066338 | 0.99702 | -0.066373 | 1.3655
7 | -0.09338 | -0.04449 | 0.093384 | 0.036607 | 3.853e-06 | -0.0078831 | 0.0029949 | 0.002904 | 0.0029949 | 0.99702 | -0.066373 | 0.99705 | -0.066646 | 1.3613
8 | -4.8638 | -2.1639 | 4.8638 | 2.1638 | 5.1805e-06 | -8.5755e-05 | 0.15413 | 0.15413 | 0.15413 | 0.99705 | -0.066646 | 0.99706 | -0.066622 | 18.305
9 | 4.7704 | 2.1273 | -4.7687 | -2.1558 | 0.0016625 | -0.028563 | 0.15123 | 0.15158 | 0.15158 | 0.99705 | -0.066646 | 0.99665 | -0.074442 | 18.0028
10 | -4.9573 | -2.2091 | 4.9584 | 2.2103 | 0.0010812 | 0.001249 | 0.15713 | 0.15713 | 0.15713 | 0.99706 | -0.066622 | 0.99735 | -0.056176 | 19.1626
11 | 4.3655 | 1.9628 | -4.3593 | -1.9809 | 0.0061823 | -0.018121 | 0.13864 | 0.13891 | 0.13891 | 0.99665 | -0.074442 | 0.99509 | -0.092963 | 38.3725
12 | 0.40322 | 0.19308 | -0.4032 | -0.19448 | 1.3273e-05 | -0.0014004 | 0.012949 | 0.012967 | 0.012967 | 0.99665 | -0.074442 | 0.99662 | -0.07416 | 5.8939
13 | 0.32597 | 0.15782 | -0.32596 | -0.15787 | 9.7177e-06 | -5.2315e-05 | 0.010506 | 0.010507 | 0.010507 | 0.99509 | -0.092963 | 0.99506 | -0.09316 | 5.0034
14 | 4.0334 | 1.8231 | -4.0299 | -1.8352 | 0.0034508 | -0.012178 | 0.12841 | 0.12858 | 0.12858 | 0.99509 | -0.092963 | 0.99415 | -0.10407 | 35.5197
15 | 0.4032 | 0.19448 | -0.40319 | -0.19522 | 7.0577e-06 | -0.00074304 | 0.012967 | 0.012976 | 0.012976 | 0.99662 | -0.07416 | 0.9966 | -0.074008 | 5.8981
16 | 2.8714 | 1.2825 | -2.8659 | -1.2926 | 0.0055619 | -0.010101 | 0.091317 | 0.091457 | 0.091457 | 0.99415 | -0.10407 | 0.99233 | -0.089994 | 41.5713
17 | 0.8915 | 0.42427 | -0.89126 | -0.42929 | 0.00023725 | -0.0050195 | 0.028669 | 0.028733 | 0.028733 | 0.99415 | -0.10407 | 0.9939 | -0.10181 | 13.0603
18 | 0.26699 | 0.12852 | -0.26699 | -0.12931 | 3.3054e-06 | -0.00078731 | 0.0086041 | 0.0086141 | 0.0086141 | 0.99415 | -0.10407 | 0.99414 | -0.10396 | 3.9155
19 | 0.083293 | 0.039709 | -0.083292 | -0.04034 | 2.5891e-07 | -0.00063088 | 0.0026843 | 0.0026922 | 0.0026922 | 0.99233 | -0.089994 | 0.99233 | -0.089967 | 1.2237
20 | 2.7826 | 1.2528 | -2.781 | -1.2559 | 0.0015757 | -0.0030505 | 0.088773 | 0.088815 | 0.088815 | 0.99233 | -0.089994 | 0.9918 | -0.085832 | 40.3705
21 | 0.89126 | 0.42929 | -0.89125 | -0.42962 | 1.5661e-05 | -0.00033046 | 0.028733 | 0.028737 | 0.028737 | 0.9939 | -0.10181 | 0.99389 | -0.10165 | 13.0623
22 | 0.57262 | 0.25583 | -0.57245 | -0.26492 | 0.0001703 | -0.009089 | 0.018151 | 0.018261 | 0.018261 | 0.99743 | -0.051979 | 0.99715 | -0.049746 | 8.3005
23 | -0.57262 | -0.25583 | 0.57263 | 0.25531 | 9.7606e-06 | -0.0005244 | 0.018151 | 0.018145 | 0.018151 | 0.99743 | -0.051979 | 0.99745 | -0.052101 | 8.2507
24 | 0.23936 | 0.11505 | -0.23936 | -0.11593 | 2.9214e-06 | -0.00087673 | 0.0076885 | 0.0076995 | 0.0076995 | 0.99715 | -0.049746 | 0.99714 | -0.04964 | 3.4998
25 | 0.33309 | 0.14987 | -0.33302 | -0.16109 | 7.1583e-05 | -0.011217 | 0.010574 | 0.010712 | 0.010712 | 0.99715 | -0.049746 | 0.99695 | -0.048025 | 4.8689
26 | -0.75283 | -0.34258 | 0.75297 | 0.34251 | 0.0001391 | -7.4741e-05 | 0.023938 | 0.023936 | 0.023938 | 0.99745 | -0.052101 | 0.99764 | -0.050598 | 11.399
27 | 0.33302 | 0.16109 | -0.33301 | -0.16129 | 1.2983e-06 | -0.00020071 | 0.010712 | 0.010714 | 0.010714 | 0.99695 | -0.048025 | 0.99695 | -0.047991 | 4.8701
28 | 0.16407 | 0.07818 | -0.16406 | -0.079459 | 1.9976e-06 | -0.0012798 | 0.0052603 | 0.0052764 | 0.0052764 | 0.99735 | -0.056176 | 0.99734 | -0.056072 | 2.3983
29 | -5.1224 | -2.2885 | 5.1233 | 2.2757 | 0.0008641 | -0.012831 | 0.16239 | 0.16223 | 0.16239 | 0.99735 | -0.056176 | 0.99755 | -0.052366 | 19.286
30 | 0.37414 | 0.18015 | -0.37413 | -0.1812 | 8.7565e-06 | -0.0010508 | 0.012086 | 0.0121 | 0.0121 | 0.9918 | -0.085832 | 0.99178 | -0.08563 | 5.4998
31 | 0.32878 | 0.15918 | -0.32877 | -0.15923 | 9.4253e-06 | -5.0118e-05 | 0.010581 | 0.010582 | 0.010582 | 0.9966 | -0.074008 | 0.99657 | -0.074197 | 5.0388
32 | 1.3225 | 0.59685 | -1.3224 | -0.59707 | 2.3241e-05 | -0.00022136 | 0.042276 | 0.042279 | 0.042279 | 0.99073 | -0.077421 | 0.99071 | -0.077291 | 19.2176
33 | 0.74931 | 0.36088 | -0.74924 | -0.36287 | 6.6579e-05 | -0.0019937 | 0.024156 | 0.024182 | 0.024182 | 0.99389 | -0.10165 | 0.99381 | -0.10089 | 10.9917
34 | -6.4262 | -2.876 | 6.4267 | 2.8712 | 0.00053036 | -0.0048256 | 0.20372 | 0.20366 | 0.20372 | 0.99764 | -0.050598 | 0.99774 | -0.048742 | 24.1946
35 | 5.6732 | 2.5335 | -5.673 | -2.5359 | 0.00020241 | -0.0024159 | 0.17978 | 0.17981 | 0.17981 | 0.99764 | -0.050598 | 0.9976 | -0.051401 | 21.3556
36 | -15.0118 | -6.8516 | 15.02 | 6.844 | 0.008263 | -0.007594 | 0.47666 | 0.47648 | 0.47666 | 0.99935 | -0.012058 | 1 | 0 | 56.6109
37 | 0.33925 | 0.16074 | -0.33923 | -0.16361 | 1.8997e-05 | -0.0028703 | 0.010844 | 0.01088 | 0.01088 | 0.99935 | -0.012058 | 0.9993 | -0.011585 | 4.9453
38 | 14.5659 | 6.6402 | -14.558 | -6.6483 | 0.0078875 | -0.0081242 | 0.46241 | 0.46259 | 0.46259 | 0.99935 | -0.012058 | 0.99872 | -0.02392 | 54.9399
39 | 0.10666 | 0.050716 | -0.10666 | -0.051659 | 6.1628e-07 | -0.0009423 | 0.0034116 | 0.0034234 | 0.0034234 | 0.99935 | -0.012058 | 0.99935 | -0.012009 | 1.5561
40 | 0.35476 | 0.1714 | -0.35475 | -0.17182 | 2.9865e-06 | -0.00041182 | 0.011374 | 0.011379 | 0.011379 | 1 | 0 | 0.99999 | 7.3136e-05 | 5.1722
41 | 0.2984 | 0.14336 | -0.2984 | -0.14439 | 5.304e-06 | -0.0010357 | 0.0095566 | 0.0095696 | 0.0095696 | 1 | 0 | 0.99998 | 0.00015331 | 4.3498
42 | 1.4713 | 0.68139 | -1.4699 | -0.69218 | 0.0013767 | -0.010787 | 0.046807 | 0.046944 | 0.046944 | 1 | 0 | 0.99913 | 0.0075023 | 21.338
43 | 0.33923 | 0.16361 | -0.33922 | -0.16429 | 4.5369e-06 | -0.00068264 | 0.01088 | 0.010888 | 0.010888 | 0.9993 | -0.011585 | 0.99929 | -0.011469 | 4.9493
44 | 7.0529 | 3.1401 | -7.0493 | -3.1664 | 0.0035409 | -0.026297 | 0.22315 | 0.2235 | 0.2235 | 0.99872 | -0.02392 | 0.99813 | -0.035209 | 26.5441
45 | 7.5051 | 3.5082 | -7.5049 | -3.5095 | 0.00021276 | -0.0013496 | 0.23946 | 0.23948 | 0.23948 | 0.99872 | -0.02392 | 0.99869 | -0.02452 | 28.4418
46 | 0.2984 | 0.14439 | -0.2984 | -0.14452 | 6.4465e-07 | -0.00012568 | 0.0095696 | 0.0095712 | 0.0095712 | 0.99998 | 0.00015331 | 0.99998 | 0.00017211 | 4.3506
47 | 1.4699 | 0.69218 | -1.4699 | -0.69233 | 1.8573e-05 | -0.00014496 | 0.046944 | 0.046945 | 0.046945 | 0.99913 | 0.0075023 | 0.99911 | 0.0076056 | 21.3388
48 | 1.2299 | 0.5761 | -1.2298 | -0.57741 | 0.00011621 | -0.0013121 | 0.039242 | 0.039258 | 0.039258 | 0.99911 | 0.0076056 | 0.99903 | 0.0083704 | 17.8447
49 | 0.22497 | 0.1089 | -0.22496 | -0.10895 | 4.2656e-06 | -5.1815e-05 | 0.0072287 | 0.0072293 | 0.0072293 | 0.99813 | -0.035209 | 0.99811 | -0.035334 | 3.4425
50 | 6.5431 | 2.929 | -6.5412 | -2.9266 | 0.0018542 | 0.0023725 | 0.20733 | 0.20733 | 0.20733 | 0.99813 | -0.035209 | 0.99774 | -0.048742 | 25.2847
51 | 0.28131 | 0.12851 | -0.28128 | -0.13512 | 2.9999e-05 | -0.0066117 | 0.0089447 | 0.0090259 | 0.0090259 | 0.99813 | -0.035209 | 0.99803 | -0.034347 | 4.1027
52 | 7.4219 | 3.4693 | -7.4218 | -3.4697 | 5.9024e-05 | -0.00038405 | 0.23682 | 0.23682 | 0.23682 | 0.99869 | -0.02452 | 0.99868 | -0.024689 | 28.126
53 | 0.28128 | 0.13512 | -0.28127 | -0.13623 | 5.0666e-06 | -0.0011047 | 0.0090259 | 0.0090398 | 0.0090398 | 0.99803 | -0.034347 | 0.99801 | -0.034192 | 4.109
54 | -0.088238 | -0.042736 | 0.08824 | 0.04261 | 1.5354e-06 | -0.00012625 | 0.0028374 | 0.0028358 | 0.0028374 | 0.99747 | -0.051884 | 0.99749 | -0.051769 | 1.3512
55 | -0.42681 | -0.20659 | 0.42681 | 0.20648 | 1.0963e-06 | -0.00010328 | 0.013723 | 0.013722 | 0.013723 | 0.99749 | -0.051769 | 0.99749 | -0.051791 | 6.2377
56 | 1.3224 | 0.59707 | -1.3213 | -0.60743 | 0.0010919 | -0.010359 | 0.042279 | 0.042408 | 0.042408 | 0.99071 | -0.077291 | 0.98994 | -0.071061 | 19.2763
57 | 1.2298 | 0.57741 | -1.229 | -0.58645 | 0.00080358 | -0.0090358 | 0.039258 | 0.039373 | 0.039373 | 0.99903 | 0.0083704 | 0.99842 | 0.013777 | 17.8968
58 | 0.409 | 0.19159 | -0.40895 | -0.19716 | 5.3767e-05 | -0.0055748 | 0.013059 | 0.013128 | 0.013128 | 0.99842 | 0.013777 | 0.9983 | 0.014875 | 5.9673
59 | 0.82001 | 0.39486 | -0.81994 | -0.3966 | 6.8501e-05 | -0.0017417 | 0.026315 | 0.026337 | 0.026337 | 0.99842 | 0.013777 | 0.99834 | 0.014499 | 11.9713
60 | 0.40895 | 0.19716 | -0.40894 | -0.19806 | 8.6946e-06 | -0.0008958 | 0.013128 | 0.013139 | 0.013139 | 0.9983 | 0.014875 | 0.99828 | 0.015059 | 5.9725
61 | 0.27152 | 0.13099 | -0.27151 | -0.13112 | 1.5888e-05 | -0.00012964 | 0.0087172 | 0.0087189 | 0.0087189 | 0.99834 | 0.014499 | 0.99828 | 0.014108 | 4.1519
62 | 7.4218 | 3.4697 | -7.4208 | -3.4767 | 0.0010647 | -0.0069227 | 0.23682 | 0.23692 | 0.23692 | 0.99868 | -0.024689 | 0.99851 | -0.027723 | 28.1375
63 | 5.5504 | 2.4765 | -5.5502 | -2.4795 | 0.00023765 | -0.0029734 | 0.17587 | 0.17591 | 0.17591 | 0.9976 | -0.051401 | 0.99755 | -0.052366 | 20.892
64 | 0.42684 | 0.20378 | -0.42681 | -0.20648 | 2.862e-05 | -0.0027034 | 0.013688 | 0.013722 | 0.013722 | 0.99755 | -0.052366 | 0.99749 | -0.051791 | 6.2371
65 | 0.27151 | 0.13112 | -0.27151 | -0.1315 | 1.6142e-06 | -0.00037777 | 0.0087189 | 0.0087237 | 0.0087237 | 0.99828 | 0.014108 | 0.99827 | 0.01416 | 3.9653
66 | -4.662 | -2.2208 | 4.6633 | 2.2223 | 0.0013063 | 0.0014148 | 0.14963 | 0.14963 | 0.14963 | 0.99624 | -0.066007 | 0.99659 | -0.057277 | 42.7522
67 | 3.9095 | 1.8569 | -3.9029 | -1.8499 | 0.0066028 | 0.0069831 | 0.12541 | 0.12542 | 0.12542 | 0.99624 | -0.066007 | 0.99412 | -0.11892 | 35.8341
68 | 0.41428 | 0.2002 | -0.41416 | -0.20059 | 0.00012497 | -0.00038891 | 0.013333 | 0.013338 | 0.013338 | 0.99624 | -0.066007 | 0.99592 | -0.068005 | 6.3517
69 | -4.6633 | -2.2223 | 4.6661 | 2.2154 | 0.0028131 | -0.0068315 | 0.14963 | 0.14952 | 0.14963 | 0.99659 | -0.057277 | 0.99725 | -0.050203 | 41.3347
70 | 3.3679 | 1.5918 | -3.3527 | -1.6101 | 0.015209 | -0.018307 | 0.10817 | 0.10846 | 0.10846 | 0.99412 | -0.11892 | 0.98995 | -0.080918 | 49.2983
71 | 0.53501 | 0.25811 | -0.53501 | -0.25816 | 7.7097e-07 | -4.5572e-05 | 0.017249 | 0.01725 | 0.01725 | 0.99412 | -0.11892 | 0.99412 | -0.11891 | 7.8408
72 | -4.9974 | -2.375 | 4.9985 | 2.3581 | 0.0011031 | -0.016872 | 0.16017 | 0.15994 | 0.16017 | 0.99725 | -0.050203 | 0.99751 | -0.045611 | 19.022
73 | 0.3313 | 0.15954 | -0.3313 | -0.16046 | 5.8178e-06 | -0.00091057 | 0.010644 | 0.010656 | 0.010656 | 0.99725 | -0.050203 | 0.99724 | -0.050051 | 4.8436
74 | 0.33859 | 0.16302 | -0.33849 | -0.1635 | 9.6651e-05 | -0.00047644 | 0.010912 | 0.010919 | 0.010919 | 0.99412 | -0.11891 | 0.99382 | -0.12082 | 5.1995
75 | 0.33849 | 0.1635 | -0.33849 | -0.16394 | 2.9524e-06 | -0.00043633 | 0.010919 | 0.010925 | 0.010925 | 0.99382 | -0.12082 | 0.99381 | -0.12074 | 4.9657
76 | 3.3527 | 1.6101 | -3.3521 | -1.6107 | 0.00057213 | -0.00068256 | 0.10846 | 0.10847 | 0.10847 | 0.98995 | -0.080918 | 0.98979 | -0.079458 | 49.3032
77 | 0.23847 | 0.11505 | -0.23847 | -0.11532 | 8.6743e-07 | -0.00026255 | 0.0076624 | 0.0076657 | 0.0076657 | 0.99751 | -0.045611 | 0.99751 | -0.04558 | 3.4844
78 | -5.237 | -2.4732 | 5.2371 | 2.4712 | 0.00013881 | -0.0019257 | 0.16761 | 0.16758 | 0.16761 | 0.99751 | -0.045611 | 0.99754 | -0.045058 | 19.9057
79 | 0.23847 | 0.11532 | -0.23847 | -0.11549 | 5.9418e-07 | -0.00017971 | 0.0076657 | 0.007668 | 0.007668 | 0.99751 | -0.04558 | 0.99751 | -0.045558 | 3.4854
80 | -5.4536 | -2.5761 | 5.4537 | 2.5741 | 0.00015359 | -0.0019539 | 0.17454 | 0.17451 | 0.17454 | 0.99754 | -0.045058 | 0.99757 | -0.044469 | 20.7293
81 | -5.4537 | -2.5741 | 5.454 | 2.5713 | 0.00022268 | -0.0028342 | 0.17451 | 0.17448 | 0.17451 | 0.99757 | -0.044469 | 0.99762 | -0.043615 | 20.7262
82 | 2.9689 | 1.4251 | -2.9632 | -1.422 | 0.0056618 | 0.0031443 | 0.096048 | 0.096053 | 0.096053 | 0.98979 | -0.079458 | 0.98779 | -0.092473 | 45.7394
83 | 2.6375 | 1.2642 | -2.6373 | -1.2646 | 0.00018171 | -0.00038006 | 0.085476 | 0.085482 | 0.085482 | 0.98779 | -0.092473 | 0.98773 | -0.091886 | 38.8554
84 | 2.6373 | 1.2646 | -2.6371 | -1.2652 | 0.00026031 | -0.00054425 | 0.085482 | 0.08549 | 0.08549 | 0.98773 | -0.091886 | 0.98764 | -0.091045 | 38.859
85 | -0.2559 | -0.12394 | 0.2559 | 0.12391 | 2.6361e-06 | -2.3509e-05 | 0.0082929 | 0.0082926 | 0.0082929 | 0.98975 | -0.069651 | 0.98976 | -0.069583 | 3.949
86 | 0.47558 | 0.21288 | -0.4754 | -0.22635 | 0.00018024 | -0.01347 | 0.015197 | 0.015363 | 0.015363 | 0.98976 | -0.069583 | 0.98941 | -0.066625 | 6.983
87 | -0.73148 | -0.33679 | 0.73163 | 0.33231 | 0.00014198 | -0.0044786 | 0.023487 | 0.023432 | 0.023487 | 0.98976 | -0.069583 | 0.98994 | -0.071061 | 10.676
88 | 0.2597 | 0.12429 | -0.2597 | -0.12482 | 2.1653e-06 | -0.00053733 | 0.0083957 | 0.0084025 | 0.0084025 | 0.98994 | -0.071061 | 0.98994 | -0.07099 | 3.8193
89 | 0.33002 | 0.15083 | -0.32998 | -0.15624 | 3.4879e-05 | -0.0054152 | 0.010581 | 0.010648 | 0.010648 | 0.98994 | -0.071061 | 0.98984 | -0.070221 | 4.8399
90 | 0.12672 | 0.060418 | -0.12672 | -0.061373 | 9.1632e-07 | -0.00095516 | 0.0040938 | 0.0041059 | 0.0041059 | 0.98994 | -0.07099 | 0.98993 | -0.070928 | 1.8663
91 | 0.21922 | 0.10347 | -0.21922 | -0.10614 | 7.6719e-06 | -0.0026747 | 0.0070697 | 0.0071034 | 0.0071034 | 0.98984 | -0.070221 | 0.98981 | -0.069925 | 3.2288
92 | 0.11076 | 0.052773 | -0.11076 | -0.053643 | 6.3834e-07 | -0.00087083 | 0.0035781 | 0.0035891 | 0.0035891 | 0.98984 | -0.070221 | 0.98984 | -0.070172 | 1.6314
93 | 2.5543 | 1.2257 | -2.5535 | -1.2274 | 0.00076391 | -0.0017157 | 0.082809 | 0.082834 | 0.082834 | 0.98764 | -0.091045 | 0.98737 | -0.088488 | 37.6518
94 | 0.082788 | 0.039435 | -0.082788 | -0.040096 | 2.7296e-07 | -0.0006607 | 0.0026803 | 0.0026887 | 0.0026887 | 0.98764 | -0.091045 | 0.98764 | -0.091017 | 1.2221
95 | 2.4405 | 1.1735 | -2.4404 | -1.1739 | 0.00014328 | -0.00035597 | 0.079174 | 0.079179 | 0.079179 | 0.98737 | -0.088488 | 0.98731 | -0.087984 | 35.9905
96 | 0.11297 | 0.053914 | -0.11297 | -0.054716 | 6.1739e-07 | -0.00080125 | 0.0036599 | 0.00367 | 0.00367 | 0.98737 | -0.088488 | 0.98736 | -0.088441 | 1.6682
97 | 2.4404 | 1.1739 | -2.4399 | -1.175 | 0.00045258 | -0.0011238 | 0.079179 | 0.079195 | 0.079195 | 0.98731 | -0.087984 | 0.98714 | -0.086391 | 35.9978
98 | 1.9591 | 0.94212 | -1.9591 | -0.94218 | 1.5214e-05 | -6.1097e-05 | 0.063571 | 0.063572 | 0.063572 | 0.98714 | -0.086391 | 0.98714 | -0.086324 | 28.8963
99 | -0.093184 | -0.045131 | 0.093184 | 0.043896 | 6.4036e-07 | -0.0012346 | 0.003021 | 0.0030054 | 0.003021 | 0.98937 | -0.066449 | 0.98938 | -0.066507 | 1.3732
100 | -0.093184 | -0.043896 | 0.093185 | 0.041768 | 1.0889e-06 | -0.0021287 | 0.0030054 | 0.0029795 | 0.0030054 | 0.98938 | -0.066507 | 0.98939 | -0.066598 | 1.3661
101 | -0.093185 | -0.041768 | 0.093186 | 0.0417 | 9.2091e-07 | -6.7482e-05 | 0.0029795 | 0.0029787 | 0.0029795 | 0.98939 | -0.066598 | 0.9894 | -0.066513 | 1.4188
102 | -0.4754 | -0.22681 | 0.4754 | 0.22635 | 6.3142e-06 | -0.00046636 | 0.015368 | 0.015363 | 0.015368 | 0.9894 | -0.066513 | 0.98941 | -0.066625 | 6.9856
103 | -0.7289 | -0.35236 | 0.72891 | 0.35225 | 3.3693e-06 | -0.00010828 | 0.023427 | 0.023426 | 0.023427 | 0.99762 | -0.043575 | 0.99762 | -0.043615 | 10.6487
104 | 0.30956 | 0.14926 | -0.30955 | -0.14992 | 3.6922e-06 | -0.00066292 | 0.0099443 | 0.0099527 | 0.0099527 | 0.99762 | -0.043575 | 0.99761 | -0.043472 | 4.524
105 | -6.1829 | -2.9235 | 6.1835 | 2.9174 | 0.00063151 | -0.0061239 | 0.1979 | 0.19782 | 0.1979 | 0.99762 | -0.043615 | 0.99774 | -0.041483 | 23.5038
106 | 0.3593 | 0.17381 | -0.3593 | -0.17401 | 1.5267e-06 | -0.00020332 | 0.011548 | 0.011551 | 0.011551 | 0.99774 | -0.041483 | 0.99774 | -0.041446 | 5.2502
107 | -6.5428 | -3.0912 | 6.5436 | 3.0841 | 0.00083518 | -0.0071571 | 0.20937 | 0.20927 | 0.20937 | 0.99774 | -0.041483 | 0.99789 | -0.038814 | 24.8654
108 | -7.017 | -3.31 | 7.0203 | 3.2857 | 0.0033081 | -0.024321 | 0.22444 | 0.22411 | 0.22444 | 0.99789 | -0.038814 | 0.99844 | -0.0289 | 26.6558
109 | 0.14117 | 0.066494 | -0.14116 | -0.068304 | 2.0817e-06 | -0.0018097 | 0.0045141 | 0.0045367 | 0.0045367 | 0.99789 | -0.038814 | 0.99788 | -0.03869 | 2.0621
110 | 0.33217 | 0.15945 | -0.33217 | -0.16088 | 9.1484e-06 | -0.0014289 | 0.010659 | 0.010677 | 0.010677 | 0.99789 | -0.038814 | 0.99787 | -0.038577 | 4.8532
111 | -7.0203 | -3.2857 | 7.0205 | 3.2841 | 0.00021116 | -0.0015563 | 0.22411 | 0.22408 | 0.22411 | 0.99844 | -0.0289 | 0.99848 | -0.028264 | 26.6158
112 | 0.14116 | 0.068304 | -0.14116 | -0.068369 | 7.5859e-08 | -6.5596e-05 | 0.0045367 | 0.0045375 | 0.0045375 | 0.99788 | -0.03869 | 0.99788 | -0.038685 | 2.0625
113 | -7.4206 | -3.4779 | 7.4208 | 3.4767 | 0.00019009 | -0.0012351 | 0.23693 | 0.23692 | 0.23693 | 0.99848 | -0.028264 | 0.99851 | -0.027723 | 28.1395
114 | 0.21922 | 0.10614 | -0.21921 | -0.10617 | 2.0285e-06 | -2.5119e-05 | 0.0071034 | 0.0071037 | 0.0071037 | 0.98981 | -0.069925 | 0.9898 | -0.069986 | 3.3827
115 | 1.9591 | 0.94218 | -1.9591 | -0.94223 | 1.0938e-05 | -4.3923e-05 | 0.063572 | 0.063573 | 0.063573 | 0.98714 | -0.086324 | 0.98713 | -0.086276 | 28.8966
116 | 1.8595 | 0.89403 | -1.8593 | -0.89495 | 0.00020558 | -0.00092278 | 0.060339 | 0.060351 | 0.060351 | 0.98713 | -0.086276 | 0.98703 | -0.085328 | 27.4324
117 | 1.8593 | 0.89495 | -1.8585 | -0.89855 | 0.00080424 | -0.0036041 | 0.060351 | 0.0604 | 0.0604 | 0.98703 | -0.085328 | 0.98663 | -0.081592 | 27.4546
118 | 1.8585 | 0.89855 | -1.8582 | -0.89998 | 0.00031802 | -0.0014226 | 0.0604 | 0.06042 | 0.06042 | 0.98663 | -0.081592 | 0.98648 | -0.080104 | 27.4634

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 17.1585 | 7.8507

## res_load
| p_mw | q_mvar
0 | 0.30859 | 0.14946
1 | 0.36918 | 0.1788
2 | 0.09338 | 0.045226
3 | 0.093503 | 0.045286
4 | 0.26699 | 0.12931
5 | 0.32596 | 0.15787
6 | 0.1802 | 0.087276
7 | 0.33301 | 0.16129
8 | 0.23936 | 0.11593
9 | 0.37413 | 0.1812
10 | 0.083292 | 0.04034
11 | 0.074418 | 0.036042
12 | 0.40333 | 0.19534
13 | 0.14194 | 0.068744
14 | 0.10666 | 0.051659
15 | 0.35475 | 0.17182
16 | 0.2984 | 0.14452
17 | 0.23998 | 0.11623
18 | 0.08298 | 0.040189
19 | 0.28127 | 0.13623
20 | 0.22496 | 0.10895
21 | 0.11449 | 0.055451
22 | 0.088238 | 0.042736
23 | 0.33857 | 0.16398
24 | 0.74924 | 0.36287
25 | 0.54842 | 0.26561
26 | 0.40894 | 0.19806
27 | 0.33922 | 0.16429
28 | 0.12263 | 0.059393
29 | 0.33819 | 0.16379
30 | 0.41416 | 0.20059
31 | 0.19642 | 0.095133
32 | 0.33849 | 0.16394
33 | 0.3313 | 0.16046
34 | 0.21646 | 0.10484
35 | 0.23847 | 0.11549
36 | 0.16406 | 0.079459
37 | 0.38324 | 0.18561
38 | 0.32572 | 0.15775
39 | 0.2559 | 0.12394
40 | 0.13298 | 0.064405
41 | 0.082788 | 0.040096
42 | 0.11297 | 0.054716
43 | 0.48085 | 0.23289
44 | 0.093184 | 0.045131
45 | 0.38221 | 0.18511
46 | 0.41935 | 0.2031
47 | 0.30955 | 0.14992
48 | 0.33217 | 0.16088
49 | 0.3593 | 0.17401
50 | 0.14116 | 0.068369
51 | 0.40008 | 0.19377
52 | 0.11076 | 0.053643
53 | 0.21921 | 0.10617
54 | 0.12672 | 0.061373
55 | 0.32877 | 0.15923
56 | 0.27151 | 0.1315
57 | 0.099519 | 0.048199
58 | 1.8582 | 0.89998

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1