## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_303_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_303_0_node_114 | 20 | n |  | TRUE
2 | bus_MV_303_0_node_103 | 20 | n |  | TRUE
3 | bus_MV_303_0_node_112 | 20 | n |  | TRUE
4 | bus_MV_303_0_node_107 | 20 | n |  | TRUE
5 | bus_MV_303_0_node_104 | 20 | n |  | TRUE
6 | bus_MV_303_0_node_1 | 20 | n |  | TRUE
7 | bus_MV_303_0_node_3 | 20 | n |  | TRUE
8 | bus_MV_303_0_node_2 | 20 | n |  | TRUE
9 | bus_MV_303_0_node_6 | 20 | n |  | TRUE
10 | bus_MV_303_0_node_5 | 20 | n |  | TRUE
11 | bus_MV_303_0_node_4 | 20 | n |  | TRUE
12 | bus_MV_303_0_node_108 | 20 | n |  | TRUE
13 | bus_MV_303_0_node_7 | 20 | n |  | TRUE
14 | bus_MV_303_0_node_102 | 20 | n |  | TRUE
15 | bus_MV_303_0_node_45 | 20 | n |  | TRUE
16 | bus_MV_303_0_node_44 | 20 | n |  | TRUE
17 | bus_MV_303_0_node_46 | 20 | n |  | TRUE
18 | bus_MV_303_0_node_93 | 20 | n |  | TRUE
19 | bus_MV_303_0_node_8 | 20 | n |  | TRUE
20 | bus_MV_303_0_node_9 | 20 | n |  | TRUE
21 | bus_MV_303_0_node_51 | 20 | n |  | TRUE
22 | bus_MV_303_0_node_55 | 20 | n |  | TRUE
23 | bus_MV_303_0_node_48 | 20 | n |  | TRUE
24 | bus_MV_303_0_node_61 | 20 | n |  | TRUE
25 | bus_MV_303_0_node_60 | 20 | n |  | TRUE
26 | bus_MV_303_0_node_77 | 20 | n |  | TRUE
27 | bus_MV_303_0_node_82 | 20 | n |  | TRUE
28 | bus_MV_303_0_node_33 | 20 | n |  | TRUE
29 | bus_MV_303_0_node_11 | 20 | n |  | TRUE
30 | bus_MV_303_0_node_13 | 20 | n |  | TRUE
31 | bus_MV_303_0_node_70 | 20 | n |  | TRUE
32 | bus_MV_303_0_node_106 | 20 | n |  | TRUE
33 | bus_MV_303_0_node_15 | 20 | n |  | TRUE
34 | bus_MV_303_0_node_12 | 20 | n |  | TRUE
35 | bus_MV_303_0_node_14 | 20 | n |  | TRUE
36 | bus_MV_303_0_node_23 | 20 | n |  | TRUE
37 | bus_MV_303_0_node_16 | 20 | n |  | TRUE
38 | bus_MV_303_0_node_69 | 20 | n |  | TRUE
39 | bus_MV_303_0_node_71 | 20 | n |  | TRUE
40 | bus_MV_303_0_node_101 | 20 | n |  | TRUE
41 | bus_MV_303_0_node_21 | 20 | n |  | TRUE
42 | bus_MV_303_0_node_47 | 20 | n |  | TRUE
43 | bus_MV_303_0_node_58 | 20 | n |  | TRUE
44 | bus_MV_303_0_node_17 | 20 | n |  | TRUE
45 | bus_MV_303_0_node_83 | 20 | n |  | TRUE
46 | bus_MV_303_0_node_87 | 20 | n |  | TRUE
47 | bus_MV_303_0_node_56 | 20 | n |  | TRUE
48 | bus_MV_303_0_node_57 | 20 | n |  | TRUE
49 | bus_MV_303_0_node_86 | 20 | n |  | TRUE
50 | bus_MV_303_0_node_84 | 20 | n |  | TRUE
51 | bus_MV_303_0_node_85 | 20 | n |  | TRUE
52 | bus_MV_303_0_node_89 | 20 | n |  | TRUE
53 | bus_MV_303_0_node_59 | 20 | n |  | TRUE
54 | bus_MV_303_0_node_88 | 20 | n |  | TRUE
55 | bus_MV_303_0_node_19 | 20 | n |  | TRUE
56 | bus_MV_303_0_node_99 | 20 | n |  | TRUE
57 | bus_MV_303_0_node_91 | 20 | n |  | TRUE
58 | bus_MV_303_0_node_100 | 20 | n |  | TRUE
59 | bus_MV_303_0_node_64 | 20 | n |  | TRUE
60 | bus_MV_303_0_node_90 | 20 | n |  | TRUE
61 | bus_MV_303_0_node_92 | 20 | n |  | TRUE
62 | bus_MV_303_0_node_20 | 20 | n |  | TRUE
63 | bus_MV_303_0_node_22 | 20 | n |  | TRUE
64 | bus_MV_303_0_node_26 | 20 | n |  | TRUE
65 | bus_MV_303_0_node_24 | 20 | n |  | TRUE
66 | bus_MV_303_0_node_27 | 20 | n |  | TRUE
67 | bus_MV_303_0_node_72 | 20 | n |  | TRUE
68 | bus_MV_303_0_node_28 | 20 | n |  | TRUE
69 | bus_MV_303_0_node_43 | 20 | n |  | TRUE
70 | bus_MV_303_0_node_42 | 20 | n |  | TRUE
71 | bus_MV_303_0_node_73 | 20 | n |  | TRUE
72 | bus_MV_303_0_node_29 | 20 | n |  | TRUE
73 | bus_MV_303_0_node_105 | 20 | n |  | TRUE
74 | bus_MV_303_0_node_30 | 20 | n |  | TRUE
75 | bus_MV_303_0_node_31 | 20 | n |  | TRUE
76 | bus_MV_303_0_node_32 | 20 | n |  | TRUE
77 | bus_MV_303_0_node_40 | 20 | n |  | TRUE
78 | bus_MV_303_0_node_39 | 20 | n |  | TRUE
79 | bus_MV_303_0_node_35 | 20 | n |  | TRUE
80 | bus_MV_303_0_node_34 | 20 | n |  | TRUE
81 | bus_MV_303_0_node_36 | 20 | n |  | TRUE
82 | bus_MV_303_0_node_37 | 20 | n |  | TRUE
83 | bus_MV_303_0_node_38 | 20 | n |  | TRUE
84 | bus_MV_303_0_node_115 | 20 | n |  | TRUE
85 | bus_MV_303_0_node_41 | 20 | n |  | TRUE
86 | bus_MV_303_0_node_116 | 20 | n |  | TRUE
87 | bus_MV_303_0_node_50 | 20 | n |  | TRUE
88 | bus_MV_303_0_node_54 | 20 | n |  | TRUE
89 | bus_MV_303_0_node_49 | 20 | n |  | TRUE
90 | bus_MV_303_0_node_52 | 20 | n |  | TRUE
91 | bus_MV_303_0_node_109 | 20 | n |  | TRUE
92 | bus_MV_303_0_node_110 | 20 | n |  | TRUE
93 | bus_MV_303_0_node_53 | 20 | n |  | TRUE
94 | bus_MV_303_0_node_78 | 20 | n |  | TRUE
95 | bus_MV_303_0_node_94 | 20 | n |  | TRUE
96 | bus_MV_303_0_node_81 | 20 | n |  | TRUE
97 | bus_MV_303_0_node_95 | 20 | n |  | TRUE
98 | bus_MV_303_0_node_96 | 20 | n |  | TRUE
99 | bus_MV_303_0_node_62 | 20 | n |  | TRUE
100 | bus_MV_303_0_node_63 | 20 | n |  | TRUE
101 | bus_MV_303_0_node_98 | 20 | n |  | TRUE
102 | bus_MV_303_0_node_97 | 20 | n |  | TRUE
103 | bus_MV_303_0_node_65 | 20 | n |  | TRUE
104 | bus_MV_303_0_node_66 | 20 | n |  | TRUE
105 | bus_MV_303_0_node_113 | 20 | n |  | TRUE
106 | bus_MV_303_0_node_68 | 20 | n |  | TRUE
107 | bus_MV_303_0_node_111 | 20 | n |  | TRUE
108 | bus_MV_303_0_node_74 | 20 | n |  | TRUE
109 | bus_MV_303_0_node_75 | 20 | n |  | TRUE
110 | bus_MV_303_0_node_76 | 20 | n |  | TRUE
111 | bus_MV_303_0_node_79 | 20 | n |  | TRUE
112 | bus_MV_303_0_node_80 | 20 | n |  | TRUE
113 | bus_HV_303_0_node_11 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_303_0_load_0 | 0 | 0.27707 | 0.13419 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_303_0_load_114 | 1 | 0.20333 | 0.09848 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_303_0_load_112 | 3 | 0.069012 | 0.033424 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_303_0_load_107 | 4 | 0.19883 | 0.096299 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_303_0_load_104 | 5 | 0.39687 | 0.19221 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_303_0_load_1 | 6 | 0.22551 | 0.10922 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_303_0_load_108 | 12 | 0.30694 | 0.14866 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_303_0_load_7 | 13 | 0.31575 | 0.15292 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_303_0_load_102 | 14 | 0.11071 | 0.053619 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_303_0_load_44 | 16 | 0.11356 | 0.055 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_303_0_load_46 | 17 | 0.75927 | 0.36773 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_303_0_load_93 | 18 | 0.65643 | 0.31792 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_303_0_load_8 | 19 | 0.37497 | 0.18161 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_303_0_load_55 | 22 | 0.11847 | 0.057379 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_303_0_load_61 | 24 | 0.36361 | 0.1761 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_303_0_load_77 | 26 | 0.085743 | 0.041527 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_303_0_load_82 | 27 | 0.31115 | 0.1507 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_303_0_load_11 | 29 | 0.19241 | 0.093189 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_303_0_load_13 | 30 | 0.26848 | 0.13003 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_303_0_load_106 | 32 | 0.28167 | 0.13642 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_303_0_load_12 | 34 | 0.1089 | 0.052742 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_303_0_load_69 | 38 | 0.10805 | 0.052332 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_303_0_load_71 | 39 | 0.22698 | 0.10993 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_303_0_load_101 | 40 | 0.12616 | 0.061101 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_303_0_load_47 | 42 | 0.32035 | 0.15515 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_303_0_load_17 | 44 | 0.14306 | 0.069287 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_303_0_load_83 | 45 | 0.19047 | 0.092248 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_303_0_load_87 | 46 | 0.1184 | 0.057343 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_303_0_load_56 | 47 | 0.36787 | 0.17817 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_303_0_load_86 | 49 | 0.13169 | 0.06378 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_303_0_load_85 | 51 | 0.21955 | 0.10633 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_303_0_load_91 | 57 | 0.37041 | 0.1794 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_303_0_load_100 | 58 | 0.1125 | 0.054488 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_303_0_load_90 | 60 | 0.095469 | 0.046238 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_303_0_load_92 | 61 | 0.10023 | 0.048543 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_303_0_load_20 | 62 | 0.344 | 0.1666 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_303_0_load_27 | 66 | 0.23366 | 0.11317 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_303_0_load_72 | 67 | 0.074402 | 0.036035 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_303_0_load_43 | 69 | 0.36109 | 0.17488 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_303_0_load_105 | 73 | 0.31719 | 0.15362 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_303_0_load_30 | 74 | 0.25845 | 0.12517 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_303_0_load_39 | 78 | 0.40959 | 0.19837 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_303_0_load_35 | 79 | 0.070014 | 0.033909 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_303_0_load_36 | 81 | 0.12264 | 0.059395 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_303_0_load_41 | 85 | 0.075678 | 0.036652 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_303_0_load_116 | 86 | 0.28387 | 0.13749 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_303_0_load_109 | 91 | 0.334 | 0.16176 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_303_0_load_110 | 92 | 0.098052 | 0.047489 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_303_0_load_78 | 94 | 0.2038 | 0.098706 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_303_0_load_94 | 95 | 0.095984 | 0.046487 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_303_0_load_95 | 97 | 0.28767 | 0.13932 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_303_0_load_62 | 99 | 0.15772 | 0.076389 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_303_0_load_98 | 101 | 0.30361 | 0.14704 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_303_0_load_65 | 103 | 0.36571 | 0.17712 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_303_0_load_113 | 105 | 0.15349 | 0.074337 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_303_0_load_68 | 106 | 0.23378 | 0.11322 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_303_0_load_76 | 110 | 0.11121 | 0.05386 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_303_0_load_79 | 111 | 0.094348 | 0.045695 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_303_0_line_0 |  | 0 | 1 | 0.539 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_303_0_line_1 |  | 0 | 2 | 1.8027 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_303_0_line_2 |  | 2 | 5 | 0.03798 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_303_0_line_3 |  | 3 | 4 | 3.1548 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_303_0_line_4 |  | 4 | 28 | 2.8389 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_303_0_line_5 |  | 5 | 72 | 0.76397 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_303_0_line_6 |  | 6 | 7 | 0.074837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_303_0_line_7 |  | 6 | 8 | 0.066529 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_303_0_line_8 |  | 7 | 9 | 0.073568 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_303_0_line_9 |  | 8 | 10 | 1.2123 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_303_0_line_10 |  | 9 | 14 | 0.10161 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_303_0_line_11 |  | 10 | 13 | 0.034864 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_303_0_line_12 |  | 10 | 11 | 0.90386 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_303_0_line_13 |  | 11 | 12 | 0.044321 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_303_0_line_14 |  | 13 | 15 | 0.3716 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
15 | MV_303_0_line_15 |  | 15 | 17 | 0.16661 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
16 | MV_303_0_line_16 |  | 15 | 16 | 0.36397 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_303_0_line_17 |  | 17 | 18 | 0.9167 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
18 | MV_303_0_line_18 |  | 18 | 61 | 0.057785 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
19 | MV_303_0_line_19 |  | 19 | 20 | 0.058241 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_303_0_line_20 |  | 20 | 21 | 1.068 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_303_0_line_21 |  | 21 | 22 | 0.038761 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_303_0_line_22 |  | 21 | 23 | 0.42848 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_303_0_line_23 |  | 23 | 87 | 0.52663 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_303_0_line_24 |  | 23 | 88 | 0.34668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_303_0_line_25 |  | 23 | 42 | 0.07674 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_303_0_line_26 |  | 24 | 25 | 0.007547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_303_0_line_27 |  | 25 | 43 | 0.72037 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
28 | MV_303_0_line_28 |  | 25 | 37 | 0.84977 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
29 | MV_303_0_line_29 |  | 26 | 27 | 1.2778 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_303_0_line_30 |  | 26 | 28 | 0.16126 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_303_0_line_31 |  | 27 | 89 | 0.0030485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_303_0_line_32 |  | 28 | 80 | 0.40847 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_303_0_line_33 |  | 28 | 75 | 0.263 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_303_0_line_34 |  | 29 | 30 | 0.041486 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
35 | MV_303_0_line_35 |  | 30 | 31 | 0.12059 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
36 | MV_303_0_line_36 |  | 31 | 32 | 0.022665 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_303_0_line_37 |  | 31 | 33 | 0.37476 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
38 | MV_303_0_line_38 |  | 33 | 37 | 0.78118 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
39 | MV_303_0_line_39 |  | 33 | 38 | 0.019031 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_303_0_line_40 |  | 33 | 35 | 0.15572 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
41 | MV_303_0_line_41 |  | 34 | 35 | 0.068317 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_303_0_line_42 |  | 35 | 36 | 0.27551 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
43 | MV_303_0_line_43 |  | 36 | 40 | 0.068931 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_303_0_line_44 |  | 36 | 41 | 0.48379 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
45 | MV_303_0_line_45 |  | 37 | 39 | 0.051893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_303_0_line_46 |  | 41 | 65 | 0.68448 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_303_0_line_47 |  | 41 | 62 | 0.11019 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
48 | MV_303_0_line_48 |  | 43 | 49 | 0.044305 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
49 | MV_303_0_line_49 |  | 43 | 48 | 0.19864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_303_0_line_50 |  | 44 | 45 | 0.91505 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
51 | MV_303_0_line_51 |  | 44 | 46 | 0.7651 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
52 | MV_303_0_line_52 |  | 45 | 50 | 0.045494 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
53 | MV_303_0_line_53 |  | 46 | 54 | 0.0073723 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
54 | MV_303_0_line_54 |  | 47 | 48 | 0.034623 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_303_0_line_55 |  | 49 | 50 | 0.046612 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
56 | MV_303_0_line_56 |  | 51 | 52 | 0.051079 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
57 | MV_303_0_line_57 |  | 51 | 53 | 0.12771 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
58 | MV_303_0_line_58 |  | 52 | 54 | 0.041178 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
59 | MV_303_0_line_59 |  | 53 | 97 | 0.75472 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
60 | MV_303_0_line_60 |  | 55 | 56 | 0.16306 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
61 | MV_303_0_line_61 |  | 55 | 57 | 0.12672 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
62 | MV_303_0_line_62 |  | 56 | 58 | 0.017116 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_303_0_line_63 |  | 56 | 59 | 0.069147 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
64 | MV_303_0_line_64 |  | 57 | 60 | 0.017014 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
65 | MV_303_0_line_65 |  | 59 | 101 | 0.058074 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
66 | MV_303_0_line_66 |  | 59 | 100 | 0.25214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_303_0_line_67 |  | 60 | 61 | 0.018251 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
68 | MV_303_0_line_68 |  | 62 | 63 | 0.063177 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
69 | MV_303_0_line_69 |  | 63 | 64 | 0.92589 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
70 | MV_303_0_line_70 |  | 64 | 67 | 0.079506 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
71 | MV_303_0_line_71 |  | 65 | 66 | 0.042986 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_303_0_line_72 |  | 66 | 68 | 0.034953 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_303_0_line_73 |  | 67 | 71 | 0.027896 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
74 | MV_303_0_line_74 |  | 68 | 72 | 1.0049 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_303_0_line_75 |  | 69 | 70 | 0.053565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_303_0_line_76 |  | 70 | 77 | 0.04104 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_303_0_line_77 |  | 71 | 108 | 0.032232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_303_0_line_78 |  | 71 | 109 | 0.17059 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_303_0_line_79 |  | 72 | 73 | 0.033485 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_303_0_line_80 |  | 74 | 75 | 0.065839 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
81 | MV_303_0_line_81 |  | 75 | 76 | 0.020189 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_303_0_line_82 |  | 76 | 79 | 0.028664 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_303_0_line_83 |  | 77 | 78 | 0.054014 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_303_0_line_84 |  | 78 | 83 | 0.057214 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_303_0_line_85 |  | 80 | 81 | 0.073306 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_303_0_line_86 |  | 81 | 82 | 0.067131 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_303_0_line_87 |  | 82 | 83 | 0.26129 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_303_0_line_88 |  | 82 | 84 | 0.29574 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
89 | MV_303_0_line_89 |  | 83 | 85 | 0.070479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_303_0_line_90 |  | 84 | 86 | 0.011081 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_303_0_line_91 |  | 86 | 109 | 0.02929 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_303_0_line_92 |  | 87 | 91 | 0.004912 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_303_0_line_93 |  | 87 | 89 | 0.98038 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_303_0_line_94 |  | 88 | 95 | 0.078776 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_303_0_line_95 |  | 88 | 93 | 0.39486 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_303_0_line_96 |  | 89 | 90 | 0.2133 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_303_0_line_97 |  | 90 | 92 | 0.013247 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_303_0_line_98 |  | 92 | 96 | 0.048059 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_303_0_line_99 |  | 93 | 94 | 0.10511 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_303_0_line_100 |  | 96 | 112 | 0.018136 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_303_0_line_101 |  | 97 | 98 | 0.045161 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
102 | MV_303_0_line_102 |  | 98 | 107 | 0.45893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_303_0_line_103 |  | 98 | 102 | 0.31075 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
104 | MV_303_0_line_104 |  | 99 | 100 | 0.075793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_303_0_line_105 |  | 101 | 102 | 0.018975 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
106 | MV_303_0_line_106 |  | 103 | 104 | 0.018463 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
107 | MV_303_0_line_107 |  | 104 | 105 | 0.7144 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
108 | MV_303_0_line_108 |  | 105 | 106 | 0.80925 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
109 | MV_303_0_line_109 |  | 105 | 107 | 0.046615 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_303_0_line_110 |  | 108 | 110 | 0.017984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_303_0_line_111 |  | 111 | 112 | 0.0096151 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_303_0_trafo_11 | 25 MVA 110/20 kV | 113 | 29 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2650247.9339 | 1254494.0895
1 | 2649919.1916 | 1254066.9486
2 | 2652037.4481 | 1254712.0731
3 | 2648944.7814 | 1257637.9422
4 | 2651995.2375 | 1258442.4468
5 | 2652044.3237 | 1254749.4262
6 | 2652378.2798 | 1251978.4566
7 | 2652346.7183 | 1251912.7213
8 | 2652444.6959 | 1251982.3241
9 | 2652282.1332 | 1251877.4494
10 | 2653287.0903 | 1252019.8506
11 | 2652694.5796 | 1252209.0298
12 | 2652732.7985 | 1252231.5963
13 | 2653321.8494 | 1252022.5539
14 | 2652193.1945 | 1251832.5681
15 | 2653400.8322 | 1251659.4472
16 | 2653270.0266 | 1251319.7917
17 | 2653563.3849 | 1251695.9905
18 | 2654478.1001 | 1251756.3067
19 | 2656312.8014 | 1255413.2762
20 | 2656283.0319 | 1255363.1691
21 | 2655229.892 | 1255540.7169
22 | 2655225.49 | 1255579.2252
23 | 2655059.1029 | 1255514.62
24 | 2655069.3568 | 1253525.1976
25 | 2655062.0427 | 1253527.1421
26 | 2653574.9248 | 1255989.9487
27 | 2654733.3445 | 1256529.2166
28 | 2653413.9659 | 1255983.4455
29 | 2654060.2994 | 1253831.6277
30 | 2654101.6926 | 1253828.8587
31 | 2654220.4489 | 1253807.9347
32 | 2654243.1289 | 1253809.4767
33 | 2654153.608 | 1254166.374
34 | 2654023.95 | 1254087.4857
35 | 2654028.507 | 1254152.756
36 | 2653786.3458 | 1254284.1561
37 | 2654275.1207 | 1253847.8741
38 | 2654168.7528 | 1254155.3142
39 | 2654271.6141 | 1253899.6483
40 | 2653762.3803 | 1254348.7838
41 | 2653538.2811 | 1254369.6585
42 | 2655056.8747 | 1255437.9119
43 | 2655089.078 | 1253157.8578
44 | 2654337.7016 | 1252481.8296
45 | 2655019.9658 | 1253091.6141
46 | 2654983.2929 | 1252892.4313
47 | 2655151.7056 | 1253121.3592
48 | 2655158.7921 | 1253155.2488
49 | 2655106.1238 | 1253117.947
50 | 2655064.9944 | 1253096.0131
51 | 2655079.8221 | 1252871.9725
52 | 2655029.5508 | 1252881.023
53 | 2655109.9 | 1252747.8545
54 | 2654990.6355 | 1252891.7693
55 | 2654628.7789 | 1251913.7106
56 | 2654692.018 | 1251812.0677
57 | 2654531.8644 | 1251832.0618
58 | 2654706.6441 | 1251803.1075
59 | 2654733.6915 | 1251766.5207
60 | 2654521.0176 | 1251818.9532
61 | 2654509.3824 | 1251804.8918
62 | 2653428.0918 | 1254370.0532
63 | 2653412.2187 | 1254431.2084
64 | 2653300.5772 | 1255054.8394
65 | 2653166.256 | 1254351.9525
66 | 2653150.0264 | 1254391.7569
67 | 2653378.8995 | 1255041.2628
68 | 2653117.37 | 1254379.0441
69 | 2653109.4359 | 1255382.1969
70 | 2653106.2473 | 1255426.555
71 | 2653406.2095 | 1255035.577
72 | 2652729.2109 | 1255087.9285
73 | 2652727.2538 | 1255121.3567
74 | 2653447.2912 | 1255781.4819
75 | 2653475.9209 | 1255840.7707
76 | 2653490.033 | 1255833.9711
77 | 2653134.9774 | 1255455.8998
78 | 2653174.2587 | 1255418.9374
79 | 2653507.7689 | 1255836.6477
80 | 2653404.5941 | 1255644.5117
81 | 2653441.253 | 1255581.4424
82 | 2653467.6055 | 1255519.6813
83 | 2653229.6582 | 1255433.2338
84 | 2653493.181 | 1255225.0499
85 | 2653229.6022 | 1255484.4926
86 | 2653492.104 | 1255214.0213
87 | 2655051.7132 | 1255955.6623
88 | 2655084.1082 | 1255188.4784
89 | 2654736.3353 | 1256528.9782
90 | 2654794.6767 | 1256585.6687
91 | 2655056.6104 | 1255956.197
92 | 2654781.5406 | 1256587.2484
93 | 2654924.6782 | 1255412.5338
94 | 2654932.4397 | 1255517.3566
95 | 2655130.1866 | 1255124.5842
96 | 2654761.845 | 1256631.0861
97 | 2654982.6368 | 1252003.9445
98 | 2654959.2373 | 1251965.334
99 | 2654699.3206 | 1251545.8951
100 | 2654732.84 | 1251613.6069
101 | 2654778.3132 | 1251803.792
102 | 2654794.6309 | 1251798.8171
103 | 2655999.672 | 1251982.0602
104 | 2655984.5385 | 1251992.6357
105 | 2655270.5013 | 1251969.7308
106 | 2655977.2104 | 1252364.0028
107 | 2655230.8904 | 1251994.49
108 | 2653388.3707 | 1255008.7531
109 | 2653486.5253 | 1255185.2953
110 | 2653379.2021 | 1254993.2818
111 | 2654768.9044 | 1256654.6125
112 | 2654761.2723 | 1256648.9824
113 | 2654060.2994 | 1253831.6277

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9905 | -0.089692 | 0.27707 | 0.13419
1 | 0.99029 | -0.091057 | 0.20333 | 0.09848
2 | 0.99219 | -0.07878 | 0 | 0
3 | 0.98827 | -0.12949 | 0.069012 | 0.033424
4 | 0.98869 | -0.1263 | 0.19883 | 0.096299
5 | 0.99222 | -0.078995 | 0.39687 | 0.19221
6 | 0.98377 | -0.4971 | 0.22551 | 0.10922
7 | 0.98376 | -0.49702 | 0 | 0
8 | 0.98381 | -0.49679 | 0 | 0
9 | 0.98375 | -0.49694 | 0 | 0
10 | 0.98433 | -0.50024 | 0 | 0
11 | 0.98398 | -0.4975 | 0 | 0
12 | 0.98396 | -0.49733 | 0.30694 | 0.14866
13 | 0.98437 | -0.49979 | 0.31575 | 0.15292
14 | 0.98373 | -0.49681 | 0.11071 | 0.053619
15 | 0.98479 | -0.48822 | 0 | 0
16 | 0.9847 | -0.48874 | 0.11356 | 0.055
17 | 0.98488 | -0.48695 | 0.75927 | 0.36773
18 | 0.986 | -0.42093 | 0.65643 | 0.31792
19 | 0.98125 | -0.13445 | 0.37497 | 0.18161
20 | 0.98128 | -0.13471 | 0 | 0
21 | 0.98207 | -0.12951 | 0 | 0
22 | 0.98206 | -0.12945 | 0.11847 | 0.057379
23 | 0.98234 | -0.13189 | 0 | 0
24 | 0.99437 | -0.16028 | 0.36361 | 0.1761
25 | 0.99438 | -0.16031 | 0 | 0
26 | 0.98974 | -0.11236 | 0.085743 | 0.041527
27 | 0.98492 | -0.15174 | 0.31115 | 0.1507
28 | 0.99016 | -0.11559 | 0 | 0
29 | 1 | 0 | -13.3033 | -5.8913
30 | 0.99988 | -0.0022903 | 0.26848 | 0.13003
31 | 0.99912 | -0.029192 | 0 | 0
32 | 0.99911 | -0.029116 | 0.28167 | 0.13642
33 | 0.99809 | -0.049111 | 0 | 0
34 | 0.99788 | -0.05305 | 0.1089 | 0.052742
35 | 0.99789 | -0.053136 | 0 | 0
36 | 0.99708 | -0.081787 | 0 | 0
37 | 0.997 | -0.06984 | 0 | 0
38 | 0.99809 | -0.049086 | 0.10805 | 0.052332
39 | 0.99698 | -0.0697 | 0.22698 | 0.10993
40 | 0.99707 | -0.081686 | 0.12616 | 0.061101
41 | 0.99647 | -0.093778 | 0 | 0
42 | 0.98229 | -0.1322 | 0.32035 | 0.15515
43 | 0.99345 | -0.17759 | 0 | 0
44 | 0.99086 | -0.26478 | 0.14306 | 0.069287
45 | 0.99322 | -0.18383 | 0.19047 | 0.092248
46 | 0.98895 | -0.33089 | 0.1184 | 0.057343
47 | 0.99334 | -0.17689 | 0.36787 | 0.17817
48 | 0.99336 | -0.17673 | 0 | 0
49 | 0.9934 | -0.17858 | 0.13169 | 0.06378
50 | 0.99328 | -0.18284 | 0 | 0
51 | 0.98884 | -0.33291 | 0.21955 | 0.10633
52 | 0.9889 | -0.33188 | 0 | 0
53 | 0.98854 | -0.34323 | 0 | 0
54 | 0.98894 | -0.33104 | 0 | 0
55 | 0.98628 | -0.41388 | 0 | 0
56 | 0.98639 | -0.41184 | 0 | 0
57 | 0.98608 | -0.42056 | 0.37041 | 0.1794
58 | 0.98638 | -0.41181 | 0.1125 | 0.054488
59 | 0.98643 | -0.41093 | 0 | 0
60 | 0.98607 | -0.42063 | 0.095469 | 0.046238
61 | 0.98605 | -0.42071 | 0.10023 | 0.048543
62 | 0.99623 | -0.10226 | 0.344 | 0.1666
63 | 0.99618 | -0.10336 | 0 | 0
64 | 0.99536 | -0.11922 | 0 | 0
65 | 0.99523 | -0.083595 | 0 | 0
66 | 0.99511 | -0.084454 | 0.23366 | 0.11317
67 | 0.99518 | -0.12129 | 0.074402 | 0.036035
68 | 0.99506 | -0.084013 | 0 | 0
69 | 0.99158 | -0.12722 | 0.36109 | 0.17488
70 | 0.99161 | -0.12746 | 0 | 0
71 | 0.99512 | -0.12201 | 0 | 0
72 | 0.99352 | -0.070509 | 0 | 0
73 | 0.9935 | -0.070639 | 0.31719 | 0.15362
74 | 0.99002 | -0.11482 | 0.25845 | 0.12517
75 | 0.99005 | -0.11461 | 0 | 0
76 | 0.99005 | -0.1146 | 0 | 0
77 | 0.99163 | -0.12763 | 0 | 0
78 | 0.99165 | -0.12786 | 0.40959 | 0.19837
79 | 0.99005 | -0.11457 | 0.070014 | 0.033909
80 | 0.99154 | -0.12618 | 0 | 0
81 | 0.99178 | -0.12805 | 0.12264 | 0.059395
82 | 0.99202 | -0.12985 | 0 | 0
83 | 0.99174 | -0.1273 | 0 | 0
84 | 0.99408 | -0.1137 | 0 | 0
85 | 0.99173 | -0.12724 | 0.075678 | 0.036652
86 | 0.99413 | -0.1141 | 0.28387 | 0.13749
87 | 0.98309 | -0.13781 | 0 | 0
88 | 0.98221 | -0.13096 | 0 | 0
89 | 0.98491 | -0.1517 | 0 | 0
90 | 0.98486 | -0.15124 | 0 | 0
91 | 0.98309 | -0.13778 | 0.334 | 0.16176
92 | 0.98486 | -0.15121 | 0.098052 | 0.047489
93 | 0.98211 | -0.13015 | 0 | 0
94 | 0.98208 | -0.12989 | 0.2038 | 0.098706
95 | 0.98219 | -0.13106 | 0.095984 | 0.046487
96 | 0.98485 | -0.15127 | 0 | 0
97 | 0.98678 | -0.40432 | 0.28767 | 0.13932
98 | 0.98674 | -0.40515 | 0 | 0
99 | 0.98637 | -0.41038 | 0.15772 | 0.076389
100 | 0.98638 | -0.41052 | 0 | 0
101 | 0.98648 | -0.41013 | 0.30361 | 0.14704
102 | 0.98649 | -0.40984 | 0 | 0
103 | 0.98572 | -0.40408 | 0.36571 | 0.17712
104 | 0.98574 | -0.40399 | 0 | 0
105 | 0.98625 | -0.40072 | 0.15349 | 0.074337
106 | 0.98588 | -0.4031 | 0.23378 | 0.11322
107 | 0.98629 | -0.40114 | 0 | 0
108 | 0.99512 | -0.12197 | 0 | 0
109 | 0.99427 | -0.11526 | 0 | 0
110 | 0.99511 | -0.12194 | 0.11121 | 0.05386
111 | 0.98485 | -0.15123 | 0.094348 | 0.045695
112 | 0.98485 | -0.15125 | 0 | 0
113 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.20338 | 0.097874 | -0.20333 | -0.09848 | 4.1603e-05 | -0.0006051 | 0.0065779 | 0.0065859 | 0.0065859 | 0.9905 | -0.089692 | 0.99029 | -0.091057 | 3.1362
1 | -0.48044 | -0.23206 | 0.48122 | 0.23043 | 0.00077532 | -0.0016294 | 0.01555 | 0.015523 | 0.01555 | 0.9905 | -0.089692 | 0.99219 | -0.07878 | 7.4048
2 | -0.48122 | -0.23043 | 0.48123 | 0.22954 | 1.2209e-05 | -0.00088911 | 0.015523 | 0.015512 | 0.015523 | 0.99219 | -0.07878 | 0.99222 | -0.078995 | 7.0561
3 | -0.069012 | -0.033424 | 0.06904 | 0.029762 | 2.7626e-05 | -0.0036626 | 0.0022399 | 0.0021951 | 0.0022399 | 0.98827 | -0.12949 | 0.98869 | -0.1263 | 1.0666
4 | -0.26787 | -0.12606 | 0.26825 | 0.12298 | 0.00037615 | -0.0030822 | 0.0086441 | 0.0086033 | 0.0086441 | 0.98869 | -0.1263 | 0.99016 | -0.11559 | 4.1162
5 | -0.8781 | -0.42176 | 0.8792 | 0.42154 | 0.0010929 | -0.0002145 | 0.028342 | 0.02833 | 0.028342 | 0.99222 | -0.078995 | 0.99352 | -0.070509 | 13.496
6 | 0.11071 | 0.047844 | -0.11071 | -0.049573 | 1.2586e-06 | -0.0017289 | 0.0035392 | 0.0035596 | 0.0035596 | 0.98377 | -0.4971 | 0.98376 | -0.49702 | 1.618
7 | -0.33622 | -0.15706 | 0.33624 | 0.15699 | 1.4055e-05 | -6.8065e-05 | 0.010889 | 0.010888 | 0.010889 | 0.98377 | -0.4971 | 0.98381 | -0.49679 | 5.1854
8 | 0.11071 | 0.049573 | -0.11071 | -0.051272 | 1.2516e-06 | -0.0016995 | 0.0035596 | 0.0035803 | 0.0035803 | 0.98376 | -0.49702 | 0.98375 | -0.49694 | 1.6274
9 | -0.33624 | -0.15699 | 0.33642 | 0.12902 | 0.00018602 | -0.027975 | 0.010888 | 0.010567 | 0.010888 | 0.98381 | -0.49679 | 0.98433 | -0.50024 | 4.9493
10 | 0.11071 | 0.051272 | -0.11071 | -0.053619 | 1.7529e-06 | -0.0023472 | 0.0035803 | 0.0036098 | 0.0036098 | 0.98375 | -0.49694 | 0.98373 | -0.49681 | 1.6408
11 | -0.64348 | -0.25579 | 0.64351 | 0.25576 | 2.5617e-05 | -2.4283e-05 | 0.020308 | 0.020307 | 0.020308 | 0.98433 | -0.50024 | 0.98437 | -0.49979 | 9.6703
12 | 0.30706 | 0.12677 | -0.30694 | -0.14763 | 0.00011739 | -0.020867 | 0.0097424 | 0.0099924 | 0.0099924 | 0.98433 | -0.50024 | 0.98398 | -0.4975 | 4.542
13 | 0.30694 | 0.14763 | -0.30694 | -0.14866 | 5.9156e-06 | -0.0010228 | 0.0099924 | 0.010005 | 0.010005 | 0.98398 | -0.4975 | 0.98396 | -0.49733 | 4.548
14 | -0.95926 | -0.40869 | 0.95958 | 0.4086 | 0.0003189 | -8.7923e-05 | 0.030578 | 0.030572 | 0.030578 | 0.98437 | -0.49979 | 0.98479 | -0.48822 | 8.7365
15 | -1.0731 | -0.46318 | 1.0732 | 0.45771 | 9.4294e-05 | -0.0054753 | 0.034263 | 0.034199 | 0.034263 | 0.98479 | -0.48822 | 0.98488 | -0.48695 | 9.4648
16 | 0.11357 | 0.054585 | -0.11356 | -0.055 | 8.8605e-06 | -0.00041581 | 0.0036937 | 0.0036991 | 0.0036991 | 0.98479 | -0.48822 | 0.9847 | -0.48874 | 1.7615
17 | -1.8325 | -0.82544 | 1.8336 | 0.82726 | 0.0011354 | 0.0018227 | 0.058909 | 0.058895 | 0.058909 | 0.98488 | -0.48695 | 0.986 | -0.42093 | 9.1333
18 | -2.4901 | -1.1452 | 2.4902 | 1.1417 | 0.00011491 | -0.0034653 | 0.080243 | 0.0802 | 0.080243 | 0.986 | -0.42093 | 0.98605 | -0.42071 | 12.5772
19 | -0.37497 | -0.18161 | 0.37499 | 0.18027 | 1.1665e-05 | -0.0013355 | 0.012257 | 0.01224 | 0.012257 | 0.98125 | -0.13445 | 0.98128 | -0.13471 | 5.5714
20 | -0.37499 | -0.18027 | 0.37527 | 0.17922 | 0.00028472 | -0.0010503 | 0.01224 | 0.012224 | 0.01224 | 0.98128 | -0.13471 | 0.98207 | -0.12951 | 5.8286
21 | 0.11847 | 0.056487 | -0.11847 | -0.057379 | 7.7248e-07 | -0.00089233 | 0.0038581 | 0.0038694 | 0.0038694 | 0.98207 | -0.12951 | 0.98206 | -0.12945 | 1.7588
22 | -0.49374 | -0.23571 | 0.49389 | 0.22588 | 0.00014681 | -0.0098259 | 0.016082 | 0.01596 | 0.016082 | 0.98207 | -0.12951 | 0.98234 | -0.13189 | 7.3102
23 | -1.1141 | -0.50658 | 1.115 | 0.4947 | 0.00090569 | -0.011874 | 0.035965 | 0.035819 | 0.035965 | 0.98234 | -0.13189 | 0.98309 | -0.13781 | 16.3479
24 | 0.29986 | 0.12562 | -0.29982 | -0.1336 | 4.2652e-05 | -0.007974 | 0.0095538 | 0.009647 | 0.009647 | 0.98234 | -0.13189 | 0.98221 | -0.13096 | 4.385
25 | 0.32036 | 0.15507 | -0.32035 | -0.15515 | 1.4959e-05 | -7.9032e-05 | 0.010459 | 0.01046 | 0.01046 | 0.98234 | -0.13189 | 0.98229 | -0.1322 | 4.9811
26 | -0.36361 | -0.1761 | 0.36361 | 0.17593 | 1.3857e-06 | -0.00017776 | 0.011729 | 0.011727 | 0.011729 | 0.99437 | -0.16028 | 0.99438 | -0.16031 | 5.3313
27 | 5.8738 | 2.6533 | -5.8691 | -2.7034 | 0.0046314 | -0.050119 | 0.18711 | 0.18777 | 0.18777 | 0.99438 | -0.16031 | 0.99345 | -0.17759 | 22.3
28 | -6.2374 | -2.8292 | 6.2494 | 2.8443 | 0.011972 | 0.015152 | 0.19883 | 0.19881 | 0.19883 | 0.99438 | -0.16031 | 0.997 | -0.06984 | 24.2479
29 | 1.9644 | 0.87653 | -1.9554 | -0.8724 | 0.0089641 | 0.0041278 | 0.06274 | 0.062758 | 0.062758 | 0.98974 | -0.11236 | 0.98492 | -0.15174 | 29.8847
30 | -2.0501 | -0.91806 | 2.0511 | 0.91456 | 0.00092349 | -0.0034994 | 0.065517 | 0.065473 | 0.065517 | 0.98974 | -0.11236 | 0.99016 | -0.11559 | 29.7807
31 | 1.6443 | 0.72171 | -1.6443 | -0.72177 | 1.1273e-05 | -6.7263e-05 | 0.052631 | 0.052632 | 0.052632 | 0.98492 | -0.15174 | 0.98491 | -0.1517 | 23.9235
32 | -2.6478 | -1.1893 | 2.6517 | 1.1808 | 0.0038998 | -0.0084181 | 0.084624 | 0.08451 | 0.084624 | 0.99016 | -0.11559 | 0.99154 | -0.12618 | 38.4656
33 | 0.32851 | 0.15172 | -0.32847 | -0.15787 | 3.9357e-05 | -0.0061441 | 0.01055 | 0.010626 | 0.010626 | 0.99016 | -0.11559 | 0.99005 | -0.11461 | 4.83
34 | 13.2893 | 5.8808 | -13.2879 | -5.8827 | 0.0013362 | -0.0019426 | 0.41951 | 0.41955 | 0.41955 | 1 | 0 | 0.99988 | -0.0022903 | 49.8276
35 | 13.0194 | 5.7527 | -13.0122 | -5.7425 | 0.0072577 | 0.010196 | 0.41094 | 0.41095 | 0.41095 | 0.99988 | -0.0022903 | 0.99912 | -0.029192 | 50.1152
36 | 0.28167 | 0.13588 | -0.28167 | -0.13642 | 2.4723e-06 | -0.00053946 | 0.0090359 | 0.0090427 | 0.0090427 | 0.99912 | -0.029192 | 0.99911 | -0.029116 | 4.1103
37 | 12.7305 | 5.6066 | -12.7194 | -5.625 | 0.011087 | -0.018374 | 0.40191 | 0.40225 | 0.40225 | 0.99912 | -0.029192 | 0.99809 | -0.049111 | 47.7729
38 | 6.4824 | 2.8992 | -6.4763 | -2.953 | 0.006051 | -0.053837 | 0.20538 | 0.20609 | 0.20609 | 0.99809 | -0.049111 | 0.997 | -0.06984 | 24.4765
39 | 0.10805 | 0.05188 | -0.10805 | -0.052332 | 3.0584e-07 | -0.00045256 | 0.0034667 | 0.0034724 | 0.0034724 | 0.99809 | -0.049111 | 0.99809 | -0.049086 | 1.5784
40 | 6.129 | 2.6739 | -6.1279 | -2.6848 | 0.0010666 | -0.01087 | 0.1934 | 0.19354 | 0.19354 | 0.99809 | -0.049111 | 0.99789 | -0.053136 | 22.9857
41 | -0.1089 | -0.052742 | 0.1089 | 0.051118 | 1.111e-06 | -0.0016239 | 0.0035004 | 0.0034801 | 0.0035004 | 0.99788 | -0.05305 | 0.99789 | -0.053136 | 1.5911
42 | 6.019 | 2.6337 | -6.0155 | -2.6293 | 0.0035472 | 0.004426 | 0.19006 | 0.19007 | 0.19007 | 0.99789 | -0.053136 | 0.99708 | -0.081787 | 23.1791
43 | 0.12616 | 0.059465 | -0.12616 | -0.061101 | 1.508e-06 | -0.0016358 | 0.0040379 | 0.0040584 | 0.0040584 | 0.99708 | -0.081787 | 0.99707 | -0.081686 | 1.8447
44 | 5.8893 | 2.5698 | -5.8862 | -2.6037 | 0.003071 | -0.033906 | 0.18603 | 0.18646 | 0.18646 | 0.99708 | -0.081787 | 0.99647 | -0.093778 | 22.1449
45 | 0.22698 | 0.1087 | -0.22698 | -0.10993 | 3.6862e-06 | -0.0012305 | 0.0072868 | 0.0073023 | 0.0073023 | 0.997 | -0.06984 | 0.99698 | -0.0697 | 3.3192
46 | 1.4342 | 0.64877 | -1.4323 | -0.66441 | 0.0019083 | -0.015641 | 0.045601 | 0.045796 | 0.045796 | 0.99647 | -0.093778 | 0.99523 | -0.083595 | 20.8166
47 | 4.4521 | 1.9549 | -4.4513 | -1.9541 | 0.00077925 | 0.00084503 | 0.14086 | 0.14086 | 0.14086 | 0.99647 | -0.093778 | 0.99623 | -0.10226 | 17.1786
48 | 5.5012 | 2.5299 | -5.501 | -2.533 | 0.00025106 | -0.0031103 | 0.17595 | 0.17599 | 0.17599 | 0.99345 | -0.17759 | 0.9934 | -0.17858 | 20.9011
49 | 0.36792 | 0.17346 | -0.36788 | -0.17813 | 3.7231e-05 | -0.0046695 | 0.01182 | 0.011878 | 0.011878 | 0.99345 | -0.17759 | 0.99336 | -0.17673 | 5.3992
50 | -5.1691 | -2.369 | 5.1781 | 2.3796 | 0.0089481 | 0.010624 | 0.16566 | 0.16563 | 0.16566 | 0.99086 | -0.26478 | 0.99322 | -0.18383 | 20.2022
51 | 5.0261 | 2.2997 | -5.019 | -2.2914 | 0.0070717 | 0.0082976 | 0.16103 | 0.16105 | 0.16105 | 0.99086 | -0.26478 | 0.98895 | -0.33089 | 19.6404
52 | -5.3686 | -2.4719 | 5.3688 | 2.4687 | 0.0002456 | -0.0032036 | 0.17178 | 0.17174 | 0.17178 | 0.99322 | -0.18383 | 0.99328 | -0.18284 | 20.4013
53 | 4.9006 | 2.2341 | -4.9006 | -2.2346 | 3.3346e-05 | -0.00052027 | 0.15721 | 0.15722 | 0.15722 | 0.98895 | -0.33089 | 0.98894 | -0.33104 | 18.6721
54 | -0.36787 | -0.17817 | 0.36788 | 0.17813 | 8.7039e-06 | -3.5333e-05 | 0.011879 | 0.011878 | 0.011879 | 0.99334 | -0.17689 | 0.99336 | -0.17673 | 5.6565
55 | 5.3693 | 2.4692 | -5.3688 | -2.4687 | 0.00048997 | 0.00059032 | 0.17174 | 0.17174 | 0.17174 | 0.9934 | -0.17858 | 0.99328 | -0.18284 | 20.9436
56 | -4.9002 | -2.2411 | 4.9004 | 2.2375 | 0.00023123 | -0.0036039 | 0.1573 | 0.15726 | 0.1573 | 0.98884 | -0.33291 | 0.9889 | -0.33188 | 18.682
57 | 4.6806 | 2.1348 | -4.6796 | -2.1336 | 0.0010266 | 0.0011632 | 0.15018 | 0.15019 | 0.15019 | 0.98884 | -0.33291 | 0.98854 | -0.34323 | 18.3155
58 | -4.9004 | -2.2375 | 4.9006 | 2.2346 | 0.00018631 | -0.0029058 | 0.15726 | 0.15722 | 0.15726 | 0.9889 | -0.33188 | 0.98894 | -0.33104 | 18.6765
59 | 4.6796 | 2.1336 | -4.6735 | -2.1267 | 0.0060681 | 0.0068796 | 0.15019 | 0.15021 | 0.15021 | 0.98854 | -0.34323 | 0.98678 | -0.40432 | 18.3183
60 | -3.0568 | -1.4141 | 3.0571 | 1.4022 | 0.00028955 | -0.011854 | 0.09858 | 0.098432 | 0.09858 | 0.98628 | -0.41388 | 0.98639 | -0.41184 | 11.7079
61 | 3.0568 | 1.4141 | -3.0564 | -1.4138 | 0.00043893 | 0.00031644 | 0.09858 | 0.098584 | 0.098584 | 0.98628 | -0.41388 | 0.98608 | -0.42056 | 12.0225
62 | 0.1125 | 0.05409 | -0.1125 | -0.054488 | 3.0539e-07 | -0.00039752 | 0.0036533 | 0.0036584 | 0.0036584 | 0.98639 | -0.41184 | 0.98638 | -0.41181 | 1.6629
63 | -3.1696 | -1.4563 | 3.1697 | 1.4513 | 0.00013179 | -0.0050195 | 0.10208 | 0.10202 | 0.10208 | 0.98639 | -0.41184 | 0.98643 | -0.41093 | 12.1241
64 | 2.686 | 1.2344 | -2.6859 | -1.2354 | 3.9378e-05 | -0.0010173 | 0.086538 | 0.08655 | 0.08655 | 0.98608 | -0.42056 | 0.98607 | -0.42063 | 13.5659
65 | -3.3275 | -1.5201 | 3.3276 | 1.5159 | 0.00012174 | -0.0042059 | 0.10706 | 0.107 | 0.10706 | 0.98643 | -0.41093 | 0.98648 | -0.41013 | 12.7146
66 | 0.15774 | 0.068775 | -0.15773 | -0.07463 | 8.6546e-06 | -0.0058551 | 0.0050358 | 0.0051067 | 0.0051067 | 0.98643 | -0.41093 | 0.98638 | -0.41052 | 2.3212
67 | 2.5905 | 1.1892 | -2.5904 | -1.1903 | 3.9276e-05 | -0.0010929 | 0.083446 | 0.083459 | 0.083459 | 0.98607 | -0.42063 | 0.98605 | -0.42071 | 13.0814
68 | 4.1073 | 1.7875 | -4.1071 | -1.7921 | 0.00019486 | -0.0046115 | 0.1298 | 0.12985 | 0.12985 | 0.99623 | -0.10226 | 0.99618 | -0.10336 | 15.422
69 | 4.1071 | 1.7921 | -4.1042 | -1.8596 | 0.0028751 | -0.067504 | 0.12985 | 0.13068 | 0.13068 | 0.99618 | -0.10336 | 0.99536 | -0.11922 | 15.5201
70 | 4.1042 | 1.8596 | -4.1036 | -1.8618 | 0.00065594 | -0.0022251 | 0.13068 | 0.13071 | 0.13071 | 0.99536 | -0.11922 | 0.99518 | -0.12129 | 36.1082
71 | 1.4323 | 0.66441 | -1.4321 | -0.66436 | 0.00016063 | 4.9792e-05 | 0.045796 | 0.045797 | 0.045797 | 0.99523 | -0.083595 | 0.99511 | -0.084454 | 21.8081
72 | 1.1984 | 0.55119 | -1.1984 | -0.552 | 6.8348e-05 | -0.00080608 | 0.038267 | 0.038277 | 0.038277 | 0.99511 | -0.084454 | 0.99506 | -0.084013 | 17.3986
73 | 4.0292 | 1.8258 | -4.0289 | -1.8266 | 0.00022186 | -0.00078651 | 0.12831 | 0.12833 | 0.12833 | 0.99518 | -0.12129 | 0.99512 | -0.12201 | 35.4491
74 | 1.1984 | 0.552 | -1.1964 | -0.57513 | 0.0019805 | -0.023133 | 0.038277 | 0.03857 | 0.03857 | 0.99506 | -0.084013 | 0.99352 | -0.070509 | 17.5319
75 | -0.36109 | -0.17488 | 0.3611 | 0.17363 | 9.7426e-06 | -0.0012546 | 0.01168 | 0.011664 | 0.01168 | 0.99158 | -0.12722 | 0.99161 | -0.12746 | 5.3092
76 | -0.3611 | -0.17363 | 0.36111 | 0.17267 | 7.4466e-06 | -0.00096131 | 0.011664 | 0.011652 | 0.011664 | 0.99161 | -0.12746 | 0.99163 | -0.12763 | 5.302
77 | 0.11121 | 0.052673 | -0.11121 | -0.053435 | 5.4974e-07 | -0.00076192 | 0.0035696 | 0.0035791 | 0.0035791 | 0.99512 | -0.12201 | 0.99512 | -0.12197 | 1.6269
78 | 3.9177 | 1.7739 | -3.9142 | -1.7769 | 0.0035459 | -0.0029781 | 0.12476 | 0.12481 | 0.12481 | 0.99512 | -0.12201 | 0.99427 | -0.11526 | 56.7296
79 | 0.3172 | 0.15359 | -0.31719 | -0.15362 | 6.2562e-06 | -3.5539e-05 | 0.01024 | 0.01024 | 0.01024 | 0.99352 | -0.070509 | 0.9935 | -0.070639 | 4.8764
80 | -0.25845 | -0.12517 | 0.25845 | 0.1251 | 8.2235e-06 | -7.189e-05 | 0.0083732 | 0.0083723 | 0.0083732 | 0.99002 | -0.11482 | 0.99005 | -0.11461 | 3.9873
81 | 0.070015 | 0.032766 | -0.070014 | -0.033239 | 1.3729e-07 | -0.00047245 | 0.002254 | 0.0022598 | 0.0022598 | 0.99005 | -0.11461 | 0.99005 | -0.1146 | 1.0272
82 | 0.070014 | 0.033239 | -0.070014 | -0.033909 | 1.9615e-07 | -0.00067078 | 0.0022598 | 0.0022683 | 0.0022683 | 0.99005 | -0.1146 | 0.99005 | -0.11457 | 1.031
83 | -0.36111 | -0.17267 | 0.36112 | 0.1714 | 9.7771e-06 | -0.0012653 | 0.011652 | 0.011636 | 0.011652 | 0.99163 | -0.12763 | 0.99165 | -0.12786 | 5.2965
84 | -0.77071 | -0.36978 | 0.77077 | 0.36975 | 6.3122e-05 | -2.7636e-05 | 0.024884 | 0.024883 | 0.024884 | 0.99165 | -0.12786 | 0.99174 | -0.1273 | 11.8497
85 | -2.6517 | -1.1808 | 2.6524 | 1.1793 | 0.00069877 | -0.0015139 | 0.08451 | 0.08449 | 0.08451 | 0.99154 | -0.12618 | 0.99178 | -0.12805 | 38.4138
86 | -2.775 | -1.2387 | 2.7757 | 1.2374 | 0.00070105 | -0.001369 | 0.088454 | 0.088435 | 0.088454 | 0.99178 | -0.12805 | 0.99202 | -0.12985 | 40.2064
87 | 0.84671 | 0.39868 | -0.84645 | -0.40475 | 0.00025943 | -0.0060606 | 0.027234 | 0.02731 | 0.02731 | 0.99202 | -0.12985 | 0.99174 | -0.1273 | 12.4138
88 | -3.6225 | -1.636 | 3.6295 | 1.6401 | 0.007049 | 0.0040671 | 0.11566 | 0.11566 | 0.11566 | 0.99202 | -0.12985 | 0.99408 | -0.1137 | 55.0784
89 | 0.075678 | 0.034997 | -0.075678 | -0.036652 | 5.5889e-07 | -0.0016549 | 0.002427 | 0.0024476 | 0.0024476 | 0.99174 | -0.1273 | 0.99173 | -0.12724 | 1.1125
90 | -3.6295 | -1.6401 | 3.6297 | 1.6399 | 0.00019789 | -0.00020276 | 0.11566 | 0.11566 | 0.11566 | 0.99408 | -0.1137 | 0.99413 | -0.1141 | 52.573
91 | -3.9136 | -1.7774 | 3.9142 | 1.7769 | 0.00060911 | -0.00051056 | 0.12481 | 0.12481 | 0.12481 | 0.99413 | -0.1141 | 0.99427 | -0.11526 | 56.7334
92 | 0.334 | 0.16165 | -0.334 | -0.16176 | 7.7859e-07 | -0.00011312 | 0.010896 | 0.010897 | 0.010897 | 0.98309 | -0.13781 | 0.98309 | -0.13778 | 4.9533
93 | -1.449 | -0.65635 | 1.4519 | 0.63453 | 0.002839 | -0.021823 | 0.04671 | 0.04644 | 0.04671 | 0.98309 | -0.13781 | 0.98491 | -0.1517 | 21.232
94 | 0.095986 | 0.046397 | -0.095984 | -0.046487 | 1.3785e-06 | -8.9862e-05 | 0.0031333 | 0.0031345 | 0.0031345 | 0.98221 | -0.13096 | 0.98219 | -0.13106 | 1.4926
95 | 0.20383 | 0.0872 | -0.20381 | -0.096287 | 2.2751e-05 | -0.0090874 | 0.0065158 | 0.0066255 | 0.0066255 | 0.98221 | -0.13096 | 0.98211 | -0.13015 | 3.0116
96 | 0.19241 | 0.087242 | -0.1924 | -0.092179 | 1.1025e-05 | -0.0049367 | 0.0061922 | 0.0062534 | 0.0062534 | 0.98491 | -0.1517 | 0.98486 | -0.15124 | 2.8424
97 | 0.1924 | 0.092179 | -0.1924 | -0.092486 | 6.9198e-07 | -0.00030658 | 0.0062534 | 0.0062572 | 0.0062572 | 0.98486 | -0.15124 | 0.98486 | -0.15121 | 2.8442
98 | 0.094349 | 0.044997 | -0.094348 | -0.045052 | 8.0401e-07 | -5.5145e-05 | 0.0030639 | 0.0030646 | 0.0030646 | 0.98486 | -0.15121 | 0.98485 | -0.15127 | 1.4593
99 | 0.20381 | 0.096287 | -0.2038 | -0.098706 | 6.1882e-06 | -0.0024187 | 0.0066255 | 0.0066562 | 0.0066562 | 0.98211 | -0.13015 | 0.98208 | -0.12989 | 3.0256
100 | 0.094348 | 0.045052 | -0.094348 | -0.045472 | 2.2778e-07 | -0.00041992 | 0.0030646 | 0.0030699 | 0.0030699 | 0.98485 | -0.15127 | 0.98485 | -0.15125 | 1.3954
101 | 4.3858 | 1.9874 | -4.3857 | -1.9906 | 0.00016403 | -0.0032091 | 0.14086 | 0.1409 | 0.1409 | 0.98678 | -0.40432 | 0.98674 | -0.40515 | 16.7343
102 | 0.75365 | 0.35143 | -0.75328 | -0.36199 | 0.00036458 | -0.010556 | 0.024328 | 0.024461 | 0.024461 | 0.98674 | -0.40515 | 0.98629 | -0.40114 | 11.1187
103 | 3.632 | 1.6392 | -3.6313 | -1.6616 | 0.00077469 | -0.0224 | 0.11658 | 0.11686 | 0.11686 | 0.98674 | -0.40515 | 0.98649 | -0.40984 | 13.8784
104 | -0.15772 | -0.076389 | 0.15773 | 0.07463 | 2.6501e-06 | -0.0017599 | 0.0051289 | 0.0051067 | 0.0051289 | 0.98637 | -0.41038 | 0.98638 | -0.41052 | 2.3313
105 | -3.6312 | -1.6629 | 3.6313 | 1.6616 | 4.7424e-05 | -0.0013673 | 0.11687 | 0.11686 | 0.11687 | 0.98648 | -0.41013 | 0.98649 | -0.40984 | 13.8805
106 | -0.36571 | -0.17712 | 0.36572 | 0.17711 | 4.6583e-06 | -1.8498e-05 | 0.0119 | 0.0119 | 0.0119 | 0.98572 | -0.40408 | 0.98574 | -0.40399 | 5.6668
107 | -0.36572 | -0.17711 | 0.3659 | 0.17639 | 0.00018009 | -0.00071633 | 0.0119 | 0.011889 | 0.0119 | 0.98574 | -0.40399 | 0.98625 | -0.40072 | 5.6666
108 | 0.23386 | 0.11234 | -0.23378 | -0.11322 | 8.3277e-05 | -0.00088719 | 0.0075939 | 0.0076058 | 0.0076058 | 0.98625 | -0.40072 | 0.98588 | -0.4031 | 3.6218
109 | -0.75325 | -0.36306 | 0.75328 | 0.36199 | 3.7257e-05 | -0.0010716 | 0.024475 | 0.024461 | 0.024475 | 0.98625 | -0.40072 | 0.98629 | -0.40114 | 11.125
110 | 0.11121 | 0.053435 | -0.11121 | -0.05386 | 3.0801e-07 | -0.00042511 | 0.0035791 | 0.0035845 | 0.0035845 | 0.99512 | -0.12197 | 0.99511 | -0.12194 | 1.6293
111 | -0.094348 | -0.045695 | 0.094348 | 0.045472 | 1.211e-07 | -0.00022263 | 0.0030728 | 0.0030699 | 0.0030728 | 0.98485 | -0.15123 | 0.98485 | -0.15125 | 1.3967

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 13.4957 | 5.9845

## res_load
| p_mw | q_mvar
0 | 0.27707 | 0.13419
1 | 0.20333 | 0.09848
2 | 0.069012 | 0.033424
3 | 0.19883 | 0.096299
4 | 0.39687 | 0.19221
5 | 0.22551 | 0.10922
6 | 0.30694 | 0.14866
7 | 0.31575 | 0.15292
8 | 0.11071 | 0.053619
9 | 0.11356 | 0.055
10 | 0.75927 | 0.36773
11 | 0.65643 | 0.31792
12 | 0.37497 | 0.18161
13 | 0.11847 | 0.057379
14 | 0.36361 | 0.1761
15 | 0.085743 | 0.041527
16 | 0.31115 | 0.1507
17 | 0.19241 | 0.093189
18 | 0.26848 | 0.13003
19 | 0.28167 | 0.13642
20 | 0.1089 | 0.052742
21 | 0.10805 | 0.052332
22 | 0.22698 | 0.10993
23 | 0.12616 | 0.061101
24 | 0.32035 | 0.15515
25 | 0.14306 | 0.069287
26 | 0.19047 | 0.092248
27 | 0.1184 | 0.057343
28 | 0.36787 | 0.17817
29 | 0.13169 | 0.06378
30 | 0.21955 | 0.10633
31 | 0.37041 | 0.1794
32 | 0.1125 | 0.054488
33 | 0.095469 | 0.046238
34 | 0.10023 | 0.048543
35 | 0.344 | 0.1666
36 | 0.23366 | 0.11317
37 | 0.074402 | 0.036035
38 | 0.36109 | 0.17488
39 | 0.31719 | 0.15362
40 | 0.25845 | 0.12517
41 | 0.40959 | 0.19837
42 | 0.070014 | 0.033909
43 | 0.12264 | 0.059395
44 | 0.075678 | 0.036652
45 | 0.28387 | 0.13749
46 | 0.334 | 0.16176
47 | 0.098052 | 0.047489
48 | 0.2038 | 0.098706
49 | 0.095984 | 0.046487
50 | 0.28767 | 0.13932
51 | 0.15772 | 0.076389
52 | 0.30361 | 0.14704
53 | 0.36571 | 0.17712
54 | 0.15349 | 0.074337
55 | 0.23378 | 0.11322
56 | 0.11121 | 0.05386
57 | 0.094348 | 0.045695

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1