## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_315_1_node_3 | 20 | n |  | TRUE
1 | bus_MV_315_1_node_33 | 20 | n |  | TRUE
2 | bus_MV_315_1_node_5 | 20 | n |  | TRUE
3 | bus_MV_315_1_node_6 | 20 | n |  | TRUE
4 | bus_MV_315_1_node_82 | 20 | n |  | TRUE
5 | bus_MV_315_1_node_7 | 20 | n |  | TRUE
6 | bus_MV_315_1_node_166 | 20 | n |  | TRUE
7 | bus_MV_315_1_node_11 | 20 | n |  | TRUE
8 | bus_MV_315_1_node_13 | 20 | n |  | TRUE
9 | bus_MV_315_1_node_16 | 20 | n |  | TRUE
10 | bus_MV_315_1_node_14 | 20 | n |  | TRUE
11 | bus_MV_315_1_node_15 | 20 | n |  | TRUE
12 | bus_MV_315_1_node_154 | 20 | n |  | TRUE
13 | bus_MV_315_1_node_17 | 20 | n |  | TRUE
14 | bus_MV_315_1_node_26 | 20 | n |  | TRUE
15 | bus_MV_315_1_node_20 | 20 | n |  | TRUE
16 | bus_MV_315_1_node_18 | 20 | n |  | TRUE
17 | bus_MV_315_1_node_19 | 20 | n |  | TRUE
18 | bus_MV_315_1_node_190 | 20 | n |  | TRUE
19 | bus_MV_315_1_node_55 | 20 | n |  | TRUE
20 | bus_MV_315_1_node_21 | 20 | n |  | TRUE
21 | bus_MV_315_1_node_22 | 20 | n |  | TRUE
22 | bus_MV_315_1_node_106 | 20 | n |  | TRUE
23 | bus_MV_315_1_node_112 | 20 | n |  | TRUE
24 | bus_MV_315_1_node_24 | 20 | n |  | TRUE
25 | bus_MV_315_1_node_25 | 20 | n |  | TRUE
26 | bus_MV_315_1_node_27 | 20 | n |  | TRUE
27 | bus_MV_315_1_node_107 | 20 | n |  | TRUE
28 | bus_MV_315_1_node_177 | 20 | n |  | TRUE
29 | bus_MV_315_1_node_28 | 20 | n |  | TRUE
30 | bus_MV_315_1_node_172 | 20 | n |  | TRUE
31 | bus_MV_315_1_node_29 | 20 | n |  | TRUE
32 | bus_MV_315_1_node_30 | 20 | n |  | TRUE
33 | bus_MV_315_1_node_31 | 20 | n |  | TRUE
34 | bus_MV_315_1_node_32 | 20 | n |  | TRUE
35 | bus_MV_315_1_node_118 | 20 | n |  | TRUE
36 | bus_MV_315_1_node_161 | 20 | n |  | TRUE
37 | bus_MV_315_1_node_34 | 20 | n |  | TRUE
38 | bus_MV_315_1_node_168 | 20 | n |  | TRUE
39 | bus_MV_315_1_node_59 | 20 | n |  | TRUE
40 | bus_MV_315_1_node_60 | 20 | n |  | TRUE
41 | bus_MV_315_1_node_61 | 20 | n |  | TRUE
42 | bus_MV_315_1_node_62 | 20 | n |  | TRUE
43 | bus_MV_315_1_node_73 | 20 | n |  | TRUE
44 | bus_MV_315_1_node_63 | 20 | n |  | TRUE
45 | bus_MV_315_1_node_64 | 20 | n |  | TRUE
46 | bus_MV_315_1_node_65 | 20 | n |  | TRUE
47 | bus_MV_315_1_node_67 | 20 | n |  | TRUE
48 | bus_MV_315_1_node_66 | 20 | n |  | TRUE
49 | bus_MV_315_1_node_71 | 20 | n |  | TRUE
50 | bus_MV_315_1_node_152 | 20 | n |  | TRUE
51 | bus_MV_315_1_node_150 | 20 | n |  | TRUE
52 | bus_MV_315_1_node_68 | 20 | n |  | TRUE
53 | bus_MV_315_1_node_149 | 20 | n |  | TRUE
54 | bus_MV_315_1_node_69 | 20 | n |  | TRUE
55 | bus_MV_315_1_node_70 | 20 | n |  | TRUE
56 | bus_MV_315_1_node_72 | 20 | n |  | TRUE
57 | bus_MV_315_1_node_76 | 20 | n |  | TRUE
58 | bus_MV_315_1_node_151 | 20 | n |  | TRUE
59 | bus_MV_315_1_node_156 | 20 | n |  | TRUE
60 | bus_MV_315_1_node_74 | 20 | n |  | TRUE
61 | bus_MV_315_1_node_187 | 20 | n |  | TRUE
62 | bus_MV_315_1_node_75 | 20 | n |  | TRUE
63 | bus_MV_315_1_node_165 | 20 | n |  | TRUE
64 | bus_MV_315_1_node_170 | 20 | n |  | TRUE
65 | bus_MV_315_1_node_77 | 20 | n |  | TRUE
66 | bus_MV_315_1_node_78 | 20 | n |  | TRUE
67 | bus_MV_315_1_node_79 | 20 | n |  | TRUE
68 | bus_MV_315_1_node_80 | 20 | n |  | TRUE
69 | bus_MV_315_1_node_83 | 20 | n |  | TRUE
70 | bus_MV_315_1_node_81 | 20 | n |  | TRUE
71 | bus_MV_315_1_node_157 | 20 | n |  | TRUE
72 | bus_MV_315_1_node_84 | 20 | n |  | TRUE
73 | bus_MV_315_1_node_155 | 20 | n |  | TRUE
74 | bus_MV_315_1_node_85 | 20 | n |  | TRUE
75 | bus_MV_315_1_node_86 | 20 | n |  | TRUE
76 | bus_MV_315_1_node_108 | 20 | n |  | TRUE
77 | bus_MV_315_1_node_109 | 20 | n |  | TRUE
78 | bus_MV_315_1_node_110 | 20 | n |  | TRUE
79 | bus_MV_315_1_node_111 | 20 | n |  | TRUE
80 | bus_MV_315_1_node_113 | 20 | n |  | TRUE
81 | bus_MV_315_1_node_160 | 20 | n |  | TRUE
82 | bus_MV_315_1_node_167 | 20 | n |  | TRUE
83 | bus_MV_315_1_node_169 | 20 | n |  | TRUE
84 | bus_HV_315_1_node_72 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_315_1_load_3 | 0 | 0.28725 | 0.13912 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_315_1_load_5 | 2 | 0.22462 | 0.10879 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_315_1_load_7 | 5 | 0.24268 | 0.11754 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_315_1_load_166 | 6 | 0.31469 | 0.15241 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_315_1_load_11 | 7 | 0.37533 | 0.18178 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_315_1_load_154 | 12 | 0.28447 | 0.13777 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_315_1_load_17 | 13 | 0.39276 | 0.19022 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_315_1_load_20 | 15 | 0.26476 | 0.12823 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_315_1_load_18 | 16 | 0.067549 | 0.032716 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_315_1_load_190 | 18 | 0.28618 | 0.1386 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_315_1_load_55 | 19 | 0.26612 | 0.12889 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_315_1_load_106 | 22 | 0.079166 | 0.038342 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_315_1_load_112 | 23 | 0.086692 | 0.041987 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_315_1_load_24 | 24 | 0.1586 | 0.076815 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_315_1_load_107 | 27 | 0.069828 | 0.033819 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_315_1_load_177 | 28 | 0.28351 | 0.13731 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_315_1_load_172 | 30 | 0.23076 | 0.11176 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_315_1_load_29 | 31 | 0.32465 | 0.15723 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_315_1_load_118 | 35 | 0.097315 | 0.047132 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_315_1_load_161 | 36 | 0.39971 | 0.19359 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_315_1_load_34 | 37 | 0.30452 | 0.14749 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_315_1_load_59 | 39 | 0.30158 | 0.14606 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_315_1_load_62 | 42 | 0.22698 | 0.10993 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_315_1_load_63 | 44 | 0.20417 | 0.098883 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_315_1_load_152 | 50 | 0.083784 | 0.040579 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_315_1_load_150 | 51 | 1.2035 | 0.58288 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_315_1_load_149 | 53 | 0.12659 | 0.061309 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_315_1_load_69 | 54 | 0.1973 | 0.095558 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_315_1_load_151 | 58 | 0.069136 | 0.033484 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_315_1_load_156 | 59 | 0.16809 | 0.08141 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_315_1_load_187 | 61 | 0.40806 | 0.19763 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_315_1_load_165 | 63 | 0.23952 | 0.11601 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_315_1_load_170 | 64 | 0.35069 | 0.16985 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_315_1_load_77 | 65 | 0.31897 | 0.15448 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_315_1_load_81 | 70 | 0.15977 | 0.077382 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_315_1_load_157 | 71 | 0.085549 | 0.041433 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_315_1_load_84 | 72 | 0.23517 | 0.1139 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_315_1_load_155 | 73 | 0.31481 | 0.15247 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_315_1_load_85 | 74 | 0.21997 | 0.10654 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_315_1_load_108 | 76 | 0.36267 | 0.17565 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_315_1_load_113 | 80 | 0.086624 | 0.041954 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_315_1_load_160 | 81 | 0.079211 | 0.038364 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_315_1_load_169 | 83 | 0.13178 | 0.063826 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 56 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_315_1_line_0 |  | 0 | 1 | 1.9264 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_315_1_line_1 |  | 1 | 37 | 0.023076 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_315_1_line_2 |  | 1 | 3 | 1.9936 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_315_1_line_3 |  | 1 | 34 | 0.61078 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_315_1_line_4 |  | 2 | 3 | 0.055023 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_315_1_line_5 |  | 2 | 4 | 1.6549 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
6 | MV_315_1_line_6 |  | 4 | 69 | 0.51867 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
7 | MV_315_1_line_7 |  | 4 | 72 | 0.13629 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_315_1_line_8 |  | 5 | 6 | 2.1461 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_315_1_line_9 |  | 6 | 82 | 0.01393 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_315_1_line_10 |  | 7 | 8 | 0.027238 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_315_1_line_11 |  | 8 | 9 | 0.12236 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_315_1_line_12 |  | 9 | 15 | 0.015194 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_315_1_line_13 |  | 10 | 11 | 0.28379 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_315_1_line_14 |  | 10 | 12 | 0.037853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_315_1_line_15 |  | 11 | 13 | 0.12525 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_315_1_line_16 |  | 11 | 14 | 0.2307 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_315_1_line_17 |  | 12 | 26 | 0.05218 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_315_1_line_18 |  | 14 | 28 | 0.033523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_315_1_line_19 |  | 15 | 20 | 0.020568 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_315_1_line_20 |  | 16 | 17 | 0.047743 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_315_1_line_21 |  | 16 | 18 | 0.69131 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
22 | MV_315_1_line_22 |  | 17 | 19 | 1.5871 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_315_1_line_23 |  | 18 | 79 | 0.016531 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
24 | MV_315_1_line_24 |  | 19 | 38 | 1.723 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_315_1_line_25 |  | 20 | 21 | 0.10015 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
26 | MV_315_1_line_26 |  | 20 | 22 | 0.68894 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
27 | MV_315_1_line_27 |  | 21 | 23 | 0.005698 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
28 | MV_315_1_line_28 |  | 22 | 47 | 0.41998 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
29 | MV_315_1_line_29 |  | 23 | 30 | 0.099235 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
30 | MV_315_1_line_30 |  | 24 | 25 | 0.03428 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_315_1_line_31 |  | 25 | 26 | 0.93604 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
32 | MV_315_1_line_32 |  | 25 | 27 | 0.41307 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
33 | MV_315_1_line_33 |  | 26 | 29 | 0.15896 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
34 | MV_315_1_line_34 |  | 27 | 76 | 0.046106 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
35 | MV_315_1_line_35 |  | 29 | 30 | 0.005073 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
36 | MV_315_1_line_36 |  | 31 | 32 | 0.065981 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_315_1_line_37 |  | 32 | 33 | 0.01168 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_315_1_line_38 |  | 32 | 34 | 0.10328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_315_1_line_39 |  | 33 | 35 | 0.027325 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_315_1_line_40 |  | 34 | 36 | 0.017005 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_315_1_line_41 |  | 38 | 83 | 0.040279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_315_1_line_42 |  | 38 | 82 | 0.67374 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_315_1_line_43 |  | 39 | 40 | 0.018377 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_315_1_line_44 |  | 40 | 41 | 0.031166 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_315_1_line_45 |  | 41 | 42 | 0.040124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_315_1_line_46 |  | 42 | 43 | 0.045858 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_315_1_line_47 |  | 43 | 60 | 0.70616 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_315_1_line_48 |  | 43 | 55 | 0.69089 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_315_1_line_49 |  | 44 | 45 | 0.014544 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_315_1_line_50 |  | 45 | 46 | 0.2662 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
51 | MV_315_1_line_51 |  | 45 | 47 | 0.34203 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
52 | MV_315_1_line_52 |  | 46 | 48 | 0.20254 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_315_1_line_53 |  | 46 | 49 | 0.54824 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
54 | MV_315_1_line_54 |  | 46 | 50 | 0.18782 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_315_1_line_55 |  | 47 | 52 | 0.32262 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_315_1_line_56 |  | 48 | 51 | 0.094814 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_315_1_line_57 |  | 49 | 56 | 0.22311 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
58 | MV_315_1_line_58 |  | 49 | 57 | 0.50369 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
59 | MV_315_1_line_59 |  | 49 | 58 | 0.029511 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_315_1_line_60 |  | 52 | 53 | 0.071222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_315_1_line_61 |  | 54 | 55 | 0.038203 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_315_1_line_62 |  | 55 | 56 | 0.46178 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_315_1_line_63 |  | 56 | 59 | 0.02346 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_315_1_line_64 |  | 57 | 64 | 0.032107 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
65 | MV_315_1_line_65 |  | 57 | 62 | 0.38808 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_315_1_line_66 |  | 60 | 61 | 0.063933 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_315_1_line_67 |  | 62 | 63 | 0.055785 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_315_1_line_68 |  | 64 | 75 | 0.47115 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
69 | MV_315_1_line_69 |  | 65 | 66 | 0.064054 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
70 | MV_315_1_line_70 |  | 66 | 67 | 0.67978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_315_1_line_71 |  | 67 | 68 | 0.76616 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_315_1_line_72 |  | 67 | 69 | 0.35126 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_315_1_line_73 |  | 67 | 70 | 0.13576 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
74 | MV_315_1_line_74 |  | 68 | 71 | 0.10232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_315_1_line_75 |  | 69 | 73 | 0.040535 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
76 | MV_315_1_line_76 |  | 71 | 81 | 0.33841 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
77 | MV_315_1_line_77 |  | 73 | 74 | 0.45014 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
78 | MV_315_1_line_78 |  | 74 | 75 | 0.077038 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
79 | MV_315_1_line_79 |  | 76 | 77 | 0.020818 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
80 | MV_315_1_line_80 |  | 77 | 78 | 0.011145 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_315_1_line_81 |  | 77 | 79 | 0.3758 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
82 | MV_315_1_line_82 |  | 78 | 80 | 0.039615 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_315_1_trafo_72 | 25 MVA 110/20 kV | 84 | 56 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2534028.8492 | 1164376.1543
1 | 2532221.2172 | 1163710.1594
2 | 2532869.38 | 1161774.0963
3 | 2532879.1268 | 1161828.2397
4 | 2531294.6539 | 1161265.3151
5 | 2526044.5324 | 1163282.9692
6 | 2527234.4138 | 1161496.9888
7 | 2528765.5388 | 1162977.1642
8 | 2528749.2836 | 1162955.3337
9 | 2528737.6939 | 1162845.1534
10 | 2528700.214 | 1163044.8224
11 | 2528593.5849 | 1163223.9022
12 | 2528662.289 | 1163046.4183
13 | 2528626.7978 | 1163344.6644
14 | 2528381.7736 | 1163132.4739
15 | 2528738.2184 | 1162829.972
16 | 2528798.336 | 1161421.1636
17 | 2528845.1118 | 1161410.9589
18 | 2528732.0028 | 1162109.2833
19 | 2528710.583 | 1159829.6081
20 | 2528739.6604 | 1162809.4766
21 | 2528674.7982 | 1162798.8965
22 | 2529422.9462 | 1162721.3704
23 | 2528669.7263 | 1162796.2997
24 | 2528216.3724 | 1162616.4909
25 | 2528249.5583 | 1162607.9004
26 | 2528659.8306 | 1162994.2959
27 | 2528639.8143 | 1162472.5129
28 | 2528350.1199 | 1163142.7686
29 | 2528612.5149 | 1162880.8053
30 | 2528610.6965 | 1162876.0687
31 | 2531719.6201 | 1163717.0377
32 | 2531783.7403 | 1163700.8217
33 | 2531792.3708 | 1163708.7169
34 | 2531849.463 | 1163653.0372
35 | 2531819.4948 | 1163709.3692
36 | 2531864.5278 | 1163660.9262
37 | 2532199.0494 | 1163704.729
38 | 2527524.2793 | 1161079.1464
39 | 2530306.6741 | 1162949.5802
40 | 2530293.1731 | 1162937.1522
41 | 2530266.0047 | 1162921.748
42 | 2530237.416 | 1162893.5755
43 | 2530218.4269 | 1162935.2752
44 | 2529787.6964 | 1162197.8273
45 | 2529780.836 | 1162210.6592
46 | 2529936.8987 | 1162146.9001
47 | 2529642.6784 | 1162422.4293
48 | 2529864.4512 | 1162018.7295
49 | 2530106.4999 | 1162370.9268
50 | 2529960.5477 | 1161968.2881
51 | 2529850.3382 | 1161925.0582
52 | 2529620.6636 | 1162489.4362
53 | 2529580.7605 | 1162548.4286
54 | 2529722.2022 | 1162634.7781
55 | 2529758.6776 | 1162623.5841
56 | 2530040.734 | 1162472.9057
57 | 2530264.996 | 1162101.2989
58 | 2530136.0098 | 1162370.6674
59 | 2530061.0662 | 1162484.6087
60 | 2530002.2966 | 1162886.6309
61 | 2529938.6274 | 1162880.8259
62 | 2530335.3275 | 1162399.1051
63 | 2530279.4126 | 1162401.0331
64 | 2530256.8123 | 1162070.2543
65 | 2530988.4019 | 1160582.9234
66 | 2530971.9789 | 1160521.0108
67 | 2531065.1564 | 1161079.3638
68 | 2530546.7023 | 1160946.575
69 | 2530996.2815 | 1161357.4771
70 | 2530960.8334 | 1160992.4915
71 | 2530461.0235 | 1160998.6847
72 | 2531258.4591 | 1161134.6563
73 | 2530960.5931 | 1161376.587
74 | 2530620.1726 | 1161671.0982
75 | 2530548.7297 | 1161700.4295
76 | 2528684.7875 | 1162462.3655
77 | 2528683.7972 | 1162441.5766
78 | 2528672.6195 | 1162441.6206
79 | 2528733.983 | 1162125.6912
80 | 2528636.739 | 1162453.109
81 | 2530123.3591 | 1160976.2364
82 | 2527248.0216 | 1161500.0367
83 | 2527489.826 | 1161100.1742
84 | 2530040.734 | 1162472.9057

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98447 | -0.23389 | 0.28725 | 0.13912
1 | 0.98556 | -0.2268 | 0 | 0
2 | 0.99115 | -0.1888 | 0.22462 | 0.10879
3 | 0.99105 | -0.18793 | 0 | 0
4 | 0.99438 | -0.10701 | 0 | 0
5 | 0.98268 | -0.22179 | 0.24268 | 0.11754
6 | 0.98371 | -0.21505 | 0.31469 | 0.15241
7 | 0.99332 | -0.10382 | 0.37533 | 0.18178
8 | 0.99333 | -0.10394 | 0 | 0
9 | 0.99339 | -0.10448 | 0 | 0
10 | 0.99246 | -0.11997 | 0 | 0
11 | 0.99222 | -0.11772 | 0 | 0
12 | 0.99249 | -0.12026 | 0.28447 | 0.13777
13 | 0.99212 | -0.11832 | 0.39276 | 0.19022
14 | 0.99209 | -0.11854 | 0 | 0
15 | 0.9934 | -0.10455 | 0.26476 | 0.12823
16 | 0.98951 | -0.18009 | 0.067549 | 0.032716
17 | 0.98945 | -0.1796 | 0 | 0
18 | 0.99035 | -0.15839 | 0.28618 | 0.1386
19 | 0.9865 | -0.20146 | 0.26612 | 0.12889
20 | 0.99341 | -0.1047 | 0 | 0
21 | 0.99323 | -0.10676 | 0 | 0
22 | 0.99659 | -0.023064 | 0.079166 | 0.038342
23 | 0.99322 | -0.10688 | 0.086692 | 0.041987
24 | 0.99157 | -0.1315 | 0.1586 | 0.076815
25 | 0.99158 | -0.13143 | 0 | 0
26 | 0.99259 | -0.1196 | 0 | 0
27 | 0.99069 | -0.15448 | 0.069828 | 0.033819
28 | 0.99208 | -0.11842 | 0.28351 | 0.13731
29 | 0.99285 | -0.11663 | 0 | 0
30 | 0.99285 | -0.11653 | 0.23076 | 0.11176
31 | 0.98483 | -0.22032 | 0.32465 | 0.15723
32 | 0.98485 | -0.22058 | 0 | 0
33 | 0.98485 | -0.22057 | 0 | 0
34 | 0.98491 | -0.2211 | 0 | 0
35 | 0.98485 | -0.22054 | 0.097315 | 0.047132
36 | 0.9849 | -0.22118 | 0.39971 | 0.19359
37 | 0.98555 | -0.22672 | 0.30452 | 0.14749
38 | 0.9842 | -0.21932 | 0 | 0
39 | 0.99846 | 0.012113 | 0.30158 | 0.14606
40 | 0.99846 | 0.012046 | 0 | 0
41 | 0.99847 | 0.011935 | 0 | 0
42 | 0.99849 | 0.011794 | 0.22698 | 0.10993
43 | 0.99852 | 0.011511 | 0 | 0
44 | 0.99795 | -0.010384 | 0.20417 | 0.098883
45 | 0.99795 | -0.010419 | 0 | 0
46 | 0.99833 | -0.0085184 | 0 | 0
47 | 0.99749 | -0.012684 | 0 | 0
48 | 0.99801 | -0.0056518 | 0 | 0
49 | 0.99932 | -0.0034851 | 0 | 0
50 | 0.99831 | -0.0083564 | 0.083784 | 0.040579
51 | 0.99787 | -0.0042879 | 1.2035 | 0.58288
52 | 0.99744 | -0.012307 | 0 | 0
53 | 0.99743 | -0.012202 | 0.12659 | 0.061309
54 | 0.99933 | 0.0050921 | 0.1973 | 0.095558
55 | 0.99934 | 0.0050029 | 0 | 0
56 | 1 | 0 | -10.6969 | -4.8095
57 | 0.99833 | -0.015108 | 0 | 0
58 | 0.99932 | -0.0034613 | 0.069136 | 0.033484
59 | 0.99999 | -4.7679e-05 | 0.16809 | 0.08141
60 | 0.99816 | 0.014588 | 0 | 0
61 | 0.99811 | 0.014271 | 0.40806 | 0.19763
62 | 0.99822 | -0.014139 | 0 | 0
63 | 0.9982 | -0.013981 | 0.23952 | 0.11601
64 | 0.99828 | -0.015791 | 0.35069 | 0.16985
65 | 0.99431 | -0.097233 | 0.31897 | 0.15448
66 | 0.99435 | -0.096983 | 0 | 0
67 | 0.99463 | -0.099252 | 0 | 0
68 | 0.99447 | -0.09831 | 0 | 0
69 | 0.99491 | -0.10105 | 0 | 0
70 | 0.99459 | -0.099517 | 0.15977 | 0.077382
71 | 0.99445 | -0.098117 | 0.085549 | 0.041433
72 | 0.99434 | -0.10663 | 0.23517 | 0.1139
73 | 0.99497 | -0.10038 | 0.31481 | 0.15247
74 | 0.99646 | -0.061219 | 0.21997 | 0.10654
75 | 0.99659 | -0.059725 | 0 | 0
76 | 0.99064 | -0.15499 | 0.36267 | 0.17565
77 | 0.99063 | -0.15517 | 0 | 0
78 | 0.99063 | -0.15516 | 0 | 0
79 | 0.99036 | -0.15826 | 0 | 0
80 | 0.99062 | -0.15512 | 0.086624 | 0.041954
81 | 0.9944 | -0.09845 | 0.079211 | 0.038364
82 | 0.98372 | -0.21514 | 0 | 0
83 | 0.98419 | -0.21925 | 0.13178 | 0.063826
84 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.28725 | -0.13912 | 0.28755 | 0.13708 | 0.00029973 | -0.0020436 | 0.009359 | 0.0093307 | 0.009359 | 0.98447 | -0.23389 | 0.98556 | -0.2268 | 4.4567
1 | 0.30452 | 0.14695 | -0.30452 | -0.14749 | 3.0238e-06 | -0.00053426 | 0.0099039 | 0.0099107 | 0.0099107 | 0.98556 | -0.2268 | 0.98555 | -0.22672 | 4.5049
2 | -1.4144 | -0.66317 | 1.4218 | 0.6655 | 0.0074317 | 0.0023303 | 0.045756 | 0.045727 | 0.045756 | 0.98556 | -0.2268 | 0.99105 | -0.18793 | 21.7883
3 | 0.82229 | 0.37914 | -0.82171 | -0.39313 | 0.00057736 | -0.013984 | 0.026522 | 0.026699 | 0.026699 | 0.98556 | -0.2268 | 0.98491 | -0.2211 | 12.1357
4 | 1.422 | 0.66426 | -1.4218 | -0.6655 | 0.00015354 | -0.0012449 | 0.045711 | 0.045727 | 0.045727 | 0.99115 | -0.1888 | 0.99105 | -0.18793 | 20.7849
5 | -1.6466 | -0.77305 | 1.6508 | 0.77587 | 0.004262 | 0.0028252 | 0.052979 | 0.052954 | 0.052979 | 0.99115 | -0.1888 | 0.99438 | -0.10701 | 15.1369
6 | -1.886 | -0.88655 | 1.8869 | 0.86961 | 0.00091367 | -0.01694 | 0.0605 | 0.060284 | 0.0605 | 0.99438 | -0.10701 | 0.99491 | -0.10105 | 16.7126
7 | 0.23518 | 0.11068 | -0.23517 | -0.1139 | 1.0415e-05 | -0.0032145 | 0.0075457 | 0.0075859 | 0.0075859 | 0.99438 | -0.10701 | 0.99434 | -0.10663 | 3.4481
8 | -0.24268 | -0.11754 | 0.24292 | 0.11521 | 0.00023896 | -0.0023269 | 0.0079212 | 0.0078898 | 0.0079212 | 0.98268 | -0.22179 | 0.98371 | -0.21505 | 3.772
9 | -0.55762 | -0.26762 | 0.55762 | 0.2673 | 6.1252e-06 | -0.00032003 | 0.018151 | 0.018147 | 0.018151 | 0.98371 | -0.21505 | 0.98372 | -0.21514 | 8.2503
10 | -0.37533 | -0.18178 | 0.37534 | 0.18114 | 5.3377e-06 | -0.0006401 | 0.01212 | 0.012112 | 0.01212 | 0.99332 | -0.10382 | 0.99333 | -0.10394 | 5.509
11 | -0.37534 | -0.18114 | 0.37536 | 0.17827 | 2.3891e-05 | -0.0028758 | 0.012112 | 0.012075 | 0.012112 | 0.99333 | -0.10394 | 0.99339 | -0.10448 | 5.5053
12 | -0.37536 | -0.17827 | 0.37536 | 0.17791 | 2.9567e-06 | -0.00035712 | 0.012075 | 0.012071 | 0.012075 | 0.99339 | -0.10448 | 0.9934 | -0.10455 | 5.4889
13 | 0.67652 | 0.31975 | -0.67634 | -0.32637 | 0.00018016 | -0.006619 | 0.021765 | 0.021849 | 0.021849 | 0.99246 | -0.11997 | 0.99222 | -0.11772 | 9.9313
14 | -0.67652 | -0.31975 | 0.67655 | 0.31887 | 2.3927e-05 | -0.00088314 | 0.021765 | 0.021754 | 0.021765 | 0.99246 | -0.11997 | 0.99249 | -0.12026 | 9.8933
15 | 0.39279 | 0.1901 | -0.39276 | -0.19022 | 3.5974e-05 | -0.00012465 | 0.012696 | 0.012698 | 0.012698 | 0.99222 | -0.11772 | 0.99212 | -0.11832 | 6.0465
16 | 0.28355 | 0.13628 | -0.28352 | -0.13653 | 3.4449e-05 | -0.00024953 | 0.009153 | 0.0091564 | 0.0091564 | 0.99222 | -0.11772 | 0.99209 | -0.11854 | 4.3602
17 | -0.96102 | -0.45664 | 0.96111 | 0.45664 | 8.9037e-05 | -5.5977e-06 | 0.030947 | 0.030946 | 0.030947 | 0.99249 | -0.12026 | 0.99259 | -0.1196 | 14.7367
18 | 0.28352 | 0.13653 | -0.28351 | -0.13731 | 3.7562e-06 | -0.00078666 | 0.0091564 | 0.0091664 | 0.0091664 | 0.99209 | -0.11854 | 0.99208 | -0.11842 | 4.1665
19 | -0.64012 | -0.30614 | 0.64013 | 0.30566 | 1.1671e-05 | -0.00048116 | 0.020619 | 0.020613 | 0.020619 | 0.9934 | -0.10455 | 0.99341 | -0.1047 | 9.3725
20 | 0.96009 | 0.44129 | -0.96002 | -0.44239 | 6.0593e-05 | -0.0010981 | 0.030826 | 0.03084 | 0.03084 | 0.98951 | -0.18009 | 0.98945 | -0.1796 | 14.018
21 | -1.0276 | -0.474 | 1.0283 | 0.47394 | 0.00069153 | -6.0355e-05 | 0.033015 | 0.033005 | 0.033015 | 0.98951 | -0.18009 | 0.99035 | -0.15839 | 9.4329
22 | 0.96002 | 0.44239 | -0.95733 | -0.44255 | 0.0026913 | -0.0001636 | 0.03084 | 0.030862 | 0.030862 | 0.98945 | -0.1796 | 0.9865 | -0.20146 | 14.6963
23 | -1.3145 | -0.61255 | 1.3145 | 0.612 | 1.4266e-05 | -0.00054586 | 0.042272 | 0.042265 | 0.042272 | 0.99035 | -0.15839 | 0.99036 | -0.15826 | 11.6774
24 | 0.69122 | 0.31366 | -0.6897 | -0.31471 | 0.0015162 | -0.0010474 | 0.022212 | 0.022236 | 0.022236 | 0.9865 | -0.20146 | 0.9842 | -0.21932 | 10.5886
25 | 3.2766 | 1.4983 | -3.2761 | -1.5013 | 0.00053045 | -0.0030047 | 0.1047 | 0.10474 | 0.10474 | 0.99341 | -0.1047 | 0.99323 | -0.10676 | 28.9331
26 | -3.9167 | -1.8039 | 3.9267 | 1.8144 | 0.0099299 | 0.010501 | 0.12531 | 0.1253 | 0.12531 | 0.99341 | -0.1047 | 0.99659 | -0.023064 | 35.8022
27 | 3.2761 | 1.5013 | -3.276 | -1.5015 | 3.0192e-05 | -0.0001709 | 0.10474 | 0.10474 | 0.10474 | 0.99323 | -0.10676 | 0.99322 | -0.10688 | 28.9337
28 | -4.0058 | -1.8528 | 4.0091 | 1.8409 | 0.0033109 | -0.011917 | 0.12784 | 0.12767 | 0.12784 | 0.99659 | -0.023064 | 0.99749 | -0.012684 | 35.3162
29 | 3.1893 | 1.4595 | -3.1884 | -1.4585 | 0.0009467 | 0.00095986 | 0.10194 | 0.10194 | 0.10194 | 0.99322 | -0.10688 | 0.99285 | -0.11653 | 29.1264
30 | -0.1586 | -0.076815 | 0.15861 | 0.076776 | 1.6075e-06 | -3.923e-05 | 0.0051305 | 0.0051299 | 0.0051305 | 0.99157 | -0.1315 | 0.99158 | -0.13143 | 2.4431
31 | -1.994 | -0.9254 | 1.9958 | 0.89514 | 0.0018406 | -0.030268 | 0.063997 | 0.063615 | 0.063997 | 0.99158 | -0.13143 | 0.99259 | -0.1196 | 17.6787
32 | 1.8354 | 0.84863 | -1.8341 | -0.84763 | 0.0013142 | 0.00099328 | 0.058868 | 0.058874 | 0.058874 | 0.99158 | -0.13143 | 0.99069 | -0.15448 | 16.8211
33 | -2.9569 | -1.3518 | 2.9576 | 1.3469 | 0.00068599 | -0.0048757 | 0.094556 | 0.094492 | 0.094556 | 0.99259 | -0.1196 | 0.99285 | -0.11663 | 26.1206
34 | 1.7642 | 0.81382 | -1.7642 | -0.81532 | 7.1399e-05 | -0.0015005 | 0.056614 | 0.056632 | 0.056632 | 0.99069 | -0.15448 | 0.99064 | -0.15499 | 15.6443
35 | -2.9576 | -1.3469 | 2.9576 | 1.3467 | 2.1877e-05 | -0.00015566 | 0.094492 | 0.09449 | 0.094492 | 0.99285 | -0.11663 | 0.99285 | -0.11653 | 26.1026
36 | -0.32465 | -0.15723 | 0.32466 | 0.15571 | 9.8295e-06 | -0.0015251 | 0.010573 | 0.010554 | 0.010573 | 0.98483 | -0.22032 | 0.98485 | -0.22058 | 4.8061
37 | 0.097316 | 0.046229 | -0.097316 | -0.046499 | 1.5567e-07 | -0.00027044 | 0.003158 | 0.0031614 | 0.0031614 | 0.98485 | -0.22058 | 0.98485 | -0.22057 | 1.437
38 | -0.42197 | -0.20194 | 0.422 | 0.19955 | 2.5868e-05 | -0.0023844 | 0.013712 | 0.013682 | 0.013712 | 0.98485 | -0.22058 | 0.98491 | -0.2211 | 6.2327
39 | 0.097316 | 0.046499 | -0.097315 | -0.047132 | 3.6551e-07 | -0.00063269 | 0.0031614 | 0.0031694 | 0.0031694 | 0.98485 | -0.22057 | 0.98485 | -0.22054 | 1.4406
40 | 0.39972 | 0.19357 | -0.39971 | -0.19359 | 5.134e-06 | -1.6477e-05 | 0.013017 | 0.013017 | 0.013017 | 0.98491 | -0.2211 | 0.9849 | -0.22118 | 6.1987
41 | 0.13178 | 0.062894 | -0.13178 | -0.063826 | 9.8912e-07 | -0.00093126 | 0.004283 | 0.0042948 | 0.0042948 | 0.9842 | -0.21932 | 0.98419 | -0.21925 | 1.9522
42 | 0.55791 | 0.25182 | -0.55762 | -0.2673 | 0.00029301 | -0.015487 | 0.017954 | 0.018147 | 0.018147 | 0.9842 | -0.21932 | 0.98372 | -0.21514 | 8.2484
43 | -0.30158 | -0.14606 | 0.30158 | 0.14562 | 2.3014e-06 | -0.00043674 | 0.0096881 | 0.0096826 | 0.0096881 | 0.99846 | 0.012113 | 0.99846 | 0.012046 | 4.4037
44 | -0.30158 | -0.14562 | 0.30159 | 0.14488 | 3.897e-06 | -0.00074069 | 0.0096826 | 0.0096733 | 0.0096826 | 0.99846 | 0.012046 | 0.99847 | 0.011935 | 4.4012
45 | -0.30159 | -0.14488 | 0.30159 | 0.14393 | 5.0061e-06 | -0.00095361 | 0.0096733 | 0.0096614 | 0.0096733 | 0.99847 | 0.011935 | 0.99849 | 0.011794 | 4.397
46 | -0.52857 | -0.25386 | 0.52859 | 0.25278 | 1.758e-05 | -0.0010864 | 0.016953 | 0.016939 | 0.016953 | 0.99849 | 0.011794 | 0.99852 | 0.011511 | 7.7058
47 | 0.40824 | 0.18081 | -0.40808 | -0.19757 | 0.00015953 | -0.016757 | 0.012908 | 0.013112 | 0.013112 | 0.99852 | 0.011511 | 0.99816 | 0.014588 | 5.9602
48 | -0.93683 | -0.43359 | 0.93764 | 0.41737 | 0.00081605 | -0.016218 | 0.029844 | 0.029647 | 0.029844 | 0.99852 | 0.011511 | 0.99934 | 0.0050029 | 13.5655
49 | -0.20417 | -0.098883 | 0.20417 | 0.098538 | 8.3556e-07 | -0.00034558 | 0.0065622 | 0.0065578 | 0.0065622 | 0.99795 | -0.010384 | 0.99795 | -0.010419 | 2.9828
50 | -4.3417 | -1.971 | 4.3433 | 1.9552 | 0.0015626 | -0.015784 | 0.13793 | 0.13773 | 0.13793 | 0.99795 | -0.010419 | 0.99833 | -0.0085184 | 21.6188
51 | 4.1376 | 1.8725 | -4.1357 | -1.8928 | 0.0018275 | -0.020363 | 0.13137 | 0.13163 | 0.13163 | 0.99795 | -0.010419 | 0.99749 | -0.012684 | 20.6314
52 | 1.2041 | 0.57599 | -1.2037 | -0.58069 | 0.00040342 | -0.0046986 | 0.038596 | 0.038657 | 0.038657 | 0.99833 | -0.0085184 | 0.99801 | -0.0056518 | 17.5711
53 | -5.6312 | -2.5673 | 5.6366 | 2.536 | 0.0054128 | -0.031318 | 0.17895 | 0.17855 | 0.17895 | 0.99833 | -0.0085184 | 0.99932 | -0.0034851 | 28.0494
54 | 0.083786 | 0.03611 | -0.083784 | -0.040579 | 1.7801e-06 | -0.0044688 | 0.0026382 | 0.0026919 | 0.0026919 | 0.99833 | -0.0085184 | 0.99831 | -0.0083564 | 1.2236
55 | 0.1266 | 0.051956 | -0.12659 | -0.059618 | 6.9038e-06 | -0.007662 | 0.0039602 | 0.0040496 | 0.0040496 | 0.99749 | -0.012684 | 0.99744 | -0.012307 | 1.8407
56 | 1.2037 | 0.58069 | -1.2035 | -0.58288 | 0.00018929 | -0.0021983 | 0.038657 | 0.038685 | 0.038685 | 0.99801 | -0.0056518 | 0.99787 | -0.0042879 | 17.584
57 | -9.373 | -4.2269 | 9.3791 | 4.2164 | 0.0060785 | -0.010586 | 0.29702 | 0.29685 | 0.29702 | 0.99932 | -0.0034851 | 1 | 0 | 46.5544
58 | 3.6673 | 1.6582 | -3.664 | -1.673 | 0.0032943 | -0.014845 | 0.11626 | 0.11647 | 0.11647 | 0.99932 | -0.0034851 | 0.99833 | -0.015108 | 32.1736
59 | 0.069136 | 0.03278 | -0.069136 | -0.033484 | 1.9323e-07 | -0.0007036 | 0.0022103 | 0.002219 | 0.002219 | 0.99932 | -0.0034851 | 0.99932 | -0.0034613 | 1.0087
60 | 0.12659 | 0.059618 | -0.12659 | -0.061309 | 1.5674e-06 | -0.0016913 | 0.0040496 | 0.0040707 | 0.0040707 | 0.99744 | -0.012307 | 0.99743 | -0.012202 | 1.8503
61 | -0.1973 | -0.095558 | 0.19731 | 0.094648 | 2.0416e-06 | -0.00091031 | 0.0063328 | 0.0063213 | 0.0063328 | 0.99933 | 0.0050921 | 0.99934 | 0.0050029 | 2.8785
62 | -1.1349 | -0.51202 | 1.1357 | 0.50123 | 0.00079459 | -0.010783 | 0.035967 | 0.035837 | 0.035967 | 0.99934 | 0.0050029 | 1 | 0 | 16.3485
63 | 0.16809 | 0.081382 | -0.16809 | -0.08141 | 1.2149e-06 | -2.7245e-05 | 0.0053912 | 0.0053915 | 0.0053915 | 1 | 0 | 0.99999 | -4.7679e-05 | 2.5674
64 | 3.4244 | 1.5676 | -3.4242 | -1.5685 | 0.00018393 | -0.00096407 | 0.1089 | 0.10891 | 0.10891 | 0.99833 | -0.015108 | 0.99828 | -0.015791 | 30.0867
65 | 0.23956 | 0.10545 | -0.23953 | -0.11468 | 3.0108e-05 | -0.0092251 | 0.0075684 | 0.0076799 | 0.0076799 | 0.99833 | -0.015108 | 0.99822 | -0.014139 | 3.4909
66 | 0.40808 | 0.19757 | -0.40806 | -0.19763 | 1.9587e-05 | -6.377e-05 | 0.013112 | 0.013113 | 0.013113 | 0.99816 | 0.014588 | 0.99811 | 0.014271 | 6.2445
67 | 0.23953 | 0.11468 | -0.23952 | -0.11601 | 4.402e-06 | -0.0013259 | 0.0076799 | 0.0076965 | 0.0076965 | 0.99822 | -0.014139 | 0.9982 | -0.013981 | 3.4984
68 | 3.0735 | 1.3987 | -3.0694 | -1.3946 | 0.0041245 | 0.0041285 | 0.097649 | 0.097656 | 0.097656 | 0.99828 | -0.015791 | 0.99659 | -0.059725 | 27.9017
69 | -0.31897 | -0.15448 | 0.31898 | 0.15441 | 1.2081e-05 | -6.8036e-05 | 0.010289 | 0.010288 | 0.010289 | 0.99431 | -0.097233 | 0.99435 | -0.096983 | 4.8997
70 | -0.31898 | -0.15441 | 0.31907 | 0.13839 | 9.4214e-05 | -0.016024 | 0.010288 | 0.010094 | 0.010288 | 0.99435 | -0.096983 | 0.99463 | -0.099252 | 4.6765
71 | 0.16479 | 0.058899 | -0.16477 | -0.076985 | 2.7376e-05 | -0.018086 | 0.0050792 | 0.0052792 | 0.0052792 | 0.99463 | -0.099252 | 0.99447 | -0.09831 | 2.3996
72 | -0.64365 | -0.27451 | 0.64384 | 0.26627 | 0.00019252 | -0.0082421 | 0.020309 | 0.020216 | 0.020309 | 0.99463 | -0.099252 | 0.99491 | -0.10105 | 9.2313
73 | 0.15978 | 0.077226 | -0.15977 | -0.077382 | 6.4193e-06 | -0.0001563 | 0.0051506 | 0.0051526 | 0.0051526 | 0.99463 | -0.099252 | 0.99459 | -0.099517 | 2.4536
74 | 0.16477 | 0.076985 | -0.16476 | -0.0794 | 3.8285e-06 | -0.0024148 | 0.0052792 | 0.0053093 | 0.0053093 | 0.99447 | -0.09831 | 0.99445 | -0.098117 | 2.4133
75 | -2.5308 | -1.1359 | 2.5309 | 1.1346 | 0.00012681 | -0.0012844 | 0.080488 | 0.080471 | 0.080488 | 0.99491 | -0.10105 | 0.99497 | -0.10038 | 22.2342
76 | 0.079215 | 0.037966 | -0.079211 | -0.038364 | 3.9283e-06 | -0.00039704 | 0.00255 | 0.002555 | 0.002555 | 0.99445 | -0.098117 | 0.9944 | -0.09845 | 1.2167
77 | -2.8457 | -1.2871 | 2.8491 | 1.2904 | 0.0033928 | 0.0033199 | 0.090616 | 0.090609 | 0.090616 | 0.99497 | -0.10038 | 0.99646 | -0.061219 | 25.8903
78 | -3.0691 | -1.3969 | 3.0694 | 1.3946 | 0.00035497 | -0.0023666 | 0.097688 | 0.097656 | 0.097688 | 0.99646 | -0.061219 | 0.99659 | -0.059725 | 26.9855
79 | 1.4015 | 0.63967 | -1.4015 | -0.64035 | 2.0268e-05 | -0.00068615 | 0.044892 | 0.044901 | 0.044901 | 0.99064 | -0.15499 | 0.99063 | -0.15517 | 12.4035
80 | 0.086625 | 0.040765 | -0.086625 | -0.041026 | 1.1593e-07 | -0.0002611 | 0.0027898 | 0.0027931 | 0.0027931 | 0.99063 | -0.15517 | 0.99063 | -0.15516 | 1.2696
81 | 1.3148 | 0.59959 | -1.3145 | -0.612 | 0.00032306 | -0.012414 | 0.042111 | 0.042265 | 0.042265 | 0.99063 | -0.15517 | 0.99036 | -0.15826 | 11.6755
82 | 0.086625 | 0.041026 | -0.086624 | -0.041954 | 4.143e-07 | -0.00092807 | 0.0027931 | 0.0028048 | 0.0028048 | 0.99063 | -0.15516 | 0.99062 | -0.15512 | 1.2749

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 10.6969 | 4.8095

## res_load
| p_mw | q_mvar
0 | 0.28725 | 0.13912
1 | 0.22462 | 0.10879
2 | 0.24268 | 0.11754
3 | 0.31469 | 0.15241
4 | 0.37533 | 0.18178
5 | 0.28447 | 0.13777
6 | 0.39276 | 0.19022
7 | 0.26476 | 0.12823
8 | 0.067549 | 0.032716
9 | 0.28618 | 0.1386
10 | 0.26612 | 0.12889
11 | 0.079166 | 0.038342
12 | 0.086692 | 0.041987
13 | 0.1586 | 0.076815
14 | 0.069828 | 0.033819
15 | 0.28351 | 0.13731
16 | 0.23076 | 0.11176
17 | 0.32465 | 0.15723
18 | 0.097315 | 0.047132
19 | 0.39971 | 0.19359
20 | 0.30452 | 0.14749
21 | 0.30158 | 0.14606
22 | 0.22698 | 0.10993
23 | 0.20417 | 0.098883
24 | 0.083784 | 0.040579
25 | 1.2035 | 0.58288
26 | 0.12659 | 0.061309
27 | 0.1973 | 0.095558
28 | 0.069136 | 0.033484
29 | 0.16809 | 0.08141
30 | 0.40806 | 0.19763
31 | 0.23952 | 0.11601
32 | 0.35069 | 0.16985
33 | 0.31897 | 0.15448
34 | 0.15977 | 0.077382
35 | 0.085549 | 0.041433
36 | 0.23517 | 0.1139
37 | 0.31481 | 0.15247
38 | 0.21997 | 0.10654
39 | 0.36267 | 0.17565
40 | 0.086624 | 0.041954
41 | 0.079211 | 0.038364
42 | 0.13178 | 0.063826

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1