## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_316_1_node_25 | 20 | n |  | TRUE
1 | bus_MV_316_1_node_26 | 20 | n |  | TRUE
2 | bus_MV_316_1_node_51 | 20 | n |  | TRUE
3 | bus_MV_316_1_node_27 | 20 | n |  | TRUE
4 | bus_MV_316_1_node_40 | 20 | n |  | TRUE
5 | bus_MV_316_1_node_28 | 20 | n |  | TRUE
6 | bus_MV_316_1_node_83 | 20 | n |  | TRUE
7 | bus_MV_316_1_node_85 | 20 | n |  | TRUE
8 | bus_MV_316_1_node_82 | 20 | n |  | TRUE
9 | bus_MV_316_1_node_37 | 20 | n |  | TRUE
10 | bus_MV_316_1_node_39 | 20 | n |  | TRUE
11 | bus_MV_316_1_node_42 | 20 | n |  | TRUE
12 | bus_MV_316_1_node_52 | 20 | n |  | TRUE
13 | bus_MV_316_1_node_43 | 20 | n |  | TRUE
14 | bus_MV_316_1_node_44 | 20 | n |  | TRUE
15 | bus_MV_316_1_node_164 | 20 | n |  | TRUE
16 | bus_MV_316_1_node_147 | 20 | n |  | TRUE
17 | bus_MV_316_1_node_46 | 20 | n |  | TRUE
18 | bus_MV_316_1_node_120 | 20 | n |  | TRUE
19 | bus_MV_316_1_node_45 | 20 | n |  | TRUE
20 | bus_MV_316_1_node_110 | 20 | n |  | TRUE
21 | bus_MV_316_1_node_96 | 20 | n |  | TRUE
22 | bus_MV_316_1_node_102 | 20 | n |  | TRUE
23 | bus_MV_316_1_node_159 | 20 | n |  | TRUE
24 | bus_MV_316_1_node_97 | 20 | n |  | TRUE
25 | bus_MV_316_1_node_98 | 20 | n |  | TRUE
26 | bus_MV_316_1_node_105 | 20 | n |  | TRUE
27 | bus_MV_316_1_node_95 | 20 | n |  | TRUE
28 | bus_MV_316_1_node_160 | 20 | n |  | TRUE
29 | bus_MV_316_1_node_107 | 20 | n |  | TRUE
30 | bus_MV_316_1_node_106 | 20 | n |  | TRUE
31 | bus_MV_316_1_node_168 | 20 | n |  | TRUE
32 | bus_MV_316_1_node_101 | 20 | n |  | TRUE
33 | bus_MV_316_1_node_173 | 20 | n |  | TRUE
34 | bus_MV_316_1_node_99 | 20 | n |  | TRUE
35 | bus_MV_316_1_node_100 | 20 | n |  | TRUE
36 | bus_MV_316_1_node_104 | 20 | n |  | TRUE
37 | bus_MV_316_1_node_178 | 20 | n |  | TRUE
38 | bus_MV_316_1_node_156 | 20 | n |  | TRUE
39 | bus_MV_316_1_node_103 | 20 | n |  | TRUE
40 | bus_MV_316_1_node_169 | 20 | n |  | TRUE
41 | bus_MV_316_1_node_158 | 20 | n |  | TRUE
42 | bus_MV_316_1_node_90 | 20 | n |  | TRUE
43 | bus_MV_316_1_node_58 | 20 | n |  | TRUE
44 | bus_MV_316_1_node_59 | 20 | n |  | TRUE
45 | bus_MV_316_1_node_60 | 20 | n |  | TRUE
46 | bus_MV_316_1_node_61 | 20 | n |  | TRUE
47 | bus_MV_316_1_node_62 | 20 | n |  | TRUE
48 | bus_MV_316_1_node_73 | 20 | n |  | TRUE
49 | bus_MV_316_1_node_75 | 20 | n |  | TRUE
50 | bus_MV_316_1_node_170 | 20 | n |  | TRUE
51 | bus_MV_316_1_node_76 | 20 | n |  | TRUE
52 | bus_MV_316_1_node_63 | 20 | n |  | TRUE
53 | bus_MV_316_1_node_144 | 20 | n |  | TRUE
54 | bus_MV_316_1_node_74 | 20 | n |  | TRUE
55 | bus_MV_316_1_node_64 | 20 | n |  | TRUE
56 | bus_MV_316_1_node_65 | 20 | n |  | TRUE
57 | bus_MV_316_1_node_69 | 20 | n |  | TRUE
58 | bus_MV_316_1_node_84 | 20 | n |  | TRUE
59 | bus_MV_316_1_node_66 | 20 | n |  | TRUE
60 | bus_MV_316_1_node_68 | 20 | n |  | TRUE
61 | bus_MV_316_1_node_67 | 20 | n |  | TRUE
62 | bus_MV_316_1_node_70 | 20 | n |  | TRUE
63 | bus_MV_316_1_node_150 | 20 | n |  | TRUE
64 | bus_MV_316_1_node_172 | 20 | n |  | TRUE
65 | bus_MV_316_1_node_149 | 20 | n |  | TRUE
66 | bus_MV_316_1_node_71 | 20 | n |  | TRUE
67 | bus_MV_316_1_node_145 | 20 | n |  | TRUE
68 | bus_MV_316_1_node_72 | 20 | n |  | TRUE
69 | bus_MV_316_1_node_115 | 20 | n |  | TRUE
70 | bus_MV_316_1_node_157 | 20 | n |  | TRUE
71 | bus_MV_316_1_node_112 | 20 | n |  | TRUE
72 | bus_MV_316_1_node_114 | 20 | n |  | TRUE
73 | bus_MV_316_1_node_111 | 20 | n |  | TRUE
74 | bus_MV_316_1_node_113 | 20 | n |  | TRUE
75 | bus_MV_316_1_node_117 | 20 | n |  | TRUE
76 | bus_MV_316_1_node_116 | 20 | n |  | TRUE
77 | bus_MV_316_1_node_118 | 20 | n |  | TRUE
78 | bus_MV_316_1_node_119 | 20 | n |  | TRUE
79 | bus_MV_316_1_node_77 | 20 | n |  | TRUE
80 | bus_MV_316_1_node_79 | 20 | n |  | TRUE
81 | bus_MV_316_1_node_78 | 20 | n |  | TRUE
82 | bus_MV_316_1_node_81 | 20 | n |  | TRUE
83 | bus_MV_316_1_node_80 | 20 | n |  | TRUE
84 | bus_MV_316_1_node_146 | 20 | n |  | TRUE
85 | bus_MV_316_1_node_177 | 20 | n |  | TRUE
86 | bus_MV_316_1_node_148 | 20 | n |  | TRUE
87 | bus_MV_316_1_node_86 | 20 | n |  | TRUE
88 | bus_MV_316_1_node_87 | 20 | n |  | TRUE
89 | bus_MV_316_1_node_88 | 20 | n |  | TRUE
90 | bus_MV_316_1_node_89 | 20 | n |  | TRUE
91 | bus_MV_316_1_node_91 | 20 | n |  | TRUE
92 | bus_MV_316_1_node_184 | 20 | n |  | TRUE
93 | bus_MV_316_1_node_180 | 20 | n |  | TRUE
94 | bus_MV_316_1_node_92 | 20 | n |  | TRUE
95 | bus_MV_316_1_node_122 | 20 | n |  | TRUE
96 | bus_MV_316_1_node_93 | 20 | n |  | TRUE
97 | bus_MV_316_1_node_182 | 20 | n |  | TRUE
98 | bus_MV_316_1_node_185 | 20 | n |  | TRUE
99 | bus_MV_316_1_node_108 | 20 | n |  | TRUE
100 | bus_MV_316_1_node_109 | 20 | n |  | TRUE
101 | bus_MV_316_1_node_155 | 20 | n |  | TRUE
102 | bus_MV_316_1_node_181 | 20 | n |  | TRUE
103 | bus_MV_316_1_node_167 | 20 | n |  | TRUE
104 | bus_MV_316_1_node_121 | 20 | n |  | TRUE
105 | bus_MV_316_1_node_153 | 20 | n |  | TRUE
106 | bus_MV_316_1_node_176 | 20 | n |  | TRUE
107 | bus_MV_316_1_node_165 | 20 | n |  | TRUE
108 | bus_MV_316_1_node_166 | 20 | n |  | TRUE
109 | bus_MV_316_1_node_151 | 20 | n |  | TRUE
110 | bus_MV_316_1_node_152 | 20 | n |  | TRUE
111 | bus_HV_316_1_node_168 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_316_1_load_25 | 0 | 0.39574 | 0.19167 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_316_1_load_51 | 2 | 0.11834 | 0.057317 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_316_1_load_28 | 5 | 0.065642 | 0.031792 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_316_1_load_82 | 8 | 0.19878 | 0.096274 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_316_1_load_37 | 9 | 0.40581 | 0.19654 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_316_1_load_52 | 12 | 0.32033 | 0.15514 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_316_1_load_164 | 15 | 0.16247 | 0.078689 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_316_1_load_147 | 16 | 0.14179 | 0.068672 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_316_1_load_120 | 18 | 0.30005 | 0.14532 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_316_1_load_110 | 20 | 0.36789 | 0.17818 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_316_1_load_159 | 23 | 0.22111 | 0.10709 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_316_1_load_95 | 27 | 0.34379 | 0.16651 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_316_1_load_160 | 28 | 0.091155 | 0.044148 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_316_1_load_106 | 30 | 0.25671 | 0.12433 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_316_1_load_168 | 31 | 0.081163 | 0.039309 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_316_1_load_173 | 33 | 0.34197 | 0.16562 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_316_1_load_178 | 37 | 0.21203 | 0.10269 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_316_1_load_156 | 38 | 0.070332 | 0.034064 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_316_1_load_169 | 40 | 0.14801 | 0.071682 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_316_1_load_158 | 41 | 1.0054 | 0.48695 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_316_1_load_58 | 43 | 0.28809 | 0.13953 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_316_1_load_170 | 50 | 0.18051 | 0.087425 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_316_1_load_63 | 52 | 0.091659 | 0.044392 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_316_1_load_144 | 53 | 0.12309 | 0.059614 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_316_1_load_64 | 55 | 0.13567 | 0.06571 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_316_1_load_69 | 57 | 0.17277 | 0.083677 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_316_1_load_66 | 59 | 0.44581 | 0.21592 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_316_1_load_67 | 61 | 0.24471 | 0.11852 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_316_1_load_70 | 62 | 0.099135 | 0.048013 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_316_1_load_172 | 64 | 0.31841 | 0.15421 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_316_1_load_145 | 67 | 0.19841 | 0.096095 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_316_1_load_72 | 68 | 0.349 | 0.16903 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_316_1_load_157 | 70 | 0.073789 | 0.035738 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_316_1_load_111 | 73 | 0.166 | 0.080396 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_316_1_load_116 | 76 | 0.39207 | 0.18989 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_316_1_load_118 | 77 | 0.3541 | 0.1715 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_316_1_load_119 | 78 | 0.25322 | 0.12264 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_316_1_load_77 | 79 | 0.21722 | 0.10521 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_316_1_load_146 | 84 | 0.091728 | 0.044426 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_316_1_load_177 | 85 | 0.14908 | 0.072201 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_316_1_load_148 | 86 | 0.10075 | 0.048796 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_316_1_load_86 | 87 | 0.33253 | 0.16105 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_316_1_load_184 | 92 | 0.18097 | 0.08765 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_316_1_load_180 | 93 | 0.14683 | 0.071114 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_316_1_load_122 | 95 | 0.16184 | 0.078384 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_316_1_load_182 | 97 | 0.21278 | 0.10305 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_316_1_load_185 | 98 | 0.37295 | 0.18063 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_316_1_load_155 | 101 | 0.12989 | 0.062908 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_316_1_load_181 | 102 | 0.23044 | 0.11161 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_316_1_load_167 | 103 | 0.18402 | 0.089123 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_316_1_load_121 | 104 | 0.16917 | 0.081933 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_316_1_load_176 | 106 | 0.17347 | 0.084017 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_316_1_load_166 | 108 | 0.18442 | 0.089317 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_316_1_load_151 | 109 | 0.070322 | 0.034059 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_316_1_line_0 |  | 0 | 1 | 0.052917 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_316_1_line_1 |  | 0 | 2 | 1.4138 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_316_1_line_2 |  | 1 | 3 | 0.39367 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_316_1_line_3 |  | 2 | 4 | 0.18485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_316_1_line_4 |  | 3 | 5 | 0.083828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_316_1_line_5 |  | 4 | 10 | 0.13571 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_316_1_line_6 |  | 6 | 7 | 0.78272 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
7 | MV_316_1_line_7 |  | 6 | 8 | 0.019544 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
8 | MV_316_1_line_8 |  | 7 | 85 | 0.009515 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
9 | MV_316_1_line_9 |  | 7 | 65 | 0.75361 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
10 | MV_316_1_line_10 |  | 8 | 58 | 0.026684 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
11 | MV_316_1_line_11 |  | 9 | 10 | 0.005479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_316_1_line_12 |  | 10 | 11 | 0.66997 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_316_1_line_13 |  | 10 | 12 | 0.28992 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_316_1_line_14 |  | 11 | 13 | 0.44486 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_316_1_line_15 |  | 11 | 14 | 0.30859 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_316_1_line_16 |  | 11 | 15 | 0.063099 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_316_1_line_17 |  | 13 | 16 | 0.058805 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_316_1_line_18 |  | 14 | 17 | 0.42815 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_316_1_line_19 |  | 14 | 18 | 0.04163 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_316_1_line_20 |  | 17 | 21 | 0.37226 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
21 | MV_316_1_line_21 |  | 17 | 22 | 0.44985 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_316_1_line_22 |  | 17 | 23 | 0.02446 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
23 | MV_316_1_line_23 |  | 17 | 19 | 0.073711 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_316_1_line_24 |  | 19 | 20 | 0.062581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_316_1_line_25 |  | 21 | 24 | 0.14709 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_316_1_line_26 |  | 21 | 25 | 0.6863 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
27 | MV_316_1_line_27 |  | 21 | 26 | 0.53691 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_316_1_line_28 |  | 21 | 27 | 0.005528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_316_1_line_29 |  | 22 | 29 | 0.30215 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_316_1_line_30 |  | 22 | 30 | 0.046359 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_316_1_line_31 |  | 23 | 42 | 0.031276 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
32 | MV_316_1_line_32 |  | 24 | 28 | 0.068745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_316_1_line_33 |  | 25 | 31 | 0.00331 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
34 | MV_316_1_line_34 |  | 25 | 32 | 0.25413 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
35 | MV_316_1_line_35 |  | 26 | 38 | 0.02636 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_316_1_line_36 |  | 26 | 39 | 0.3724 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_316_1_line_37 |  | 26 | 36 | 0.10943 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_316_1_line_38 |  | 29 | 99 | 0.13209 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_316_1_line_39 |  | 29 | 100 | 0.43623 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_316_1_line_40 |  | 29 | 101 | 0.04021 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_316_1_line_41 |  | 32 | 33 | 0.0628 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
42 | MV_316_1_line_42 |  | 32 | 34 | 0.13992 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
43 | MV_316_1_line_43 |  | 32 | 35 | 0.43815 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
44 | MV_316_1_line_44 |  | 34 | 40 | 0.003649 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_316_1_line_45 |  | 35 | 86 | 0.039413 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
46 | MV_316_1_line_46 |  | 36 | 37 | 0.026596 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_316_1_line_47 |  | 39 | 41 | 0.0215 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_316_1_line_48 |  | 42 | 88 | 0.33005 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
49 | MV_316_1_line_49 |  | 43 | 44 | 0.053573 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
50 | MV_316_1_line_50 |  | 43 | 45 | 0.058582 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
51 | MV_316_1_line_51 |  | 44 | 46 | 0.43042 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
52 | MV_316_1_line_52 |  | 45 | 47 | 0.017396 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
53 | MV_316_1_line_53 |  | 46 | 50 | 0.11061 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
54 | MV_316_1_line_54 |  | 46 | 51 | 0.36216 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
55 | MV_316_1_line_55 |  | 47 | 52 | 0.019614 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
56 | MV_316_1_line_56 |  | 47 | 48 | 0.42625 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
57 | MV_316_1_line_57 |  | 48 | 49 | 1.2539 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
58 | MV_316_1_line_58 |  | 49 | 69 | 0.54737 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
59 | MV_316_1_line_59 |  | 49 | 70 | 0.15529 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
60 | MV_316_1_line_60 |  | 51 | 53 | 0.22955 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
61 | MV_316_1_line_61 |  | 51 | 54 | 0.30964 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_316_1_line_62 |  | 53 | 67 | 0.078625 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
63 | MV_316_1_line_63 |  | 54 | 68 | 0.085629 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_316_1_line_64 |  | 55 | 56 | 0.11385 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
65 | MV_316_1_line_65 |  | 55 | 57 | 1.8746 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
66 | MV_316_1_line_66 |  | 55 | 58 | 1.9501 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
67 | MV_316_1_line_67 |  | 56 | 59 | 0.10114 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
68 | MV_316_1_line_68 |  | 59 | 60 | 1.2708 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
69 | MV_316_1_line_69 |  | 60 | 61 | 0.016435 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
70 | MV_316_1_line_70 |  | 61 | 62 | 2.2147 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
71 | MV_316_1_line_71 |  | 62 | 66 | 0.039039 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
72 | MV_316_1_line_72 |  | 63 | 64 | 0.027482 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
73 | MV_316_1_line_73 |  | 63 | 65 | 0.82862 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
74 | MV_316_1_line_74 |  | 64 | 83 | 0.005664 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
75 | MV_316_1_line_75 |  | 65 | 86 | 0.063887 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
76 | MV_316_1_line_76 |  | 66 | 67 | 1.9815 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
77 | MV_316_1_line_77 |  | 69 | 78 | 0.004849 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_316_1_line_78 |  | 69 | 74 | 0.55731 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
79 | MV_316_1_line_79 |  | 71 | 72 | 0.41949 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_316_1_line_80 |  | 71 | 73 | 0.064904 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_316_1_line_81 |  | 72 | 77 | 0.047184 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_316_1_line_82 |  | 72 | 74 | 0.54154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_316_1_line_83 |  | 74 | 75 | 0.6717 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
84 | MV_316_1_line_84 |  | 74 | 76 | 0.006421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_316_1_line_85 |  | 75 | 106 | 0.003817 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
86 | MV_316_1_line_86 |  | 75 | 107 | 0.045528 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
87 | MV_316_1_line_87 |  | 79 | 80 | 0.099226 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_316_1_line_88 |  | 79 | 81 | 0.079457 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
89 | MV_316_1_line_89 |  | 80 | 82 | 0.015138 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_316_1_line_90 |  | 81 | 83 | 0.39693 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
91 | MV_316_1_line_91 |  | 82 | 84 | 0.063864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_316_1_line_92 |  | 87 | 88 | 0.013374 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_316_1_line_93 |  | 88 | 89 | 0.53744 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_316_1_line_94 |  | 88 | 90 | 0.28419 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_316_1_line_95 |  | 88 | 91 | 0.23781 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_316_1_line_96 |  | 89 | 92 | 0.004447 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_316_1_line_97 |  | 90 | 93 | 0.005957 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_316_1_line_98 |  | 91 | 94 | 0.56138 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_316_1_line_99 |  | 91 | 95 | 0.039505 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_316_1_line_100 |  | 94 | 96 | 0.7648 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_316_1_line_101 |  | 94 | 97 | 0.002135 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_316_1_line_102 |  | 96 | 98 | 0.004029 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_316_1_line_103 |  | 99 | 102 | 0.032808 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_316_1_line_104 |  | 100 | 103 | 0.050973 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_316_1_line_105 |  | 101 | 104 | 0.083373 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
106 | MV_316_1_line_106 |  | 102 | 105 | 0.004681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_316_1_line_107 |  | 105 | 110 | 0.10681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_316_1_line_108 |  | 107 | 108 | 0.011203 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
109 | MV_316_1_line_109 |  | 109 | 110 | 0.01819 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_316_1_trafo_168 | 25 MVA 110/20 kV | 111 | 31 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2537371.2886 | 1184816.4896
1 | 2537391.3037 | 1184865.4857
2 | 2538179.2969 | 1183656.3457
3 | 2537150.7761 | 1185154.6515
4 | 2538095.1883 | 1183495.4355
5 | 2537121.7611 | 1185233.3125
6 | 2536717.3087 | 1183473.0748
7 | 2537129.0654 | 1183045.8233
8 | 2536698.3957 | 1183468.1508
9 | 2538134.4424 | 1183363.1544
10 | 2538129.0154 | 1183364.011
11 | 2538082.2685 | 1182714.5267
12 | 2537895.2555 | 1183192.5251
13 | 2537926.6749 | 1182533.7813
14 | 2538185.3626 | 1182456.0366
15 | 2538025.7462 | 1182701.5602
16 | 2537959.5979 | 1182485.0561
17 | 2538354.0736 | 1182181.8407
18 | 2538222.7179 | 1182474.6168
19 | 2538349.0175 | 1182132.8652
20 | 2538375.1657 | 1182075.9859
21 | 2538039.2846 | 1182092.9756
22 | 2538313.2118 | 1181869.3854
23 | 2538373.0761 | 1182183.3638
24 | 2537999.619 | 1182147.195
25 | 2537631.2138 | 1182229.4818
26 | 2537964.3579 | 1181766.1784
27 | 2538033.7797 | 1182092.3212
28 | 2537931.3779 | 1182142.3098
29 | 2538512.4379 | 1181817.8055
30 | 2538272.8765 | 1181846.5329
31 | 2537628.6189 | 1182227.4188
32 | 2537654.6178 | 1182383.9476
33 | 2537591.8408 | 1182382.2568
34 | 2537608.6892 | 1182473.3437
35 | 2537617.2635 | 1182687.7092
36 | 2537902.7657 | 1181821.1039
37 | 2537877.917 | 1181811.6232
38 | 2537940.5563 | 1181754.8492
39 | 2537646.8561 | 1181657.8619
40 | 2537610.0455 | 1182476.7315
41 | 2537643.7984 | 1181639.2722
42 | 2538401.514 | 1182196.3825
43 | 2536589.4802 | 1181261.2389
44 | 2536541.0228 | 1181238.6168
45 | 2536647.0658 | 1181268.6991
46 | 2536304.3627 | 1180955.3149
47 | 2536646.4693 | 1181251.3178
48 | 2536688.3913 | 1180827.1337
49 | 2537687.7342 | 1181258.9772
50 | 2536194.6702 | 1180941.0865
51 | 2536414.3671 | 1180610.2606
52 | 2536665.5165 | 1181255.9975
53 | 2536254.719 | 1180445.3149
54 | 2536676.2088 | 1180656.8773
55 | 2534887.5404 | 1182679.3024
56 | 2534776.936 | 1182651.0466
57 | 2535045.5692 | 1184547.2096
58 | 2536672.1758 | 1183465.3814
59 | 2534807.6127 | 1182554.6695
60 | 2533807.2255 | 1181770.9257
61 | 2533796.3969 | 1181758.5384
62 | 2534336.4554 | 1179610.7068
63 | 2536866.8065 | 1182587.2025
64 | 2536883.7115 | 1182608.8697
65 | 2537521.2951 | 1182725.9323
66 | 2534374.9309 | 1179617.9334
67 | 2536200.5358 | 1180388.3425
68 | 2536747.9398 | 1180703.9454
69 | 2538113.0354 | 1181175.7275
70 | 2537618.2443 | 1181386.0675
71 | 2538038.3231 | 1181569.045
72 | 2538098.0488 | 1181347.4462
73 | 2537982.7051 | 1181535.3355
74 | 2538428.4553 | 1181353.207
75 | 2538660.1322 | 1181552.2842
76 | 2538433.3176 | 1181357.4149
77 | 2538060.6966 | 1181376.3379
78 | 2538113.3214 | 1181170.8885
79 | 2537170.8625 | 1182831.0177
80 | 2537085.5585 | 1182867.1125
81 | 2537118.1413 | 1182771.5712
82 | 2537085.0229 | 1182882.2378
83 | 2536887.6941 | 1182612.9078
84 | 2537021.2322 | 1182885.293
85 | 2537127.2319 | 1183055.159
86 | 2537580.6482 | 1182702.2932
87 | 2538455.8891 | 1182424.7075
88 | 2538461.0077 | 1182412.3479
89 | 2538512.1383 | 1182623.3191
90 | 2538563.7752 | 1182197.259
91 | 2538593.849 | 1182338.0631
92 | 2538510.5164 | 1182627.4604
93 | 2538569.1323 | 1182199.8944
94 | 2538894.9781 | 1182238.557
95 | 2538629.3806 | 1182355.3305
96 | 2538715.0561 | 1182007.467
97 | 2538896.0358 | 1182236.7007
98 | 2538712.1602 | 1182010.276
99 | 2538511.4689 | 1181749.5659
100 | 2538224.9623 | 1181728.0272
101 | 2538546.578 | 1181796.5665
102 | 2538484.3057 | 1181731.0569
103 | 2538181.4863 | 1181701.4167
104 | 2538598.8746 | 1181861.4981
105 | 2538480.4297 | 1181728.4174
106 | 2538663.2178 | 1181554.5427
107 | 2538632.4835 | 1181588.4548
108 | 2538623.0431 | 1181582.3815
109 | 2538388.3701 | 1181650.6875
110 | 2538394.2749 | 1181666.4022
111 | 2537628.6189 | 1182227.4188

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99429 | -0.014093 | 0.39574 | 0.19167
1 | 0.99429 | -0.014091 | 0 | 0
2 | 0.99555 | -0.0045069 | 0.11834 | 0.057317
3 | 0.99426 | -0.013947 | 0 | 0
4 | 0.99568 | -0.0056077 | 0 | 0
5 | 0.99425 | -0.013885 | 0.065642 | 0.031792
6 | 0.99781 | -0.050385 | 0 | 0
7 | 0.99848 | -0.035335 | 0 | 0
8 | 0.99779 | -0.050756 | 0.19878 | 0.096274
9 | 0.99583 | -0.0044047 | 0.40581 | 0.19654
10 | 0.99583 | -0.0044315 | 0 | 0
11 | 0.99694 | -0.013817 | 0 | 0
12 | 0.99565 | -0.0055676 | 0.32033 | 0.15514
13 | 0.99687 | -0.013248 | 0 | 0
14 | 0.99757 | -0.018767 | 0 | 0
15 | 0.99693 | -0.013697 | 0.16247 | 0.078689
16 | 0.99685 | -0.013151 | 0.14179 | 0.068672
17 | 0.99861 | -0.026898 | 0 | 0
18 | 0.99756 | -0.018618 | 0.30005 | 0.14532
19 | 0.99858 | -0.026584 | 0 | 0
20 | 0.99855 | -0.026311 | 0.36789 | 0.17818
21 | 0.99901 | -0.019225 | 0 | 0
22 | 0.99802 | -0.022173 | 0 | 0
23 | 0.9986 | -0.027067 | 0.22111 | 0.10709
24 | 0.99899 | -0.019096 | 0 | 0
25 | 0.99999 | -0.00018037 | 0 | 0
26 | 0.99813 | -0.011582 | 0 | 0
27 | 0.999 | -0.019202 | 0.34379 | 0.16651
28 | 0.99898 | -0.019025 | 0.091155 | 0.044148
29 | 0.99772 | -0.019754 | 0 | 0
30 | 0.998 | -0.022317 | 0.25671 | 0.12433
31 | 1 | 0 | -12.2321 | -4.9906
32 | 0.9997 | -0.0069051 | 0 | 0
33 | 0.99968 | -0.0075263 | 0.34197 | 0.16562
34 | 0.99969 | -0.0070289 | 0 | 0
35 | 0.99925 | -0.017573 | 0 | 0
36 | 0.9981 | -0.011312 | 0 | 0
37 | 0.99809 | -0.011381 | 0.21203 | 0.10269
38 | 0.99813 | -0.01156 | 0.070332 | 0.034064
39 | 0.99765 | -0.0072009 | 0 | 0
40 | 0.99969 | -0.0070225 | 0.14801 | 0.071682
41 | 0.99762 | -0.0069414 | 1.0054 | 0.48695
42 | 0.99859 | -0.027256 | 0 | 0
43 | 0.98582 | -0.52219 | 0.28809 | 0.13953
44 | 0.98584 | -0.52165 | 0 | 0
45 | 0.9858 | -0.52272 | 0 | 0
46 | 0.98601 | -0.51719 | 0 | 0
47 | 0.98579 | -0.52288 | 0 | 0
48 | 0.98549 | -0.53636 | 0 | 0
49 | 0.98508 | -0.54665 | 0 | 0
50 | 0.986 | -0.51796 | 0.18051 | 0.087425
51 | 0.98636 | -0.50205 | 0 | 0
52 | 0.98579 | -0.52288 | 0.091659 | 0.044392
53 | 0.98648 | -0.49913 | 0.12309 | 0.059614
54 | 0.98623 | -0.50083 | 0 | 0
55 | 0.99416 | -0.19063 | 0.13567 | 0.06571
56 | 0.99407 | -0.19257 | 0 | 0
57 | 0.99394 | -0.20298 | 0.17277 | 0.083677
58 | 0.99777 | -0.051241 | 0 | 0
59 | 0.994 | -0.19429 | 0.44581 | 0.21592
60 | 0.99212 | -0.26921 | 0 | 0
61 | 0.99211 | -0.26947 | 0.24471 | 0.11852
62 | 0.98912 | -0.3914 | 0.099135 | 0.048013
63 | 0.99904 | -0.022504 | 0 | 0
64 | 0.99903 | -0.022804 | 0.31841 | 0.15421
65 | 0.99915 | -0.020047 | 0 | 0
66 | 0.9891 | -0.39195 | 0 | 0
67 | 0.98652 | -0.49808 | 0.19841 | 0.096095
68 | 0.98619 | -0.50047 | 0.349 | 0.16903
69 | 0.98491 | -0.5506 | 0 | 0
70 | 0.98508 | -0.5467 | 0.073789 | 0.035738
71 | 0.98431 | -0.55037 | 0 | 0
72 | 0.9844 | -0.55106 | 0 | 0
73 | 0.98429 | -0.55024 | 0.166 | 0.080396
74 | 0.98476 | -0.55387 | 0 | 0
75 | 0.98471 | -0.55499 | 0 | 0
76 | 0.98475 | -0.55384 | 0.39207 | 0.18989
77 | 0.98438 | -0.55085 | 0.3541 | 0.1715
78 | 0.98491 | -0.55059 | 0.25322 | 0.12264
79 | 0.99898 | -0.024164 | 0.21722 | 0.10521
80 | 0.99897 | -0.024074 | 0 | 0
81 | 0.99901 | -0.023345 | 0 | 0
82 | 0.99897 | -0.024059 | 0 | 0
83 | 0.99903 | -0.022812 | 0 | 0
84 | 0.99896 | -0.023992 | 0.091728 | 0.044426
85 | 0.99848 | -0.03534 | 0.14908 | 0.072201
86 | 0.99921 | -0.018527 | 0.10075 | 0.048796
87 | 0.99844 | -0.028077 | 0.33253 | 0.16105
88 | 0.99844 | -0.02813 | 0 | 0
89 | 0.99832 | -0.027186 | 0 | 0
90 | 0.99839 | -0.027693 | 0 | 0
91 | 0.99822 | -0.026522 | 0 | 0
92 | 0.99832 | -0.027177 | 0.18097 | 0.08765
93 | 0.99839 | -0.027683 | 0.14683 | 0.071114
94 | 0.9978 | -0.02347 | 0 | 0
95 | 0.99821 | -0.026599 | 0.16184 | 0.078384
96 | 0.99744 | -0.020491 | 0 | 0
97 | 0.9978 | -0.023464 | 0.21278 | 0.10305
98 | 0.99744 | -0.020473 | 0.37295 | 0.18063
99 | 0.99767 | -0.019323 | 0 | 0
100 | 0.99762 | -0.018936 | 0 | 0
101 | 0.9977 | -0.019611 | 0.12989 | 0.062908
102 | 0.99766 | -0.019211 | 0.23044 | 0.11161
103 | 0.9976 | -0.01905 | 0.18402 | 0.089123
104 | 0.99768 | -0.019783 | 0.16917 | 0.081933
105 | 0.99765 | -0.019208 | 0 | 0
106 | 0.98471 | -0.55499 | 0.17347 | 0.084017
107 | 0.9847 | -0.55502 | 0 | 0
108 | 0.9847 | -0.55503 | 0.18442 | 0.089317
109 | 0.99764 | -0.019114 | 0.070322 | 0.034059
110 | 0.99765 | -0.01913 | 0 | 0
111 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.065645 | 0.019273 | -0.065644 | -0.020522 | 2.8018e-07 | -0.001249 | 0.0019863 | 0.0019968 | 0.0019968 | 0.99429 | -0.014093 | 0.99429 | -0.014091 | 0.90765
1 | -0.46139 | -0.21094 | 0.46193 | 0.20961 | 0.00054573 | -0.0013289 | 0.014729 | 0.014709 | 0.014729 | 0.99429 | -0.014093 | 0.99555 | -0.0045069 | 7.0139
2 | 0.065644 | 0.020522 | -0.065642 | -0.029813 | 2.1896e-06 | -0.0092913 | 0.0019968 | 0.0020932 | 0.0020932 | 0.99429 | -0.014091 | 0.99426 | -0.013947 | 0.95147
3 | -0.58028 | -0.26693 | 0.58036 | 0.26258 | 8.4407e-05 | -0.0043497 | 0.018521 | 0.018468 | 0.018521 | 0.99555 | -0.0045069 | 0.99568 | -0.0056077 | 8.4186
4 | 0.065642 | 0.029813 | -0.065642 | -0.031792 | 4.96e-07 | -0.0019784 | 0.0020932 | 0.0021176 | 0.0021176 | 0.99426 | -0.013947 | 0.99425 | -0.013885 | 0.96256
5 | -0.58036 | -0.26258 | 0.58044 | 0.26247 | 8.2461e-05 | -0.00010899 | 0.018468 | 0.018466 | 0.018468 | 0.99568 | -0.0056077 | 0.99583 | -0.0044315 | 8.7944
6 | -4.1554 | -1.6522 | 4.1578 | 1.5948 | 0.0023858 | -0.05739 | 0.12937 | 0.12875 | 0.12937 | 0.99781 | -0.050385 | 0.99848 | -0.035335 | 15.3651
7 | 4.1554 | 1.6522 | -4.1554 | -1.6536 | 5.9869e-05 | -0.0014317 | 0.12937 | 0.12939 | 0.12939 | 0.99781 | -0.050385 | 0.99779 | -0.050756 | 15.367
8 | 0.14908 | 0.071476 | -0.14908 | -0.072201 | 3.99e-08 | -0.00072474 | 0.0047798 | 0.0047889 | 0.0047889 | 0.99848 | -0.035335 | 0.99848 | -0.03534 | 0.56875
9 | -4.3069 | -1.6663 | 4.3093 | 1.6111 | 0.0024474 | -0.055196 | 0.13351 | 0.13292 | 0.13351 | 0.99848 | -0.035335 | 0.99915 | -0.020047 | 15.8566
10 | 3.9566 | 1.5574 | -3.9565 | -1.5593 | 7.3911e-05 | -0.0019618 | 0.12302 | 0.12304 | 0.12304 | 0.99779 | -0.050756 | 0.99777 | -0.051241 | 14.6127
11 | -0.40581 | -0.19654 | 0.40581 | 0.19641 | 1.2495e-06 | -0.00012936 | 0.013071 | 0.013069 | 0.013071 | 0.99583 | -0.0044047 | 0.99583 | -0.0044315 | 5.9413
12 | -1.3066 | -0.61372 | 1.3082 | 0.5983 | 0.001559 | -0.015419 | 0.041847 | 0.041654 | 0.041847 | 0.99583 | -0.0044315 | 0.99694 | -0.013817 | 19.0215
13 | 0.32038 | 0.15483 | -0.32033 | -0.15514 | 5.4984e-05 | -0.00030872 | 0.010315 | 0.010319 | 0.010319 | 0.99583 | -0.0044315 | 0.99565 | -0.0055676 | 4.914
14 | 0.1418 | 0.056725 | -0.14179 | -0.067277 | 1.1927e-05 | -0.010552 | 0.0044224 | 0.0045448 | 0.0045448 | 0.99694 | -0.013817 | 0.99687 | -0.013248 | 2.0658
15 | -1.6125 | -0.73221 | 1.6136 | 0.72521 | 0.0010814 | -0.0070069 | 0.051279 | 0.051192 | 0.051279 | 0.99694 | -0.013817 | 0.99757 | -0.018767 | 23.3087
16 | 0.16247 | 0.077192 | -0.16247 | -0.078689 | 2.2935e-06 | -0.0014967 | 0.0052086 | 0.0052273 | 0.0052273 | 0.99694 | -0.013817 | 0.99693 | -0.013697 | 2.3761
17 | 0.14179 | 0.067277 | -0.14179 | -0.068672 | 1.6278e-06 | -0.0013948 | 0.0045448 | 0.0045623 | 0.0045623 | 0.99687 | -0.013248 | 0.99685 | -0.013151 | 2.0738
18 | -1.9136 | -0.86954 | 1.9157 | 0.85998 | 0.0021104 | -0.0095575 | 0.060824 | 0.060703 | 0.060824 | 0.99757 | -0.018767 | 0.99861 | -0.026898 | 27.6475
19 | 0.30006 | 0.14433 | -0.30005 | -0.14532 | 5.1663e-06 | -0.0009876 | 0.0096353 | 0.0096477 | 0.0096477 | 0.99757 | -0.018767 | 0.99756 | -0.018618 | 4.3853
20 | -4.955 | -2.2096 | 4.9567 | 2.1828 | 0.0016721 | -0.026839 | 0.15683 | 0.1565 | 0.15683 | 0.99861 | -0.026898 | 0.99901 | -0.019225 | 18.6264
21 | 1.0415 | 0.46783 | -1.0409 | -0.47834 | 0.00065675 | -0.01051 | 0.033006 | 0.033134 | 0.033134 | 0.99861 | -0.026898 | 0.99802 | -0.022173 | 15.0608
22 | 1.6299 | 0.70687 | -1.6298 | -0.70872 | 1.181e-05 | -0.0018528 | 0.051356 | 0.051377 | 0.051377 | 0.99861 | -0.026898 | 0.9986 | -0.027067 | 6.1018
23 | 0.36792 | 0.17494 | -0.3679 | -0.17669 | 1.3673e-05 | -0.0017509 | 0.011777 | 0.011799 | 0.011799 | 0.99861 | -0.026898 | 0.99858 | -0.026584 | 5.363
24 | 0.3679 | 0.17669 | -0.36789 | -0.17818 | 1.1649e-05 | -0.0014864 | 0.011799 | 0.011817 | 0.011817 | 0.99858 | -0.026584 | 0.99855 | -0.026311 | 5.3715
25 | 0.091157 | 0.039006 | -0.091156 | -0.04251 | 1.6349e-06 | -0.0035045 | 0.0028651 | 0.0029065 | 0.0029065 | 0.99901 | -0.019225 | 0.99899 | -0.019096 | 1.3211
26 | -6.6812 | -2.987 | 6.6868 | 2.9397 | 0.0056004 | -0.047242 | 0.21148 | 0.21086 | 0.21148 | 0.99901 | -0.019225 | 0.99999 | -0.00018037 | 25.116
27 | 1.2895 | 0.59882 | -1.2883 | -0.61124 | 0.0012145 | -0.012422 | 0.041085 | 0.041242 | 0.041242 | 0.99901 | -0.019225 | 0.99813 | -0.011582 | 18.7462
28 | 0.34379 | 0.16637 | -0.34379 | -0.16651 | 8.9902e-07 | -0.00013146 | 0.011036 | 0.011038 | 0.011038 | 0.99901 | -0.019225 | 0.999 | -0.019202 | 5.0173
29 | 0.78414 | 0.35406 | -0.78389 | -0.36117 | 0.00025068 | -0.0071091 | 0.024886 | 0.024972 | 0.024972 | 0.99802 | -0.022173 | 0.99772 | -0.019754 | 11.351
30 | 0.25672 | 0.12428 | -0.25671 | -0.12433 | 5.6221e-06 | -5.1602e-05 | 0.0082499 | 0.0082506 | 0.0082506 | 0.99802 | -0.022173 | 0.998 | -0.022317 | 3.9288
31 | 1.4087 | 0.60163 | -1.4087 | -0.604 | 1.123e-05 | -0.0023726 | 0.044282 | 0.044309 | 0.044309 | 0.9986 | -0.027067 | 0.99859 | -0.027256 | 5.2623
32 | 0.091156 | 0.04251 | -0.091155 | -0.044148 | 7.8065e-07 | -0.0016378 | 0.0029065 | 0.0029268 | 0.0029268 | 0.99899 | -0.019096 | 0.99898 | -0.019025 | 1.3304
33 | -12.218 | -4.9803 | 12.2181 | 4.9801 | 8.7873e-05 | -0.00017222 | 0.38088 | 0.38088 | 0.38088 | 0.99999 | -0.00018037 | 1 | 0 | 45.2354
34 | 5.5312 | 2.0405 | -5.5299 | -2.0587 | 0.0013486 | -0.018172 | 0.17019 | 0.17039 | 0.17039 | 0.99999 | -0.00018037 | 0.9997 | -0.0069051 | 20.236
35 | 0.070333 | 0.033437 | -0.070332 | -0.034064 | 1.7914e-07 | -0.00062697 | 0.0022523 | 0.0022601 | 0.0022601 | 0.99813 | -0.011582 | 0.99813 | -0.01156 | 1.0273
36 | 1.006 | 0.47774 | -1.0054 | -0.48644 | 0.00051751 | -0.0087004 | 0.032208 | 0.032319 | 0.032319 | 0.99813 | -0.011582 | 0.99765 | -0.0072009 | 14.6905
37 | 0.21204 | 0.10006 | -0.21203 | -0.10266 | 6.7491e-06 | -0.0026008 | 0.0067809 | 0.0068134 | 0.0068134 | 0.99813 | -0.011582 | 0.9981 | -0.011312 | 3.097
38 | 0.30078 | 0.13867 | -0.30077 | -0.14181 | 1.6259e-05 | -0.0031344 | 0.0095831 | 0.0096215 | 0.0096215 | 0.99772 | -0.019754 | 0.99767 | -0.019323 | 4.3734
39 | 0.18404 | 0.078704 | -0.18402 | -0.089065 | 1.9944e-05 | -0.010361 | 0.0057914 | 0.0059158 | 0.0059158 | 0.99772 | -0.019754 | 0.99762 | -0.018936 | 2.689
40 | 0.29907 | 0.14379 | -0.29906 | -0.14474 | 4.9547e-06 | -0.0009542 | 0.0096013 | 0.0096133 | 0.0096133 | 0.99772 | -0.019754 | 0.9977 | -0.019611 | 4.3697
41 | 0.34197 | 0.16555 | -0.34197 | -0.16562 | 6.9398e-06 | -7.093e-05 | 0.010971 | 0.010972 | 0.010972 | 0.9997 | -0.0069051 | 0.99968 | -0.0075263 | 3.1349
42 | 0.14801 | 0.066799 | -0.14801 | -0.071595 | 1.5043e-06 | -0.0047962 | 0.004689 | 0.0047476 | 0.0047476 | 0.9997 | -0.0069051 | 0.99969 | -0.0070289 | 1.3115
43 | 5.0399 | 1.8263 | -5.038 | -1.858 | 0.0019253 | -0.031674 | 0.15479 | 0.15512 | 0.15512 | 0.9997 | -0.0069051 | 0.99925 | -0.017573 | 18.4233
44 | 0.14801 | 0.071595 | -0.14801 | -0.071682 | 1.098e-07 | -8.7038e-05 | 0.0047476 | 0.0047487 | 0.0047487 | 0.99969 | -0.0070289 | 0.99969 | -0.0070225 | 2.1585
45 | 5.038 | 1.858 | -5.0378 | -1.8609 | 0.00017359 | -0.0028473 | 0.15512 | 0.15515 | 0.15515 | 0.99925 | -0.017573 | 0.99921 | -0.018527 | 18.4269
46 | 0.21203 | 0.10266 | -0.21203 | -0.10269 | 2.1999e-06 | -3.0251e-05 | 0.0068134 | 0.0068138 | 0.0068138 | 0.9981 | -0.011312 | 0.99809 | -0.011381 | 3.2447
47 | 1.0054 | 0.48644 | -1.0054 | -0.48695 | 2.9987e-05 | -0.00050202 | 0.032319 | 0.032326 | 0.032326 | 0.99765 | -0.0072009 | 0.99762 | -0.0069414 | 14.6935
48 | 1.4087 | 0.604 | -1.4085 | -0.62456 | 0.0002013 | -0.020563 | 0.044309 | 0.044548 | 0.044548 | 0.99859 | -0.027256 | 0.99844 | -0.02813 | 6.9824
49 | -1.9784 | -0.68505 | 1.9785 | 0.6811 | 3.6828e-05 | -0.0039442 | 0.061309 | 0.061271 | 0.061309 | 0.98582 | -0.52219 | 0.98584 | -0.52165 | 7.2813
50 | 1.6903 | 0.54552 | -1.6903 | -0.54984 | 2.9023e-05 | -0.0043231 | 0.052012 | 0.052051 | 0.052051 | 0.98582 | -0.52219 | 0.9858 | -0.52272 | 6.1818
51 | -1.9785 | -0.6811 | 1.9788 | 0.6494 | 0.00029425 | -0.031697 | 0.061271 | 0.060972 | 0.061271 | 0.98584 | -0.52165 | 0.98601 | -0.51719 | 7.2768
52 | 1.6903 | 0.54984 | -1.6903 | -0.55112 | 8.6269e-06 | -0.0012837 | 0.052051 | 0.052063 | 0.052063 | 0.9858 | -0.52272 | 0.98579 | -0.52288 | 6.1832
53 | 0.18051 | 0.08728 | -0.18051 | -0.087425 | 1.3612e-06 | -0.00014499 | 0.0058702 | 0.0058721 | 0.0058721 | 0.98601 | -0.51719 | 0.986 | -0.51796 | 0.9104
54 | -2.1593 | -0.73668 | 2.1599 | 0.73661 | 0.00057581 | -7.8147e-05 | 0.066795 | 0.066786 | 0.066795 | 0.98601 | -0.51719 | 0.98636 | -0.50205 | 8.1457
55 | 0.091659 | 0.042936 | -0.091659 | -0.044392 | 3.1726e-08 | -0.0014562 | 0.002964 | 0.0029823 | 0.0029823 | 0.98579 | -0.52288 | 0.98579 | -0.52288 | 0.3542
56 | 1.5986 | 0.50819 | -1.5983 | -0.50873 | 0.00036665 | -0.00054113 | 0.049122 | 0.049132 | 0.049132 | 0.98579 | -0.52288 | 0.98549 | -0.53636 | 5.9917
57 | 1.5983 | 0.50873 | -1.5977 | -0.60121 | 0.00056364 | -0.092484 | 0.049132 | 0.050026 | 0.050026 | 0.98549 | -0.53636 | 0.98508 | -0.54665 | 5.9413
58 | 1.5239 | 0.57699 | -1.5237 | -0.61735 | 0.00023046 | -0.040364 | 0.047752 | 0.048186 | 0.048186 | 0.98508 | -0.54665 | 0.98491 | -0.5506 | 5.7228
59 | 0.073789 | 0.024224 | -0.073789 | -0.035738 | 1.5481e-07 | -0.011513 | 0.0022759 | 0.0024026 | 0.0024026 | 0.98508 | -0.54665 | 0.98508 | -0.5467 | 0.28535
60 | -2.5089 | -0.89647 | 2.5092 | 0.87964 | 0.00025486 | -0.016832 | 0.077974 | 0.077807 | 0.077974 | 0.98636 | -0.50205 | 0.98648 | -0.49913 | 9.2606
61 | 0.34907 | 0.15987 | -0.34901 | -0.16704 | 5.2602e-05 | -0.0071761 | 0.011236 | 0.011326 | 0.011326 | 0.98636 | -0.50205 | 0.98623 | -0.50083 | 5.148
62 | -2.6323 | -0.93926 | 2.6324 | 0.9335 | 9.6173e-05 | -0.0057579 | 0.081785 | 0.081728 | 0.081785 | 0.98648 | -0.49913 | 0.98652 | -0.49808 | 9.7132
63 | 0.34901 | 0.16704 | -0.349 | -0.16903 | 1.4696e-05 | -0.0019841 | 0.011326 | 0.011351 | 0.011351 | 0.98623 | -0.50083 | 0.98619 | -0.50047 | 5.1595
64 | 3.6375 | 1.4022 | -3.6372 | -1.4106 | 0.00026718 | -0.0083511 | 0.1132 | 0.11329 | 0.11329 | 0.99416 | -0.19063 | 0.99407 | -0.19257 | 13.4547
65 | 0.17279 | 0.081172 | -0.17277 | -0.083677 | 2.0683e-05 | -0.0025049 | 0.0055434 | 0.0055754 | 0.0055754 | 0.99416 | -0.19063 | 0.99394 | -0.20298 | 0.86441
66 | -3.946 | -1.5491 | 3.9565 | 1.5593 | 0.010526 | 0.010232 | 0.12309 | 0.12304 | 0.12309 | 0.99416 | -0.19063 | 0.99777 | -0.051241 | 15.0113
67 | 3.6372 | 1.4106 | -3.637 | -1.418 | 0.00023772 | -0.0074174 | 0.11329 | 0.11337 | 0.11337 | 0.99407 | -0.19257 | 0.994 | -0.19429 | 13.4642
68 | 3.1912 | 1.2021 | -3.1867 | -1.1989 | 0.0044438 | 0.0031894 | 0.099035 | 0.099068 | 0.099068 | 0.994 | -0.19429 | 0.99212 | -0.26921 | 12.0815
69 | 3.1867 | 1.1989 | -3.1867 | -1.2001 | 2.9522e-05 | -0.0012089 | 0.099068 | 0.099081 | 0.099081 | 0.99212 | -0.26921 | 0.99211 | -0.26947 | 11.7673
70 | 2.942 | 1.0816 | -2.9354 | -1.0777 | 0.0065699 | 0.0038859 | 0.091205 | 0.091261 | 0.091261 | 0.99211 | -0.26947 | 0.98912 | -0.3914 | 11.1294
71 | 2.8363 | 1.0297 | -2.8362 | -1.0325 | 5.5422e-05 | -0.0028672 | 0.088063 | 0.088092 | 0.088092 | 0.98912 | -0.3914 | 0.9891 | -0.39195 | 10.4623
72 | 0.62738 | 0.26874 | -0.62737 | -0.26881 | 3.8096e-06 | -6.5489e-05 | 0.019721 | 0.019722 | 0.019722 | 0.99904 | -0.022504 | 0.99903 | -0.022804 | 2.4051
73 | -0.62738 | -0.26874 | 0.62743 | 0.2056 | 5.6953e-05 | -0.063143 | 0.019721 | 0.019076 | 0.019721 | 0.99904 | -0.022504 | 0.99915 | -0.020047 | 2.3422
74 | 0.30897 | 0.1146 | -0.30897 | -0.11503 | 9.3985e-08 | -0.00043183 | 0.009522 | 0.0095264 | 0.0095264 | 0.99903 | -0.022804 | 0.99903 | -0.022812 | 1.1314
75 | -4.9368 | -1.8167 | 4.937 | 1.8121 | 0.00026998 | -0.0046254 | 0.15198 | 0.15194 | 0.15198 | 0.99915 | -0.020047 | 0.99921 | -0.018527 | 18.0504
76 | 2.8362 | 1.0325 | -2.8308 | -1.0296 | 0.0054835 | 0.0029338 | 0.088092 | 0.088142 | 0.088142 | 0.9891 | -0.39195 | 0.98652 | -0.49808 | 10.7491
77 | 0.25322 | 0.12253 | -0.25322 | -0.12264 | 4.4012e-07 | -0.00011218 | 0.0082451 | 0.0082466 | 0.0082466 | 0.98491 | -0.5506 | 0.98491 | -0.55059 | 3.7484
78 | 1.2705 | 0.49482 | -1.2703 | -0.53597 | 0.0001647 | -0.041148 | 0.039962 | 0.040417 | 0.040417 | 0.98491 | -0.5506 | 0.98476 | -0.55387 | 4.8001
79 | -0.166 | -0.078896 | 0.16602 | 0.069196 | 1.5914e-05 | -0.0097001 | 0.0053903 | 0.0052744 | 0.0053903 | 0.98431 | -0.55037 | 0.9844 | -0.55106 | 2.4501
80 | 0.166 | 0.078896 | -0.166 | -0.080396 | 2.5264e-06 | -0.0015006 | 0.0053903 | 0.0054093 | 0.0054093 | 0.98431 | -0.55037 | 0.98429 | -0.55024 | 2.4588
81 | 0.35411 | 0.17041 | -0.3541 | -0.1715 | 8.3757e-06 | -0.0010892 | 0.011524 | 0.011538 | 0.011538 | 0.9844 | -0.55106 | 0.98438 | -0.55085 | 5.2446
82 | -0.52013 | -0.23961 | 0.52033 | 0.22713 | 0.00020204 | -0.012474 | 0.016793 | 0.016643 | 0.016793 | 0.9844 | -0.55106 | 0.98476 | -0.55387 | 7.6333
83 | 0.35791 | 0.1191 | -0.35789 | -0.16885 | 1.5721e-05 | -0.049751 | 0.011057 | 0.011601 | 0.011601 | 0.98476 | -0.55387 | 0.98471 | -0.55499 | 1.3778
84 | 0.39207 | 0.18974 | -0.39207 | -0.18989 | 1.3978e-06 | -0.00014826 | 0.012769 | 0.01277 | 0.01277 | 0.98476 | -0.55387 | 0.98475 | -0.55384 | 5.8047
85 | 0.17347 | 0.083735 | -0.17347 | -0.084017 | 2.2294e-08 | -0.00028276 | 0.005647 | 0.0056506 | 0.0056506 | 0.98471 | -0.55499 | 0.98471 | -0.55499 | 0.67109
86 | 0.18442 | 0.085114 | -0.18442 | -0.088487 | 2.9748e-07 | -0.0033726 | 0.0059543 | 0.0059965 | 0.0059965 | 0.98471 | -0.55499 | 0.9847 | -0.55502 | 0.71217
87 | 0.091731 | 0.04018 | -0.091729 | -0.042544 | 1.12e-06 | -0.002364 | 0.0028939 | 0.0029219 | 0.0029219 | 0.99898 | -0.024164 | 0.99897 | -0.024074 | 1.3282
88 | -0.30895 | -0.14539 | 0.30896 | 0.14529 | 5.5132e-06 | -9.4655e-05 | 0.0098669 | 0.0098656 | 0.0098669 | 0.99898 | -0.024164 | 0.99901 | -0.023345 | 2.4066
89 | 0.091729 | 0.042544 | -0.091729 | -0.042905 | 1.728e-07 | -0.00036064 | 0.0029219 | 0.0029263 | 0.0029263 | 0.99897 | -0.024074 | 0.99897 | -0.024059 | 1.3302
90 | -0.30896 | -0.14529 | 0.30897 | 0.11503 | 6.8172e-06 | -0.030262 | 0.0098656 | 0.0095264 | 0.0098656 | 0.99901 | -0.023345 | 0.99903 | -0.022812 | 1.1717
91 | 0.091729 | 0.042905 | -0.091728 | -0.044426 | 7.348e-07 | -0.0015215 | 0.0029263 | 0.0029452 | 0.0029452 | 0.99897 | -0.024059 | 0.99896 | -0.023992 | 1.3387
92 | -0.33253 | -0.16105 | 0.33253 | 0.16073 | 2.0367e-06 | -0.00031772 | 0.010683 | 0.010679 | 0.010683 | 0.99844 | -0.028077 | 0.99844 | -0.02813 | 4.8557
93 | 0.181 | 0.07476 | -0.18097 | -0.087544 | 2.3599e-05 | -0.012783 | 0.0056619 | 0.0058132 | 0.0058132 | 0.99844 | -0.02813 | 0.99832 | -0.027186 | 2.6424
94 | 0.14684 | 0.064211 | -0.14683 | -0.070972 | 8.2872e-06 | -0.0067613 | 0.0046337 | 0.0047154 | 0.0047154 | 0.99844 | -0.02813 | 0.99839 | -0.027693 | 2.1434
95 | 0.74815 | 0.32486 | -0.74797 | -0.33047 | 0.00017704 | -0.0056065 | 0.023582 | 0.023648 | 0.023648 | 0.99844 | -0.02813 | 0.99822 | -0.026522 | 10.7489
96 | 0.18097 | 0.087544 | -0.18097 | -0.08765 | 2.0067e-07 | -0.00010576 | 0.0058132 | 0.0058145 | 0.0058145 | 0.99832 | -0.027186 | 0.99832 | -0.027177 | 2.643
97 | 0.14683 | 0.070972 | -0.14683 | -0.071114 | 1.769e-07 | -0.00014172 | 0.0047154 | 0.0047172 | 0.0047172 | 0.99839 | -0.027693 | 0.99839 | -0.027683 | 2.1442
98 | 0.58613 | 0.25213 | -0.58587 | -0.2654 | 0.0002573 | -0.013274 | 0.018452 | 0.018608 | 0.018608 | 0.99822 | -0.026522 | 0.9978 | -0.02347 | 8.4581
99 | 0.16184 | 0.078338 | -0.16184 | -0.078384 | 1.9033e-06 | -4.5801e-05 | 0.0051998 | 0.0052004 | 0.0052004 | 0.99822 | -0.026522 | 0.99821 | -0.026599 | 2.4764
100 | 0.37309 | 0.1624 | -0.37295 | -0.18053 | 0.00014409 | -0.018131 | 0.011772 | 0.011992 | 0.011992 | 0.9978 | -0.02347 | 0.99744 | -0.020491 | 5.4508
101 | 0.21278 | 0.103 | -0.21278 | -0.10305 | 1.3334e-07 | -5.0712e-05 | 0.0068392 | 0.0068398 | 0.0068398 | 0.9978 | -0.02347 | 0.9978 | -0.023464 | 3.109
102 | 0.37295 | 0.18053 | -0.37295 | -0.18063 | 7.7356e-07 | -9.5476e-05 | 0.011992 | 0.011993 | 0.011993 | 0.99744 | -0.020491 | 0.99744 | -0.020473 | 5.4514
103 | 0.30077 | 0.14181 | -0.30076 | -0.14258 | 4.0586e-06 | -0.00077846 | 0.0096215 | 0.0096311 | 0.0096311 | 0.99767 | -0.019323 | 0.99766 | -0.019211 | 4.3778
104 | 0.18402 | 0.089065 | -0.18402 | -0.089123 | 3.1788e-06 | -5.857e-05 | 0.0059158 | 0.0059165 | 0.0059165 | 0.99762 | -0.018936 | 0.9976 | -0.01905 | 2.8174
105 | 0.16917 | 0.081836 | -0.16917 | -0.081933 | 4.393e-06 | -9.632e-05 | 0.0054375 | 0.0054388 | 0.0054388 | 0.9977 | -0.019611 | 0.99768 | -0.019783 | 2.5899
106 | 0.070323 | 0.030977 | -0.070323 | -0.031088 | 3.0928e-08 | -0.00011123 | 0.0022235 | 0.0022248 | 0.0022248 | 0.99766 | -0.019211 | 0.99765 | -0.019208 | 1.0113
107 | 0.070323 | 0.031088 | -0.070323 | -0.033626 | 7.1541e-07 | -0.002538 | 0.0022248 | 0.0022555 | 0.0022555 | 0.99765 | -0.019208 | 0.99765 | -0.01913 | 1.0252
108 | 0.18442 | 0.088487 | -0.18442 | -0.089317 | 7.3801e-08 | -0.0008299 | 0.0059965 | 0.006007 | 0.006007 | 0.9847 | -0.55502 | 0.9847 | -0.55503 | 0.71342
109 | -0.070322 | -0.034059 | 0.070323 | 0.033626 | 1.2383e-07 | -0.00043222 | 0.0022609 | 0.0022555 | 0.0022609 | 0.99764 | -0.019114 | 0.99765 | -0.01913 | 1.0277

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 12.3132 | 5.0299

## res_load
| p_mw | q_mvar
0 | 0.39574 | 0.19167
1 | 0.11834 | 0.057317
2 | 0.065642 | 0.031792
3 | 0.19878 | 0.096274
4 | 0.40581 | 0.19654
5 | 0.32033 | 0.15514
6 | 0.16247 | 0.078689
7 | 0.14179 | 0.068672
8 | 0.30005 | 0.14532
9 | 0.36789 | 0.17818
10 | 0.22111 | 0.10709
11 | 0.34379 | 0.16651
12 | 0.091155 | 0.044148
13 | 0.25671 | 0.12433
14 | 0.081163 | 0.039309
15 | 0.34197 | 0.16562
16 | 0.21203 | 0.10269
17 | 0.070332 | 0.034064
18 | 0.14801 | 0.071682
19 | 1.0054 | 0.48695
20 | 0.28809 | 0.13953
21 | 0.18051 | 0.087425
22 | 0.091659 | 0.044392
23 | 0.12309 | 0.059614
24 | 0.13567 | 0.06571
25 | 0.17277 | 0.083677
26 | 0.44581 | 0.21592
27 | 0.24471 | 0.11852
28 | 0.099135 | 0.048013
29 | 0.31841 | 0.15421
30 | 0.19841 | 0.096095
31 | 0.349 | 0.16903
32 | 0.073789 | 0.035738
33 | 0.166 | 0.080396
34 | 0.39207 | 0.18989
35 | 0.3541 | 0.1715
36 | 0.25322 | 0.12264
37 | 0.21722 | 0.10521
38 | 0.091728 | 0.044426
39 | 0.14908 | 0.072201
40 | 0.10075 | 0.048796
41 | 0.33253 | 0.16105
42 | 0.18097 | 0.08765
43 | 0.14683 | 0.071114
44 | 0.16184 | 0.078384
45 | 0.21278 | 0.10305
46 | 0.37295 | 0.18063
47 | 0.12989 | 0.062908
48 | 0.23044 | 0.11161
49 | 0.18402 | 0.089123
50 | 0.16917 | 0.081933
51 | 0.17347 | 0.084017
52 | 0.18442 | 0.089317
53 | 0.070322 | 0.034059

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1