## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_318_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_318_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_318_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_318_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_318_0_node_105 | 20 | n |  | TRUE
5 | bus_MV_318_0_node_90 | 20 | n |  | TRUE
6 | bus_MV_318_0_node_7 | 20 | n |  | TRUE
7 | bus_MV_318_0_node_6 | 20 | n |  | TRUE
8 | bus_MV_318_0_node_4 | 20 | n |  | TRUE
9 | bus_MV_318_0_node_5 | 20 | n |  | TRUE
10 | bus_MV_318_0_node_102 | 20 | n |  | TRUE
11 | bus_MV_318_0_node_101 | 20 | n |  | TRUE
12 | bus_MV_318_0_node_8 | 20 | n |  | TRUE
13 | bus_MV_318_0_node_15 | 20 | n |  | TRUE
14 | bus_MV_318_0_node_9 | 20 | n |  | TRUE
15 | bus_MV_318_0_node_13 | 20 | n |  | TRUE
16 | bus_MV_318_0_node_53 | 20 | n |  | TRUE
17 | bus_MV_318_0_node_54 | 20 | n |  | TRUE
18 | bus_MV_318_0_node_109 | 20 | n |  | TRUE
19 | bus_MV_318_0_node_52 | 20 | n |  | TRUE
20 | bus_MV_318_0_node_10 | 20 | n |  | TRUE
21 | bus_MV_318_0_node_11 | 20 | n |  | TRUE
22 | bus_MV_318_0_node_12 | 20 | n |  | TRUE
23 | bus_MV_318_0_node_14 | 20 | n |  | TRUE
24 | bus_MV_318_0_node_16 | 20 | n |  | TRUE
25 | bus_MV_318_0_node_92 | 20 | n |  | TRUE
26 | bus_MV_318_0_node_17 | 20 | n |  | TRUE
27 | bus_MV_318_0_node_18 | 20 | n |  | TRUE
28 | bus_MV_318_0_node_83 | 20 | n |  | TRUE
29 | bus_MV_318_0_node_20 | 20 | n |  | TRUE
30 | bus_MV_318_0_node_23 | 20 | n |  | TRUE
31 | bus_MV_318_0_node_24 | 20 | n |  | TRUE
32 | bus_MV_318_0_node_25 | 20 | n |  | TRUE
33 | bus_MV_318_0_node_26 | 20 | n |  | TRUE
34 | bus_MV_318_0_node_86 | 20 | n |  | TRUE
35 | bus_MV_318_0_node_49 | 20 | n |  | TRUE
36 | bus_MV_318_0_node_50 | 20 | n |  | TRUE
37 | bus_MV_318_0_node_59 | 20 | n |  | TRUE
38 | bus_MV_318_0_node_87 | 20 | n |  | TRUE
39 | bus_MV_318_0_node_19 | 20 | n |  | TRUE
40 | bus_MV_318_0_node_21 | 20 | n |  | TRUE
41 | bus_MV_318_0_node_31 | 20 | n |  | TRUE
42 | bus_MV_318_0_node_104 | 20 | n |  | TRUE
43 | bus_MV_318_0_node_22 | 20 | n |  | TRUE
44 | bus_MV_318_0_node_66 | 20 | n |  | TRUE
45 | bus_MV_318_0_node_45 | 20 | n |  | TRUE
46 | bus_MV_318_0_node_97 | 20 | n |  | TRUE
47 | bus_MV_318_0_node_29 | 20 | n |  | TRUE
48 | bus_MV_318_0_node_67 | 20 | n |  | TRUE
49 | bus_MV_318_0_node_43 | 20 | n |  | TRUE
50 | bus_MV_318_0_node_44 | 20 | n |  | TRUE
51 | bus_MV_318_0_node_42 | 20 | n |  | TRUE
52 | bus_MV_318_0_node_88 | 20 | n |  | TRUE
53 | bus_MV_318_0_node_58 | 20 | n |  | TRUE
54 | bus_MV_318_0_node_61 | 20 | n |  | TRUE
55 | bus_MV_318_0_node_47 | 20 | n |  | TRUE
56 | bus_MV_318_0_node_27 | 20 | n |  | TRUE
57 | bus_MV_318_0_node_28 | 20 | n |  | TRUE
58 | bus_MV_318_0_node_30 | 20 | n |  | TRUE
59 | bus_MV_318_0_node_84 | 20 | n |  | TRUE
60 | bus_MV_318_0_node_32 | 20 | n |  | TRUE
61 | bus_MV_318_0_node_33 | 20 | n |  | TRUE
62 | bus_MV_318_0_node_34 | 20 | n |  | TRUE
63 | bus_MV_318_0_node_85 | 20 | n |  | TRUE
64 | bus_MV_318_0_node_35 | 20 | n |  | TRUE
65 | bus_MV_318_0_node_36 | 20 | n |  | TRUE
66 | bus_MV_318_0_node_37 | 20 | n |  | TRUE
67 | bus_MV_318_0_node_38 | 20 | n |  | TRUE
68 | bus_MV_318_0_node_51 | 20 | n |  | TRUE
69 | bus_MV_318_0_node_57 | 20 | n |  | TRUE
70 | bus_MV_318_0_node_69 | 20 | n |  | TRUE
71 | bus_MV_318_0_node_39 | 20 | n |  | TRUE
72 | bus_MV_318_0_node_108 | 20 | n |  | TRUE
73 | bus_MV_318_0_node_56 | 20 | n |  | TRUE
74 | bus_MV_318_0_node_107 | 20 | n |  | TRUE
75 | bus_MV_318_0_node_63 | 20 | n |  | TRUE
76 | bus_MV_318_0_node_41 | 20 | n |  | TRUE
77 | bus_MV_318_0_node_106 | 20 | n |  | TRUE
78 | bus_MV_318_0_node_98 | 20 | n |  | TRUE
79 | bus_MV_318_0_node_95 | 20 | n |  | TRUE
80 | bus_MV_318_0_node_99 | 20 | n |  | TRUE
81 | bus_MV_318_0_node_93 | 20 | n |  | TRUE
82 | bus_MV_318_0_node_94 | 20 | n |  | TRUE
83 | bus_MV_318_0_node_48 | 20 | n |  | TRUE
84 | bus_MV_318_0_node_46 | 20 | n |  | TRUE
85 | bus_MV_318_0_node_55 | 20 | n |  | TRUE
86 | bus_MV_318_0_node_89 | 20 | n |  | TRUE
87 | bus_MV_318_0_node_70 | 20 | n |  | TRUE
88 | bus_MV_318_0_node_71 | 20 | n |  | TRUE
89 | bus_MV_318_0_node_72 | 20 | n |  | TRUE
90 | bus_MV_318_0_node_103 | 20 | n |  | TRUE
91 | bus_MV_318_0_node_73 | 20 | n |  | TRUE
92 | bus_MV_318_0_node_74 | 20 | n |  | TRUE
93 | bus_MV_318_0_node_75 | 20 | n |  | TRUE
94 | bus_MV_318_0_node_76 | 20 | n |  | TRUE
95 | bus_MV_318_0_node_77 | 20 | n |  | TRUE
96 | bus_MV_318_0_node_80 | 20 | n |  | TRUE
97 | bus_MV_318_0_node_78 | 20 | n |  | TRUE
98 | bus_MV_318_0_node_79 | 20 | n |  | TRUE
99 | bus_MV_318_0_node_81 | 20 | n |  | TRUE
100 | bus_MV_318_0_node_82 | 20 | n |  | TRUE
101 | bus_MV_318_0_node_91 | 20 | n |  | TRUE
102 | bus_MV_318_0_node_60 | 20 | n |  | TRUE
103 | bus_MV_318_0_node_96 | 20 | n |  | TRUE
104 | bus_MV_318_0_node_68 | 20 | n |  | TRUE
105 | bus_HV_318_0_node_30 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_318_0_load_0 | 0 | 0.2785 | 0.13488 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_318_0_load_105 | 4 | 0.072329 | 0.035031 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_318_0_load_90 | 5 | 0.32395 | 0.15689 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_318_0_load_7 | 6 | 0.2519 | 0.122 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_318_0_load_4 | 8 | 0.2981 | 0.14437 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_318_0_load_101 | 11 | 0.12951 | 0.062722 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_318_0_load_8 | 12 | 0.090164 | 0.043668 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_318_0_load_15 | 13 | 0.11562 | 0.055997 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_318_0_load_9 | 14 | 0.058678 | 0.028419 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_318_0_load_109 | 18 | 0.14918 | 0.072249 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_318_0_load_52 | 19 | 0.15547 | 0.075297 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_318_0_load_10 | 20 | 0.15153 | 0.073391 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_318_0_load_16 | 24 | 0.091798 | 0.04446 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_318_0_load_92 | 25 | 0.15782 | 0.076433 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_318_0_load_17 | 26 | 0.14266 | 0.069092 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_318_0_load_83 | 28 | 0.17529 | 0.084898 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_318_0_load_23 | 30 | 0.11144 | 0.053974 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_318_0_load_26 | 33 | 0.086272 | 0.041784 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_318_0_load_86 | 34 | 0.16496 | 0.079895 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_318_0_load_87 | 38 | 0.22064 | 0.10686 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_318_0_load_31 | 41 | 0.09562 | 0.046311 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_318_0_load_104 | 42 | 0.15997 | 0.077475 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_318_0_load_66 | 44 | 0.16217 | 0.078541 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_318_0_load_97 | 46 | 0.14756 | 0.071467 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_318_0_load_42 | 51 | 0.16125 | 0.078099 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_318_0_load_88 | 52 | 0.19763 | 0.095717 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_318_0_load_58 | 53 | 0.1045 | 0.050611 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_318_0_load_27 | 56 | 0.069346 | 0.033586 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_318_0_load_84 | 59 | 0.12964 | 0.062788 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_318_0_load_32 | 60 | 0.10623 | 0.05145 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_318_0_load_85 | 63 | 0.14354 | 0.06952 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_318_0_load_35 | 64 | 0.16015 | 0.077564 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_318_0_load_51 | 68 | 0.14735 | 0.071367 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_318_0_load_69 | 70 | 0.15895 | 0.076982 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_318_0_load_39 | 71 | 0.12164 | 0.058914 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_318_0_load_108 | 72 | 0.14731 | 0.071343 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_318_0_load_56 | 73 | 0.13053 | 0.063219 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_318_0_load_107 | 74 | 0.16393 | 0.079393 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_318_0_load_106 | 77 | 0.14412 | 0.069802 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_318_0_load_95 | 79 | 0.15211 | 0.07367 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_318_0_load_99 | 80 | 0.12403 | 0.06007 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_318_0_load_46 | 84 | 0.10167 | 0.049243 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_318_0_load_55 | 85 | 0.10616 | 0.051416 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_318_0_load_89 | 86 | 0.20074 | 0.097224 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_318_0_load_103 | 90 | 0.16302 | 0.078953 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_318_0_load_73 | 91 | 0.075662 | 0.036645 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_318_0_load_74 | 92 | 0.13649 | 0.066105 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_318_0_load_75 | 93 | 0.083017 | 0.040207 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_318_0_load_77 | 95 | 0.093758 | 0.045409 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_318_0_load_80 | 96 | 0.10545 | 0.051073 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_318_0_load_91 | 101 | 0.097411 | 0.047178 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_318_0_load_60 | 102 | 0.09477 | 0.045899 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_318_0_load_96 | 103 | 0.12893 | 0.062444 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 58 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_318_0_line_0 |  | 0 | 1 | 0.051595 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_318_0_line_1 |  | 1 | 2 | 0.17141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_318_0_line_2 |  | 1 | 3 | 0.30062 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_318_0_line_3 |  | 2 | 4 | 0.052327 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_318_0_line_4 |  | 3 | 5 | 0.050744 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_318_0_line_5 |  | 4 | 6 | 2.5468 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
6 | MV_318_0_line_6 |  | 5 | 7 | 0.035025 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_318_0_line_7 |  | 6 | 12 | 1.0489 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_318_0_line_8 |  | 6 | 13 | 2.4645 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
9 | MV_318_0_line_9 |  | 7 | 10 | 0.1389 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_318_0_line_10 |  | 7 | 9 | 0.25154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_318_0_line_11 |  | 8 | 9 | 0.030884 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_318_0_line_12 |  | 10 | 11 | 0.051373 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_318_0_line_13 |  | 13 | 14 | 1.785 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_318_0_line_14 |  | 13 | 15 | 0.019215 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
15 | MV_318_0_line_15 |  | 15 | 21 | 0.2899 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_318_0_line_16 |  | 15 | 22 | 0.50106 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
17 | MV_318_0_line_17 |  | 16 | 17 | 0.4331 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
18 | MV_318_0_line_18 |  | 16 | 18 | 1.1972 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
19 | MV_318_0_line_19 |  | 16 | 19 | 0.011319 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_318_0_line_20 |  | 17 | 42 | 0.03044 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
21 | MV_318_0_line_21 |  | 18 | 25 | 0.97274 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
22 | MV_318_0_line_22 |  | 20 | 21 | 0.099379 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_318_0_line_23 |  | 22 | 23 | 1.3075 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
24 | MV_318_0_line_24 |  | 22 | 24 | 0.09223 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_318_0_line_25 |  | 23 | 25 | 0.21185 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
26 | MV_318_0_line_26 |  | 26 | 27 | 0.024921 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
27 | MV_318_0_line_27 |  | 26 | 28 | 0.13445 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
28 | MV_318_0_line_28 |  | 27 | 29 | 0.26965 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
29 | MV_318_0_line_29 |  | 28 | 36 | 0.0964 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
30 | MV_318_0_line_30 |  | 29 | 42 | 0.02111 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
31 | MV_318_0_line_31 |  | 30 | 31 | 0.033096 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_318_0_line_32 |  | 31 | 32 | 0.063421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_318_0_line_33 |  | 31 | 33 | 0.056573 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_318_0_line_34 |  | 32 | 34 | 0.039719 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_318_0_line_35 |  | 33 | 35 | 0.067956 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_318_0_line_36 |  | 34 | 38 | 0.015795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_318_0_line_37 |  | 35 | 55 | 0.15081 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_318_0_line_38 |  | 35 | 36 | 0.23589 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_318_0_line_39 |  | 36 | 37 | 0.091422 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
40 | MV_318_0_line_40 |  | 37 | 53 | 0.033215 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
41 | MV_318_0_line_41 |  | 38 | 84 | 0.082445 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_318_0_line_42 |  | 39 | 40 | 0.13303 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
43 | MV_318_0_line_43 |  | 39 | 41 | 0.005598 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
44 | MV_318_0_line_44 |  | 40 | 43 | 0.21794 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
45 | MV_318_0_line_45 |  | 40 | 44 | 0.007901 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_318_0_line_46 |  | 41 | 47 | 0.036984 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
47 | MV_318_0_line_47 |  | 43 | 45 | 0.19949 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
48 | MV_318_0_line_48 |  | 43 | 46 | 0.04939 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_318_0_line_49 |  | 44 | 48 | 0.033164 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_318_0_line_50 |  | 45 | 53 | 0.0802 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
51 | MV_318_0_line_51 |  | 46 | 54 | 0.11967 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_318_0_line_52 |  | 47 | 57 | 0.029429 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
53 | MV_318_0_line_53 |  | 48 | 104 | 0.14397 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_318_0_line_54 |  | 49 | 50 | 0.12784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_318_0_line_55 |  | 49 | 51 | 0.073576 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_318_0_line_56 |  | 50 | 52 | 0.10001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_318_0_line_57 |  | 51 | 55 | 0.24631 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_318_0_line_58 |  | 51 | 83 | 0.28744 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_318_0_line_59 |  | 52 | 86 | 0.15789 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
60 | MV_318_0_line_60 |  | 54 | 75 | 0.27592 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_318_0_line_61 |  | 54 | 102 | 0.006846 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_318_0_line_62 |  | 56 | 57 | 0.051898 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_318_0_line_63 |  | 57 | 58 | 0.24427 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
64 | MV_318_0_line_64 |  | 58 | 59 | 0.049623 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_318_0_line_65 |  | 59 | 63 | 0.076997 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_318_0_line_66 |  | 60 | 61 | 0.030333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_318_0_line_67 |  | 61 | 62 | 0.12091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_318_0_line_68 |  | 62 | 63 | 0.06749 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_318_0_line_69 |  | 64 | 65 | 0.068895 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_318_0_line_70 |  | 65 | 66 | 0.53927 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_318_0_line_71 |  | 65 | 67 | 0.39349 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_318_0_line_72 |  | 66 | 72 | 0.006639 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_318_0_line_73 |  | 67 | 73 | 0.034807 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_318_0_line_74 |  | 68 | 69 | 1.5285 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_318_0_line_75 |  | 68 | 70 | 3.7579 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
76 | MV_318_0_line_76 |  | 68 | 71 | 1.4725 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
77 | MV_318_0_line_77 |  | 69 | 73 | 0.099257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_318_0_line_78 |  | 70 | 87 | 0.047695 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
79 | MV_318_0_line_79 |  | 71 | 74 | 0.15466 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_318_0_line_80 |  | 74 | 75 | 0.019233 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_318_0_line_81 |  | 76 | 77 | 0.031887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_318_0_line_82 |  | 76 | 78 | 0.1496 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_318_0_line_83 |  | 76 | 79 | 0.25565 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
84 | MV_318_0_line_84 |  | 78 | 80 | 0.043413 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_318_0_line_85 |  | 79 | 81 | 0.070184 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
86 | MV_318_0_line_86 |  | 80 | 104 | 0.008902 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_318_0_line_87 |  | 81 | 82 | 0.060887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_318_0_line_88 |  | 82 | 103 | 0.016501 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_318_0_line_89 |  | 83 | 85 | 0.26275 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
90 | MV_318_0_line_90 |  | 87 | 88 | 0.21285 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_318_0_line_91 |  | 87 | 89 | 0.29375 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_318_0_line_92 |  | 88 | 90 | 0.017535 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_318_0_line_93 |  | 89 | 91 | 0.36342 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_318_0_line_94 |  | 90 | 98 | 0.079377 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_318_0_line_95 |  | 92 | 93 | 0.021523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_318_0_line_96 |  | 92 | 94 | 0.048641 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_318_0_line_97 |  | 94 | 95 | 0.003057 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_318_0_line_98 |  | 94 | 96 | 4.0706 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_318_0_line_99 |  | 95 | 97 | 0.045906 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_318_0_line_100 |  | 96 | 99 | 0.098406 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_318_0_line_101 |  | 97 | 98 | 0.17418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_318_0_line_102 |  | 99 | 100 | 0.30906 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_318_0_line_103 |  | 100 | 101 | 0.1738 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_318_0_trafo_30 | 25 MVA 110/20 kV | 105 | 58 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2530300.4296 | 1182587.2958
1 | 2530255.9737 | 1182561.1098
2 | 2530269.7958 | 1182697.4055
3 | 2530040.4375 | 1182625.2299
4 | 2530318.0022 | 1182717.9113
5 | 2530016.6015 | 1182580.4604
6 | 2532185.2865 | 1184449.8559
7 | 2529985.1018 | 1182595.9602
8 | 2529957.8056 | 1182332.749
9 | 2529946.2057 | 1182361.3792
10 | 2529937.1453 | 1182671.9212
11 | 2529891.135 | 1182694.9513
12 | 2533064.1832 | 1183877.3698
13 | 2532462.2964 | 1186898.7859
14 | 2534075.565 | 1186134.7602
15 | 2532449.4255 | 1186913.0841
16 | 2529302.1087 | 1185851.5928
17 | 2528883.3829 | 1185929.5034
18 | 2530416.5904 | 1186288.9876
19 | 2529296.8929 | 1185861.6381
20 | 2532547.7106 | 1187238.8305
21 | 2532581.7391 | 1187145.459
22 | 2532227.2152 | 1186988.9541
23 | 2531454.5342 | 1186839.7313
24 | 2532135.1226 | 1186993.9794
25 | 2531251.3941 | 1186788.3226
26 | 2528600.531 | 1185924.3263
27 | 2528620.1982 | 1185939.7006
28 | 2528599.9536 | 1185789.8784
29 | 2528835.0877 | 1185947.8998
30 | 2528569.7565 | 1185638.5704
31 | 2528583.5082 | 1185608.4552
32 | 2528606.0704 | 1185549.1843
33 | 2528530.4177 | 1185597.3279
34 | 2528566.3612 | 1185550.0725
35 | 2528466.1806 | 1185611.6259
36 | 2528509.7887 | 1185823.9848
37 | 2528476.7555 | 1185879.2233
38 | 2528550.5706 | 1185550.4257
39 | 2528706.6802 | 1186093.9262
40 | 2528603.6603 | 1186139.6377
41 | 2528711.6321 | 1186091.2878
42 | 2528854.8236 | 1185940.2605
43 | 2528495.9848 | 1186085.0366
44 | 2528596.6452 | 1186143.3125
45 | 2528415.6355 | 1185952.6867
46 | 2528483.5341 | 1186131.913
47 | 2528746.8642 | 1186080.2281
48 | 2528568.4344 | 1186160.7486
49 | 2528204.3377 | 1185677.4801
50 | 2528196.9218 | 1185691.0216
51 | 2528173.4272 | 1185610.712
52 | 2528124.6688 | 1185680.7439
53 | 2528484.4685 | 1185911.5279
54 | 2528372.4667 | 1186176.4575
55 | 2528392.4683 | 1185498.0636
56 | 2528805.2148 | 1186136.0103
57 | 2528769.509 | 1186098.3467
58 | 2528913.0698 | 1186225.2685
59 | 2528962.0436 | 1186217.2707
60 | 2529040.363 | 1186173.5485
61 | 2529051.3214 | 1186201.8239
62 | 2529075.3399 | 1186302.3758
63 | 2529019.2536 | 1186267.8989
64 | 2525531.1036 | 1185724.1409
65 | 2525565.532 | 1185664.533
66 | 2525082.6043 | 1185676.0476
67 | 2525888.4763 | 1185774.81
68 | 2526777.8956 | 1187143.5978
69 | 2526013.1481 | 1185820.1822
70 | 2527419.688 | 1190846.2826
71 | 2528125.9481 | 1186551.1471
72 | 2525079.2203 | 1185670.331
73 | 2525919.5666 | 1185789.9959
74 | 2528206.9465 | 1186419.3965
75 | 2528220.4646 | 1186405.715
76 | 2528396.5334 | 1186383.8913
77 | 2528402.8855 | 1186413.4437
78 | 2528488.1612 | 1186288.3719
79 | 2528160.351 | 1186286.0442
80 | 2528511.233 | 1186251.5967
81 | 2528180.1154 | 1186218.7005
82 | 2528182.5919 | 1186159.3358
83 | 2528165.5246 | 1185323.3825
84 | 2528492.3928 | 1185492.0089
85 | 2528133.8359 | 1185062.5544
86 | 2527985.191 | 1185754.7346
87 | 2527455.9345 | 1190877.2832
88 | 2527574.1982 | 1191016.3981
89 | 2527294.3609 | 1190964.3544
90 | 2527583.2637 | 1191031.4194
91 | 2526937.6191 | 1190952.1708
92 | 2527792.8789 | 1191225.3276
93 | 2527787.6895 | 1191204.4393
94 | 2527745.0343 | 1191231.4247
95 | 2527742.1104 | 1191230.504
96 | 2526923.3276 | 1195218.2573
97 | 2527716.5401 | 1191192.3794
98 | 2527653.7437 | 1191047.8421
99 | 2526825.0372 | 1195209.389
100 | 2526593.1672 | 1195281.423
101 | 2526553.8674 | 1195450.6753
102 | 2528368.0086 | 1186171.2522
103 | 2528185.4186 | 1186143.0812
104 | 2528516.3579 | 1186244.3089
105 | 2528913.0698 | 1186225.2685

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98172 | -0.47619 | 0.2785 | 0.13488
1 | 0.98175 | -0.47601 | 0 | 0
2 | 0.98198 | -0.47795 | 0 | 0
3 | 0.98146 | -0.47353 | 0 | 0
4 | 0.98205 | -0.47854 | 0.072329 | 0.035031
5 | 0.98141 | -0.4731 | 0.32395 | 0.15689
6 | 0.98539 | -0.39155 | 0.2519 | 0.122
7 | 0.98139 | -0.47294 | 0 | 0
8 | 0.98128 | -0.47195 | 0.2981 | 0.14437
9 | 0.98129 | -0.47206 | 0 | 0
10 | 0.98137 | -0.47274 | 0 | 0
11 | 0.98136 | -0.47266 | 0.12951 | 0.062722
12 | 0.9852 | -0.39279 | 0.090164 | 0.043668
13 | 0.98963 | -0.28256 | 0.11562 | 0.055997
14 | 0.98943 | -0.28401 | 0.058678 | 0.028419
15 | 0.98965 | -0.28237 | 0 | 0
16 | 0.99583 | -0.091921 | 0 | 0
17 | 0.99627 | -0.0833 | 0 | 0
18 | 0.99328 | -0.18307 | 0.14918 | 0.072249
19 | 0.99583 | -0.091943 | 0.15547 | 0.075297
20 | 0.98956 | -0.28208 | 0.15153 | 0.073391
21 | 0.98959 | -0.2819 | 0 | 0
22 | 0.99013 | -0.27675 | 0 | 0
23 | 0.99119 | -0.25603 | 0 | 0
24 | 0.99012 | -0.27685 | 0.091798 | 0.04446
25 | 0.99136 | -0.25257 | 0.15782 | 0.076433
26 | 0.99664 | -0.07594 | 0.14266 | 0.069092
27 | 0.99661 | -0.076475 | 0 | 0
28 | 0.99698 | -0.063574 | 0.17529 | 0.084898
29 | 0.99632 | -0.08224 | 0 | 0
30 | 0.99659 | -0.056758 | 0.11144 | 0.053974
31 | 0.99659 | -0.056802 | 0 | 0
32 | 0.99655 | -0.056438 | 0 | 0
33 | 0.99663 | -0.057194 | 0.086272 | 0.041784
34 | 0.99653 | -0.056208 | 0.16496 | 0.079895
35 | 0.99669 | -0.057729 | 0 | 0
36 | 0.9971 | -0.061269 | 0 | 0
37 | 0.99726 | -0.058099 | 0 | 0
38 | 0.99652 | -0.056147 | 0.22064 | 0.10686
39 | 0.99902 | -0.018838 | 0 | 0
40 | 0.99862 | -0.026603 | 0 | 0
41 | 0.99904 | -0.018511 | 0.09562 | 0.046311
42 | 0.9963 | -0.08269 | 0.15997 | 0.077475
43 | 0.99803 | -0.038092 | 0 | 0
44 | 0.99861 | -0.026541 | 0.16217 | 0.078541
45 | 0.99766 | -0.045181 | 0 | 0
46 | 0.9979 | -0.037157 | 0.14756 | 0.071467
47 | 0.99915 | -0.016324 | 0 | 0
48 | 0.99858 | -0.026791 | 0 | 0
49 | 0.99619 | -0.059126 | 0 | 0
50 | 0.99613 | -0.058545 | 0 | 0
51 | 0.99625 | -0.058733 | 0.16125 | 0.078099
52 | 0.99608 | -0.058073 | 0.19763 | 0.095717
53 | 0.99732 | -0.056946 | 0.1045 | 0.050611
54 | 0.99747 | -0.040798 | 0 | 0
55 | 0.99657 | -0.0566 | 0 | 0
56 | 0.99924 | -0.014628 | 0.069346 | 0.033586
57 | 0.99924 | -0.014584 | 0 | 0
58 | 1 | 0 | -7.6075 | -3.3913
59 | 0.99996 | -0.00025746 | 0.12964 | 0.062788
60 | 0.99991 | 0.00018413 | 0.10623 | 0.05145
61 | 0.99991 | 0.00014628 | 0 | 0
62 | 0.99993 | 9.2915e-06 | 0 | 0
63 | 0.99994 | -5.7494e-05 | 0.14354 | 0.06952
64 | 0.9906 | -0.087603 | 0.16015 | 0.077564
65 | 0.99062 | -0.087734 | 0 | 0
66 | 0.99051 | -0.086992 | 0 | 0
67 | 0.99077 | -0.088723 | 0 | 0
68 | 0.9921 | -0.077271 | 0.14735 | 0.071367
69 | 0.99084 | -0.089164 | 0 | 0
70 | 0.98553 | -0.13562 | 0.15895 | 0.076982
71 | 0.99632 | -0.040107 | 0.12164 | 0.058914
72 | 0.99051 | -0.08698 | 0.14731 | 0.071343
73 | 0.99078 | -0.088799 | 0.13053 | 0.063219
74 | 0.9968 | -0.03598 | 0.16393 | 0.079393
75 | 0.99684 | -0.036299 | 0 | 0
76 | 0.99835 | -0.025396 | 0 | 0
77 | 0.99835 | -0.025342 | 0.14412 | 0.069802
78 | 0.99844 | -0.026114 | 0 | 0
79 | 0.99822 | -0.026312 | 0.15211 | 0.07367
80 | 0.99847 | -0.025866 | 0.12403 | 0.06007
81 | 0.9982 | -0.026433 | 0 | 0
82 | 0.99819 | -0.026344 | 0 | 0
83 | 0.99619 | -0.059116 | 0 | 0
84 | 0.9965 | -0.056249 | 0.10167 | 0.049243
85 | 0.99613 | -0.05946 | 0.10616 | 0.051416
86 | 0.99601 | -0.058461 | 0.20074 | 0.097224
87 | 0.98546 | -0.13626 | 0 | 0
88 | 0.98528 | -0.13488 | 0 | 0
89 | 0.98543 | -0.13621 | 0 | 0
90 | 0.98526 | -0.13476 | 0.16302 | 0.078953
91 | 0.9854 | -0.13597 | 0.075662 | 0.036645
92 | 0.98503 | -0.13376 | 0.13649 | 0.066105
93 | 0.98503 | -0.13374 | 0.083017 | 0.040207
94 | 0.98505 | -0.13389 | 0 | 0
95 | 0.98505 | -0.1339 | 0.093758 | 0.045409
96 | 0.98348 | -0.14983 | 0.10545 | 0.051073
97 | 0.98509 | -0.13352 | 0 | 0
98 | 0.98521 | -0.13438 | 0 | 0
99 | 0.98347 | -0.14979 | 0 | 0
100 | 0.98343 | -0.14957 | 0 | 0
101 | 0.98341 | -0.14938 | 0.097411 | 0.047178
102 | 0.99747 | -0.04079 | 0.09477 | 0.045899
103 | 0.99819 | -0.026318 | 0.12893 | 0.062444
104 | 0.99848 | -0.025921 | 0 | 0
105 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.2785 | -0.13488 | 0.27851 | 0.13483 | 7.6104e-06 | -5.4598e-05 | 0.0090992 | 0.0090984 | 0.0090992 | 0.98172 | -0.47619 | 0.98175 | -0.47601 | 4.3329
1 | -1.0304 | -0.47916 | 1.0306 | 0.47529 | 0.0002551 | -0.0038698 | 0.033413 | 0.033365 | 0.033413 | 0.98175 | -0.47601 | 0.98198 | -0.47795 | 15.1879
2 | 0.75188 | 0.34433 | -0.75164 | -0.35118 | 0.00023813 | -0.0068453 | 0.024316 | 0.024402 | 0.024402 | 0.98175 | -0.47601 | 0.98146 | -0.47353 | 11.0917
3 | -1.0306 | -0.47529 | 1.0307 | 0.47411 | 7.7729e-05 | -0.0011818 | 0.033365 | 0.03335 | 0.033365 | 0.98198 | -0.47795 | 0.98205 | -0.47854 | 15.1657
4 | 0.75164 | 0.35118 | -0.7516 | -0.35233 | 4.0362e-05 | -0.001155 | 0.024402 | 0.024416 | 0.024416 | 0.98146 | -0.47353 | 0.98141 | -0.4731 | 11.0983
5 | -1.103 | -0.50914 | 1.106 | 0.50945 | 0.0029785 | 0.00030973 | 0.035712 | 0.035674 | 0.035712 | 0.98205 | -0.47854 | 0.98539 | -0.39155 | 10.2033
6 | 0.42765 | 0.19544 | -0.42764 | -0.19624 | 8.9503e-06 | -0.00080279 | 0.01383 | 0.01384 | 0.01384 | 0.98141 | -0.4731 | 0.98139 | -0.47294 | 6.291
7 | 0.09018 | 0.042463 | -0.090164 | -0.043668 | 1.6019e-05 | -0.0012056 | 0.0029201 | 0.0029354 | 0.0029354 | 0.98539 | -0.39155 | 0.9852 | -0.39279 | 1.3978
8 | -1.4481 | -0.67391 | 1.4531 | 0.67656 | 0.0049497 | 0.0026412 | 0.046792 | 0.046755 | 0.046792 | 0.98539 | -0.39155 | 0.98963 | -0.28256 | 13.3692
9 | 0.12951 | 0.058348 | -0.12951 | -0.061541 | 3.2676e-06 | -0.003193 | 0.0041783 | 0.0042178 | 0.0042178 | 0.98139 | -0.47294 | 0.98137 | -0.47274 | 1.9172
10 | 0.29813 | 0.13789 | -0.2981 | -0.14367 | 3.1584e-05 | -0.0057745 | 0.0096621 | 0.0097348 | 0.0097348 | 0.98139 | -0.47294 | 0.98129 | -0.47206 | 4.4249
11 | -0.2981 | -0.14437 | 0.2981 | 0.14367 | 3.9109e-06 | -0.00070889 | 0.0097439 | 0.0097348 | 0.0097439 | 0.98128 | -0.47195 | 0.98129 | -0.47206 | 4.429
12 | 0.12951 | 0.061541 | -0.12951 | -0.062722 | 1.2244e-06 | -0.0011809 | 0.0042178 | 0.0042328 | 0.0042328 | 0.98137 | -0.47274 | 0.98136 | -0.47266 | 1.924
13 | 0.058689 | 0.026339 | -0.058678 | -0.028419 | 1.135e-05 | -0.0020795 | 0.0018765 | 0.0019022 | 0.0019022 | 0.98963 | -0.28256 | 0.98943 | -0.28401 | 0.90581
14 | -1.6274 | -0.75889 | 1.6274 | 0.75826 | 2.5458e-05 | -0.00062711 | 0.052378 | 0.05237 | 0.052378 | 0.98963 | -0.28256 | 0.98965 | -0.28237 | 14.4691
15 | 0.15155 | 0.066501 | -0.15154 | -0.073277 | 9.1713e-06 | -0.006776 | 0.0048274 | 0.0049102 | 0.0049102 | 0.98965 | -0.28237 | 0.98959 | -0.2819 | 2.2319
16 | -1.7789 | -0.82477 | 1.7797 | 0.8085 | 0.00078888 | -0.01627 | 0.057196 | 0.056991 | 0.057196 | 0.98965 | -0.28237 | 0.99013 | -0.27675 | 15.8001
17 | -2.3429 | -1.029 | 2.3438 | 1.0133 | 0.00086999 | -0.015616 | 0.074179 | 0.073989 | 0.074179 | 0.99583 | -0.091921 | 0.99627 | -0.0833 | 17.6196
18 | 2.1875 | 0.95368 | -2.1834 | -0.94929 | 0.0040847 | 0.004381 | 0.069175 | 0.069193 | 0.069193 | 0.99583 | -0.091921 | 0.99328 | -0.18307 | 16.8763
19 | 0.15547 | 0.075284 | -0.15547 | -0.075297 | 5.0567e-07 | -1.3083e-05 | 0.0050074 | 0.0050075 | 0.0050075 | 0.99583 | -0.091921 | 0.99583 | -0.091943 | 2.3845
20 | -2.3438 | -1.0133 | 2.3439 | 1.0122 | 6.0979e-05 | -0.0010983 | 0.073989 | 0.073975 | 0.073989 | 0.99627 | -0.0833 | 0.9963 | -0.08269 | 17.5745
21 | 2.0342 | 0.87705 | -2.0313 | -0.87412 | 0.0028745 | 0.0029219 | 0.06438 | 0.064394 | 0.064394 | 0.99328 | -0.18307 | 0.99136 | -0.25257 | 15.7059
22 | -0.15153 | -0.073391 | 0.15154 | 0.073277 | 4.2703e-06 | -0.0001135 | 0.0049117 | 0.0049102 | 0.0049117 | 0.98956 | -0.28208 | 0.98959 | -0.2819 | 2.3389
23 | -1.8715 | -0.85285 | 1.8732 | 0.80539 | 0.0017039 | -0.047456 | 0.059963 | 0.059385 | 0.059963 | 0.99013 | -0.27675 | 0.99119 | -0.25603 | 14.243
24 | 0.091799 | 0.044353 | -0.091798 | -0.04446 | 1.4526e-06 | -0.00010703 | 0.0029724 | 0.0029738 | 0.0029738 | 0.99013 | -0.27675 | 0.99012 | -0.27685 | 1.4161
25 | -1.8732 | -0.80539 | 1.8735 | 0.79769 | 0.00027302 | -0.0077019 | 0.059385 | 0.059294 | 0.059385 | 0.99119 | -0.25603 | 0.99136 | -0.25257 | 14.1056
26 | 2.5045 | 1.0784 | -2.5045 | -1.0793 | 5.6908e-05 | -0.00089336 | 0.078983 | 0.078994 | 0.078994 | 0.99664 | -0.07594 | 0.99661 | -0.076475 | 18.7634
27 | -2.6472 | -1.1475 | 2.6479 | 1.1483 | 0.00066929 | 0.00079609 | 0.08357 | 0.083568 | 0.08357 | 0.99664 | -0.07594 | 0.99698 | -0.063574 | 20.3829
28 | 2.5045 | 1.0793 | -2.5039 | -1.089 | 0.00061677 | -0.0096624 | 0.078994 | 0.079111 | 0.079111 | 0.99661 | -0.076475 | 0.99632 | -0.08224 | 18.7913
29 | -2.8232 | -1.2332 | 2.8234 | 1.2298 | 0.00028061 | -0.0034033 | 0.089203 | 0.08916 | 0.089203 | 0.99698 | -0.063574 | 0.9971 | -0.061269 | 21.1883
30 | 2.5039 | 1.089 | -2.5038 | -1.0897 | 4.8361e-05 | -0.0007561 | 0.079111 | 0.079121 | 0.079121 | 0.99632 | -0.08224 | 0.9963 | -0.08269 | 18.7935
31 | -0.11144 | -0.053974 | 0.11144 | 0.053189 | 5.6685e-07 | -0.00078465 | 0.0035868 | 0.0035769 | 0.0035868 | 0.99659 | -0.056758 | 0.99659 | -0.056802 | 1.6303
32 | 0.48732 | 0.23309 | -0.48729 | -0.23459 | 2.0755e-05 | -0.0014977 | 0.015647 | 0.015666 | 0.015666 | 0.99659 | -0.056802 | 0.99655 | -0.056438 | 7.121
33 | -0.59876 | -0.28628 | 0.59879 | 0.28495 | 2.7888e-05 | -0.0013333 | 0.019224 | 0.019208 | 0.019224 | 0.99659 | -0.056802 | 0.99663 | -0.057194 | 8.7383
34 | 0.48729 | 0.23459 | -0.48728 | -0.23553 | 1.3024e-05 | -0.00093792 | 0.015666 | 0.015678 | 0.015678 | 0.99655 | -0.056438 | 0.99653 | -0.056208 | 7.1264
35 | -0.68506 | -0.32673 | 0.6851 | 0.32513 | 4.3806e-05 | -0.0015987 | 0.021984 | 0.021964 | 0.021984 | 0.99663 | -0.057194 | 0.99669 | -0.057729 | 9.9927
36 | 0.32232 | 0.15563 | -0.32232 | -0.15601 | 2.2678e-06 | -0.00037382 | 0.010368 | 0.010373 | 0.010373 | 0.99653 | -0.056208 | 0.99652 | -0.056147 | 4.7151
37 | 0.66617 | 0.31246 | -0.66608 | -0.31601 | 9.1629e-05 | -0.0035493 | 0.021312 | 0.021356 | 0.021356 | 0.99669 | -0.057729 | 0.99657 | -0.0566 | 9.7071
38 | -1.3513 | -0.63759 | 1.3519 | 0.63217 | 0.00058881 | -0.0054225 | 0.043275 | 0.043206 | 0.043275 | 0.99669 | -0.057729 | 0.9971 | -0.061269 | 19.6706
39 | -4.1753 | -1.862 | 4.1759 | 1.859 | 0.00058599 | -0.0029348 | 0.13236 | 0.13232 | 0.13236 | 0.9971 | -0.061269 | 0.99726 | -0.058099 | 31.4386
40 | -4.1759 | -1.859 | 4.1761 | 1.858 | 0.00021281 | -0.0010666 | 0.13232 | 0.1323 | 0.13232 | 0.99726 | -0.058099 | 0.99732 | -0.056946 | 31.4289
41 | 0.10168 | 0.049146 | -0.10167 | -0.049243 | 1.5727e-06 | -9.6753e-05 | 0.0032714 | 0.0032727 | 0.0032727 | 0.99652 | -0.056147 | 0.9965 | -0.056249 | 1.5584
42 | 7.0431 | 3.1309 | -7.0407 | -3.1338 | 0.0024158 | -0.0028523 | 0.22272 | 0.22278 | 0.22278 | 0.99902 | -0.018838 | 0.99862 | -0.026603 | 52.9164
43 | -7.0431 | -3.1309 | 7.0432 | 3.1308 | 0.00010163 | -0.00012014 | 0.22272 | 0.22272 | 0.22272 | 0.99902 | -0.018838 | 0.99904 | -0.018511 | 52.9023
44 | 6.3292 | 2.7996 | -6.326 | -2.805 | 0.003194 | -0.0053654 | 0.20006 | 0.20016 | 0.20016 | 0.99862 | -0.026603 | 0.99803 | -0.038092 | 47.5432
45 | 0.71154 | 0.33414 | -0.71153 | -0.33432 | 5.4471e-06 | -0.00018651 | 0.022724 | 0.022726 | 0.022726 | 0.99862 | -0.026603 | 0.99861 | -0.026541 | 10.33
46 | -7.1388 | -3.1771 | 7.1395 | 3.1763 | 0.00069 | -0.00077686 | 0.22578 | 0.22577 | 0.22578 | 0.99904 | -0.018511 | 0.99915 | -0.016324 | 53.6305
47 | 4.283 | 1.9036 | -4.2817 | -1.91 | 0.0013428 | -0.0063553 | 0.13557 | 0.13566 | 0.13566 | 0.99803 | -0.038092 | 0.99766 | -0.045181 | 32.223
48 | 2.043 | 0.90135 | -2.0427 | -0.90244 | 0.00027511 | -0.0010928 | 0.064588 | 0.064601 | 0.064601 | 0.99803 | -0.038092 | 0.9979 | -0.037157 | 29.3642
49 | 0.54936 | 0.25578 | -0.54935 | -0.25581 | 1.8133e-05 | -2.8122e-05 | 0.017518 | 0.017518 | 0.017518 | 0.99861 | -0.026541 | 0.99858 | -0.026791 | 8.342
50 | 4.2817 | 1.91 | -4.2806 | -1.9086 | 0.0010521 | 0.0014199 | 0.13566 | 0.13566 | 0.13566 | 0.99766 | -0.045181 | 0.99732 | -0.056946 | 33.0878
51 | 1.8951 | 0.83098 | -1.8944 | -0.83064 | 0.00076404 | 0.00033637 | 0.059861 | 0.059863 | 0.059863 | 0.9979 | -0.037157 | 0.99747 | -0.040798 | 28.5062
52 | -7.1395 | -3.1763 | 7.1401 | 3.1757 | 0.00054898 | -0.00061846 | 0.22577 | 0.22575 | 0.22577 | 0.99915 | -0.016324 | 0.99924 | -0.014584 | 53.6266
53 | 0.54935 | 0.25581 | -0.54929 | -0.25922 | 5.9124e-05 | -0.0034097 | 0.017518 | 0.01756 | 0.01756 | 0.99858 | -0.026791 | 0.99848 | -0.025921 | 7.982
54 | 0.39843 | 0.18738 | -0.39841 | -0.1904 | 2.7865e-05 | -0.0030207 | 0.012759 | 0.012796 | 0.012796 | 0.99619 | -0.059126 | 0.99613 | -0.058545 | 5.8166
55 | -0.39843 | -0.18738 | 0.39846 | 0.1873 | 2.1338e-05 | -7.3807e-05 | 0.012759 | 0.012758 | 0.012759 | 0.99619 | -0.059126 | 0.99625 | -0.058733 | 6.0756
56 | 0.39841 | 0.1904 | -0.39838 | -0.19276 | 2.1914e-05 | -0.0023628 | 0.012796 | 0.012826 | 0.012826 | 0.99613 | -0.058545 | 0.99608 | -0.058073 | 5.8301
57 | -0.66588 | -0.31617 | 0.66608 | 0.31601 | 0.00020018 | -0.00016655 | 0.021359 | 0.021356 | 0.021359 | 0.99625 | -0.058733 | 0.99657 | -0.0566 | 10.1711
58 | 0.10617 | 0.050771 | -0.10617 | -0.051108 | 5.963e-06 | -0.00033682 | 0.0034101 | 0.0034144 | 0.0034144 | 0.99625 | -0.058733 | 0.99619 | -0.059116 | 1.6259
59 | 0.20075 | 0.097044 | -0.20074 | -0.097224 | 1.1752e-05 | -0.00017964 | 0.0064622 | 0.0064646 | 0.0064646 | 0.99608 | -0.058073 | 0.99601 | -0.058461 | 3.0784
60 | 1.7996 | 0.7849 | -1.7984 | -0.7911 | 0.0011908 | -0.0061974 | 0.05682 | 0.056896 | 0.056896 | 0.99747 | -0.040798 | 0.99684 | -0.036299 | 25.8618
61 | 0.09477 | 0.045736 | -0.09477 | -0.045899 | 8.4817e-08 | -0.0001626 | 0.0030454 | 0.0030475 | 0.0030475 | 0.99747 | -0.040798 | 0.99747 | -0.04079 | 1.3852
62 | -0.069346 | -0.033586 | 0.069346 | 0.033524 | 4.5801e-07 | -6.1576e-05 | 0.002226 | 0.0022252 | 0.002226 | 0.99924 | -0.014628 | 0.99924 | -0.014584 | 1.06
63 | -7.2094 | -3.2092 | 7.2141 | 3.2042 | 0.0046445 | -0.0050609 | 0.22798 | 0.22787 | 0.22798 | 0.99924 | -0.014584 | 1 | 0 | 54.1517
64 | 0.37943 | 0.17665 | -0.37942 | -0.1767 | 1.2907e-05 | -5.1153e-05 | 0.012082 | 0.012083 | 0.012083 | 1 | 0 | 0.99996 | -0.00025746 | 5.7538
65 | 0.24978 | 0.11391 | -0.24977 | -0.11575 | 6.4742e-06 | -0.0018363 | 0.0079253 | 0.0079474 | 0.0079474 | 0.99996 | -0.00025746 | 0.99994 | -5.7494e-05 | 3.6125
66 | -0.10623 | -0.05145 | 0.10623 | 0.050726 | 4.6897e-07 | -0.00072397 | 0.0034076 | 0.0033986 | 0.0034076 | 0.99991 | 0.00018413 | 0.99991 | 0.00014628 | 1.5489
67 | -0.10623 | -0.050726 | 0.10623 | 0.04784 | 1.845e-06 | -0.0028858 | 0.0033986 | 0.0033635 | 0.0033986 | 0.99991 | 0.00014628 | 0.99993 | 9.2915e-06 | 1.5448
68 | -0.10623 | -0.04784 | 0.10623 | 0.046229 | 1.0136e-06 | -0.0016109 | 0.0033635 | 0.0033447 | 0.0033635 | 0.99993 | 9.2915e-06 | 0.99994 | -5.7494e-05 | 1.5289
69 | -0.16015 | -0.077564 | 0.16015 | 0.075951 | 2.4635e-06 | -0.0016135 | 0.0051856 | 0.0051652 | 0.0051856 | 0.9906 | -0.087603 | 0.99062 | -0.087734 | 2.3571
70 | 0.14732 | 0.058559 | -0.14731 | -0.071188 | 1.5842e-05 | -0.012629 | 0.0046198 | 0.0047681 | 0.0047681 | 0.99062 | -0.087734 | 0.99051 | -0.086992 | 2.1673
71 | -0.30747 | -0.13451 | 0.30752 | 0.1253 | 4.97e-05 | -0.0092061 | 0.00978 | 0.0096754 | 0.00978 | 0.99062 | -0.087734 | 0.99077 | -0.088723 | 4.4454
72 | 0.14731 | 0.071188 | -0.14731 | -0.071343 | 2.0159e-07 | -0.00015546 | 0.0047681 | 0.0047701 | 0.0047701 | 0.99051 | -0.086992 | 0.99051 | -0.08698 | 2.1682
73 | -0.30752 | -0.1253 | 0.30753 | 0.12449 | 4.3459e-06 | -0.00081449 | 0.0096754 | 0.0096665 | 0.0096754 | 0.99077 | -0.088723 | 0.99078 | -0.088799 | 4.3979
74 | 0.43861 | 0.18392 | -0.43808 | -0.18539 | 0.00052232 | -0.0014666 | 0.013839 | 0.013859 | 0.013859 | 0.9921 | -0.077271 | 0.99084 | -0.089164 | 6.5996
75 | 0.92008 | 0.39565 | -0.91438 | -0.39647 | 0.0056961 | -0.00081861 | 0.029142 | 0.029193 | 0.029193 | 0.9921 | -0.077271 | 0.98553 | -0.13562 | 13.9013
76 | -1.506 | -0.65094 | 1.512 | 0.65295 | 0.0059768 | 0.0020061 | 0.04774 | 0.04772 | 0.04774 | 0.9921 | -0.077271 | 0.99632 | -0.040107 | 22.7332
77 | 0.43808 | 0.18539 | -0.43806 | -0.18771 | 2.55e-05 | -0.0023189 | 0.013859 | 0.013886 | 0.013886 | 0.99084 | -0.089164 | 0.99078 | -0.088799 | 6.3117
78 | 0.75543 | 0.31949 | -0.75538 | -0.31951 | 4.9052e-05 | -2.4575e-05 | 0.024025 | 0.024026 | 0.024026 | 0.98553 | -0.13562 | 0.98546 | -0.13626 | 11.4409
79 | -1.6337 | -0.71186 | 1.6344 | 0.71214 | 0.00073457 | 0.00027675 | 0.051632 | 0.05163 | 0.051632 | 0.99632 | -0.040107 | 0.9968 | -0.03598 | 24.5868
80 | -1.7983 | -0.79153 | 1.7984 | 0.7911 | 8.3125e-05 | -0.00043164 | 0.056901 | 0.056896 | 0.056901 | 0.9968 | -0.03598 | 0.99684 | -0.036299 | 25.8642
81 | 0.14412 | 0.069043 | -0.14412 | -0.069802 | 9.1082e-07 | -0.00075856 | 0.0046208 | 0.0046304 | 0.0046304 | 0.99835 | -0.025396 | 0.99835 | -0.025342 | 2.1047
82 | -0.4252 | -0.20295 | 0.42524 | 0.1994 | 3.6948e-05 | -0.0035495 | 0.013624 | 0.01358 | 0.013624 | 0.99835 | -0.025396 | 0.99844 | -0.026114 | 6.1925
83 | 0.28108 | 0.13391 | -0.28104 | -0.13419 | 3.6932e-05 | -0.00028102 | 0.0090027 | 0.0090065 | 0.0090065 | 0.99835 | -0.025396 | 0.99822 | -0.026312 | 4.2888
84 | -0.42524 | -0.1994 | 0.42526 | 0.19936 | 1.4263e-05 | -4.2733e-05 | 0.01358 | 0.013579 | 0.01358 | 0.99844 | -0.026114 | 0.99847 | -0.025866 | 6.4664
85 | 0.12893 | 0.060521 | -0.12893 | -0.060604 | 2.1221e-06 | -8.2157e-05 | 0.004119 | 0.0041201 | 0.0041201 | 0.99822 | -0.026312 | 0.9982 | -0.026433 | 1.9619
86 | -0.54928 | -0.25943 | 0.54929 | 0.25922 | 3.6652e-06 | -0.00021081 | 0.017563 | 0.01756 | 0.017563 | 0.99847 | -0.025866 | 0.99848 | -0.025921 | 7.9832
87 | 0.12893 | 0.060604 | -0.12893 | -0.062052 | 1.3858e-06 | -0.0014481 | 0.0041201 | 0.004138 | 0.004138 | 0.9982 | -0.026433 | 0.99819 | -0.026344 | 1.8809
88 | 0.12893 | 0.062052 | -0.12893 | -0.062444 | 3.7766e-07 | -0.00039244 | 0.004138 | 0.004143 | 0.004143 | 0.99819 | -0.026344 | 0.99819 | -0.026318 | 1.8832
89 | 0.10617 | 0.051108 | -0.10616 | -0.051416 | 5.4639e-06 | -0.00030784 | 0.0034144 | 0.0034183 | 0.0034183 | 0.99619 | -0.059116 | 0.99613 | -0.05946 | 1.6278
90 | 0.67972 | 0.2981 | -0.67958 | -0.303 | 0.00013468 | -0.0048945 | 0.021742 | 0.0218 | 0.0218 | 0.98546 | -0.13626 | 0.98528 | -0.13488 | 9.9093
91 | 0.075667 | 0.021409 | -0.075664 | -0.02822 | 2.1339e-06 | -0.0068103 | 0.0023036 | 0.0023657 | 0.0023657 | 0.98546 | -0.13626 | 0.98543 | -0.13621 | 1.0753
92 | 0.67958 | 0.303 | -0.67957 | -0.3034 | 1.1128e-05 | -0.00040312 | 0.0218 | 0.021805 | 0.021805 | 0.98528 | -0.13488 | 0.98526 | -0.13476 | 9.9115
93 | 0.075664 | 0.02822 | -0.075662 | -0.036645 | 2.8216e-06 | -0.0084249 | 0.0023657 | 0.0024628 | 0.0024628 | 0.98543 | -0.13621 | 0.9854 | -0.13597 | 1.1195
94 | 0.51655 | 0.22445 | -0.51652 | -0.22628 | 2.8893e-05 | -0.0018311 | 0.016502 | 0.016523 | 0.016523 | 0.98526 | -0.13476 | 0.98521 | -0.13438 | 7.5106
95 | 0.083017 | 0.039708 | -0.083017 | -0.040207 | 2.0949e-07 | -0.00049856 | 0.0026969 | 0.0027032 | 0.0027032 | 0.98503 | -0.13376 | 0.98503 | -0.13374 | 1.2287
96 | -0.21951 | -0.10581 | 0.21951 | 0.10469 | 3.305e-06 | -0.0011259 | 0.0071413 | 0.007127 | 0.0071413 | 0.98503 | -0.13376 | 0.98505 | -0.13389 | 3.2461
97 | -0.42268 | -0.185 | 0.42268 | 0.18493 | 7.4607e-07 | -7.0601e-05 | 0.013521 | 0.013521 | 0.013521 | 0.98505 | -0.13389 | 0.98505 | -0.1339 | 6.1461
98 | 0.20317 | 0.08031 | -0.20287 | -0.08483 | 0.00029968 | -0.0045201 | 0.0064023 | 0.0064543 | 0.0064543 | 0.98505 | -0.13389 | 0.98348 | -0.14983 | 3.0735
99 | -0.51644 | -0.23034 | 0.51646 | 0.2303 | 2.246e-05 | -3.911e-05 | 0.016572 | 0.016571 | 0.016572 | 0.98505 | -0.1339 | 0.98509 | -0.13352 | 7.8913
100 | 0.097418 | 0.033758 | -0.097417 | -0.03603 | 1.212e-06 | -0.0022722 | 0.0030263 | 0.0030488 | 0.0030488 | 0.98348 | -0.14983 | 0.98347 | -0.14979 | 1.3858
101 | -0.51646 | -0.2303 | 0.51652 | 0.22628 | 6.3669e-05 | -0.0040173 | 0.016571 | 0.016523 | 0.016571 | 0.98509 | -0.13352 | 0.98521 | -0.13438 | 7.5323
102 | 0.097417 | 0.03603 | -0.097413 | -0.043165 | 3.931e-06 | -0.0071358 | 0.0030488 | 0.0031276 | 0.0031276 | 0.98347 | -0.14979 | 0.98343 | -0.14957 | 1.4216
103 | 0.097413 | 0.043165 | -0.097411 | -0.047178 | 2.3051e-06 | -0.0040126 | 0.0031276 | 0.0031772 | 0.0031772 | 0.98343 | -0.14957 | 0.98341 | -0.14938 | 1.4442

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 7.6075 | 3.3913

## res_load
| p_mw | q_mvar
0 | 0.2785 | 0.13488
1 | 0.072329 | 0.035031
2 | 0.32395 | 0.15689
3 | 0.2519 | 0.122
4 | 0.2981 | 0.14437
5 | 0.12951 | 0.062722
6 | 0.090164 | 0.043668
7 | 0.11562 | 0.055997
8 | 0.058678 | 0.028419
9 | 0.14918 | 0.072249
10 | 0.15547 | 0.075297
11 | 0.15153 | 0.073391
12 | 0.091798 | 0.04446
13 | 0.15782 | 0.076433
14 | 0.14266 | 0.069092
15 | 0.17529 | 0.084898
16 | 0.11144 | 0.053974
17 | 0.086272 | 0.041784
18 | 0.16496 | 0.079895
19 | 0.22064 | 0.10686
20 | 0.09562 | 0.046311
21 | 0.15997 | 0.077475
22 | 0.16217 | 0.078541
23 | 0.14756 | 0.071467
24 | 0.16125 | 0.078099
25 | 0.19763 | 0.095717
26 | 0.1045 | 0.050611
27 | 0.069346 | 0.033586
28 | 0.12964 | 0.062788
29 | 0.10623 | 0.05145
30 | 0.14354 | 0.06952
31 | 0.16015 | 0.077564
32 | 0.14735 | 0.071367
33 | 0.15895 | 0.076982
34 | 0.12164 | 0.058914
35 | 0.14731 | 0.071343
36 | 0.13053 | 0.063219
37 | 0.16393 | 0.079393
38 | 0.14412 | 0.069802
39 | 0.15211 | 0.07367
40 | 0.12403 | 0.06007
41 | 0.10167 | 0.049243
42 | 0.10616 | 0.051416
43 | 0.20074 | 0.097224
44 | 0.16302 | 0.078953
45 | 0.075662 | 0.036645
46 | 0.13649 | 0.066105
47 | 0.083017 | 0.040207
48 | 0.093758 | 0.045409
49 | 0.10545 | 0.051073
50 | 0.097411 | 0.047178
51 | 0.09477 | 0.045899
52 | 0.12893 | 0.062444

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1