## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_337_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_337_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_337_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_337_0_node_182 | 20 | n |  | TRUE
4 | bus_MV_337_0_node_179 | 20 | n |  | TRUE
5 | bus_MV_337_0_node_12 | 20 | n |  | TRUE
6 | bus_MV_337_0_node_3 | 20 | n |  | TRUE
7 | bus_MV_337_0_node_4 | 20 | n |  | TRUE
8 | bus_MV_337_0_node_177 | 20 | n |  | TRUE
9 | bus_MV_337_0_node_5 | 20 | n |  | TRUE
10 | bus_MV_337_0_node_6 | 20 | n |  | TRUE
11 | bus_MV_337_0_node_7 | 20 | n |  | TRUE
12 | bus_MV_337_0_node_8 | 20 | n |  | TRUE
13 | bus_MV_337_0_node_137 | 20 | n |  | TRUE
14 | bus_MV_337_0_node_136 | 20 | n |  | TRUE
15 | bus_MV_337_0_node_9 | 20 | n |  | TRUE
16 | bus_MV_337_0_node_11 | 20 | n |  | TRUE
17 | bus_MV_337_0_node_13 | 20 | n |  | TRUE
18 | bus_MV_337_0_node_135 | 20 | n |  | TRUE
19 | bus_MV_337_0_node_15 | 20 | n |  | TRUE
20 | bus_MV_337_0_node_14 | 20 | n |  | TRUE
21 | bus_MV_337_0_node_125 | 20 | n |  | TRUE
22 | bus_MV_337_0_node_124 | 20 | n |  | TRUE
23 | bus_MV_337_0_node_108 | 20 | n |  | TRUE
24 | bus_MV_337_0_node_110 | 20 | n |  | TRUE
25 | bus_MV_337_0_node_114 | 20 | n |  | TRUE
26 | bus_MV_337_0_node_121 | 20 | n |  | TRUE
27 | bus_MV_337_0_node_119 | 20 | n |  | TRUE
28 | bus_MV_337_0_node_116 | 20 | n |  | TRUE
29 | bus_MV_337_0_node_117 | 20 | n |  | TRUE
30 | bus_MV_337_0_node_118 | 20 | n |  | TRUE
31 | bus_MV_337_0_node_134 | 20 | n |  | TRUE
32 | bus_MV_337_0_node_120 | 20 | n |  | TRUE
33 | bus_MV_337_0_node_123 | 20 | n |  | TRUE
34 | bus_MV_337_0_node_170 | 20 | n |  | TRUE
35 | bus_MV_337_0_node_126 | 20 | n |  | TRUE
36 | bus_MV_337_0_node_128 | 20 | n |  | TRUE
37 | bus_MV_337_0_node_173 | 20 | n |  | TRUE
38 | bus_MV_337_0_node_127 | 20 | n |  | TRUE
39 | bus_MV_337_0_node_129 | 20 | n |  | TRUE
40 | bus_MV_337_0_node_130 | 20 | n |  | TRUE
41 | bus_MV_337_0_node_131 | 20 | n |  | TRUE
42 | bus_MV_337_0_node_169 | 20 | n |  | TRUE
43 | bus_MV_337_0_node_138 | 20 | n |  | TRUE
44 | bus_MV_337_0_node_140 | 20 | n |  | TRUE
45 | bus_MV_337_0_node_139 | 20 | n |  | TRUE
46 | bus_MV_337_0_node_181 | 20 | n |  | TRUE
47 | bus_MV_337_0_node_16 | 20 | n |  | TRUE
48 | bus_MV_337_0_node_18 | 20 | n |  | TRUE
49 | bus_MV_337_0_node_17 | 20 | n |  | TRUE
50 | bus_MV_337_0_node_20 | 20 | n |  | TRUE
51 | bus_MV_337_0_node_19 | 20 | n |  | TRUE
52 | bus_MV_337_0_node_21 | 20 | n |  | TRUE
53 | bus_MV_337_0_node_22 | 20 | n |  | TRUE
54 | bus_MV_337_0_node_23 | 20 | n |  | TRUE
55 | bus_MV_337_0_node_183 | 20 | n |  | TRUE
56 | bus_MV_337_0_node_99 | 20 | n |  | TRUE
57 | bus_MV_337_0_node_24 | 20 | n |  | TRUE
58 | bus_MV_337_0_node_25 | 20 | n |  | TRUE
59 | bus_MV_337_0_node_27 | 20 | n |  | TRUE
60 | bus_MV_337_0_node_57 | 20 | n |  | TRUE
61 | bus_MV_337_0_node_35 | 20 | n |  | TRUE
62 | bus_MV_337_0_node_56 | 20 | n |  | TRUE
63 | bus_MV_337_0_node_28 | 20 | n |  | TRUE
64 | bus_MV_337_0_node_107 | 20 | n |  | TRUE
65 | bus_MV_337_0_node_31 | 20 | n |  | TRUE
66 | bus_MV_337_0_node_26 | 20 | n |  | TRUE
67 | bus_MV_337_0_node_58 | 20 | n |  | TRUE
68 | bus_MV_337_0_node_176 | 20 | n |  | TRUE
69 | bus_MV_337_0_node_63 | 20 | n |  | TRUE
70 | bus_MV_337_0_node_29 | 20 | n |  | TRUE
71 | bus_MV_337_0_node_175 | 20 | n |  | TRUE
72 | bus_MV_337_0_node_30 | 20 | n |  | TRUE
73 | bus_MV_337_0_node_49 | 20 | n |  | TRUE
74 | bus_MV_337_0_node_46 | 20 | n |  | TRUE
75 | bus_MV_337_0_node_47 | 20 | n |  | TRUE
76 | bus_MV_337_0_node_48 | 20 | n |  | TRUE
77 | bus_MV_337_0_node_167 | 20 | n |  | TRUE
78 | bus_MV_337_0_node_32 | 20 | n |  | TRUE
79 | bus_MV_337_0_node_33 | 20 | n |  | TRUE
80 | bus_MV_337_0_node_34 | 20 | n |  | TRUE
81 | bus_MV_337_0_node_45 | 20 | n |  | TRUE
82 | bus_MV_337_0_node_155 | 20 | n |  | TRUE
83 | bus_MV_337_0_node_44 | 20 | n |  | TRUE
84 | bus_MV_337_0_node_43 | 20 | n |  | TRUE
85 | bus_MV_337_0_node_148 | 20 | n |  | TRUE
86 | bus_MV_337_0_node_147 | 20 | n |  | TRUE
87 | bus_MV_337_0_node_152 | 20 | n |  | TRUE
88 | bus_MV_337_0_node_36 | 20 | n |  | TRUE
89 | bus_MV_337_0_node_37 | 20 | n |  | TRUE
90 | bus_MV_337_0_node_53 | 20 | n |  | TRUE
91 | bus_MV_337_0_node_54 | 20 | n |  | TRUE
92 | bus_MV_337_0_node_55 | 20 | n |  | TRUE
93 | bus_MV_337_0_node_52 | 20 | n |  | TRUE
94 | bus_MV_337_0_node_38 | 20 | n |  | TRUE
95 | bus_MV_337_0_node_39 | 20 | n |  | TRUE
96 | bus_MV_337_0_node_40 | 20 | n |  | TRUE
97 | bus_MV_337_0_node_41 | 20 | n |  | TRUE
98 | bus_MV_337_0_node_42 | 20 | n |  | TRUE
99 | bus_MV_337_0_node_88 | 20 | n |  | TRUE
100 | bus_MV_337_0_node_149 | 20 | n |  | TRUE
101 | bus_MV_337_0_node_89 | 20 | n |  | TRUE
102 | bus_MV_337_0_node_50 | 20 | n |  | TRUE
103 | bus_MV_337_0_node_51 | 20 | n |  | TRUE
104 | bus_MV_337_0_node_165 | 20 | n |  | TRUE
105 | bus_MV_337_0_node_156 | 20 | n |  | TRUE
106 | bus_MV_337_0_node_168 | 20 | n |  | TRUE
107 | bus_MV_337_0_node_84 | 20 | n |  | TRUE
108 | bus_MV_337_0_node_98 | 20 | n |  | TRUE
109 | bus_MV_337_0_node_67 | 20 | n |  | TRUE
110 | bus_MV_337_0_node_59 | 20 | n |  | TRUE
111 | bus_MV_337_0_node_60 | 20 | n |  | TRUE
112 | bus_MV_337_0_node_61 | 20 | n |  | TRUE
113 | bus_MV_337_0_node_62 | 20 | n |  | TRUE
114 | bus_MV_337_0_node_65 | 20 | n |  | TRUE
115 | bus_MV_337_0_node_66 | 20 | n |  | TRUE
116 | bus_MV_337_0_node_81 | 20 | n |  | TRUE
117 | bus_MV_337_0_node_64 | 20 | n |  | TRUE
118 | bus_MV_337_0_node_74 | 20 | n |  | TRUE
119 | bus_MV_337_0_node_70 | 20 | n |  | TRUE
120 | bus_MV_337_0_node_72 | 20 | n |  | TRUE
121 | bus_MV_337_0_node_73 | 20 | n |  | TRUE
122 | bus_MV_337_0_node_69 | 20 | n |  | TRUE
123 | bus_MV_337_0_node_75 | 20 | n |  | TRUE
124 | bus_MV_337_0_node_71 | 20 | n |  | TRUE
125 | bus_MV_337_0_node_82 | 20 | n |  | TRUE
126 | bus_MV_337_0_node_83 | 20 | n |  | TRUE
127 | bus_MV_337_0_node_76 | 20 | n |  | TRUE
128 | bus_MV_337_0_node_77 | 20 | n |  | TRUE
129 | bus_MV_337_0_node_78 | 20 | n |  | TRUE
130 | bus_MV_337_0_node_79 | 20 | n |  | TRUE
131 | bus_MV_337_0_node_80 | 20 | n |  | TRUE
132 | bus_MV_337_0_node_91 | 20 | n |  | TRUE
133 | bus_MV_337_0_node_161 | 20 | n |  | TRUE
134 | bus_MV_337_0_node_132 | 20 | n |  | TRUE
135 | bus_MV_337_0_node_85 | 20 | n |  | TRUE
136 | bus_MV_337_0_node_86 | 20 | n |  | TRUE
137 | bus_MV_337_0_node_87 | 20 | n |  | TRUE
138 | bus_MV_337_0_node_159 | 20 | n |  | TRUE
139 | bus_MV_337_0_node_164 | 20 | n |  | TRUE
140 | bus_MV_337_0_node_172 | 20 | n |  | TRUE
141 | bus_MV_337_0_node_163 | 20 | n |  | TRUE
142 | bus_MV_337_0_node_178 | 20 | n |  | TRUE
143 | bus_MV_337_0_node_145 | 20 | n |  | TRUE
144 | bus_MV_337_0_node_158 | 20 | n |  | TRUE
145 | bus_MV_337_0_node_90 | 20 | n |  | TRUE
146 | bus_MV_337_0_node_100 | 20 | n |  | TRUE
147 | bus_MV_337_0_node_93 | 20 | n |  | TRUE
148 | bus_MV_337_0_node_174 | 20 | n |  | TRUE
149 | bus_MV_337_0_node_92 | 20 | n |  | TRUE
150 | bus_MV_337_0_node_94 | 20 | n |  | TRUE
151 | bus_MV_337_0_node_96 | 20 | n |  | TRUE
152 | bus_MV_337_0_node_95 | 20 | n |  | TRUE
153 | bus_MV_337_0_node_162 | 20 | n |  | TRUE
154 | bus_MV_337_0_node_101 | 20 | n |  | TRUE
155 | bus_MV_337_0_node_102 | 20 | n |  | TRUE
156 | bus_MV_337_0_node_104 | 20 | n |  | TRUE
157 | bus_MV_337_0_node_106 | 20 | n |  | TRUE
158 | bus_MV_337_0_node_103 | 20 | n |  | TRUE
159 | bus_MV_337_0_node_160 | 20 | n |  | TRUE
160 | bus_MV_337_0_node_184 | 20 | n |  | TRUE
161 | bus_MV_337_0_node_171 | 20 | n |  | TRUE
162 | bus_MV_337_0_node_180 | 20 | n |  | TRUE
163 | bus_MV_337_0_node_146 | 20 | n |  | TRUE
164 | bus_MV_337_0_node_144 | 20 | n |  | TRUE
165 | bus_MV_337_0_node_115 | 20 | n |  | TRUE
166 | bus_MV_337_0_node_109 | 20 | n |  | TRUE
167 | bus_MV_337_0_node_111 | 20 | n |  | TRUE
168 | bus_MV_337_0_node_112 | 20 | n |  | TRUE
169 | bus_MV_337_0_node_113 | 20 | n |  | TRUE
170 | bus_MV_337_0_node_141 | 20 | n |  | TRUE
171 | bus_MV_337_0_node_142 | 20 | n |  | TRUE
172 | bus_MV_337_0_node_143 | 20 | n |  | TRUE
173 | bus_MV_337_0_node_157 | 20 | n |  | TRUE
174 | bus_MV_337_0_node_150 | 20 | n |  | TRUE
175 | bus_MV_337_0_node_151 | 20 | n |  | TRUE
176 | bus_MV_337_0_node_153 | 20 | n |  | TRUE
177 | bus_MV_337_0_node_154 | 20 | n |  | TRUE
178 | bus_MV_337_0_node_166 | 20 | n |  | TRUE
179 | bus_HV_337_0_node_84 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_337_0_load_0 | 0 | 0.14128 | 0.068427 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_337_0_load_182 | 3 | 0.098971 | 0.047934 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_337_0_load_179 | 4 | 0.060378 | 0.029243 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_337_0_load_3 | 6 | 0.069625 | 0.033721 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_337_0_load_177 | 8 | 0.10196 | 0.049383 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_337_0_load_6 | 10 | 0.15091 | 0.073089 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_337_0_load_136 | 14 | 0.35952 | 0.17413 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_337_0_load_9 | 15 | 0.13584 | 0.065792 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_337_0_load_135 | 18 | 0.19044 | 0.092233 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_337_0_load_14 | 20 | 0.1216 | 0.058895 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_337_0_load_124 | 22 | 0.076654 | 0.037125 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_337_0_load_108 | 23 | 0.15886 | 0.076939 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_337_0_load_110 | 24 | 0.0832 | 0.040296 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_337_0_load_114 | 25 | 0.12932 | 0.062632 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_337_0_load_116 | 28 | 0.102 | 0.0494 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_337_0_load_134 | 31 | 0.15127 | 0.073264 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_337_0_load_123 | 33 | 0.1278 | 0.061897 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_337_0_load_170 | 34 | 0.16861 | 0.081661 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_337_0_load_173 | 37 | 0.11211 | 0.0543 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_337_0_load_127 | 38 | 0.058071 | 0.028125 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_337_0_load_129 | 39 | 0.053379 | 0.025852 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_337_0_load_169 | 42 | 0.070604 | 0.034195 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_337_0_load_138 | 43 | 0.92956 | 0.45021 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_337_0_load_140 | 44 | 0.16184 | 0.078381 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_337_0_load_139 | 45 | 0.13173 | 0.063801 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_337_0_load_181 | 46 | 0.079249 | 0.038382 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_337_0_load_16 | 47 | 0.059378 | 0.028758 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_337_0_load_21 | 52 | 0.11633 | 0.056341 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_337_0_load_183 | 55 | 0.098549 | 0.047729 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_337_0_load_99 | 56 | 0.062197 | 0.030123 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_337_0_load_24 | 57 | 0.13839 | 0.067026 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_337_0_load_25 | 58 | 0.1062 | 0.051434 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_337_0_load_27 | 59 | 0.13492 | 0.065346 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_337_0_load_57 | 60 | 0.10716 | 0.051899 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_337_0_load_35 | 61 | 0.078685 | 0.038109 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_337_0_load_56 | 62 | 0.098824 | 0.047863 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_337_0_load_107 | 64 | 0.12086 | 0.058537 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_337_0_load_176 | 68 | 0.16338 | 0.079126 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_337_0_load_175 | 71 | 0.11154 | 0.054021 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_337_0_load_46 | 74 | 0.13858 | 0.067116 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_337_0_load_167 | 77 | 0.15844 | 0.076735 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_337_0_load_32 | 78 | 0.15361 | 0.074394 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_337_0_load_155 | 82 | 0.074409 | 0.036038 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_337_0_load_43 | 84 | 0.14486 | 0.070159 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_337_0_load_147 | 86 | 0.083386 | 0.040386 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_337_0_load_36 | 88 | 0.11152 | 0.054011 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_337_0_load_52 | 93 | 0.16335 | 0.079114 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_337_0_load_38 | 94 | 0.11991 | 0.058073 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_337_0_load_88 | 99 | 0.15011 | 0.072703 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_337_0_load_149 | 100 | 0.16128 | 0.078113 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_337_0_load_51 | 103 | 0.43995 | 0.21308 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_337_0_load_165 | 104 | 0.11048 | 0.053508 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_337_0_load_156 | 105 | 0.068488 | 0.03317 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_337_0_load_168 | 106 | 2.2405 | 1.0851 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_337_0_load_84 | 107 | 0.12775 | 0.061873 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_337_0_load_98 | 108 | 0.094407 | 0.045723 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_337_0_load_67 | 109 | 0.090558 | 0.043859 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_337_0_load_59 | 110 | 0.081336 | 0.039393 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_337_0_load_81 | 116 | 0.1317 | 0.063787 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_337_0_load_64 | 117 | 0.15375 | 0.074465 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_337_0_load_73 | 121 | 0.08524 | 0.041284 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_337_0_load_69 | 122 | 0.10146 | 0.049139 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_337_0_load_75 | 123 | 0.12397 | 0.060041 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_337_0_load_83 | 126 | 0.12749 | 0.061744 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_337_0_load_76 | 127 | 0.060357 | 0.029232 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_337_0_load_161 | 133 | 0.083901 | 0.040635 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_337_0_load_132 | 134 | 0.058332 | 0.028251 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_337_0_load_85 | 135 | 0.10955 | 0.053059 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_337_0_load_86 | 136 | 0.094839 | 0.045933 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_337_0_load_163 | 141 | 0.16367 | 0.079267 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_337_0_load_178 | 142 | 0.13885 | 0.067246 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_337_0_load_145 | 143 | 0.11649 | 0.05642 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_337_0_load_100 | 146 | 0.11041 | 0.053472 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_337_0_load_174 | 148 | 0.11393 | 0.055179 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_337_0_load_92 | 149 | 0.15008 | 0.072688 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_337_0_load_95 | 152 | 0.098636 | 0.047772 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_337_0_load_162 | 153 | 0.097428 | 0.047186 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_337_0_load_101 | 154 | 0.10561 | 0.051148 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_337_0_load_160 | 159 | 0.14084 | 0.068214 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_337_0_load_184 | 160 | 0.26514 | 0.12841 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_337_0_load_171 | 161 | 0.16163 | 0.078279 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_337_0_load_180 | 162 | 0.081014 | 0.039237 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_337_0_load_115 | 165 | 0.1321 | 0.06398 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_337_0_load_111 | 167 | 0.091077 | 0.044111 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_337_0_load_113 | 169 | 0.15456 | 0.074858 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_337_0_load_141 | 170 | 0.52835 | 0.25589 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_337_0_load_143 | 172 | 0.17026 | 0.082458 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_337_0_load_157 | 173 | 0.15675 | 0.075918 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_337_0_load_150 | 174 | 0.59391 | 0.28764 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_337_0_load_154 | 177 | 0.077851 | 0.037705 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_337_0_load_166 | 178 | 0.23726 | 0.11491 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 107 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_337_0_line_0 |  | 0 | 1 | 0.019204 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_337_0_line_1 |  | 1 | 2 | 0.22538 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_337_0_line_2 |  | 2 | 4 | 0.03428 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_337_0_line_3 |  | 3 | 4 | 6.2557 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
4 | MV_337_0_line_4 |  | 3 | 5 | 0.024386 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
5 | MV_337_0_line_5 |  | 5 | 18 | 1.6092 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
6 | MV_337_0_line_6 |  | 5 | 15 | 0.5605 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
7 | MV_337_0_line_7 |  | 6 | 7 | 0.14156 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
8 | MV_337_0_line_8 |  | 6 | 8 | 2.1307 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
9 | MV_337_0_line_9 |  | 7 | 9 | 0.91873 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
10 | MV_337_0_line_10 |  | 8 | 32 | 0.13948 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
11 | MV_337_0_line_11 |  | 9 | 44 | 0.018269 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
12 | MV_337_0_line_12 |  | 9 | 45 | 0.025009 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_337_0_line_13 |  | 10 | 11 | 0.077631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_337_0_line_14 |  | 11 | 12 | 0.13825 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_337_0_line_15 |  | 12 | 13 | 0.030659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_337_0_line_16 |  | 12 | 14 | 0.044097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_337_0_line_17 |  | 13 | 43 | 0.0086756 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_337_0_line_18 |  | 14 | 18 | 0.025929 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_337_0_line_19 |  | 15 | 16 | 0.057461 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
20 | MV_337_0_line_20 |  | 16 | 17 | 0.22958 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
21 | MV_337_0_line_21 |  | 17 | 19 | 0.79885 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
22 | MV_337_0_line_22 |  | 17 | 20 | 0.036974 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_337_0_line_23 |  | 19 | 21 | 0.50226 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
24 | MV_337_0_line_24 |  | 19 | 22 | 0.025234 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_337_0_line_25 |  | 21 | 34 | 0.096553 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
26 | MV_337_0_line_26 |  | 23 | 24 | 0.048668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_337_0_line_27 |  | 23 | 25 | 0.019583 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_337_0_line_28 |  | 24 | 165 | 0.043273 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_337_0_line_29 |  | 25 | 26 | 0.027223 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_337_0_line_30 |  | 25 | 27 | 0.043884 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_337_0_line_31 |  | 26 | 33 | 0.020202 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_337_0_line_32 |  | 27 | 32 | 0.19875 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
33 | MV_337_0_line_33 |  | 27 | 29 | 0.070511 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
34 | MV_337_0_line_34 |  | 28 | 29 | 0.019477 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_337_0_line_35 |  | 29 | 30 | 0.050493 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
36 | MV_337_0_line_36 |  | 30 | 31 | 0.012986 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
37 | MV_337_0_line_37 |  | 31 | 38 | 1.926 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
38 | MV_337_0_line_38 |  | 34 | 42 | 0.030176 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
39 | MV_337_0_line_39 |  | 35 | 36 | 1.2624 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
40 | MV_337_0_line_40 |  | 35 | 37 | 0.028714 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
41 | MV_337_0_line_41 |  | 36 | 38 | 0.071895 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
42 | MV_337_0_line_42 |  | 37 | 41 | 0.033608 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
43 | MV_337_0_line_43 |  | 39 | 40 | 0.079232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_337_0_line_44 |  | 40 | 41 | 0.3351 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
45 | MV_337_0_line_45 |  | 40 | 42 | 0.1909 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
46 | MV_337_0_line_46 |  | 44 | 46 | 0.091577 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
47 | MV_337_0_line_47 |  | 46 | 51 | 0.093816 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
48 | MV_337_0_line_48 |  | 47 | 48 | 0.047577 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
49 | MV_337_0_line_49 |  | 47 | 49 | 0.12244 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
50 | MV_337_0_line_50 |  | 48 | 50 | 0.20507 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
51 | MV_337_0_line_51 |  | 49 | 51 | 0.12849 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
52 | MV_337_0_line_52 |  | 50 | 52 | 0.25515 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
53 | MV_337_0_line_53 |  | 52 | 53 | 0.073109 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
54 | MV_337_0_line_54 |  | 53 | 54 | 0.17815 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
55 | MV_337_0_line_55 |  | 54 | 55 | 0.081629 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
56 | MV_337_0_line_56 |  | 55 | 56 | 1.0796 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
57 | MV_337_0_line_57 |  | 56 | 134 | 1.2905 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_337_0_line_58 |  | 56 | 107 | 1.068 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
59 | MV_337_0_line_59 |  | 57 | 58 | 0.146 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
60 | MV_337_0_line_60 |  | 57 | 59 | 0.20569 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
61 | MV_337_0_line_61 |  | 58 | 60 | 0.034279 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
62 | MV_337_0_line_62 |  | 59 | 63 | 0.072624 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
63 | MV_337_0_line_63 |  | 60 | 61 | 0.044771 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_337_0_line_64 |  | 60 | 62 | 0.063953 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
65 | MV_337_0_line_65 |  | 62 | 66 | 0.006096 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
66 | MV_337_0_line_66 |  | 63 | 70 | 0.50907 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_337_0_line_67 |  | 63 | 65 | 0.17274 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
68 | MV_337_0_line_68 |  | 64 | 65 | 0.057623 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_337_0_line_69 |  | 65 | 75 | 0.20478 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
70 | MV_337_0_line_70 |  | 66 | 67 | 0.046787 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
71 | MV_337_0_line_71 |  | 67 | 68 | 0.062529 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
72 | MV_337_0_line_72 |  | 67 | 69 | 0.72484 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_337_0_line_73 |  | 68 | 88 | 0.14064 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
74 | MV_337_0_line_74 |  | 69 | 109 | 0.050657 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_337_0_line_75 |  | 70 | 71 | 0.056165 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_337_0_line_76 |  | 72 | 73 | 0.012663 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_337_0_line_77 |  | 72 | 74 | 0.01752 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_337_0_line_78 |  | 73 | 77 | 0.015686 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_337_0_line_79 |  | 74 | 75 | 0.043854 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_337_0_line_80 |  | 75 | 76 | 0.006083 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
81 | MV_337_0_line_81 |  | 76 | 102 | 0.020793 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
82 | MV_337_0_line_82 |  | 76 | 103 | 0.055543 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_337_0_line_83 |  | 78 | 79 | 0.029692 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_337_0_line_84 |  | 79 | 80 | 0.022887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_337_0_line_85 |  | 80 | 81 | 0.17768 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
86 | MV_337_0_line_86 |  | 80 | 82 | 0.014253 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
87 | MV_337_0_line_87 |  | 81 | 85 | 0.019694 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
88 | MV_337_0_line_88 |  | 81 | 86 | 0.035461 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_337_0_line_89 |  | 81 | 83 | 0.38833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_337_0_line_90 |  | 82 | 87 | 0.047407 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
91 | MV_337_0_line_91 |  | 83 | 84 | 0.052181 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_337_0_line_92 |  | 85 | 100 | 0.10649 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
93 | MV_337_0_line_93 |  | 87 | 177 | 0.054456 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
94 | MV_337_0_line_94 |  | 87 | 175 | 0.061118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_337_0_line_95 |  | 88 | 89 | 0.02194 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
96 | MV_337_0_line_96 |  | 89 | 90 | 0.36267 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
97 | MV_337_0_line_97 |  | 90 | 91 | 0.46077 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_337_0_line_98 |  | 90 | 92 | 0.67331 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
99 | MV_337_0_line_99 |  | 90 | 93 | 0.03866 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_337_0_line_100 |  | 91 | 106 | 0.027623 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_337_0_line_101 |  | 92 | 107 | 0.055021 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
102 | MV_337_0_line_102 |  | 94 | 95 | 0.012078 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
103 | MV_337_0_line_103 |  | 94 | 96 | 0.050614 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
104 | MV_337_0_line_104 |  | 95 | 97 | 0.53974 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
105 | MV_337_0_line_105 |  | 96 | 98 | 0.28867 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
106 | MV_337_0_line_106 |  | 97 | 99 | 0.12081 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
107 | MV_337_0_line_107 |  | 98 | 100 | 0.059438 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
108 | MV_337_0_line_108 |  | 99 | 101 | 0.094952 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
109 | MV_337_0_line_109 |  | 101 | 132 | 0.60728 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
110 | MV_337_0_line_110 |  | 102 | 104 | 0.033505 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
111 | MV_337_0_line_111 |  | 104 | 105 | 0.022466 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
112 | MV_337_0_line_112 |  | 105 | 177 | 0.020603 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
113 | MV_337_0_line_113 |  | 107 | 108 | 0.67094 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
114 | MV_337_0_line_114 |  | 109 | 115 | 0.054173 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_337_0_line_115 |  | 110 | 111 | 0.0066 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_337_0_line_116 |  | 110 | 112 | 0.022227 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_337_0_line_117 |  | 111 | 113 | 0.37549 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_337_0_line_118 |  | 111 | 114 | 0.14787 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
119 | MV_337_0_line_119 |  | 112 | 115 | 0.10182 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
120 | MV_337_0_line_120 |  | 113 | 116 | 0.00984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_337_0_line_121 |  | 114 | 117 | 0.12055 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
122 | MV_337_0_line_122 |  | 116 | 118 | 0.12442 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
123 | MV_337_0_line_123 |  | 118 | 125 | 0.35504 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_337_0_line_124 |  | 118 | 124 | 0.27951 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_337_0_line_125 |  | 119 | 120 | 0.015685 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_337_0_line_126 |  | 119 | 121 | 0.087403 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_337_0_line_127 |  | 119 | 122 | 0.33425 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
128 | MV_337_0_line_128 |  | 120 | 123 | 0.10127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_337_0_line_129 |  | 122 | 124 | 0.06858 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_337_0_line_130 |  | 125 | 126 | 0.11999 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
131 | MV_337_0_line_131 |  | 126 | 130 | 0.23572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_337_0_line_132 |  | 127 | 128 | 0.030133 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_337_0_line_133 |  | 127 | 129 | 0.03347 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_337_0_line_134 |  | 128 | 130 | 0.70989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_337_0_line_135 |  | 129 | 131 | 0.035003 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_337_0_line_136 |  | 131 | 133 | 0.05352 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_337_0_line_137 |  | 132 | 148 | 0.059105 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_337_0_line_138 |  | 132 | 149 | 0.35768 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
139 | MV_337_0_line_139 |  | 135 | 136 | 0.1039 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
140 | MV_337_0_line_140 |  | 136 | 137 | 0.1041 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_337_0_line_141 |  | 137 | 138 | 0.087471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_337_0_line_142 |  | 138 | 143 | 0.034138 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_337_0_line_143 |  | 138 | 144 | 0.12754 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_337_0_line_144 |  | 138 | 140 | 0.19481 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_337_0_line_145 |  | 139 | 140 | 0.041209 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_337_0_line_146 |  | 139 | 141 | 0.008683 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_337_0_line_147 |  | 140 | 142 | 0.063924 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_337_0_line_148 |  | 141 | 153 | 0.076182 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
149 | MV_337_0_line_149 |  | 142 | 150 | 0.073742 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_337_0_line_150 |  | 144 | 173 | 0.11724 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_337_0_line_151 |  | 145 | 146 | 0.09579 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
152 | MV_337_0_line_152 |  | 145 | 147 | 0.66231 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
153 | MV_337_0_line_153 |  | 147 | 150 | 0.037149 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_337_0_line_154 |  | 147 | 149 | 0.050346 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_337_0_line_155 |  | 149 | 151 | 0.14159 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
156 | MV_337_0_line_156 |  | 151 | 152 | 0.072394 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
157 | MV_337_0_line_157 |  | 154 | 155 | 0.096105 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_337_0_line_158 |  | 155 | 156 | 0.23646 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_337_0_line_159 |  | 155 | 157 | 1.1441 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_337_0_line_160 |  | 156 | 160 | 0.024092 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_337_0_line_161 |  | 156 | 158 | 0.055525 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_337_0_line_162 |  | 157 | 161 | 0.10966 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
163 | MV_337_0_line_163 |  | 158 | 159 | 0.040062 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_337_0_line_164 |  | 160 | 162 | 0.37655 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
165 | MV_337_0_line_165 |  | 161 | 163 | 0.023516 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_337_0_line_166 |  | 163 | 164 | 0.34418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_337_0_line_167 |  | 164 | 172 | 0.026503 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_337_0_line_168 |  | 165 | 168 | 0.046038 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
169 | MV_337_0_line_169 |  | 166 | 167 | 0.006096 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_337_0_line_170 |  | 166 | 168 | 0.040365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
171 | MV_337_0_line_171 |  | 168 | 169 | 0.024007 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_337_0_line_172 |  | 170 | 171 | 0.059237 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_337_0_line_173 |  | 171 | 172 | 0.0045539 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
174 | MV_337_0_line_174 |  | 171 | 173 | 0.082759 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
175 | MV_337_0_line_175 |  | 174 | 175 | 0.045335 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_337_0_line_176 |  | 175 | 176 | 0.052247 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_337_0_line_177 |  | 176 | 178 | 0.050217 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_337_0_trafo_84 | 25 MVA 110/20 kV | 179 | 107 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2521149.4188 | 1166586.7023
1 | 2521139.7523 | 1166570.0974
2 | 2521020.5988 | 1166406.5804
3 | 2515064.3136 | 1168427.6429
4 | 2520987.0539 | 1166414.0931
5 | 2515042.3325 | 1168432.1235
6 | 2511404.6843 | 1164631.6646
7 | 2511306.625 | 1164529.3397
8 | 2511400.6923 | 1166762.3349
9 | 2510577.2863 | 1164074.0953
10 | 2514259.7547 | 1166969.6697
11 | 2514186.1894 | 1166944.2728
12 | 2514132.6939 | 1167024.4195
13 | 2514162.3488 | 1167020.8375
14 | 2514158.2372 | 1167060.119
15 | 2515162.1877 | 1168979.6549
16 | 2515120.881 | 1169019.6744
17 | 2514930.6612 | 1169126.1997
18 | 2514180.0359 | 1167073.4576
19 | 2514337.5236 | 1168793.2637
20 | 2514926.4915 | 1169160.8129
21 | 2514035.1642 | 1169020.3036
22 | 2514341.8664 | 1168818.1166
23 | 2511350.1762 | 1166871.7918
24 | 2511322.0993 | 1166903.2218
25 | 2511369.1734 | 1166876.5474
26 | 2511378.2729 | 1166850.8863
27 | 2511411.5998 | 1166888.0612
28 | 2511375.536 | 1166950.1202
29 | 2511394.0418 | 1166956.3507
30 | 2511442.7538 | 1166969.4395
31 | 2511455.6486 | 1166970.0607
32 | 2511519.4584 | 1166834.7152
33 | 2511377.2168 | 1166830.7119
34 | 2514057.9967 | 1169114.1181
35 | 2513906.4846 | 1169002.8387
36 | 2512924.0679 | 1168268.2653
37 | 2513924.728 | 1169025.0124
38 | 2512856.4078 | 1168291.9399
39 | 2514045.82 | 1169390.3179
40 | 2514003.6831 | 1169323.2149
41 | 2513892.4973 | 1169034.5363
42 | 2514066.6838 | 1169143.0108
43 | 2514169.2308 | 1167026.12
44 | 2510562.9757 | 1164062.6905
45 | 2510563.3783 | 1164094.8806
46 | 2510542.6625 | 1163973.3946
47 | 2510277.3127 | 1163816.2258
48 | 2510234.3965 | 1163796.611
49 | 2510370.7572 | 1163895.3447
50 | 2510110.8512 | 1163640.8539
51 | 2510466.9378 | 1163917.7453
52 | 2509902.8057 | 1163493.1382
53 | 2509842.4427 | 1163451.6525
54 | 2509713.767 | 1163502.3947
55 | 2509653.0049 | 1163447.7089
56 | 2508934.8361 | 1164253.8057
57 | 2507350.3019 | 1162365.437
58 | 2507416.1478 | 1162495.7457
59 | 2507216.9 | 1162208.8673
60 | 2507423.2904 | 1162529.2728
61 | 2507380.7693 | 1162543.2871
62 | 2507470.4368 | 1162530.1634
63 | 2507168.3566 | 1162154.8288
64 | 2507140.0141 | 1162220.3182
65 | 2507100.612 | 1162178.1796
66 | 2507468.1354 | 1162524.5176
67 | 2507509.0798 | 1162508.944
68 | 2507544.3177 | 1162560.1327
69 | 2507653.8604 | 1162289.0256
70 | 2507333.507 | 1161910.4062
71 | 2507382.6737 | 1161924.3675
72 | 2507004.5544 | 1162071.4675
73 | 2507009.2653 | 1162083.224
74 | 2506991.025 | 1162060.2924
75 | 2506959.9326 | 1162029.3661
76 | 2506956.3391 | 1162024.4521
77 | 2507005.5435 | 1162097.2235
78 | 2506828.9974 | 1161825.5042
79 | 2506804.9307 | 1161842.9884
80 | 2506819.2699 | 1161860.8546
81 | 2506768.9912 | 1161887.4179
82 | 2506828.4343 | 1161871.771
83 | 2506527.5124 | 1161856.8748
84 | 2506502.2006 | 1161897.6716
85 | 2506781.344 | 1161872.1167
86 | 2506745.4865 | 1161861.1645
87 | 2506858.9159 | 1161908.0797
88 | 2507528.9638 | 1162699.9325
89 | 2507539.0789 | 1162719.4109
90 | 2507767.9763 | 1162912.0976
91 | 2507969.5371 | 1163051.7682
92 | 2508197.0839 | 1163409.8037
93 | 2507789.3323 | 1162879.8721
94 | 2506475.1534 | 1161489.6754
95 | 2506468.6265 | 1161479.5041
96 | 2506504.5409 | 1161530.8543
97 | 2506173.4503 | 1161031.0211
98 | 2506713.5797 | 1161729.1478
99 | 2506146.2638 | 1160913.7515
100 | 2506722.1818 | 1161784.1368
101 | 2506135.2165 | 1160819.4439
102 | 2506944.0405 | 1162007.6657
103 | 2506977.1497 | 1161973.4095
104 | 2506921.621 | 1161982.7736
105 | 2506907.1768 | 1161965.5668
106 | 2507988.0727 | 1163072.2484
107 | 2508220.9634 | 1163459.3912
108 | 2507617.4855 | 1163752.6149
109 | 2507699.6319 | 1162267.3198
110 | 2507718.6507 | 1162157.7049
111 | 2507722.5378 | 1162152.3641
112 | 2507705.5636 | 1162175.6948
113 | 2507946.0983 | 1161850.7266
114 | 2507864.4595 | 1162193.8771
115 | 2507753.3885 | 1162265.5816
116 | 2507952.0006 | 1161842.8425
117 | 2507966.7347 | 1162130.0588
118 | 2508027.057 | 1161743.6097
119 | 2508528.3098 | 1162179.8203
120 | 2508538.4916 | 1162191.7725
121 | 2508539.4752 | 1162250.7781
122 | 2508281.9903 | 1161953.8727
123 | 2508603.9063 | 1162269.2016
124 | 2508223.4472 | 1161917.8895
125 | 2507802.7534 | 1161478.5647
126 | 2507726.0105 | 1161386.3202
127 | 2507052.5695 | 1160703.3696
128 | 2507082.3467 | 1160707.9834
129 | 2507019.8181 | 1160696.5218
130 | 2507567.8585 | 1161211.3228
131 | 2507044.4964 | 1160674.6375
132 | 2506131.6785 | 1160230.893
133 | 2507003.8296 | 1160639.8442
134 | 2509826.7391 | 1165186.5207
135 | 2506074.7464 | 1159465.2603
136 | 2506027.9004 | 1159558.002
137 | 2505974.3586 | 1159641.0907
138 | 2505914.3761 | 1159671.6485
139 | 2506046.2153 | 1159820.1432
140 | 2506022.0228 | 1159811.3607
141 | 2506052.6615 | 1159825.9794
142 | 2505971.8734 | 1159842.6757
143 | 2505885.2468 | 1159655.0946
144 | 2505876.7812 | 1159567.8958
145 | 2505369.0168 | 1160297.2435
146 | 2505386.4906 | 1160391.4264
147 | 2505906.8697 | 1159910.7575
148 | 2506088.4898 | 1160271.3706
149 | 2505956.4393 | 1159919.0863
150 | 2505919.0448 | 1159894.2567
151 | 2506081.5854 | 1159985.325
152 | 2506152.1052 | 1159968.9574
153 | 2506109.3061 | 1159876.9215
154 | 2504338.7004 | 1158712.1111
155 | 2504375.7554 | 1158644.9386
156 | 2504212.7994 | 1158672.1397
157 | 2505336.1883 | 1159263.6238
158 | 2504238.3355 | 1158712.7912
159 | 2504266.4451 | 1158741.3359
160 | 2504194.7844 | 1158688.1924
161 | 2505425.4853 | 1159327.2679
162 | 2503857.8873 | 1158856.3884
163 | 2505444.6372 | 1159340.986
164 | 2505730.0151 | 1159532.7641
165 | 2511284.3422 | 1166924.3633
166 | 2511276.7063 | 1166859.5147
167 | 2511273.6346 | 1166854.2458
168 | 2511252.429 | 1166891.1818
169 | 2511239.7838 | 1166911.5812
170 | 2505714.623 | 1159570.4852
171 | 2505756.0916 | 1159549.6321
172 | 2505752.2679 | 1159547.1587
173 | 2505799.9213 | 1159479.4319
174 | 2506938.5633 | 1161911.688
175 | 2506909.1734 | 1161877.1704
176 | 2506948.8702 | 1161843.2011
177 | 2506893.9301 | 1161949.7865
178 | 2506919.4674 | 1161803.4083
179 | 2508220.9634 | 1163459.3912

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98789 | -0.63488 | 0.14128 | 0.068427
1 | 0.98789 | -0.63492 | 0 | 0
2 | 0.98793 | -0.63526 | 0 | 0
3 | 0.98917 | -0.5907 | 0.098971 | 0.047934
4 | 0.98794 | -0.63531 | 0.060378 | 0.029243
5 | 0.98917 | -0.59064 | 0 | 0
6 | 0.99529 | -0.26131 | 0.069625 | 0.033721
7 | 0.99538 | -0.26044 | 0 | 0
8 | 0.9928 | -0.43136 | 0.10196 | 0.049383
9 | 0.99595 | -0.25437 | 0 | 0
10 | 0.98812 | -0.63984 | 0.15091 | 0.073089
11 | 0.98813 | -0.63998 | 0 | 0
12 | 0.98816 | -0.6402 | 0 | 0
13 | 0.98812 | -0.63985 | 0 | 0
14 | 0.98822 | -0.64077 | 0.35952 | 0.17413
15 | 0.98954 | -0.56972 | 0.13584 | 0.065792
16 | 0.98956 | -0.56964 | 0 | 0
17 | 0.98964 | -0.56927 | 0 | 0
18 | 0.98827 | -0.64121 | 0.19044 | 0.092233
19 | 0.98992 | -0.56756 | 0 | 0
20 | 0.98963 | -0.56922 | 0.1216 | 0.058895
21 | 0.99011 | -0.56616 | 0 | 0
22 | 0.98992 | -0.56754 | 0.076654 | 0.037125
23 | 0.99252 | -0.43304 | 0.15886 | 0.076939
24 | 0.9925 | -0.43278 | 0.0832 | 0.040296
25 | 0.99255 | -0.43289 | 0.12932 | 0.062632
26 | 0.99254 | -0.43285 | 0 | 0
27 | 0.9926 | -0.43334 | 0 | 0
28 | 0.99254 | -0.43761 | 0.102 | 0.0494
29 | 0.99254 | -0.43764 | 0 | 0
30 | 0.99252 | -0.4379 | 0 | 0
31 | 0.99251 | -0.43796 | 0.15127 | 0.073264
32 | 0.99272 | -0.43219 | 0 | 0
33 | 0.99254 | -0.43288 | 0.1278 | 0.061897
34 | 0.99014 | -0.56587 | 0.16861 | 0.081661
35 | 0.99048 | -0.55176 | 0 | 0
36 | 0.99101 | -0.54635 | 0 | 0
37 | 0.99046 | -0.5533 | 0.11211 | 0.0543
38 | 0.99104 | -0.546 | 0.058071 | 0.028125
39 | 0.99029 | -0.55615 | 0.053379 | 0.025852
40 | 0.9903 | -0.5562 | 0 | 0
41 | 0.99043 | -0.55503 | 0 | 0
42 | 0.99015 | -0.56577 | 0.070604 | 0.034195
43 | 0.98811 | -0.63975 | 0.92956 | 0.45021
44 | 0.99596 | -0.25424 | 0.16184 | 0.078381
45 | 0.99595 | -0.25433 | 0.13173 | 0.063801
46 | 0.99608 | -0.24622 | 0.079249 | 0.038382
47 | 0.99638 | -0.23365 | 0.059378 | 0.028758
48 | 0.99642 | -0.23329 | 0 | 0
49 | 0.99623 | -0.24458 | 0 | 0
50 | 0.99656 | -0.23173 | 0 | 0
51 | 0.99614 | -0.24554 | 0 | 0
52 | 0.99688 | -0.2086 | 0.11633 | 0.056341
53 | 0.99693 | -0.20803 | 0 | 0
54 | 0.99706 | -0.20662 | 0 | 0
55 | 0.99711 | -0.20596 | 0.098549 | 0.047729
56 | 0.99854 | -0.10352 | 0.062197 | 0.030123
57 | 0.99745 | -0.053551 | 0.13839 | 0.067026
58 | 0.99773 | -0.036465 | 0.1062 | 0.051434
59 | 0.99707 | -0.077101 | 0.13492 | 0.065346
60 | 0.9978 | -0.032386 | 0.10716 | 0.051899
61 | 0.9978 | -0.032429 | 0.078685 | 0.038109
62 | 0.99787 | -0.031981 | 0.098824 | 0.047863
63 | 0.997 | -0.077535 | 0 | 0
64 | 0.99683 | -0.078437 | 0.12086 | 0.058537
65 | 0.99684 | -0.078519 | 0 | 0
66 | 0.99787 | -0.031942 | 0 | 0
67 | 0.99792 | -0.031641 | 0 | 0
68 | 0.998 | -0.031161 | 0.16338 | 0.079126
69 | 0.99698 | -0.025747 | 0 | 0
70 | 0.99693 | -0.077092 | 0 | 0
71 | 0.99692 | -0.077019 | 0.11154 | 0.054021
72 | 0.99645 | -0.10061 | 0 | 0
73 | 0.99645 | -0.10059 | 0 | 0
74 | 0.99645 | -0.10065 | 0.13858 | 0.067116
75 | 0.99648 | -0.10048 | 0 | 0
76 | 0.99647 | -0.10052 | 0 | 0
77 | 0.99644 | -0.10056 | 0.15844 | 0.076735
78 | 0.99631 | -0.10143 | 0.15361 | 0.074394
79 | 0.99632 | -0.10149 | 0 | 0
80 | 0.99632 | -0.10153 | 0 | 0
81 | 0.99623 | -0.10224 | 0 | 0
82 | 0.99633 | -0.10147 | 0.074409 | 0.036038
83 | 0.99615 | -0.10171 | 0 | 0
84 | 0.99615 | -0.10162 | 0.14486 | 0.070159
85 | 0.99622 | -0.10231 | 0 | 0
86 | 0.99622 | -0.10221 | 0.083386 | 0.040386
87 | 0.99636 | -0.10127 | 0 | 0
88 | 0.99834 | -0.010364 | 0.11152 | 0.054011
89 | 0.99837 | -0.010192 | 0 | 0
90 | 0.99882 | -0.0072843 | 0 | 0
91 | 0.9975 | 0.0049317 | 0 | 0
92 | 0.99991 | -0.00056685 | 0 | 0
93 | 0.9988 | -0.0073608 | 0.16335 | 0.079114
94 | 0.99596 | -0.10402 | 0.11991 | 0.058073
95 | 0.99596 | -0.10406 | 0 | 0
96 | 0.99599 | -0.10386 | 0 | 0
97 | 0.9957 | -0.10556 | 0 | 0
98 | 0.99613 | -0.10291 | 0 | 0
99 | 0.99564 | -0.10586 | 0.15011 | 0.072703
100 | 0.99616 | -0.1027 | 0.16128 | 0.078113
101 | 0.99555 | -0.111 | 0 | 0
102 | 0.99646 | -0.10062 | 0 | 0
103 | 0.99644 | -0.10022 | 0.43995 | 0.21308
104 | 0.99643 | -0.10079 | 0.11048 | 0.053508
105 | 0.99641 | -0.1009 | 0.068488 | 0.03317
106 | 0.99742 | 0.0056753 | 2.2405 | 1.0851
107 | 1 | 0 | -15.1058 | -6.0034
108 | 0.99988 | -0.00078836 | 0.094407 | 0.045723
109 | 0.99688 | -0.026647 | 0.090558 | 0.043859
110 | 0.9966 | -0.027747 | 0.081336 | 0.039393
111 | 0.9966 | -0.027703 | 0 | 0
112 | 0.99663 | -0.027919 | 0 | 0
113 | 0.99626 | -0.025745 | 0 | 0
114 | 0.99655 | -0.027982 | 0 | 0
115 | 0.99681 | -0.026233 | 0 | 0
116 | 0.99625 | -0.025691 | 0.1317 | 0.063787
117 | 0.99652 | -0.028209 | 0.15375 | 0.074465
118 | 0.99612 | -0.027086 | 0 | 0
119 | 0.99584 | -0.026988 | 0 | 0
120 | 0.99584 | -0.026967 | 0 | 0
121 | 0.99583 | -0.026904 | 0.08524 | 0.041284
122 | 0.99598 | -0.025991 | 0.10146 | 0.049139
123 | 0.99583 | -0.026823 | 0.12397 | 0.060041
124 | 0.99601 | -0.026222 | 0 | 0
125 | 0.996 | -0.026615 | 0 | 0
126 | 0.99593 | -0.02728 | 0.12749 | 0.061744
127 | 0.99576 | -0.026488 | 0.060357 | 0.029232
128 | 0.99577 | -0.026534 | 0 | 0
129 | 0.99576 | -0.026459 | 0 | 0
130 | 0.99589 | -0.027222 | 0 | 0
131 | 0.99575 | -0.026428 | 0 | 0
132 | 0.99464 | -0.12182 | 0 | 0
133 | 0.99575 | -0.026376 | 0.083901 | 0.040635
134 | 0.9984 | -0.10451 | 0.058332 | 0.028251
135 | 0.99229 | -0.14176 | 0.10955 | 0.053059
136 | 0.99231 | -0.14162 | 0.094839 | 0.045933
137 | 0.99234 | -0.14187 | 0 | 0
138 | 0.99236 | -0.14207 | 0 | 0
139 | 0.99283 | -0.14572 | 0 | 0
140 | 0.99284 | -0.14585 | 0 | 0
141 | 0.99282 | -0.14569 | 0.16367 | 0.079267
142 | 0.99302 | -0.14728 | 0.13885 | 0.067246
143 | 0.99236 | -0.14202 | 0.11649 | 0.05642
144 | 0.9921 | -0.14001 | 0 | 0
145 | 0.99321 | -0.15084 | 0 | 0
146 | 0.99319 | -0.15097 | 0.11041 | 0.053472
147 | 0.99335 | -0.14992 | 0 | 0
148 | 0.99463 | -0.12174 | 0.11393 | 0.055179
149 | 0.99351 | -0.15118 | 0.15008 | 0.072688
150 | 0.99324 | -0.14904 | 0 | 0
151 | 0.99348 | -0.15135 | 0 | 0
152 | 0.99346 | -0.15144 | 0.098636 | 0.047772
153 | 0.99281 | -0.14579 | 0.097428 | 0.047186
154 | 0.99025 | -0.13195 | 0.10561 | 0.051148
155 | 0.99026 | -0.13207 | 0 | 0
156 | 0.99012 | -0.13075 | 0 | 0
157 | 0.99113 | -0.13852 | 0 | 0
158 | 0.99011 | -0.13066 | 0 | 0
159 | 0.9901 | -0.1306 | 0.14084 | 0.068214
160 | 0.99011 | -0.13065 | 0.26514 | 0.12841
161 | 0.99125 | -0.13736 | 0.16163 | 0.078279
162 | 0.99005 | -0.13104 | 0.081014 | 0.039237
163 | 0.99127 | -0.13751 | 0 | 0
164 | 0.9916 | -0.13972 | 0 | 0
165 | 0.99246 | -0.43298 | 0.1321 | 0.06398
166 | 0.99244 | -0.43308 | 0 | 0
167 | 0.99244 | -0.43308 | 0.091077 | 0.044111
168 | 0.99244 | -0.43313 | 0 | 0
169 | 0.99244 | -0.43308 | 0.15456 | 0.074858
170 | 0.99159 | -0.13955 | 0.52835 | 0.25589
171 | 0.99163 | -0.13992 | 0 | 0
172 | 0.99162 | -0.13989 | 0.17026 | 0.082458
173 | 0.99186 | -0.1381 | 0.15675 | 0.075918
174 | 0.99626 | -0.10035 | 0.59391 | 0.28764
175 | 0.9963 | -0.10067 | 0 | 0
176 | 0.99628 | -0.10053 | 0 | 0
177 | 0.9964 | -0.101 | 0.077851 | 0.037705
178 | 0.99626 | -0.10039 | 0.23726 | 0.11491
179 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.14128 | -0.068427 | 0.14128 | 0.06798 | 5.3881e-07 | -0.00044732 | 0.0045872 | 0.0045816 | 0.0045872 | 0.98789 | -0.63488 | 0.98789 | -0.63492 | 2.0851
1 | -0.14128 | -0.06798 | 0.14129 | 0.062729 | 6.2259e-06 | -0.0052501 | 0.0045816 | 0.0045171 | 0.0045816 | 0.98789 | -0.63492 | 0.98793 | -0.63526 | 2.0825
2 | -0.14129 | -0.062729 | 0.14129 | 0.061931 | 9.3184e-07 | -0.00079856 | 0.0045171 | 0.0045077 | 0.0045171 | 0.98793 | -0.63526 | 0.98794 | -0.63531 | 2.0532
3 | 0.20185 | 0.083527 | -0.20167 | -0.091173 | 0.0001838 | -0.0076465 | 0.0063752 | 0.006467 | 0.006467 | 0.98917 | -0.5907 | 0.98794 | -0.63531 | 1.5773
4 | -0.30082 | -0.13146 | 0.30083 | 0.13055 | 8.1835e-07 | -0.00091077 | 0.0095808 | 0.0095702 | 0.0095808 | 0.98917 | -0.5907 | 0.98917 | -0.59064 | 2.2757
5 | 1.6314 | 0.77994 | -1.6306 | -0.78213 | 0.00080076 | -0.0021957 | 0.052772 | 0.052827 | 0.052827 | 0.98917 | -0.59064 | 0.98827 | -0.64121 | 4.0951
6 | -1.9323 | -0.91049 | 1.9326 | 0.91001 | 0.00038866 | -0.00047162 | 0.062337 | 0.062318 | 0.062337 | 0.98917 | -0.59064 | 0.98954 | -0.56972 | 4.8323
7 | -4.0437 | -1.4644 | 4.0441 | 1.447 | 0.00033985 | -0.017433 | 0.12474 | 0.12457 | 0.12474 | 0.99529 | -0.26131 | 0.99538 | -0.26044 | 9.7758
8 | 3.9741 | 1.4307 | -3.9684 | -1.4211 | 0.0057106 | 0.0095358 | 0.12251 | 0.12256 | 0.12256 | 0.99529 | -0.26131 | 0.9928 | -0.43136 | 9.5011
9 | -4.0441 | -1.447 | 4.0463 | 1.3337 | 0.0021831 | -0.11322 | 0.12457 | 0.12349 | 0.12457 | 0.99538 | -0.26044 | 0.99595 | -0.25437 | 9.7622
10 | 3.8664 | 1.3718 | -3.8661 | -1.3889 | 0.00030708 | -0.017102 | 0.11929 | 0.11946 | 0.11946 | 0.9928 | -0.43136 | 0.99272 | -0.43219 | 9.362
11 | -4.178 | -1.3969 | 4.178 | 1.3947 | 4.6012e-05 | -0.0022513 | 0.12769 | 0.12767 | 0.12769 | 0.99595 | -0.25437 | 0.99596 | -0.25424 | 10.0069
12 | 0.13173 | 0.063209 | -0.13173 | -0.063801 | 5.9988e-07 | -0.00059212 | 0.0042351 | 0.0042425 | 0.0042425 | 0.99595 | -0.25437 | 0.99595 | -0.25433 | 1.9284
13 | -0.15091 | -0.073089 | 0.15091 | 0.07128 | 2.4753e-06 | -0.001809 | 0.0048987 | 0.0048758 | 0.0048987 | 0.98812 | -0.63984 | 0.98813 | -0.63998 | 2.2267
14 | -0.15091 | -0.07128 | 0.15092 | 0.068058 | 4.3521e-06 | -0.0032219 | 0.0048758 | 0.0048364 | 0.0048758 | 0.98813 | -0.63998 | 0.98816 | -0.6402 | 2.2163
15 | 0.92961 | 0.4493 | -0.92957 | -0.45001 | 3.7248e-05 | -0.0007037 | 0.030163 | 0.030172 | 0.030172 | 0.98816 | -0.6402 | 0.98812 | -0.63985 | 13.7144
16 | -1.0805 | -0.51736 | 1.0806 | 0.51635 | 7.2078e-05 | -0.0010068 | 0.034997 | 0.034984 | 0.034997 | 0.98816 | -0.6402 | 0.98822 | -0.64077 | 15.9079
17 | 0.92957 | 0.45001 | -0.92956 | -0.45021 | 1.0544e-05 | -0.00019912 | 0.030172 | 0.030174 | 0.030174 | 0.98812 | -0.63985 | 0.98811 | -0.63975 | 13.7156
18 | -1.4401 | -0.69048 | 1.4402 | 0.6899 | 7.5331e-05 | -0.00058228 | 0.046654 | 0.046646 | 0.046654 | 0.98822 | -0.64077 | 0.98827 | -0.64121 | 21.2062
19 | -2.0685 | -0.97581 | 2.0685 | 0.96876 | 3.9469e-05 | -0.0070485 | 0.066721 | 0.066633 | 0.066721 | 0.98954 | -0.56972 | 0.98956 | -0.56964 | 5.2289
20 | -2.0685 | -0.96876 | 2.0687 | 0.94059 | 0.00015667 | -0.028165 | 0.066633 | 0.066288 | 0.066633 | 0.98956 | -0.56964 | 0.98964 | -0.56927 | 5.222
21 | -2.1903 | -0.99862 | 2.1909 | 0.90061 | 0.00059847 | -0.098008 | 0.070217 | 0.069077 | 0.070217 | 0.98964 | -0.56927 | 0.98992 | -0.56756 | 5.5029
22 | 0.1216 | 0.05803 | -0.1216 | -0.058895 | 7.646e-07 | -0.00086437 | 0.0039303 | 0.0039412 | 0.0039412 | 0.98964 | -0.56927 | 0.98963 | -0.56922 | 1.7915
23 | -2.2675 | -0.93715 | 2.2679 | 0.87551 | 0.00039349 | -0.06164 | 0.071549 | 0.07088 | 0.071549 | 0.98992 | -0.56756 | 0.99011 | -0.56616 | 5.6073
24 | 0.076655 | 0.036535 | -0.076654 | -0.037125 | 2.0719e-07 | -0.00059035 | 0.0024763 | 0.0024837 | 0.0024837 | 0.98992 | -0.56756 | 0.98992 | -0.56754 | 1.129
25 | -2.2679 | -0.87551 | 2.268 | 0.86366 | 7.4813e-05 | -0.011853 | 0.07088 | 0.070756 | 0.07088 | 0.99011 | -0.56616 | 0.99014 | -0.56587 | 5.5549
26 | 0.46097 | 0.22035 | -0.46096 | -0.22149 | 1.4362e-05 | -0.0011404 | 0.01486 | 0.014875 | 0.014875 | 0.99252 | -0.43304 | 0.9925 | -0.43278 | 6.7613
27 | -0.61983 | -0.29729 | 0.61985 | 0.29728 | 1.3948e-05 | -1.4294e-05 | 0.019994 | 0.019994 | 0.019994 | 0.99252 | -0.43304 | 0.99255 | -0.43289 | 9.521
28 | 0.37776 | 0.1812 | -0.37775 | -0.18124 | 1.145e-05 | -4.3714e-05 | 0.012186 | 0.012187 | 0.012187 | 0.9925 | -0.43278 | 0.99246 | -0.43298 | 5.8032
29 | 0.1278 | 0.061234 | -0.1278 | -0.061874 | 6.1861e-07 | -0.00064014 | 0.0041217 | 0.0041298 | 0.0041298 | 0.99255 | -0.43289 | 0.99254 | -0.43285 | 1.8772
30 | -0.87697 | -0.42114 | 0.87702 | 0.42012 | 4.6881e-05 | -0.0010184 | 0.028295 | 0.028282 | 0.028295 | 0.99255 | -0.43289 | 0.9926 | -0.43334 | 12.8612
31 | 0.1278 | 0.061874 | -0.1278 | -0.061897 | 6.1392e-07 | -2.3374e-05 | 0.0041298 | 0.0041301 | 0.0041301 | 0.99254 | -0.43285 | 0.99254 | -0.43288 | 1.9667
32 | -3.8657 | -1.4132 | 3.8661 | 1.3889 | 0.00043909 | -0.024363 | 0.1197 | 0.11946 | 0.1197 | 0.9926 | -0.43334 | 0.99272 | -0.43219 | 9.3811
33 | 2.9887 | 0.99309 | -2.9886 | -0.993 | 0.00010559 | 9.1889e-05 | 0.091592 | 0.091594 | 0.091594 | 0.9926 | -0.43334 | 0.99254 | -0.43764 | 7.1003
34 | -0.102 | -0.0494 | 0.102 | 0.048942 | 2.8201e-07 | -0.00045804 | 0.0032962 | 0.0032904 | 0.0032962 | 0.99254 | -0.43761 | 0.99254 | -0.43764 | 1.4983
35 | 2.8866 | 0.94406 | -2.8865 | -0.95027 | 6.0907e-05 | -0.0062164 | 0.088331 | 0.088388 | 0.088388 | 0.99254 | -0.43764 | 0.99252 | -0.4379 | 6.9269
36 | 2.8865 | 0.95027 | -2.8865 | -0.95187 | 1.5677e-05 | -0.0015987 | 0.088388 | 0.088402 | 0.088402 | 0.99252 | -0.4379 | 0.99251 | -0.43796 | 6.9281
37 | 2.7352 | 0.87861 | -2.7328 | -0.87739 | 0.0024017 | 0.001221 | 0.083559 | 0.083606 | 0.083606 | 0.99251 | -0.43796 | 0.99104 | -0.546 | 6.481
38 | -2.4366 | -0.94532 | 2.4366 | 0.94161 | 2.7056e-05 | -0.0037025 | 0.076199 | 0.076159 | 0.076199 | 0.99014 | -0.56587 | 0.99015 | -0.56577 | 5.9717
39 | -2.6734 | -1.0131 | 2.6747 | 0.85809 | 0.001329 | -0.15497 | 0.083321 | 0.081824 | 0.083321 | 0.99048 | -0.55176 | 0.99101 | -0.54635 | 6.5299
40 | 2.6734 | 1.0131 | -2.6733 | -1.013 | 3.5584e-05 | 1.781e-05 | 0.083321 | 0.083322 | 0.083322 | 0.99048 | -0.55176 | 0.99046 | -0.5533 | 6.4591
41 | -2.6747 | -0.85809 | 2.6748 | 0.84926 | 7.4296e-05 | -0.0088313 | 0.081824 | 0.081745 | 0.081824 | 0.99101 | -0.54635 | 0.99104 | -0.546 | 6.4125
42 | 2.5612 | 0.95875 | -2.5612 | -0.95874 | 3.8113e-05 | 1.1343e-05 | 0.079707 | 0.079707 | 0.079707 | 0.99046 | -0.5533 | 0.99043 | -0.55503 | 6.1789
43 | -0.053379 | -0.025852 | 0.053379 | 0.023997 | 3.1194e-07 | -0.0018551 | 0.0017289 | 0.001706 | 0.0017289 | 0.99029 | -0.55615 | 0.9903 | -0.5562 | 0.78586
44 | -2.5608 | -0.99985 | 2.5612 | 0.95874 | 0.00033069 | -0.041116 | 0.080137 | 0.079707 | 0.080137 | 0.9903 | -0.5562 | 0.99043 | -0.55503 | 6.2804
45 | 2.5075 | 0.97586 | -2.5073 | -0.97581 | 0.00020964 | 4.6248e-05 | 0.078434 | 0.078439 | 0.078439 | 0.9903 | -0.5562 | 0.99015 | -0.56577 | 6.0805
46 | -4.3399 | -1.4731 | 4.3402 | 1.4736 | 0.00028844 | 0.00052449 | 0.13284 | 0.13284 | 0.13284 | 0.99596 | -0.25424 | 0.99608 | -0.24622 | 10.2975
47 | -4.4194 | -1.512 | 4.4197 | 1.5004 | 0.00026539 | -0.011548 | 0.13537 | 0.13526 | 0.13537 | 0.99608 | -0.24622 | 0.99614 | -0.24554 | 10.6088
48 | -4.4798 | -1.5141 | 4.48 | 1.5083 | 0.00013792 | -0.0058581 | 0.137 | 0.13695 | 0.137 | 0.99638 | -0.23365 | 0.99642 | -0.23329 | 10.737
49 | 4.4205 | 1.4854 | -4.4201 | -1.4846 | 0.00039896 | 0.00073684 | 0.13511 | 0.13511 | 0.13511 | 0.99638 | -0.23365 | 0.99623 | -0.24458 | 10.4737
50 | -4.48 | -1.5083 | 4.4806 | 1.483 | 0.00059321 | -0.025255 | 0.13695 | 0.13671 | 0.13695 | 0.99642 | -0.23329 | 0.99656 | -0.23173 | 10.7327
51 | 4.4201 | 1.4846 | -4.4197 | -1.5004 | 0.00036278 | -0.015819 | 0.13511 | 0.13526 | 0.13526 | 0.99623 | -0.24458 | 0.99614 | -0.24554 | 10.6002
52 | -4.4806 | -1.483 | 4.4814 | 1.4846 | 0.00085122 | 0.0015882 | 0.13671 | 0.13671 | 0.13671 | 0.99656 | -0.23173 | 0.99688 | -0.2086 | 10.598
53 | -4.5977 | -1.5409 | 4.598 | 1.5319 | 0.00022258 | -0.009005 | 0.14042 | 0.14034 | 0.14042 | 0.99688 | -0.2086 | 0.99693 | -0.20803 | 11.0047
54 | -4.598 | -1.5319 | 4.5985 | 1.51 | 0.00054128 | -0.021948 | 0.14034 | 0.14013 | 0.14034 | 0.99693 | -0.20803 | 0.99706 | -0.20662 | 10.9981
55 | -4.5985 | -1.51 | 4.5988 | 1.4999 | 0.0002475 | -0.010059 | 0.14013 | 0.14004 | 0.14013 | 0.99706 | -0.20662 | 0.99711 | -0.20596 | 10.9822
56 | -4.6973 | -1.5476 | 4.7013 | 1.5553 | 0.0039501 | 0.0076503 | 0.14318 | 0.14316 | 0.14318 | 0.99711 | -0.20596 | 0.99854 | -0.10352 | 11.0995
57 | 0.05834 | 0.02672 | -0.058332 | -0.028251 | 7.9926e-06 | -0.0015309 | 0.0018551 | 0.001874 | 0.001874 | 0.99854 | -0.10352 | 0.9984 | -0.10451 | 0.89238
58 | -4.8218 | -1.6121 | 4.8259 | 1.6203 | 0.0041178 | 0.0081248 | 0.14698 | 0.14695 | 0.14698 | 0.99854 | -0.10352 | 1 | 0 | 11.3939
59 | -6.0379 | -2.5712 | 6.0389 | 2.5733 | 0.00094008 | 0.0021263 | 0.18993 | 0.18992 | 0.18993 | 0.99745 | -0.053551 | 0.99773 | -0.036465 | 14.7232
60 | 5.8995 | 2.5042 | -5.8983 | -2.5013 | 0.0012633 | 0.0028314 | 0.18548 | 0.18549 | 0.18549 | 0.99745 | -0.053551 | 0.99707 | -0.077101 | 14.3791
61 | -6.1451 | -2.6247 | 6.1453 | 2.6253 | 0.00022871 | 0.00052068 | 0.19333 | 0.19333 | 0.19333 | 0.99773 | -0.036465 | 0.9978 | -0.032386 | 14.9872
62 | 5.7633 | 2.436 | -5.763 | -2.4448 | 0.00036843 | -0.0088646 | 0.18116 | 0.18126 | 0.18126 | 0.99707 | -0.077101 | 0.997 | -0.077535 | 14.2052
63 | 0.078685 | 0.038056 | -0.078685 | -0.038109 | 5.1021e-07 | -5.2893e-05 | 0.0025287 | 0.0025294 | 0.0025294 | 0.9978 | -0.032386 | 0.9978 | -0.032429 | 1.2045
64 | -6.3311 | -2.7152 | 6.3315 | 2.7074 | 0.00039229 | -0.0077809 | 0.1993 | 0.19921 | 0.1993 | 0.9978 | -0.032386 | 0.99787 | -0.031981 | 15.6192
65 | -6.4303 | -2.7553 | 6.4304 | 2.7546 | 3.8575e-05 | -0.00074106 | 0.20238 | 0.20237 | 0.20238 | 0.99787 | -0.031981 | 0.99787 | -0.031942 | 15.8607
66 | 0.11155 | 0.04061 | -0.11154 | -0.052689 | 8.3296e-06 | -0.012078 | 0.0034372 | 0.0035721 | 0.0035721 | 0.997 | -0.077535 | 0.99693 | -0.077092 | 1.6237
67 | 5.6514 | 2.4042 | -5.6506 | -2.4253 | 0.00084512 | -0.021098 | 0.17783 | 0.17807 | 0.17807 | 0.997 | -0.077535 | 0.99684 | -0.078519 | 13.9554
68 | -0.12086 | -0.058537 | 0.12086 | 0.05717 | 1.1583e-06 | -0.0013668 | 0.003889 | 0.0038719 | 0.003889 | 0.99683 | -0.078437 | 0.99684 | -0.078519 | 1.7677
69 | 5.5297 | 2.3682 | -5.5286 | -2.3657 | 0.0011093 | 0.0024207 | 0.1742 | 0.17421 | 0.17421 | 0.99684 | -0.078519 | 0.99648 | -0.10048 | 13.5045
70 | -6.4304 | -2.7546 | 6.4307 | 2.7489 | 0.00029595 | -0.0056881 | 0.20237 | 0.20231 | 0.20237 | 0.99787 | -0.031942 | 0.99792 | -0.031641 | 15.86
71 | -7.4723 | -3.1761 | 7.4729 | 3.1686 | 0.00053274 | -0.0075256 | 0.23487 | 0.23478 | 0.23487 | 0.99792 | -0.031641 | 0.998 | -0.031161 | 18.407
72 | 1.0416 | 0.42727 | -1.0406 | -0.44419 | 0.0010324 | -0.016912 | 0.032569 | 0.032761 | 0.032761 | 0.99792 | -0.031641 | 0.99698 | -0.025747 | 14.8914
73 | -7.6362 | -3.2477 | 7.6377 | 3.2512 | 0.0014463 | 0.0035019 | 0.24003 | 0.24002 | 0.24003 | 0.998 | -0.031161 | 0.99834 | -0.010364 | 18.6069
74 | 1.0406 | 0.44419 | -1.0405 | -0.44418 | 9.6874e-05 | 5.7481e-07 | 0.032761 | 0.032762 | 0.032762 | 0.99698 | -0.025747 | 0.99688 | -0.026647 | 15.6009
75 | 0.11154 | 0.052689 | -0.11154 | -0.054021 | 9.6116e-07 | -0.0013325 | 0.0035721 | 0.0035887 | 0.0035887 | 0.99693 | -0.077092 | 0.99692 | -0.077019 | 1.6312
76 | 0.15844 | 0.076063 | -0.15844 | -0.076363 | 4.3858e-07 | -0.00030007 | 0.0050916 | 0.0050953 | 0.0050953 | 0.99645 | -0.10061 | 0.99645 | -0.10059 | 2.3161
77 | -0.15844 | -0.076063 | 0.15844 | 0.075648 | 6.0572e-07 | -0.00041517 | 0.0050916 | 0.0050864 | 0.0050916 | 0.99645 | -0.10061 | 0.99645 | -0.10065 | 2.3143
78 | 0.15844 | 0.076363 | -0.15844 | -0.076735 | 5.4418e-07 | -0.0003717 | 0.0050953 | 0.0051 | 0.0051 | 0.99645 | -0.10059 | 0.99644 | -0.10056 | 2.3182
79 | -0.29702 | -0.14276 | 0.29702 | 0.14272 | 7.1212e-06 | -4.7523e-05 | 0.009547 | 0.0095464 | 0.009547 | 0.99645 | -0.10065 | 0.99648 | -0.10048 | 4.5462
80 | 5.2316 | 2.223 | -5.2316 | -2.2238 | 2.5486e-05 | -0.00074468 | 0.16467 | 0.16468 | 0.16468 | 0.99648 | -0.10048 | 0.99647 | -0.10052 | 12.906
81 | 4.7916 | 2.012 | -4.7915 | -2.0146 | 7.2829e-05 | -0.0025535 | 0.15055 | 0.15058 | 0.15058 | 0.99647 | -0.10052 | 0.99646 | -0.10062 | 11.801
82 | 0.43997 | 0.21177 | -0.43995 | -0.21308 | 1.4854e-05 | -0.0013124 | 0.014145 | 0.014162 | 0.014162 | 0.99647 | -0.10052 | 0.99644 | -0.10022 | 6.4372
83 | -0.15361 | -0.074394 | 0.15361 | 0.073691 | 9.676e-07 | -0.00070343 | 0.0049451 | 0.0049363 | 0.0049451 | 0.99631 | -0.10143 | 0.99632 | -0.10149 | 2.2478
84 | -0.15361 | -0.073691 | 0.15361 | 0.073149 | 7.4348e-07 | -0.00054222 | 0.0049363 | 0.0049295 | 0.0049363 | 0.99632 | -0.10149 | 0.99632 | -0.10153 | 2.2438
85 | 3.4749 | 1.4071 | -3.4745 | -1.4291 | 0.00032462 | -0.021979 | 0.10862 | 0.10886 | 0.10886 | 0.99632 | -0.10153 | 0.99623 | -0.10224 | 8.5317
86 | -3.6285 | -1.4802 | 3.6285 | 1.4785 | 2.8385e-05 | -0.001762 | 0.11354 | 0.11352 | 0.11354 | 0.99632 | -0.10153 | 0.99633 | -0.10147 | 8.8984
87 | 3.2463 | 1.3298 | -3.2463 | -1.3322 | 3.145e-05 | -0.0024384 | 0.10165 | 0.10168 | 0.10168 | 0.99623 | -0.10224 | 0.99622 | -0.10231 | 7.9687
88 | 0.083387 | 0.039546 | -0.083386 | -0.040386 | 3.3988e-07 | -0.00084019 | 0.0026742 | 0.0026848 | 0.0026848 | 0.99623 | -0.10224 | 0.99622 | -0.10221 | 1.2203
89 | 0.14487 | 0.059725 | -0.14486 | -0.068923 | 1.0937e-05 | -0.0091982 | 0.0045407 | 0.0046489 | 0.0046489 | 0.99623 | -0.10224 | 0.99615 | -0.10171 | 2.1131
90 | -3.7029 | -1.5145 | 3.703 | 1.5086 | 9.8357e-05 | -0.0058585 | 0.11591 | 0.11585 | 0.11591 | 0.99633 | -0.10147 | 0.99636 | -0.10127 | 9.0842
91 | 0.14486 | 0.068923 | -0.14486 | -0.070159 | 1.5105e-06 | -0.0012359 | 0.0046489 | 0.0046644 | 0.0046644 | 0.99615 | -0.10171 | 0.99615 | -0.10162 | 2.1202
92 | 3.2463 | 1.3322 | -3.2461 | -1.3454 | 0.00017035 | -0.013184 | 0.10168 | 0.10183 | 0.10183 | 0.99622 | -0.10231 | 0.99616 | -0.1027 | 7.9802
93 | -4.5343 | -1.9063 | 4.5344 | 1.8996 | 0.00017078 | -0.0066975 | 0.14251 | 0.14243 | 0.14251 | 0.99636 | -0.10127 | 0.9964 | -0.101 | 11.1684
94 | 0.83126 | 0.39763 | -0.8312 | -0.39906 | 5.8195e-05 | -0.0014313 | 0.026698 | 0.026716 | 0.026716 | 0.99636 | -0.10127 | 0.9963 | -0.10067 | 12.1435
95 | -7.7492 | -3.3053 | 7.7494 | 3.3026 | 0.00020113 | -0.0026347 | 0.2436 | 0.24357 | 0.2436 | 0.99834 | -0.010364 | 0.99837 | -0.010192 | 19.0912
96 | -7.7494 | -3.3026 | 7.7527 | 3.259 | 0.0033172 | -0.043578 | 0.24357 | 0.24306 | 0.24357 | 0.99837 | -0.010192 | 0.99882 | -0.0072843 | 19.0887
97 | 2.2439 | 1.0745 | -2.2407 | -1.0845 | 0.0031864 | -0.010016 | 0.071904 | 0.072042 | 0.072042 | 0.99882 | -0.0072843 | 0.9975 | 0.0049317 | 32.7462
98 | -10.16 | -4.4126 | 10.1706 | 4.3341 | 0.010629 | -0.078517 | 0.32014 | 0.31917 | 0.32014 | 0.99882 | -0.0072843 | 0.99991 | -0.00056685 | 25.0893
99 | 0.16335 | 0.07907 | -0.16335 | -0.079114 | 1.8952e-06 | -4.4855e-05 | 0.0052452 | 0.0052458 | 0.0052458 | 0.99882 | -0.0072843 | 0.9988 | -0.0073608 | 2.498
100 | 2.2407 | 1.0845 | -2.2405 | -1.0851 | 0.00019141 | -0.0005994 | 0.072042 | 0.07205 | 0.07205 | 0.9975 | 0.0049317 | 0.99742 | 0.0056753 | 32.75
101 | -10.1706 | -4.3341 | 10.1714 | 4.3277 | 0.00086578 | -0.006426 | 0.31917 | 0.3191 | 0.31917 | 0.99991 | -0.00056685 | 1 | 0 | 25.0137
102 | 2.9643 | 1.2586 | -2.9643 | -1.2601 | 1.6262e-05 | -0.0014964 | 0.093343 | 0.09336 | 0.09336 | 0.99596 | -0.10402 | 0.99596 | -0.10406 | 7.3166
103 | -3.0842 | -1.3167 | 3.0843 | 1.3104 | 7.3826e-05 | -0.0062677 | 0.0972 | 0.097128 | 0.0972 | 0.99596 | -0.10402 | 0.99599 | -0.10386 | 7.6176
104 | 2.9643 | 1.2601 | -2.9636 | -1.327 | 0.00073285 | -0.066848 | 0.09336 | 0.09414 | 0.09414 | 0.99596 | -0.10406 | 0.9957 | -0.10556 | 7.3777
105 | -3.0843 | -1.3104 | 3.0847 | 1.2747 | 0.00041899 | -0.035754 | 0.097128 | 0.096725 | 0.097128 | 0.99599 | -0.10386 | 0.99613 | -0.10291 | 7.6119
106 | 2.9636 | 1.327 | -2.9634 | -1.3419 | 0.00016573 | -0.014957 | 0.09414 | 0.094319 | 0.094319 | 0.9957 | -0.10556 | 0.99564 | -0.10586 | 7.3918
107 | -3.0847 | -1.2747 | 3.0848 | 1.2673 | 8.5843e-05 | -0.0073634 | 0.096725 | 0.096644 | 0.096725 | 0.99613 | -0.10291 | 0.99616 | -0.1027 | 7.5804
108 | 2.8133 | 1.2692 | -2.8132 | -1.2691 | 0.00013572 | 0.00010477 | 0.089485 | 0.089488 | 0.089488 | 0.99564 | -0.10586 | 0.99555 | -0.111 | 6.9371
109 | 2.8132 | 1.2691 | -2.8108 | -1.288 | 0.0023554 | -0.018918 | 0.089488 | 0.089736 | 0.089736 | 0.99555 | -0.111 | 0.99464 | -0.12182 | 24.7889
110 | 4.7915 | 2.0146 | -4.7914 | -2.0187 | 0.00011741 | -0.0041144 | 0.15058 | 0.15063 | 0.15063 | 0.99646 | -0.10062 | 0.99643 | -0.10079 | 11.8047
111 | 4.6809 | 1.9652 | -4.6808 | -1.9679 | 7.5098e-05 | -0.0027607 | 0.14708 | 0.14711 | 0.14711 | 0.99643 | -0.10079 | 0.99641 | -0.1009 | 11.5288
112 | 4.6124 | 1.9348 | -4.6123 | -1.9373 | 6.6854e-05 | -0.0025329 | 0.14491 | 0.14494 | 0.14494 | 0.99641 | -0.1009 | 0.9964 | -0.101 | 11.3586
113 | 0.094418 | 0.044929 | -0.094407 | -0.045723 | 1.0928e-05 | -0.00079403 | 0.0030185 | 0.0030285 | 0.0030285 | 1 | 0 | 0.99988 | -0.00078836 | 1.4421
114 | 0.94996 | 0.40033 | -0.94989 | -0.40159 | 6.4478e-05 | -0.0012662 | 0.029852 | 0.029866 | 0.029866 | 0.99688 | -0.026647 | 0.99681 | -0.026233 | 13.5756
115 | 0.86837 | 0.36274 | -0.86836 | -0.36289 | 6.5477e-06 | -0.00015457 | 0.027259 | 0.027261 | 0.027261 | 0.9966 | -0.027747 | 0.9966 | -0.027703 | 12.3914
116 | -0.9497 | -0.40213 | 0.94973 | 0.40161 | 2.6476e-05 | -0.00051925 | 0.029874 | 0.029868 | 0.029874 | 0.9966 | -0.027747 | 0.99663 | -0.027919 | 13.5789
117 | 0.7146 | 0.28874 | -0.71435 | -0.29756 | 0.00025093 | -0.0088269 | 0.022325 | 0.022423 | 0.022423 | 0.9966 | -0.027703 | 0.99626 | -0.025745 | 10.1922
118 | 0.15376 | 0.074155 | -0.15376 | -0.074326 | 6.4448e-06 | -0.00017128 | 0.0049448 | 0.004947 | 0.004947 | 0.9966 | -0.027703 | 0.99655 | -0.027982 | 2.3557
119 | -0.94973 | -0.40161 | 0.94989 | 0.40159 | 0.00016182 | -1.9394e-05 | 0.029868 | 0.029866 | 0.029868 | 0.99663 | -0.027919 | 0.99681 | -0.026233 | 14.2227
120 | 0.71435 | 0.29756 | -0.71434 | -0.2978 | 6.6056e-06 | -0.00023122 | 0.022423 | 0.022425 | 0.022425 | 0.99626 | -0.025745 | 0.99625 | -0.025691 | 10.1934
121 | 0.15376 | 0.074326 | -0.15375 | -0.074465 | 5.2585e-06 | -0.00013963 | 0.004947 | 0.0049488 | 0.0049488 | 0.99655 | -0.027982 | 0.99652 | -0.028209 | 2.3566
122 | 0.58264 | 0.23401 | -0.58256 | -0.23411 | 7.3382e-05 | -0.00010144 | 0.018193 | 0.018195 | 0.018195 | 0.99625 | -0.025691 | 0.99612 | -0.027086 | 8.6643
123 | 0.27182 | 0.097094 | -0.27179 | -0.10549 | 3.3496e-05 | -0.0084002 | 0.0083648 | 0.0084499 | 0.0084499 | 0.99612 | -0.027086 | 0.996 | -0.026615 | 3.8409
124 | 0.31074 | 0.13701 | -0.31071 | -0.14363 | 3.6432e-05 | -0.0066103 | 0.0098419 | 0.0099209 | 0.0099209 | 0.99612 | -0.027086 | 0.99601 | -0.026222 | 4.5095
125 | 0.12397 | 0.057273 | -0.12397 | -0.057644 | 3.2852e-07 | -0.00037129 | 0.0039587 | 0.0039632 | 0.0039632 | 0.99584 | -0.026988 | 0.99584 | -0.026967 | 1.8015
126 | 0.085241 | 0.039214 | -0.08524 | -0.041284 | 8.7126e-07 | -0.0020693 | 0.0027199 | 0.0027455 | 0.0027455 | 0.99584 | -0.026988 | 0.99583 | -0.026904 | 1.248
127 | -0.20921 | -0.096487 | 0.20924 | 0.096108 | 2.6544e-05 | -0.00037915 | 0.0066786 | 0.0066738 | 0.0066786 | 0.99584 | -0.026988 | 0.99598 | -0.025991 | 3.1803
128 | 0.12397 | 0.057644 | -0.12397 | -0.060041 | 2.1393e-06 | -0.0023971 | 0.0039632 | 0.003993 | 0.003993 | 0.99584 | -0.026967 | 0.99583 | -0.026823 | 1.815
129 | -0.3107 | -0.14525 | 0.31071 | 0.14363 | 9.0292e-06 | -0.0016216 | 0.0099407 | 0.0099209 | 0.0099407 | 0.99598 | -0.025991 | 0.99601 | -0.026222 | 4.5185
130 | 0.27179 | 0.10549 | -0.27177 | -0.10563 | 1.5268e-05 | -0.00013253 | 0.0084499 | 0.0084514 | 0.0084514 | 0.996 | -0.026615 | 0.99593 | -0.02728 | 4.0245
131 | 0.14428 | 0.043883 | -0.14428 | -0.049463 | 6.0799e-06 | -0.0055804 | 0.0043713 | 0.0044211 | 0.0044211 | 0.99593 | -0.02728 | 0.99589 | -0.027222 | 2.0096
132 | -0.14426 | -0.066979 | 0.14426 | 0.066266 | 8.5364e-07 | -0.00071311 | 0.0046109 | 0.0046022 | 0.0046109 | 0.99576 | -0.026488 | 0.99577 | -0.026534 | 2.0959
133 | 0.083902 | 0.037747 | -0.083902 | -0.03854 | 3.1899e-07 | -0.00079227 | 0.0026672 | 0.0026767 | 0.0026767 | 0.99576 | -0.026488 | 0.99576 | -0.026459 | 1.2167
134 | -0.14426 | -0.066266 | 0.14428 | 0.049463 | 1.9242e-05 | -0.016803 | 0.0046022 | 0.0044211 | 0.0046022 | 0.99577 | -0.026534 | 0.99589 | -0.027222 | 2.0919
135 | 0.083902 | 0.03854 | -0.083901 | -0.039368 | 3.3606e-07 | -0.00082857 | 0.0026767 | 0.0026868 | 0.0026868 | 0.99576 | -0.026459 | 0.99575 | -0.026428 | 1.2213
136 | 0.083901 | 0.039368 | -0.083901 | -0.040635 | 5.188e-07 | -0.0012669 | 0.0026868 | 0.0027026 | 0.0027026 | 0.99575 | -0.026428 | 0.99575 | -0.026376 | 1.2285
137 | 0.11393 | 0.053783 | -0.11393 | -0.055179 | 1.06e-06 | -0.0013958 | 0.0036566 | 0.0036741 | 0.0036741 | 0.99464 | -0.12182 | 0.99463 | -0.12174 | 1.67
138 | 2.6969 | 1.2342 | -2.6944 | -1.2319 | 0.0024331 | 0.0023388 | 0.086079 | 0.086085 | 0.086085 | 0.99464 | -0.12182 | 0.99351 | -0.15118 | 24.5956
139 | -0.10955 | -0.053059 | 0.10956 | 0.052938 | 2.3205e-06 | -0.00012068 | 0.0035412 | 0.0035397 | 0.0035412 | 0.99229 | -0.14176 | 0.99231 | -0.14162 | 1.6863
140 | -0.20439 | -0.098871 | 0.2044 | 0.096425 | 6.0348e-06 | -0.0024457 | 0.0066052 | 0.0065745 | 0.0066052 | 0.99231 | -0.14162 | 0.99234 | -0.14187 | 3.0024
141 | -0.2044 | -0.096425 | 0.20441 | 0.09437 | 5.028e-06 | -0.0020551 | 0.0065745 | 0.0065492 | 0.0065745 | 0.99234 | -0.14187 | 0.99236 | -0.14207 | 2.9884
142 | 0.11649 | 0.055617 | -0.11649 | -0.05642 | 6.4438e-07 | -0.00080248 | 0.0037552 | 0.0037653 | 0.0037653 | 0.99236 | -0.14207 | 0.99236 | -0.14202 | 1.7115
143 | 1.6118 | 0.72578 | -1.6114 | -0.72864 | 0.00045051 | -0.0028643 | 0.051421 | 0.051457 | 0.051457 | 0.99236 | -0.14207 | 0.9921 | -0.14001 | 23.3895
144 | -1.9327 | -0.87577 | 1.9337 | 0.87148 | 0.00098998 | -0.0042892 | 0.061724 | 0.061669 | 0.061724 | 0.99236 | -0.14207 | 0.99284 | -0.14585 | 28.0565
145 | -0.2611 | -0.12616 | 0.2611 | 0.12519 | 3.9052e-06 | -0.0009687 | 0.0084315 | 0.0084192 | 0.0084315 | 0.99283 | -0.14572 | 0.99284 | -0.14585 | 3.8325
146 | 0.2611 | 0.12616 | -0.2611 | -0.12637 | 8.243e-07 | -0.00020411 | 0.0084315 | 0.008434 | 0.008434 | 0.99283 | -0.14572 | 0.99282 | -0.14569 | 3.8337
147 | -2.1948 | -0.99667 | 2.1952 | 0.99529 | 0.00041909 | -0.0013804 | 0.070087 | 0.070069 | 0.070087 | 0.99284 | -0.14585 | 0.99302 | -0.14728 | 31.8576
148 | 0.097429 | 0.047098 | -0.097428 | -0.047186 | 1.3443e-06 | -8.8803e-05 | 0.0031465 | 0.0031476 | 0.0031476 | 0.99282 | -0.14569 | 0.99281 | -0.14579 | 1.4989
149 | -2.3341 | -1.0625 | 2.3346 | 1.061 | 0.00054701 | -0.0015743 | 0.074552 | 0.074531 | 0.074552 | 0.99302 | -0.14728 | 0.99324 | -0.14904 | 33.8873
150 | 1.6114 | 0.72864 | -1.6109 | -0.73127 | 0.00041469 | -0.0026315 | 0.051457 | 0.05149 | 0.05149 | 0.9921 | -0.14001 | 0.99186 | -0.1381 | 23.4045
151 | 0.11041 | 0.05336 | -0.11041 | -0.053472 | 2.1689e-06 | -0.00011145 | 0.0035641 | 0.0035655 | 0.0035655 | 0.99321 | -0.15084 | 0.99319 | -0.15097 | 1.6979
152 | -0.11041 | -0.05336 | 0.11042 | 0.052589 | 1.4949e-05 | -0.00077071 | 0.0035641 | 0.0035543 | 0.0035641 | 0.99321 | -0.15084 | 0.99335 | -0.14992 | 1.6972
153 | 2.3349 | 1.0602 | -2.3346 | -1.061 | 0.00027545 | -0.00079341 | 0.074521 | 0.074531 | 0.074531 | 0.99335 | -0.14992 | 0.99324 | -0.14904 | 33.8778
154 | -2.4453 | -1.1128 | 2.4457 | 1.1117 | 0.00040962 | -0.0010648 | 0.078074 | 0.07806 | 0.078074 | 0.99335 | -0.14992 | 0.99351 | -0.15118 | 35.4883
155 | 0.09864 | 0.047522 | -0.098638 | -0.047687 | 2.5551e-06 | -0.00016524 | 0.0031814 | 0.0031835 | 0.0031835 | 0.99351 | -0.15118 | 0.99348 | -0.15135 | 1.516
156 | 0.098638 | 0.047687 | -0.098636 | -0.047772 | 1.3077e-06 | -8.4481e-05 | 0.0031835 | 0.0031846 | 0.0031846 | 0.99348 | -0.15135 | 0.99346 | -0.15144 | 1.5165
157 | -0.10561 | -0.051148 | 0.10561 | 0.048898 | 1.4888e-06 | -0.0022497 | 0.0034207 | 0.0033926 | 0.0034207 | 0.99025 | -0.13195 | 0.99026 | -0.13207 | 1.5549
158 | 0.48709 | 0.22711 | -0.48701 | -0.23263 | 7.7823e-05 | -0.0055125 | 0.015667 | 0.015736 | 0.015736 | 0.99026 | -0.13207 | 0.99012 | -0.13075 | 7.1526
159 | -0.59269 | -0.27601 | 0.59324 | 0.24936 | 0.0005455 | -0.02665 | 0.019059 | 0.018743 | 0.019059 | 0.99026 | -0.13207 | 0.99113 | -0.13852 | 8.6634
160 | 0.34616 | 0.16665 | -0.34616 | -0.16721 | 4.038e-06 | -0.0005627 | 0.011201 | 0.011208 | 0.011208 | 0.99012 | -0.13075 | 0.99011 | -0.13065 | 5.0947
161 | 0.14085 | 0.065977 | -0.14084 | -0.067276 | 1.5297e-06 | -0.0012992 | 0.0045347 | 0.0045509 | 0.0045509 | 0.99012 | -0.13075 | 0.99011 | -0.13066 | 2.0686
162 | -0.59324 | -0.24936 | 0.59331 | 0.24928 | 6.8631e-05 | -8.5623e-05 | 0.018743 | 0.018742 | 0.018743 | 0.99113 | -0.13852 | 0.99125 | -0.13736 | 8.9253
163 | 0.14084 | 0.067276 | -0.14084 | -0.068214 | 1.1105e-06 | -0.00093735 | 0.0045509 | 0.0045627 | 0.0045627 | 0.99011 | -0.13066 | 0.9901 | -0.1306 | 2.074
164 | 0.081019 | 0.038799 | -0.081014 | -0.039237 | 4.6119e-06 | -0.00043776 | 0.0026191 | 0.0026247 | 0.0026247 | 0.99011 | -0.13065 | 0.99005 | -0.13104 | 1.2498
165 | -0.75494 | -0.32756 | 0.75495 | 0.32701 | 1.8027e-05 | -0.00054635 | 0.023966 | 0.023959 | 0.023966 | 0.99125 | -0.13736 | 0.99127 | -0.13751 | 10.8935
166 | -0.75495 | -0.32701 | 0.75522 | 0.31901 | 0.00026274 | -0.0079995 | 0.023959 | 0.023867 | 0.023959 | 0.99127 | -0.13751 | 0.9916 | -0.13972 | 10.8906
167 | -0.75522 | -0.31901 | 0.75524 | 0.31839 | 2.0148e-05 | -0.00061623 | 0.023867 | 0.02386 | 0.023867 | 0.9916 | -0.13972 | 0.99162 | -0.13989 | 10.8486
168 | 0.24565 | 0.11726 | -0.24564 | -0.11731 | 5.1422e-06 | -5.0913e-05 | 0.0079174 | 0.0079181 | 0.0079181 | 0.99246 | -0.43298 | 0.99244 | -0.43313 | 3.7705
169 | 0.091077 | 0.043967 | -0.091077 | -0.044111 | 7.0501e-08 | -0.00014333 | 0.0029418 | 0.0029436 | 0.0029436 | 0.99244 | -0.43308 | 0.99244 | -0.43308 | 1.338
170 | -0.091077 | -0.043967 | 0.091078 | 0.043018 | 4.6444e-07 | -0.0009491 | 0.0029418 | 0.0029299 | 0.0029418 | 0.99244 | -0.43308 | 0.99244 | -0.43313 | 1.3372
171 | 0.15456 | 0.074294 | -0.15456 | -0.074858 | 7.986e-07 | -0.00056432 | 0.0049882 | 0.0049954 | 0.0049954 | 0.99244 | -0.43313 | 0.99244 | -0.43308 | 2.2706
172 | -0.52835 | -0.25589 | 0.52837 | 0.25451 | 2.3075e-05 | -0.0013839 | 0.017091 | 0.017073 | 0.017091 | 0.99159 | -0.13955 | 0.99163 | -0.13992 | 7.7685
173 | 0.9255 | 0.40075 | -0.92549 | -0.40085 | 5.2407e-06 | -0.00010536 | 0.02936 | 0.029361 | 0.029361 | 0.99163 | -0.13992 | 0.99162 | -0.13989 | 13.3459
174 | -1.4539 | -0.65526 | 1.4542 | 0.65536 | 0.00031778 | 0.00010187 | 0.046424 | 0.046423 | 0.046424 | 0.99163 | -0.13992 | 0.99186 | -0.1381 | 22.1066
175 | -0.59391 | -0.28764 | 0.59393 | 0.28657 | 2.2112e-05 | -0.0010678 | 0.019121 | 0.019108 | 0.019121 | 0.99626 | -0.10035 | 0.9963 | -0.10067 | 8.6914
176 | 0.23727 | 0.11248 | -0.23726 | -0.11372 | 4.0457e-06 | -0.001237 | 0.0076082 | 0.0076237 | 0.0076237 | 0.9963 | -0.10067 | 0.99628 | -0.10053 | 3.4653
177 | 0.23726 | 0.11372 | -0.23726 | -0.11491 | 3.904e-06 | -0.0011889 | 0.0076237 | 0.0076386 | 0.0076386 | 0.99628 | -0.10053 | 0.99626 | -0.10039 | 3.4721

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 15.2335 | 6.0652

## res_load
| p_mw | q_mvar
0 | 0.14128 | 0.068427
1 | 0.098971 | 0.047934
2 | 0.060378 | 0.029243
3 | 0.069625 | 0.033721
4 | 0.10196 | 0.049383
5 | 0.15091 | 0.073089
6 | 0.35952 | 0.17413
7 | 0.13584 | 0.065792
8 | 0.19044 | 0.092233
9 | 0.1216 | 0.058895
10 | 0.076654 | 0.037125
11 | 0.15886 | 0.076939
12 | 0.0832 | 0.040296
13 | 0.12932 | 0.062632
14 | 0.102 | 0.0494
15 | 0.15127 | 0.073264
16 | 0.1278 | 0.061897
17 | 0.16861 | 0.081661
18 | 0.11211 | 0.0543
19 | 0.058071 | 0.028125
20 | 0.053379 | 0.025852
21 | 0.070604 | 0.034195
22 | 0.92956 | 0.45021
23 | 0.16184 | 0.078381
24 | 0.13173 | 0.063801
25 | 0.079249 | 0.038382
26 | 0.059378 | 0.028758
27 | 0.11633 | 0.056341
28 | 0.098549 | 0.047729
29 | 0.062197 | 0.030123
30 | 0.13839 | 0.067026
31 | 0.1062 | 0.051434
32 | 0.13492 | 0.065346
33 | 0.10716 | 0.051899
34 | 0.078685 | 0.038109
35 | 0.098824 | 0.047863
36 | 0.12086 | 0.058537
37 | 0.16338 | 0.079126
38 | 0.11154 | 0.054021
39 | 0.13858 | 0.067116
40 | 0.15844 | 0.076735
41 | 0.15361 | 0.074394
42 | 0.074409 | 0.036038
43 | 0.14486 | 0.070159
44 | 0.083386 | 0.040386
45 | 0.11152 | 0.054011
46 | 0.16335 | 0.079114
47 | 0.11991 | 0.058073
48 | 0.15011 | 0.072703
49 | 0.16128 | 0.078113
50 | 0.43995 | 0.21308
51 | 0.11048 | 0.053508
52 | 0.068488 | 0.03317
53 | 2.2405 | 1.0851
54 | 0.12775 | 0.061873
55 | 0.094407 | 0.045723
56 | 0.090558 | 0.043859
57 | 0.081336 | 0.039393
58 | 0.1317 | 0.063787
59 | 0.15375 | 0.074465
60 | 0.08524 | 0.041284
61 | 0.10146 | 0.049139
62 | 0.12397 | 0.060041
63 | 0.12749 | 0.061744
64 | 0.060357 | 0.029232
65 | 0.083901 | 0.040635
66 | 0.058332 | 0.028251
67 | 0.10955 | 0.053059
68 | 0.094839 | 0.045933
69 | 0.16367 | 0.079267
70 | 0.13885 | 0.067246
71 | 0.11649 | 0.05642
72 | 0.11041 | 0.053472
73 | 0.11393 | 0.055179
74 | 0.15008 | 0.072688
75 | 0.098636 | 0.047772
76 | 0.097428 | 0.047186
77 | 0.10561 | 0.051148
78 | 0.14084 | 0.068214
79 | 0.26514 | 0.12841
80 | 0.16163 | 0.078279
81 | 0.081014 | 0.039237
82 | 0.1321 | 0.06398
83 | 0.091077 | 0.044111
84 | 0.15456 | 0.074858
85 | 0.52835 | 0.25589
86 | 0.17026 | 0.082458
87 | 0.15675 | 0.075918
88 | 0.59391 | 0.28764
89 | 0.077851 | 0.037705
90 | 0.23726 | 0.11491

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1