## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_339_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_339_0_node_80 | 20 | n |  | TRUE
2 | bus_MV_339_0_node_17 | 20 | n |  | TRUE
3 | bus_MV_339_0_node_99 | 20 | n |  | TRUE
4 | bus_MV_339_0_node_79 | 20 | n |  | TRUE
5 | bus_MV_339_0_node_12 | 20 | n |  | TRUE
6 | bus_MV_339_0_node_13 | 20 | n |  | TRUE
7 | bus_MV_339_0_node_19 | 20 | n |  | TRUE
8 | bus_MV_339_0_node_11 | 20 | n |  | TRUE
9 | bus_MV_339_0_node_18 | 20 | n |  | TRUE
10 | bus_MV_339_0_node_92 | 20 | n |  | TRUE
11 | bus_MV_339_0_node_1 | 20 | n |  | TRUE
12 | bus_MV_339_0_node_2 | 20 | n |  | TRUE
13 | bus_MV_339_0_node_3 | 20 | n |  | TRUE
14 | bus_MV_339_0_node_4 | 20 | n |  | TRUE
15 | bus_MV_339_0_node_6 | 20 | n |  | TRUE
16 | bus_MV_339_0_node_94 | 20 | n |  | TRUE
17 | bus_MV_339_0_node_7 | 20 | n |  | TRUE
18 | bus_MV_339_0_node_5 | 20 | n |  | TRUE
19 | bus_MV_339_0_node_103 | 20 | n |  | TRUE
20 | bus_MV_339_0_node_8 | 20 | n |  | TRUE
21 | bus_MV_339_0_node_9 | 20 | n |  | TRUE
22 | bus_MV_339_0_node_10 | 20 | n |  | TRUE
23 | bus_MV_339_0_node_84 | 20 | n |  | TRUE
24 | bus_MV_339_0_node_85 | 20 | n |  | TRUE
25 | bus_MV_339_0_node_58 | 20 | n |  | TRUE
26 | bus_MV_339_0_node_62 | 20 | n |  | TRUE
27 | bus_MV_339_0_node_96 | 20 | n |  | TRUE
28 | bus_MV_339_0_node_26 | 20 | n |  | TRUE
29 | bus_MV_339_0_node_83 | 20 | n |  | TRUE
30 | bus_MV_339_0_node_82 | 20 | n |  | TRUE
31 | bus_MV_339_0_node_14 | 20 | n |  | TRUE
32 | bus_MV_339_0_node_15 | 20 | n |  | TRUE
33 | bus_MV_339_0_node_97 | 20 | n |  | TRUE
34 | bus_MV_339_0_node_21 | 20 | n |  | TRUE
35 | bus_MV_339_0_node_16 | 20 | n |  | TRUE
36 | bus_MV_339_0_node_98 | 20 | n |  | TRUE
37 | bus_MV_339_0_node_20 | 20 | n |  | TRUE
38 | bus_MV_339_0_node_74 | 20 | n |  | TRUE
39 | bus_MV_339_0_node_76 | 20 | n |  | TRUE
40 | bus_MV_339_0_node_73 | 20 | n |  | TRUE
41 | bus_MV_339_0_node_91 | 20 | n |  | TRUE
42 | bus_MV_339_0_node_25 | 20 | n |  | TRUE
43 | bus_MV_339_0_node_77 | 20 | n |  | TRUE
44 | bus_MV_339_0_node_75 | 20 | n |  | TRUE
45 | bus_MV_339_0_node_22 | 20 | n |  | TRUE
46 | bus_MV_339_0_node_23 | 20 | n |  | TRUE
47 | bus_MV_339_0_node_24 | 20 | n |  | TRUE
48 | bus_MV_339_0_node_27 | 20 | n |  | TRUE
49 | bus_MV_339_0_node_28 | 20 | n |  | TRUE
50 | bus_MV_339_0_node_30 | 20 | n |  | TRUE
51 | bus_MV_339_0_node_29 | 20 | n |  | TRUE
52 | bus_MV_339_0_node_100 | 20 | n |  | TRUE
53 | bus_MV_339_0_node_65 | 20 | n |  | TRUE
54 | bus_MV_339_0_node_33 | 20 | n |  | TRUE
55 | bus_MV_339_0_node_31 | 20 | n |  | TRUE
56 | bus_MV_339_0_node_32 | 20 | n |  | TRUE
57 | bus_MV_339_0_node_34 | 20 | n |  | TRUE
58 | bus_MV_339_0_node_39 | 20 | n |  | TRUE
59 | bus_MV_339_0_node_102 | 20 | n |  | TRUE
60 | bus_MV_339_0_node_70 | 20 | n |  | TRUE
61 | bus_MV_339_0_node_35 | 20 | n |  | TRUE
62 | bus_MV_339_0_node_67 | 20 | n |  | TRUE
63 | bus_MV_339_0_node_71 | 20 | n |  | TRUE
64 | bus_MV_339_0_node_41 | 20 | n |  | TRUE
65 | bus_MV_339_0_node_36 | 20 | n |  | TRUE
66 | bus_MV_339_0_node_86 | 20 | n |  | TRUE
67 | bus_MV_339_0_node_38 | 20 | n |  | TRUE
68 | bus_MV_339_0_node_53 | 20 | n |  | TRUE
69 | bus_MV_339_0_node_37 | 20 | n |  | TRUE
70 | bus_MV_339_0_node_72 | 20 | n |  | TRUE
71 | bus_MV_339_0_node_93 | 20 | n |  | TRUE
72 | bus_MV_339_0_node_40 | 20 | n |  | TRUE
73 | bus_MV_339_0_node_106 | 20 | n |  | TRUE
74 | bus_MV_339_0_node_64 | 20 | n |  | TRUE
75 | bus_MV_339_0_node_43 | 20 | n |  | TRUE
76 | bus_MV_339_0_node_42 | 20 | n |  | TRUE
77 | bus_MV_339_0_node_44 | 20 | n |  | TRUE
78 | bus_MV_339_0_node_46 | 20 | n |  | TRUE
79 | bus_MV_339_0_node_51 | 20 | n |  | TRUE
80 | bus_MV_339_0_node_50 | 20 | n |  | TRUE
81 | bus_MV_339_0_node_101 | 20 | n |  | TRUE
82 | bus_MV_339_0_node_68 | 20 | n |  | TRUE
83 | bus_MV_339_0_node_49 | 20 | n |  | TRUE
84 | bus_MV_339_0_node_66 | 20 | n |  | TRUE
85 | bus_MV_339_0_node_87 | 20 | n |  | TRUE
86 | bus_MV_339_0_node_52 | 20 | n |  | TRUE
87 | bus_MV_339_0_node_47 | 20 | n |  | TRUE
88 | bus_MV_339_0_node_88 | 20 | n |  | TRUE
89 | bus_MV_339_0_node_48 | 20 | n |  | TRUE
90 | bus_MV_339_0_node_69 | 20 | n |  | TRUE
91 | bus_MV_339_0_node_104 | 20 | n |  | TRUE
92 | bus_MV_339_0_node_89 | 20 | n |  | TRUE
93 | bus_MV_339_0_node_105 | 20 | n |  | TRUE
94 | bus_MV_339_0_node_60 | 20 | n |  | TRUE
95 | bus_MV_339_0_node_54 | 20 | n |  | TRUE
96 | bus_MV_339_0_node_55 | 20 | n |  | TRUE
97 | bus_MV_339_0_node_56 | 20 | n |  | TRUE
98 | bus_MV_339_0_node_57 | 20 | n |  | TRUE
99 | bus_MV_339_0_node_59 | 20 | n |  | TRUE
100 | bus_MV_339_0_node_61 | 20 | n |  | TRUE
101 | bus_MV_339_0_node_90 | 20 | n |  | TRUE
102 | bus_MV_339_0_node_78 | 20 | n |  | TRUE
103 | bus_MV_339_0_node_81 | 20 | n |  | TRUE
104 | bus_HV_339_0_node_62 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_339_0_load_0 | 0 | 0.10937 | 0.052973 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_339_0_load_17 | 2 | 0.1548 | 0.074971 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_339_0_load_99 | 3 | 0.096488 | 0.046731 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_339_0_load_12 | 5 | 0.071894 | 0.03482 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_339_0_load_11 | 8 | 0.13532 | 0.065536 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_339_0_load_92 | 10 | 0.083351 | 0.040369 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_339_0_load_1 | 11 | 0.14222 | 0.06888 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_339_0_load_94 | 16 | 0.083205 | 0.040298 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_339_0_load_7 | 17 | 0.059748 | 0.028938 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_339_0_load_103 | 19 | 0.16038 | 0.077675 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_339_0_load_84 | 23 | 0.080466 | 0.038972 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_339_0_load_85 | 24 | 0.55002 | 0.26639 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_339_0_load_96 | 27 | 0.09443 | 0.045734 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_339_0_load_26 | 28 | 0.15527 | 0.075202 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_339_0_load_83 | 29 | 0.26557 | 0.12862 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_339_0_load_82 | 30 | 0.29327 | 0.14204 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_339_0_load_14 | 31 | 0.055107 | 0.02669 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_339_0_load_98 | 36 | 0.14338 | 0.069442 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_339_0_load_20 | 37 | 0.083553 | 0.040467 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_339_0_load_73 | 40 | 0.14019 | 0.067899 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_339_0_load_91 | 41 | 0.11643 | 0.056391 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_339_0_load_77 | 43 | 0.1559 | 0.075507 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_339_0_load_22 | 45 | 0.13833 | 0.066995 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_339_0_load_27 | 48 | 0.15352 | 0.074352 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_339_0_load_100 | 52 | 0.10702 | 0.051834 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_339_0_load_65 | 53 | 0.14706 | 0.071226 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_339_0_load_31 | 55 | 0.081724 | 0.039581 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_339_0_load_102 | 59 | 0.093001 | 0.045042 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_339_0_load_70 | 60 | 0.14995 | 0.072626 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_339_0_load_71 | 63 | 0.1472 | 0.07129 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_339_0_load_41 | 64 | 0.16452 | 0.079682 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_339_0_load_86 | 66 | 0.15294 | 0.07407 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_339_0_load_53 | 68 | 0.14845 | 0.071899 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_339_0_load_72 | 70 | 0.10002 | 0.048441 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_339_0_load_93 | 71 | 0.15971 | 0.07735 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_339_0_load_40 | 72 | 0.14553 | 0.070484 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_339_0_load_106 | 73 | 0.07581 | 0.036716 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_339_0_load_64 | 74 | 0.085449 | 0.041385 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_339_0_load_50 | 80 | 0.094021 | 0.045536 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_339_0_load_101 | 81 | 0.076972 | 0.037279 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_339_0_load_68 | 82 | 0.056909 | 0.027562 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_339_0_load_66 | 84 | 0.088059 | 0.042649 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_339_0_load_87 | 85 | 0.070844 | 0.034312 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_339_0_load_52 | 86 | 0.14414 | 0.069809 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_339_0_load_88 | 88 | 0.077699 | 0.037631 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_339_0_load_104 | 91 | 0.13553 | 0.065641 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_339_0_load_89 | 92 | 0.12826 | 0.062117 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_339_0_load_105 | 93 | 0.072491 | 0.035109 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_339_0_load_55 | 96 | 0.068234 | 0.033047 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_339_0_load_56 | 97 | 0.06366 | 0.030832 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_339_0_load_57 | 98 | 0.13422 | 0.065004 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_339_0_load_61 | 100 | 0.11673 | 0.056537 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_339_0_load_90 | 101 | 0.16737 | 0.081061 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_339_0_load_78 | 102 | 2.0839 | 1.0093 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_339_0_line_0 |  | 0 | 1 | 0.3647 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
1 | MV_339_0_line_1 |  | 0 | 2 | 2.8417 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
2 | MV_339_0_line_2 |  | 1 | 3 | 0.035542 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
3 | MV_339_0_line_3 |  | 1 | 4 | 0.195 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_339_0_line_4 |  | 2 | 9 | 0.047711 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
5 | MV_339_0_line_5 |  | 3 | 18 | 0.001082 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
6 | MV_339_0_line_6 |  | 4 | 103 | 0.075579 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_339_0_line_7 |  | 4 | 102 | 0.067785 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_339_0_line_8 |  | 5 | 6 | 0.039032 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
9 | MV_339_0_line_9 |  | 5 | 7 | 1.0934 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
10 | MV_339_0_line_10 |  | 6 | 8 | 2.2539 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
11 | MV_339_0_line_11 |  | 7 | 10 | 0.00645 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_339_0_line_12 |  | 7 | 9 | 0.51394 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
13 | MV_339_0_line_13 |  | 8 | 27 | 2.0536 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_339_0_line_14 |  | 11 | 12 | 0.021177 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_339_0_line_15 |  | 12 | 13 | 0.59129 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_339_0_line_16 |  | 12 | 14 | 0.41612 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
17 | MV_339_0_line_17 |  | 12 | 15 | 0.37136 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
18 | MV_339_0_line_18 |  | 13 | 16 | 0.02673 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_339_0_line_19 |  | 14 | 17 | 0.12171 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
20 | MV_339_0_line_20 |  | 15 | 19 | 0.024069 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_339_0_line_21 |  | 15 | 18 | 0.26 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
22 | MV_339_0_line_22 |  | 17 | 20 | 0.019409 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
23 | MV_339_0_line_23 |  | 20 | 21 | 0.25768 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_339_0_line_24 |  | 20 | 22 | 0.42038 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
25 | MV_339_0_line_25 |  | 21 | 23 | 0.07976 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_339_0_line_26 |  | 22 | 24 | 0.097724 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
27 | MV_339_0_line_27 |  | 24 | 25 | 0.85731 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
28 | MV_339_0_line_28 |  | 24 | 26 | 0.72196 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
29 | MV_339_0_line_29 |  | 25 | 98 | 0.049626 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_339_0_line_30 |  | 26 | 100 | 0.009071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_339_0_line_31 |  | 27 | 28 | 0.85856 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_339_0_line_32 |  | 28 | 47 | 0.027606 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_339_0_line_33 |  | 29 | 30 | 0.036456 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_339_0_line_34 |  | 30 | 103 | 0.021903 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_339_0_line_35 |  | 31 | 32 | 0.038807 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_339_0_line_36 |  | 31 | 33 | 1.4589 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_339_0_line_37 |  | 31 | 34 | 3.0681 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_339_0_line_38 |  | 32 | 35 | 0.088953 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_339_0_line_39 |  | 33 | 36 | 0.016027 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_339_0_line_40 |  | 34 | 37 | 0.014751 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_339_0_line_41 |  | 35 | 41 | 0.03212 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_339_0_line_42 |  | 38 | 39 | 0.26396 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_339_0_line_43 |  | 38 | 40 | 0.084337 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_339_0_line_44 |  | 39 | 43 | 0.033798 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_339_0_line_45 |  | 39 | 44 | 0.231 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_339_0_line_46 |  | 41 | 42 | 0.037926 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_339_0_line_47 |  | 42 | 47 | 1.1648 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_339_0_line_48 |  | 44 | 52 | 2.3023 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_339_0_line_49 |  | 45 | 46 | 0.019165 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_339_0_line_50 |  | 46 | 47 | 0.13136 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_339_0_line_51 |  | 48 | 49 | 0.028465 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_339_0_line_52 |  | 49 | 50 | 0.30315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_339_0_line_53 |  | 50 | 53 | 0.051374 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_339_0_line_54 |  | 50 | 51 | 0.42705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_339_0_line_55 |  | 51 | 52 | 0.069806 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_339_0_line_56 |  | 53 | 54 | 0.031796 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_339_0_line_57 |  | 54 | 58 | 0.10195 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_339_0_line_58 |  | 54 | 56 | 0.16786 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_339_0_line_59 |  | 55 | 56 | 0.035813 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
60 | MV_339_0_line_60 |  | 56 | 57 | 0.061543 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_339_0_line_61 |  | 57 | 59 | 0.1129 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_339_0_line_62 |  | 57 | 60 | 0.077778 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_339_0_line_63 |  | 58 | 72 | 0.015575 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_339_0_line_64 |  | 58 | 69 | 0.28124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_339_0_line_65 |  | 59 | 73 | 0.14425 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_339_0_line_66 |  | 59 | 74 | 0.12943 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_339_0_line_67 |  | 60 | 75 | 0.029642 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_339_0_line_68 |  | 61 | 62 | 0.40357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_339_0_line_69 |  | 61 | 63 | 0.007745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_339_0_line_70 |  | 61 | 64 | 0.18309 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_339_0_line_71 |  | 62 | 82 | 0.68962 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_339_0_line_72 |  | 62 | 83 | 0.2247 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_339_0_line_73 |  | 62 | 84 | 0.027026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_339_0_line_74 |  | 64 | 76 | 0.023404 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_339_0_line_75 |  | 65 | 66 | 0.06684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_339_0_line_76 |  | 65 | 67 | 0.19175 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_339_0_line_77 |  | 65 | 68 | 0.052851 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_339_0_line_78 |  | 66 | 85 | 0.040145 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
79 | MV_339_0_line_79 |  | 67 | 71 | 0.10877 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_339_0_line_80 |  | 67 | 69 | 0.39068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_339_0_line_81 |  | 68 | 86 | 0.01391 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_339_0_line_82 |  | 69 | 70 | 0.032367 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_339_0_line_83 |  | 73 | 78 | 0.024571 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_339_0_line_84 |  | 75 | 76 | 0.13136 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_339_0_line_85 |  | 77 | 78 | 0.32979 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_339_0_line_86 |  | 77 | 79 | 0.32421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_339_0_line_87 |  | 77 | 80 | 0.020106 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_339_0_line_88 |  | 79 | 81 | 0.030387 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_339_0_line_89 |  | 81 | 94 | 0.11096 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_339_0_line_90 |  | 82 | 89 | 0.083177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_339_0_line_91 |  | 83 | 91 | 0.046882 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_339_0_line_92 |  | 83 | 87 | 0.47575 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_339_0_line_93 |  | 86 | 95 | 0.036341 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_339_0_line_94 |  | 87 | 88 | 0.14988 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_339_0_line_95 |  | 88 | 92 | 0.0041268 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_339_0_line_96 |  | 89 | 90 | 0.79266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_339_0_line_97 |  | 90 | 93 | 0.008861 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_339_0_line_98 |  | 92 | 101 | 0.11326 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_339_0_line_99 |  | 94 | 99 | 0.83526 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_339_0_line_100 |  | 95 | 96 | 0.024505 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_339_0_line_101 |  | 95 | 97 | 0.055899 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
102 | MV_339_0_line_102 |  | 98 | 99 | 0.064403 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_339_0_trafo_62 | 25 MVA 110/20 kV | 104 | 26 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2522210.5366 | 1176187.002
1 | 2521934.1591 | 1175949.0458
2 | 2524893.1635 | 1177124.2917
3 | 2521903.4841 | 1175966.8338
4 | 2521972.5255 | 1175778.8011
5 | 2525364.6663 | 1176100.1299
6 | 2525394.2239 | 1176075.7508
7 | 2525330.2654 | 1177192.9441
8 | 2526156.0794 | 1173954.5131
9 | 2524940.3904 | 1177131.0703
10 | 2525323.9141 | 1177194.1685
11 | 2521548.4769 | 1175874.5289
12 | 2521538.1665 | 1175856.0308
13 | 2521197.8609 | 1176098.1296
14 | 2521252.1396 | 1175883.3444
15 | 2521728.9727 | 1175921.6847
16 | 2521199.7347 | 1176071.4781
17 | 2521168.9469 | 1175801.2233
18 | 2521902.4553 | 1175966.4915
19 | 2521752.6224 | 1175926.1562
20 | 2521153.2614 | 1175789.734
21 | 2520928.0073 | 1175778.1626
22 | 2520780.7566 | 1175625.9178
23 | 2520850.2403 | 1175760.4508
24 | 2520694.4115 | 1175585.2513
25 | 2519895.9034 | 1175273.2183
26 | 2520837.3297 | 1174877.5828
27 | 2526067.8102 | 1171902.8593
28 | 2525219.72 | 1171769.202
29 | 2522068.223 | 1175735.3618
30 | 2522033.6837 | 1175741.4656
31 | 2524163.4057 | 1171617.6953
32 | 2524202.1372 | 1171614.6259
33 | 2523972.3752 | 1173064.0571
34 | 2522597.2703 | 1168979.4844
35 | 2524286.0141 | 1171593.5982
36 | 2523963.3119 | 1173077.2909
37 | 2522596.6285 | 1168964.7508
38 | 2519769.8648 | 1171425.7374
39 | 2519639.7628 | 1171236.4236
40 | 2519749.893 | 1171507.6753
41 | 2524318.0306 | 1171590.0474
42 | 2524355.9077 | 1171587.1566
43 | 2519618.4181 | 1171210.2387
44 | 2519500.0853 | 1171420.4061
45 | 2525189.2604 | 1171864.3038
46 | 2525201.5694 | 1171849.6528
47 | 2525206.5594 | 1171793.4691
48 | 2518571.8827 | 1173915.7348
49 | 2518559.8013 | 1173889.9614
50 | 2518777.5709 | 1173842.9447
51 | 2518600.1619 | 1173615.2162
52 | 2518625.4404 | 1173550.1342
53 | 2518813.0615 | 1173876.7394
54 | 2518799.7492 | 1173905.6259
55 | 2518853.7847 | 1173982.94
56 | 2518888.688 | 1173990.9611
57 | 2518924.2799 | 1174022.7428
58 | 2518739.9112 | 1173964.9611
59 | 2518853.8061 | 1174110.9492
60 | 2518993.5369 | 1174058.1384
61 | 2519025.6219 | 1173905.8254
62 | 2519225.0876 | 1173802.7613
63 | 2519030.7743 | 1173900.0301
64 | 2519137.7009 | 1174050.6024
65 | 2518308.1316 | 1173769.1035
66 | 2518248.0612 | 1173739.4494
67 | 2518386.2789 | 1173895.7809
68 | 2518336.0823 | 1173724.2515
69 | 2518615.8753 | 1174096.7894
70 | 2518585.6252 | 1174085.2757
71 | 2518278.7349 | 1173912.045
72 | 2518754.7295 | 1173969.8854
73 | 2518980.1512 | 1174180.5589
74 | 2518917.646 | 1174223.5409
75 | 2519020.8792 | 1174069.7425
76 | 2519122.0986 | 1174067.1184
77 | 2519214.3787 | 1174309.9736
78 | 2518990.4803 | 1174164.0205
79 | 2519466.8093 | 1174452.416
80 | 2519232.4162 | 1174318.958
81 | 2519491.3146 | 1174470.4752
82 | 2519888.5303 | 1173990.9452
83 | 2519446.5123 | 1173841.0036
84 | 2519202.0769 | 1173788.5878
85 | 2518255.3505 | 1173699.9717
86 | 2518343.5017 | 1173712.4878
87 | 2519618.1609 | 1174097.1397
88 | 2519761.2427 | 1174141.0763
89 | 2519932.0852 | 1174047.908
90 | 2520590.9268 | 1174421.7736
91 | 2519487.8243 | 1173863.2728
92 | 2519765.0652 | 1174142.6313
93 | 2520599.5354 | 1174423.9719
94 | 2519555.5199 | 1174556.7976
95 | 2518361.571 | 1173680.9339
96 | 2518375.521 | 1173660.7875
97 | 2518398.6883 | 1173722.7311
98 | 2519882.7621 | 1175225.8882
99 | 2519882.9724 | 1175162.7479
100 | 2520830.8024 | 1174871.2838
101 | 2519813.0622 | 1174245.2164
102 | 2522040.0109 | 1175774.4733
103 | 2522012.1368 | 1175744.4539
104 | 2520837.3297 | 1174877.5828

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99303 | -0.27699 | 0.10937 | 0.052973
1 | 0.99334 | -0.25775 | 0 | 0
2 | 0.99078 | -0.41529 | 0.1548 | 0.074971
3 | 0.99339 | -0.25754 | 0.096488 | 0.046731
4 | 0.99268 | -0.25159 | 0 | 0
5 | 0.98985 | -0.46123 | 0.071894 | 0.03482
6 | 0.98984 | -0.46154 | 0 | 0
7 | 0.99057 | -0.41848 | 0 | 0
8 | 0.98779 | -0.53504 | 0.13532 | 0.065536
9 | 0.99075 | -0.41733 | 0 | 0
10 | 0.99057 | -0.41848 | 0.083351 | 0.040369
11 | 0.99425 | -0.25341 | 0.14222 | 0.06888
12 | 0.99425 | -0.25337 | 0 | 0
13 | 0.99419 | -0.25306 | 0 | 0
14 | 0.99486 | -0.2502 | 0 | 0
15 | 0.99374 | -0.25589 | 0 | 0
16 | 0.99419 | -0.25304 | 0.083205 | 0.040298
17 | 0.99503 | -0.24924 | 0.059748 | 0.028938
18 | 0.99339 | -0.25753 | 0 | 0
19 | 0.99373 | -0.25594 | 0.16038 | 0.077675
20 | 0.99506 | -0.24908 | 0 | 0
21 | 0.99503 | -0.24892 | 0 | 0
22 | 0.99569 | -0.24555 | 0 | 0
23 | 0.99503 | -0.24884 | 0.080466 | 0.038972
24 | 0.99583 | -0.2447 | 0.55002 | 0.26639
25 | 0.99223 | -0.34177 | 0 | 0
26 | 1 | 0 | -8.9613 | -4.0106
27 | 0.9847 | -0.56285 | 0.09443 | 0.045734
28 | 0.98356 | -0.5734 | 0.15527 | 0.075202
29 | 0.9926 | -0.25082 | 0.26557 | 0.12862
30 | 0.99261 | -0.25094 | 0.29327 | 0.14204
31 | 0.98286 | -0.56913 | 0.055107 | 0.02669
32 | 0.98288 | -0.56925 | 0 | 0
33 | 0.98245 | -0.57191 | 0 | 0
34 | 0.98236 | -0.57291 | 0 | 0
35 | 0.98291 | -0.56952 | 0 | 0
36 | 0.98245 | -0.57188 | 0.14338 | 0.069442
37 | 0.98236 | -0.5729 | 0.083553 | 0.040467
38 | 0.9806 | -0.3005 | 0 | 0
39 | 0.98064 | -0.30091 | 0 | 0
40 | 0.98057 | -0.30065 | 0.14019 | 0.067899
41 | 0.98292 | -0.56961 | 0.11643 | 0.056391
42 | 0.98294 | -0.56977 | 0 | 0
43 | 0.98064 | -0.30085 | 0.1559 | 0.075507
44 | 0.98078 | -0.29991 | 0 | 0
45 | 0.98351 | -0.57344 | 0.13833 | 0.066995
46 | 0.98351 | -0.57347 | 0 | 0
47 | 0.98353 | -0.57368 | 0 | 0
48 | 0.98229 | -0.29115 | 0.15352 | 0.074352
49 | 0.9823 | -0.29109 | 0 | 0
50 | 0.98236 | -0.2916 | 0 | 0
51 | 0.98214 | -0.28992 | 0 | 0
52 | 0.9821 | -0.28962 | 0.10702 | 0.051834
53 | 0.9824 | -0.29186 | 0.14706 | 0.071226
54 | 0.98243 | -0.29207 | 0 | 0
55 | 0.9828 | -0.2951 | 0.081724 | 0.039581
56 | 0.98281 | -0.29506 | 0 | 0
57 | 0.98295 | -0.29621 | 0 | 0
58 | 0.98229 | -0.29092 | 0 | 0
59 | 0.98361 | -0.29078 | 0.093001 | 0.045042
60 | 0.98277 | -0.29772 | 0.14995 | 0.072626
61 | 0.98222 | -0.29872 | 0 | 0
62 | 0.98185 | -0.29621 | 0 | 0
63 | 0.98222 | -0.2987 | 0.1472 | 0.07129
64 | 0.98253 | -0.29595 | 0.16452 | 0.079682
65 | 0.98139 | -0.28314 | 0 | 0
66 | 0.98137 | -0.28296 | 0.15294 | 0.07407
67 | 0.98155 | -0.2846 | 0 | 0
68 | 0.98136 | -0.28287 | 0.14845 | 0.071899
69 | 0.98196 | -0.28816 | 0 | 0
70 | 0.98196 | -0.28812 | 0.10002 | 0.048441
71 | 0.98152 | -0.28481 | 0.15971 | 0.07735
72 | 0.98229 | -0.29089 | 0.14553 | 0.070484
73 | 0.98451 | -0.28353 | 0.07581 | 0.036716
74 | 0.98359 | -0.29092 | 0.085449 | 0.041385
75 | 0.98273 | -0.29744 | 0 | 0
76 | 0.98256 | -0.29617 | 0 | 0
77 | 0.986 | -0.29512 | 0 | 0
78 | 0.98461 | -0.28434 | 0 | 0
79 | 0.9874 | -0.30588 | 0 | 0
80 | 0.986 | -0.29509 | 0.094021 | 0.045536
81 | 0.98754 | -0.30688 | 0.076972 | 0.037279
82 | 0.98168 | -0.29859 | 0.056909 | 0.027562
83 | 0.98162 | -0.29796 | 0 | 0
84 | 0.98184 | -0.29618 | 0.088059 | 0.042649
85 | 0.98137 | -0.28299 | 0.070844 | 0.034312
86 | 0.98136 | -0.28282 | 0.14414 | 0.069809
87 | 0.9814 | -0.29604 | 0 | 0
88 | 0.98132 | -0.29536 | 0.077699 | 0.037631
89 | 0.98168 | -0.29862 | 0 | 0
90 | 0.9816 | -0.2984 | 0 | 0
91 | 0.98162 | -0.29788 | 0.13553 | 0.065641
92 | 0.98132 | -0.29535 | 0.12826 | 0.062117
93 | 0.9816 | -0.29839 | 0.072491 | 0.035109
94 | 0.98803 | -0.31062 | 0 | 0
95 | 0.98135 | -0.28276 | 0 | 0
96 | 0.98135 | -0.28274 | 0.068234 | 0.033047
97 | 0.98134 | -0.28281 | 0.06366 | 0.030832
98 | 0.99201 | -0.34011 | 0.13422 | 0.065004
99 | 0.99172 | -0.33805 | 0 | 0
100 | 1 | 1.2606e-05 | 0.11673 | 0.056537
101 | 0.98128 | -0.29559 | 0.16737 | 0.081061
102 | 0.9925 | -0.24988 | 2.0839 | 1.0093
103 | 0.99263 | -0.25109 | 0 | 0
104 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -1.3482 | -0.57325 | 1.3485 | 0.57339 | 0.00023613 | 0.0001377 | 0.04259 | 0.042584 | 0.04259 | 0.99303 | -0.27699 | 0.99334 | -0.25775 | 6.603
1 | 1.2389 | 0.52028 | -1.2373 | -0.51998 | 0.0015496 | 0.00030231 | 0.039061 | 0.039105 | 0.039105 | 0.99303 | -0.27699 | 0.99078 | -0.41529 | 6.0628
2 | -3.9936 | -1.8447 | 3.9938 | 1.8426 | 0.00017945 | -0.0021026 | 0.12784 | 0.12781 | 0.12784 | 0.99334 | -0.25775 | 0.99339 | -0.25754 | 20.0377
3 | 2.6451 | 1.2713 | -2.6432 | -1.2753 | 0.0018948 | -0.0040289 | 0.085287 | 0.085345 | 0.085345 | 0.99334 | -0.25775 | 0.99268 | -0.25159 | 38.7931
4 | 1.0825 | 0.445 | -1.0825 | -0.44502 | 1.9808e-05 | -1.1472e-05 | 0.034102 | 0.034102 | 0.034102 | 0.99078 | -0.41529 | 0.99075 | -0.41733 | 5.2872
5 | -4.0903 | -1.8893 | 4.0903 | 1.8893 | 5.7314e-06 | -6.3861e-05 | 0.13093 | 0.13093 | 0.13093 | 0.99339 | -0.25754 | 0.99339 | -0.25753 | 20.5217
6 | 0.55889 | 0.26752 | -0.55885 | -0.26929 | 3.2799e-05 | -0.0017684 | 0.018019 | 0.018041 | 0.018041 | 0.99268 | -0.25159 | 0.99263 | -0.25109 | 8.2004
7 | 2.0843 | 1.0078 | -2.0839 | -1.0093 | 0.00041031 | -0.0014728 | 0.067326 | 0.067346 | 0.067346 | 0.99268 | -0.25159 | 0.9925 | -0.24988 | 30.612
8 | 0.92668 | 0.40199 | -0.92667 | -0.40344 | 1.2404e-05 | -0.0014496 | 0.029458 | 0.029475 | 0.029475 | 0.98985 | -0.46123 | 0.98984 | -0.46154 | 7.0013
9 | -0.99858 | -0.43681 | 0.99897 | 0.43638 | 0.00039416 | -0.00042198 | 0.031786 | 0.031769 | 0.031786 | 0.98985 | -0.46123 | 0.99057 | -0.41848 | 4.9281
10 | 0.92667 | 0.40344 | -0.92527 | -0.40427 | 0.0013974 | -0.00082928 | 0.029475 | 0.029509 | 0.029509 | 0.98984 | -0.46154 | 0.98779 | -0.53504 | 7.1972
11 | 0.083351 | 0.040218 | -0.083351 | -0.040369 | 6.2671e-08 | -0.00015109 | 0.002697 | 0.0026989 | 0.0026989 | 0.99057 | -0.41848 | 0.99057 | -0.41848 | 1.2268
12 | -1.0823 | -0.4766 | 1.0825 | 0.44502 | 0.00018662 | -0.031586 | 0.034464 | 0.034102 | 0.034464 | 0.99057 | -0.41848 | 0.99075 | -0.41733 | 5.4019
13 | 0.78996 | 0.33873 | -0.78764 | -0.33967 | 0.0023111 | -0.00093699 | 0.025119 | 0.025146 | 0.025146 | 0.98779 | -0.53504 | 0.9847 | -0.56285 | 11.9744
14 | -0.14222 | -0.06888 | 0.14222 | 0.068856 | 7.9423e-07 | -2.4494e-05 | 0.0045881 | 0.0045878 | 0.0045881 | 0.99425 | -0.25341 | 0.99425 | -0.25337 | 2.1848
15 | 0.083211 | 0.025714 | -0.083205 | -0.039667 | 5.3187e-06 | -0.013953 | 0.0025287 | 0.0026765 | 0.0026765 | 0.99425 | -0.25337 | 0.99419 | -0.25306 | 1.2166
16 | -4.4796 | -2.0243 | 4.4822 | 1.9999 | 0.0026136 | -0.02439 | 0.14272 | 0.14242 | 0.14272 | 0.99425 | -0.25337 | 0.99486 | -0.2502 | 22.3706
17 | 4.2541 | 1.9297 | -4.252 | -1.9516 | 0.0021152 | -0.021863 | 0.13563 | 0.13591 | 0.13591 | 0.99425 | -0.25337 | 0.99374 | -0.25589 | 21.3021
18 | 0.083205 | 0.039667 | -0.083205 | -0.040298 | 2.5638e-07 | -0.00063074 | 0.0026765 | 0.0026844 | 0.0026844 | 0.99419 | -0.25306 | 0.99419 | -0.25304 | 1.2202
19 | -4.4822 | -1.9999 | 4.4829 | 1.9927 | 0.00076232 | -0.0071409 | 0.14242 | 0.14233 | 0.14242 | 0.99486 | -0.2502 | 0.99503 | -0.24924 | 22.3224
20 | 0.16038 | 0.077647 | -0.16038 | -0.077675 | 1.1491e-06 | -2.7655e-05 | 0.0051763 | 0.0051766 | 0.0051766 | 0.99374 | -0.25589 | 0.99373 | -0.25594 | 2.4651
21 | 4.0916 | 1.8739 | -4.0903 | -1.8893 | 0.0013751 | -0.015352 | 0.13073 | 0.13093 | 0.13093 | 0.99374 | -0.25589 | 0.99339 | -0.25753 | 20.5216
22 | -4.5427 | -2.0217 | 4.5428 | 2.0205 | 0.00012479 | -0.0011372 | 0.14425 | 0.14424 | 0.14425 | 0.99503 | -0.24924 | 0.99506 | -0.24908 | 22.6101
23 | 0.080469 | 0.030995 | -0.080467 | -0.037086 | 2.2103e-06 | -0.006091 | 0.0025017 | 0.0025705 | 0.0025705 | 0.99506 | -0.24908 | 0.99503 | -0.24892 | 1.1684
24 | -4.6233 | -2.0515 | 4.6261 | 2.0269 | 0.0027911 | -0.024598 | 0.14674 | 0.14643 | 0.14674 | 0.99506 | -0.24908 | 0.99569 | -0.24555 | 22.9995
25 | 0.080467 | 0.037086 | -0.080466 | -0.038972 | 7.099e-07 | -0.0018853 | 0.0025705 | 0.0025939 | 0.0025939 | 0.99503 | -0.24892 | 0.99503 | -0.24884 | 1.179
26 | -4.6261 | -2.0269 | 4.6267 | 2.0212 | 0.00064716 | -0.0057238 | 0.14643 | 0.14636 | 0.14643 | 0.99569 | -0.24555 | 0.99583 | -0.2447 | 22.9515
27 | 3.6337 | 1.6031 | -3.6233 | -1.5923 | 0.010433 | 0.010869 | 0.11513 | 0.11514 | 0.11514 | 0.99583 | -0.2447 | 0.99223 | -0.34177 | 32.8982
28 | -8.8105 | -3.8907 | 8.8305 | 3.9438 | 0.02009 | 0.053029 | 0.27919 | 0.27918 | 0.27919 | 0.99583 | -0.2447 | 1 | 0 | 43.286
29 | 3.6233 | 1.5923 | -3.6224 | -1.5932 | 0.00087846 | -0.0009057 | 0.11514 | 0.11516 | 0.11516 | 0.99223 | -0.34177 | 0.99201 | -0.34011 | 52.3442
30 | 0.11673 | 0.056321 | -0.11673 | -0.056537 | 1.6964e-07 | -0.00021653 | 0.0037416 | 0.0037443 | 0.0037443 | 1 | 0 | 1 | 1.2606e-05 | 1.7019
31 | 0.69321 | 0.29393 | -0.69247 | -0.29446 | 0.00074573 | -0.00052557 | 0.022074 | 0.022085 | 0.022085 | 0.9847 | -0.56285 | 0.98356 | -0.5734 | 10.5167
32 | 0.5372 | 0.21925 | -0.53718 | -0.21928 | 1.4264e-05 | -2.2946e-05 | 0.017029 | 0.01703 | 0.01703 | 0.98356 | -0.5734 | 0.98353 | -0.57368 | 8.1094
33 | -0.26557 | -0.12862 | 0.26557 | 0.12776 | 3.5796e-06 | -0.00085653 | 0.0085817 | 0.0085708 | 0.0085817 | 0.9926 | -0.25082 | 0.99261 | -0.25094 | 3.9008
34 | -0.55884 | -0.2698 | 0.55885 | 0.26929 | 9.5208e-06 | -0.00051246 | 0.018047 | 0.018041 | 0.018047 | 0.99261 | -0.25094 | 0.99263 | -0.25109 | 8.2034
35 | -0.28214 | -0.13073 | 0.28214 | 0.12984 | 4.3161e-06 | -0.00089381 | 0.009133 | 0.009122 | 0.009133 | 0.98286 | -0.56913 | 0.98288 | -0.56925 | 4.1514
36 | 0.14344 | 0.067427 | -0.14338 | -0.069073 | 5.6584e-05 | -0.0016463 | 0.0046551 | 0.0046763 | 0.0046763 | 0.98286 | -0.56913 | 0.98245 | -0.57191 | 2.2268
37 | 0.083593 | 0.036615 | -0.083553 | -0.040127 | 3.9899e-05 | -0.0035114 | 0.0026804 | 0.0027237 | 0.0027237 | 0.98286 | -0.56913 | 0.98236 | -0.57291 | 1.297
38 | -0.28214 | -0.12984 | 0.28215 | 0.12779 | 9.8542e-06 | -0.0020489 | 0.009122 | 0.0090969 | 0.009122 | 0.98288 | -0.56925 | 0.98291 | -0.56952 | 4.1463
39 | 0.14338 | 0.069073 | -0.14338 | -0.069442 | 4.6837e-07 | -0.00036921 | 0.0046763 | 0.0046811 | 0.0046811 | 0.98245 | -0.57191 | 0.98245 | -0.57188 | 2.1278
40 | 0.083553 | 0.040127 | -0.083553 | -0.040467 | 1.4632e-07 | -0.00033984 | 0.0027237 | 0.0027281 | 0.0027281 | 0.98236 | -0.57291 | 0.98236 | -0.5729 | 1.24
41 | -0.28215 | -0.12779 | 0.28216 | 0.12705 | 3.545e-06 | -0.00073987 | 0.0090969 | 0.009088 | 0.0090969 | 0.98291 | -0.56952 | 0.98292 | -0.56961 | 4.135
42 | -0.1402 | -0.067804 | 0.1402 | 0.061746 | 7.2839e-06 | -0.0060583 | 0.0045846 | 0.0045097 | 0.0045846 | 0.9806 | -0.3005 | 0.98064 | -0.30091 | 2.0839
43 | 0.1402 | 0.067804 | -0.14019 | -0.067899 | 3.1591e-06 | -9.4831e-05 | 0.0045846 | 0.0045858 | 0.0045858 | 0.9806 | -0.3005 | 0.98057 | -0.30065 | 2.1837
44 | 0.1559 | 0.074731 | -0.1559 | -0.075507 | 1.171e-06 | -0.00077568 | 0.0050894 | 0.0050993 | 0.0050993 | 0.98064 | -0.30091 | 0.98064 | -0.30085 | 2.3179
45 | -0.29611 | -0.13648 | 0.29615 | 0.13624 | 3.79e-05 | -0.00024149 | 0.0095979 | 0.0095946 | 0.0095979 | 0.98064 | -0.30091 | 0.98078 | -0.29991 | 4.5704
46 | -0.39859 | -0.18344 | 0.3986 | 0.18257 | 8.4008e-06 | -0.00087238 | 0.012886 | 0.012876 | 0.012886 | 0.98292 | -0.56961 | 0.98294 | -0.56977 | 5.8575
47 | -0.3986 | -0.18257 | 0.39885 | 0.15576 | 0.00025145 | -0.026811 | 0.012876 | 0.012568 | 0.012876 | 0.98294 | -0.56977 | 0.98353 | -0.57368 | 5.8526
48 | -0.29615 | -0.13624 | 0.29652 | 0.13382 | 0.00037635 | -0.0024117 | 0.0095946 | 0.0095623 | 0.0095946 | 0.98078 | -0.29991 | 0.9821 | -0.28962 | 4.5689
49 | -0.13833 | -0.066995 | 0.13833 | 0.066553 | 5.2005e-07 | -0.00044246 | 0.0045113 | 0.0045056 | 0.0045113 | 0.98351 | -0.57344 | 0.98351 | -0.57347 | 2.0506
50 | -0.13833 | -0.066553 | 0.13833 | 0.06352 | 3.5299e-06 | -0.0030328 | 0.0045056 | 0.0044678 | 0.0045056 | 0.98351 | -0.57347 | 0.98353 | -0.57368 | 2.048
51 | -0.15352 | -0.074352 | 0.15352 | 0.07432 | 1.2743e-06 | -3.199e-05 | 0.0050128 | 0.0050124 | 0.0050128 | 0.98229 | -0.29115 | 0.9823 | -0.29109 | 2.3871
52 | -0.15352 | -0.07432 | 0.15353 | 0.067338 | 9.9909e-06 | -0.0069817 | 0.0050124 | 0.0049264 | 0.0050124 | 0.9823 | -0.29109 | 0.98236 | -0.2916 | 2.2784
53 | -0.55719 | -0.24158 | 0.55721 | 0.24041 | 2.1826e-05 | -0.0011773 | 0.017846 | 0.017832 | 0.017846 | 0.98236 | -0.2916 | 0.9824 | -0.29186 | 8.1119
54 | 0.40366 | 0.17425 | -0.40356 | -0.18405 | 9.6019e-05 | -0.0098091 | 0.01292 | 0.013037 | 0.013037 | 0.98236 | -0.2916 | 0.98214 | -0.28992 | 5.9259
55 | 0.40356 | 0.18405 | -0.40355 | -0.18566 | 1.5863e-05 | -0.0016029 | 0.013037 | 0.013057 | 0.013057 | 0.98214 | -0.28992 | 0.9821 | -0.28962 | 5.9349
56 | -0.70427 | -0.31163 | 0.70429 | 0.31091 | 2.173e-05 | -0.00072625 | 0.02263 | 0.022622 | 0.02263 | 0.9824 | -0.29186 | 0.98243 | -0.29207 | 10.2865
57 | 1.0545 | 0.4825 | -1.0543 | -0.4848 | 0.00015816 | -0.0023021 | 0.034075 | 0.034104 | 0.034104 | 0.98243 | -0.29207 | 0.98229 | -0.29092 | 15.5017
58 | -1.7588 | -0.79341 | 1.7595 | 0.78975 | 0.00071972 | -0.0036562 | 0.056695 | 0.056649 | 0.056695 | 0.98243 | -0.29207 | 0.98281 | -0.29506 | 25.7706
59 | -0.081724 | -0.039581 | 0.081725 | 0.03954 | 4.5383e-07 | -4.1012e-05 | 0.0026672 | 0.0026666 | 0.0026672 | 0.9828 | -0.2951 | 0.98281 | -0.29506 | 1.2701
60 | -1.8412 | -0.82929 | 1.8415 | 0.82796 | 0.00028897 | -0.0013338 | 0.059314 | 0.059297 | 0.059314 | 0.98281 | -0.29506 | 0.98295 | -0.29621 | 26.961
61 | -3.0308 | -1.3522 | 3.0327 | 1.3532 | 0.0019109 | 0.0010666 | 0.097466 | 0.097464 | 0.097466 | 0.98295 | -0.29621 | 0.98361 | -0.29078 | 46.4122
62 | 1.1893 | 0.5242 | -1.1891 | -0.52416 | 0.0002019 | 3.6764e-05 | 0.038169 | 0.03817 | 0.03817 | 0.98295 | -0.29621 | 0.98277 | -0.29772 | 18.1763
63 | 0.14553 | 0.070125 | -0.14553 | -0.070484 | 4.6909e-07 | -0.00035867 | 0.0047475 | 0.0047521 | 0.0047521 | 0.98229 | -0.29092 | 0.98229 | -0.29089 | 2.16
64 | 0.90881 | 0.41468 | -0.90849 | -0.42106 | 0.00032446 | -0.0063808 | 0.029357 | 0.029437 | 0.029437 | 0.98229 | -0.29092 | 0.98196 | -0.28816 | 13.3803
65 | -3.2112 | -1.4395 | 3.2139 | 1.4411 | 0.0027414 | 0.0015504 | 0.10328 | 0.10328 | 0.10328 | 0.98361 | -0.29078 | 0.98451 | -0.28353 | 49.1804
66 | 0.085451 | 0.041237 | -0.085449 | -0.041385 | 1.7894e-06 | -0.00014837 | 0.0027846 | 0.0027865 | 0.0027865 | 0.98361 | -0.29078 | 0.98359 | -0.29092 | 1.3269
67 | 1.0391 | 0.45154 | -1.0391 | -0.45221 | 4.3838e-05 | -0.00067053 | 0.03328 | 0.033288 | 0.033288 | 0.98277 | -0.29772 | 0.98273 | -0.29744 | 15.1308
68 | 0.72687 | 0.30496 | -0.72658 | -0.31417 | 0.00029049 | -0.0092064 | 0.023167 | 0.023274 | 0.023274 | 0.98222 | -0.29872 | 0.98185 | -0.29621 | 10.579
69 | 0.1472 | 0.071112 | -0.1472 | -0.07129 | 2.3878e-07 | -0.00017833 | 0.0048045 | 0.0048068 | 0.0048068 | 0.98222 | -0.29872 | 0.98222 | -0.2987 | 2.1849
70 | -0.87407 | -0.37608 | 0.87432 | 0.37603 | 0.0002551 | -5.1149e-05 | 0.027966 | 0.027963 | 0.027966 | 0.98222 | -0.29872 | 0.98253 | -0.29595 | 13.317
71 | 0.12943 | 0.041537 | -0.12941 | -0.042318 | 1.9659e-05 | -0.0007812 | 0.0039964 | 0.0040036 | 0.0040036 | 0.98185 | -0.29621 | 0.98168 | -0.29859 | 1.9065
72 | 0.50909 | 0.23061 | -0.50899 | -0.2308 | 0.00010812 | -0.00019082 | 0.016432 | 0.016435 | 0.016435 | 0.98185 | -0.29621 | 0.98162 | -0.29796 | 7.8263
73 | 0.088059 | 0.042027 | -0.088059 | -0.042649 | 2.9775e-07 | -0.00062196 | 0.0028688 | 0.0028767 | 0.0028767 | 0.98185 | -0.29621 | 0.98184 | -0.29618 | 1.3076
74 | -1.0388 | -0.45571 | 1.0389 | 0.45518 | 3.4701e-05 | -0.00052915 | 0.03333 | 0.033323 | 0.03333 | 0.98253 | -0.29595 | 0.98256 | -0.29617 | 15.1498
75 | 0.22378 | 0.1068 | -0.22378 | -0.10834 | 4.7598e-06 | -0.0015356 | 0.0072938 | 0.0073134 | 0.0073134 | 0.98139 | -0.28314 | 0.98137 | -0.28296 | 3.3243
76 | -0.64829 | -0.30939 | 0.6484 | 0.30502 | 0.00011398 | -0.0043762 | 0.02113 | 0.021074 | 0.02113 | 0.98139 | -0.28314 | 0.98155 | -0.2846 | 9.6044
77 | 0.4245 | 0.20259 | -0.42449 | -0.20381 | 1.3521e-05 | -0.0012113 | 0.013836 | 0.013851 | 0.013851 | 0.98139 | -0.28314 | 0.98136 | -0.28287 | 6.296
78 | 0.070845 | 0.034266 | -0.070844 | -0.034312 | 3.8339e-07 | -4.5916e-05 | 0.0023149 | 0.0023155 | 0.0023155 | 0.98137 | -0.28296 | 0.98137 | -0.28299 | 1.1026
79 | 0.15971 | 0.077228 | -0.15971 | -0.07735 | 5.277e-06 | -0.00012179 | 0.0052175 | 0.0052191 | 0.0052191 | 0.98155 | -0.2846 | 0.98152 | -0.28481 | 2.4853
80 | -0.80811 | -0.38225 | 0.80847 | 0.37336 | 0.00035897 | -0.0088841 | 0.026291 | 0.026179 | 0.026291 | 0.98155 | -0.2846 | 0.98196 | -0.28816 | 11.9506
81 | 0.27603 | 0.13191 | -0.27603 | -0.13223 | 1.5046e-06 | -0.00031941 | 0.0089992 | 0.0090033 | 0.0090033 | 0.98136 | -0.28287 | 0.98136 | -0.28282 | 4.0924
82 | 0.10002 | 0.047696 | -0.10002 | -0.048441 | 4.5986e-07 | -0.00074503 | 0.0032575 | 0.003267 | 0.003267 | 0.98196 | -0.28816 | 0.98196 | -0.28812 | 1.485
83 | -3.2897 | -1.4778 | 3.2901 | 1.4773 | 0.00036678 | -0.00045989 | 0.10575 | 0.10574 | 0.10575 | 0.98451 | -0.28353 | 0.98461 | -0.28434 | 48.0662
84 | 1.0391 | 0.45221 | -1.0389 | -0.45518 | 0.00019453 | -0.0029708 | 0.033288 | 0.033323 | 0.033323 | 0.98273 | -0.29744 | 0.98256 | -0.29617 | 15.1469
85 | 3.295 | 1.4711 | -3.2901 | -1.4773 | 0.0049183 | -0.0061856 | 0.10565 | 0.10574 | 0.10574 | 0.986 | -0.29512 | 0.98461 | -0.28434 | 48.0631
86 | -3.389 | -1.5162 | 3.3941 | 1.5102 | 0.0051097 | -0.0060207 | 0.1087 | 0.10861 | 0.1087 | 0.986 | -0.29512 | 0.9874 | -0.30588 | 49.4085
87 | 0.094021 | 0.04507 | -0.094021 | -0.045536 | 2.506e-07 | -0.00046663 | 0.0030526 | 0.0030585 | 0.0030585 | 0.986 | -0.29512 | 0.986 | -0.29509 | 1.3902
88 | -3.3941 | -1.5102 | 3.3946 | 1.5096 | 0.00047848 | -0.00056552 | 0.10861 | 0.1086 | 0.10861 | 0.9874 | -0.30588 | 0.98754 | -0.30688 | 49.3677
89 | -3.4716 | -1.5469 | 3.4734 | 1.5448 | 0.0018279 | -0.0020428 | 0.1111 | 0.11107 | 0.1111 | 0.98754 | -0.30688 | 0.98803 | -0.31062 | 50.4997
90 | 0.072497 | 0.014756 | -0.072497 | -0.01667 | 5.2837e-07 | -0.0019137 | 0.0021756 | 0.0021875 | 0.0021875 | 0.98168 | -0.29859 | 0.98168 | -0.29862 | 0.99432
91 | 0.13553 | 0.064562 | -0.13553 | -0.065641 | 1.2237e-06 | -0.0010782 | 0.0044148 | 0.0044286 | 0.0044286 | 0.98162 | -0.29796 | 0.98162 | -0.29788 | 2.013
92 | 0.37345 | 0.16624 | -0.37336 | -0.17715 | 9.2801e-05 | -0.010915 | 0.012021 | 0.012156 | 0.012156 | 0.98162 | -0.29796 | 0.9814 | -0.29604 | 5.5254
93 | 0.1319 | 0.062416 | -0.13189 | -0.063252 | 8.9604e-07 | -0.00083536 | 0.0042923 | 0.0043029 | 0.0043029 | 0.98136 | -0.28282 | 0.98135 | -0.28276 | 1.9559
94 | 0.37336 | 0.17715 | -0.37333 | -0.18059 | 2.9672e-05 | -0.0034375 | 0.012156 | 0.0122 | 0.0122 | 0.9814 | -0.29604 | 0.98132 | -0.29536 | 5.5453
95 | 0.29563 | 0.14296 | -0.29563 | -0.14305 | 5.1417e-07 | -9.4732e-05 | 0.00966 | 0.0096612 | 0.0096612 | 0.98132 | -0.29536 | 0.98132 | -0.29535 | 4.3915
96 | 0.072497 | 0.01667 | -0.072491 | -0.034905 | 5.418e-06 | -0.018236 | 0.0021875 | 0.0023661 | 0.0023661 | 0.98168 | -0.29862 | 0.9816 | -0.2984 | 1.0755
97 | 0.072491 | 0.034905 | -0.072491 | -0.035109 | 6.6306e-08 | -0.00020383 | 0.0023661 | 0.0023687 | 0.0023687 | 0.9816 | -0.2984 | 0.9816 | -0.29839 | 1.0767
98 | 0.16738 | 0.080935 | -0.16737 | -0.081061 | 6.0377e-06 | -0.00012642 | 0.0054691 | 0.0054708 | 0.0054708 | 0.98132 | -0.29535 | 0.98128 | -0.29559 | 2.6051
99 | -3.4734 | -1.5448 | 3.4871 | 1.5294 | 0.013727 | -0.015469 | 0.11107 | 0.11084 | 0.11107 | 0.98803 | -0.31062 | 0.99172 | -0.33805 | 50.4857
100 | 0.068234 | 0.032484 | -0.068234 | -0.033047 | 1.6218e-07 | -0.00056341 | 0.002223 | 0.0022302 | 0.0022302 | 0.98135 | -0.28276 | 0.98135 | -0.28274 | 1.0137
101 | 0.063661 | 0.030768 | -0.06366 | -0.030832 | 4.3102e-07 | -6.3996e-05 | 0.0020799 | 0.0020807 | 0.0020807 | 0.98135 | -0.28276 | 0.98134 | -0.28281 | 0.99082
102 | 3.4882 | 1.5282 | -3.4871 | -1.5294 | 0.0010561 | -0.0011995 | 0.11082 | 0.11084 | 0.11084 | 0.99201 | -0.34011 | 0.99172 | -0.33805 | 50.3811

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 8.9613 | 4.0106

## res_load
| p_mw | q_mvar
0 | 0.10937 | 0.052973
1 | 0.1548 | 0.074971
2 | 0.096488 | 0.046731
3 | 0.071894 | 0.03482
4 | 0.13532 | 0.065536
5 | 0.083351 | 0.040369
6 | 0.14222 | 0.06888
7 | 0.083205 | 0.040298
8 | 0.059748 | 0.028938
9 | 0.16038 | 0.077675
10 | 0.080466 | 0.038972
11 | 0.55002 | 0.26639
12 | 0.09443 | 0.045734
13 | 0.15527 | 0.075202
14 | 0.26557 | 0.12862
15 | 0.29327 | 0.14204
16 | 0.055107 | 0.02669
17 | 0.14338 | 0.069442
18 | 0.083553 | 0.040467
19 | 0.14019 | 0.067899
20 | 0.11643 | 0.056391
21 | 0.1559 | 0.075507
22 | 0.13833 | 0.066995
23 | 0.15352 | 0.074352
24 | 0.10702 | 0.051834
25 | 0.14706 | 0.071226
26 | 0.081724 | 0.039581
27 | 0.093001 | 0.045042
28 | 0.14995 | 0.072626
29 | 0.1472 | 0.07129
30 | 0.16452 | 0.079682
31 | 0.15294 | 0.07407
32 | 0.14845 | 0.071899
33 | 0.10002 | 0.048441
34 | 0.15971 | 0.07735
35 | 0.14553 | 0.070484
36 | 0.07581 | 0.036716
37 | 0.085449 | 0.041385
38 | 0.094021 | 0.045536
39 | 0.076972 | 0.037279
40 | 0.056909 | 0.027562
41 | 0.088059 | 0.042649
42 | 0.070844 | 0.034312
43 | 0.14414 | 0.069809
44 | 0.077699 | 0.037631
45 | 0.13553 | 0.065641
46 | 0.12826 | 0.062117
47 | 0.072491 | 0.035109
48 | 0.068234 | 0.033047
49 | 0.06366 | 0.030832
50 | 0.13422 | 0.065004
51 | 0.11673 | 0.056537
52 | 0.16737 | 0.081061
53 | 2.0839 | 1.0093

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1