## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_340_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_340_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_340_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_340_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_340_0_node_108 | 20 | n |  | TRUE
5 | bus_MV_340_0_node_106 | 20 | n |  | TRUE
6 | bus_MV_340_0_node_173 | 20 | n |  | TRUE
7 | bus_MV_340_0_node_174 | 20 | n |  | TRUE
8 | bus_MV_340_0_node_172 | 20 | n |  | TRUE
9 | bus_MV_340_0_node_187 | 20 | n |  | TRUE
10 | bus_MV_340_0_node_4 | 20 | n |  | TRUE
11 | bus_MV_340_0_node_194 | 20 | n |  | TRUE
12 | bus_MV_340_0_node_154 | 20 | n |  | TRUE
13 | bus_MV_340_0_node_5 | 20 | n |  | TRUE
14 | bus_MV_340_0_node_6 | 20 | n |  | TRUE
15 | bus_MV_340_0_node_7 | 20 | n |  | TRUE
16 | bus_MV_340_0_node_156 | 20 | n |  | TRUE
17 | bus_MV_340_0_node_189 | 20 | n |  | TRUE
18 | bus_MV_340_0_node_8 | 20 | n |  | TRUE
19 | bus_MV_340_0_node_155 | 20 | n |  | TRUE
20 | bus_MV_340_0_node_85 | 20 | n |  | TRUE
21 | bus_MV_340_0_node_86 | 20 | n |  | TRUE
22 | bus_MV_340_0_node_9 | 20 | n |  | TRUE
23 | bus_MV_340_0_node_10 | 20 | n |  | TRUE
24 | bus_MV_340_0_node_54 | 20 | n |  | TRUE
25 | bus_MV_340_0_node_12 | 20 | n |  | TRUE
26 | bus_MV_340_0_node_13 | 20 | n |  | TRUE
27 | bus_MV_340_0_node_52 | 20 | n |  | TRUE
28 | bus_MV_340_0_node_53 | 20 | n |  | TRUE
29 | bus_MV_340_0_node_55 | 20 | n |  | TRUE
30 | bus_MV_340_0_node_157 | 20 | n |  | TRUE
31 | bus_MV_340_0_node_11 | 20 | n |  | TRUE
32 | bus_MV_340_0_node_188 | 20 | n |  | TRUE
33 | bus_MV_340_0_node_21 | 20 | n |  | TRUE
34 | bus_MV_340_0_node_20 | 20 | n |  | TRUE
35 | bus_MV_340_0_node_14 | 20 | n |  | TRUE
36 | bus_MV_340_0_node_139 | 20 | n |  | TRUE
37 | bus_MV_340_0_node_16 | 20 | n |  | TRUE
38 | bus_MV_340_0_node_19 | 20 | n |  | TRUE
39 | bus_MV_340_0_node_56 | 20 | n |  | TRUE
40 | bus_MV_340_0_node_17 | 20 | n |  | TRUE
41 | bus_MV_340_0_node_18 | 20 | n |  | TRUE
42 | bus_MV_340_0_node_22 | 20 | n |  | TRUE
43 | bus_MV_340_0_node_30 | 20 | n |  | TRUE
44 | bus_MV_340_0_node_57 | 20 | n |  | TRUE
45 | bus_MV_340_0_node_151 | 20 | n |  | TRUE
46 | bus_MV_340_0_node_23 | 20 | n |  | TRUE
47 | bus_MV_340_0_node_28 | 20 | n |  | TRUE
48 | bus_MV_340_0_node_24 | 20 | n |  | TRUE
49 | bus_MV_340_0_node_140 | 20 | n |  | TRUE
50 | bus_MV_340_0_node_25 | 20 | n |  | TRUE
51 | bus_MV_340_0_node_146 | 20 | n |  | TRUE
52 | bus_MV_340_0_node_145 | 20 | n |  | TRUE
53 | bus_MV_340_0_node_141 | 20 | n |  | TRUE
54 | bus_MV_340_0_node_142 | 20 | n |  | TRUE
55 | bus_MV_340_0_node_180 | 20 | n |  | TRUE
56 | bus_MV_340_0_node_150 | 20 | n |  | TRUE
57 | bus_MV_340_0_node_77 | 20 | n |  | TRUE
58 | bus_MV_340_0_node_26 | 20 | n |  | TRUE
59 | bus_MV_340_0_node_27 | 20 | n |  | TRUE
60 | bus_MV_340_0_node_29 | 20 | n |  | TRUE
61 | bus_MV_340_0_node_31 | 20 | n |  | TRUE
62 | bus_MV_340_0_node_58 | 20 | n |  | TRUE
63 | bus_MV_340_0_node_59 | 20 | n |  | TRUE
64 | bus_MV_340_0_node_88 | 20 | n |  | TRUE
65 | bus_MV_340_0_node_60 | 20 | n |  | TRUE
66 | bus_MV_340_0_node_165 | 20 | n |  | TRUE
67 | bus_MV_340_0_node_122 | 20 | n |  | TRUE
68 | bus_MV_340_0_node_191 | 20 | n |  | TRUE
69 | bus_MV_340_0_node_164 | 20 | n |  | TRUE
70 | bus_MV_340_0_node_166 | 20 | n |  | TRUE
71 | bus_MV_340_0_node_167 | 20 | n |  | TRUE
72 | bus_MV_340_0_node_168 | 20 | n |  | TRUE
73 | bus_MV_340_0_node_169 | 20 | n |  | TRUE
74 | bus_MV_340_0_node_32 | 20 | n |  | TRUE
75 | bus_MV_340_0_node_33 | 20 | n |  | TRUE
76 | bus_MV_340_0_node_34 | 20 | n |  | TRUE
77 | bus_MV_340_0_node_35 | 20 | n |  | TRUE
78 | bus_MV_340_0_node_120 | 20 | n |  | TRUE
79 | bus_MV_340_0_node_121 | 20 | n |  | TRUE
80 | bus_MV_340_0_node_123 | 20 | n |  | TRUE
81 | bus_MV_340_0_node_36 | 20 | n |  | TRUE
82 | bus_MV_340_0_node_37 | 20 | n |  | TRUE
83 | bus_MV_340_0_node_38 | 20 | n |  | TRUE
84 | bus_MV_340_0_node_40 | 20 | n |  | TRUE
85 | bus_MV_340_0_node_42 | 20 | n |  | TRUE
86 | bus_MV_340_0_node_192 | 20 | n |  | TRUE
87 | bus_MV_340_0_node_39 | 20 | n |  | TRUE
88 | bus_MV_340_0_node_95 | 20 | n |  | TRUE
89 | bus_MV_340_0_node_177 | 20 | n |  | TRUE
90 | bus_MV_340_0_node_103 | 20 | n |  | TRUE
91 | bus_MV_340_0_node_162 | 20 | n |  | TRUE
92 | bus_MV_340_0_node_41 | 20 | n |  | TRUE
93 | bus_MV_340_0_node_99 | 20 | n |  | TRUE
94 | bus_MV_340_0_node_175 | 20 | n |  | TRUE
95 | bus_MV_340_0_node_171 | 20 | n |  | TRUE
96 | bus_MV_340_0_node_43 | 20 | n |  | TRUE
97 | bus_MV_340_0_node_44 | 20 | n |  | TRUE
98 | bus_MV_340_0_node_45 | 20 | n |  | TRUE
99 | bus_MV_340_0_node_46 | 20 | n |  | TRUE
100 | bus_MV_340_0_node_48 | 20 | n |  | TRUE
101 | bus_MV_340_0_node_47 | 20 | n |  | TRUE
102 | bus_MV_340_0_node_49 | 20 | n |  | TRUE
103 | bus_MV_340_0_node_183 | 20 | n |  | TRUE
104 | bus_MV_340_0_node_50 | 20 | n |  | TRUE
105 | bus_MV_340_0_node_51 | 20 | n |  | TRUE
106 | bus_MV_340_0_node_176 | 20 | n |  | TRUE
107 | bus_MV_340_0_node_107 | 20 | n |  | TRUE
108 | bus_MV_340_0_node_97 | 20 | n |  | TRUE
109 | bus_MV_340_0_node_104 | 20 | n |  | TRUE
110 | bus_MV_340_0_node_105 | 20 | n |  | TRUE
111 | bus_MV_340_0_node_117 | 20 | n |  | TRUE
112 | bus_MV_340_0_node_184 | 20 | n |  | TRUE
113 | bus_MV_340_0_node_66 | 20 | n |  | TRUE
114 | bus_MV_340_0_node_119 | 20 | n |  | TRUE
115 | bus_MV_340_0_node_115 | 20 | n |  | TRUE
116 | bus_MV_340_0_node_98 | 20 | n |  | TRUE
117 | bus_MV_340_0_node_170 | 20 | n |  | TRUE
118 | bus_MV_340_0_node_128 | 20 | n |  | TRUE
119 | bus_MV_340_0_node_127 | 20 | n |  | TRUE
120 | bus_MV_340_0_node_129 | 20 | n |  | TRUE
121 | bus_MV_340_0_node_126 | 20 | n |  | TRUE
122 | bus_MV_340_0_node_152 | 20 | n |  | TRUE
123 | bus_MV_340_0_node_118 | 20 | n |  | TRUE
124 | bus_MV_340_0_node_124 | 20 | n |  | TRUE
125 | bus_MV_340_0_node_125 | 20 | n |  | TRUE
126 | bus_MV_340_0_node_130 | 20 | n |  | TRUE
127 | bus_MV_340_0_node_131 | 20 | n |  | TRUE
128 | bus_MV_340_0_node_61 | 20 | n |  | TRUE
129 | bus_MV_340_0_node_62 | 20 | n |  | TRUE
130 | bus_MV_340_0_node_63 | 20 | n |  | TRUE
131 | bus_MV_340_0_node_186 | 20 | n |  | TRUE
132 | bus_MV_340_0_node_93 | 20 | n |  | TRUE
133 | bus_MV_340_0_node_160 | 20 | n |  | TRUE
134 | bus_MV_340_0_node_112 | 20 | n |  | TRUE
135 | bus_MV_340_0_node_113 | 20 | n |  | TRUE
136 | bus_MV_340_0_node_111 | 20 | n |  | TRUE
137 | bus_MV_340_0_node_185 | 20 | n |  | TRUE
138 | bus_MV_340_0_node_147 | 20 | n |  | TRUE
139 | bus_MV_340_0_node_148 | 20 | n |  | TRUE
140 | bus_MV_340_0_node_149 | 20 | n |  | TRUE
141 | bus_MV_340_0_node_190 | 20 | n |  | TRUE
142 | bus_MV_340_0_node_64 | 20 | n |  | TRUE
143 | bus_MV_340_0_node_65 | 20 | n |  | TRUE
144 | bus_MV_340_0_node_100 | 20 | n |  | TRUE
145 | bus_MV_340_0_node_109 | 20 | n |  | TRUE
146 | bus_MV_340_0_node_67 | 20 | n |  | TRUE
147 | bus_MV_340_0_node_68 | 20 | n |  | TRUE
148 | bus_MV_340_0_node_179 | 20 | n |  | TRUE
149 | bus_MV_340_0_node_84 | 20 | n |  | TRUE
150 | bus_MV_340_0_node_137 | 20 | n |  | TRUE
151 | bus_MV_340_0_node_138 | 20 | n |  | TRUE
152 | bus_MV_340_0_node_136 | 20 | n |  | TRUE
153 | bus_MV_340_0_node_135 | 20 | n |  | TRUE
154 | bus_MV_340_0_node_71 | 20 | n |  | TRUE
155 | bus_MV_340_0_node_72 | 20 | n |  | TRUE
156 | bus_MV_340_0_node_158 | 20 | n |  | TRUE
157 | bus_MV_340_0_node_73 | 20 | n |  | TRUE
158 | bus_MV_340_0_node_110 | 20 | n |  | TRUE
159 | bus_MV_340_0_node_159 | 20 | n |  | TRUE
160 | bus_MV_340_0_node_132 | 20 | n |  | TRUE
161 | bus_MV_340_0_node_133 | 20 | n |  | TRUE
162 | bus_MV_340_0_node_163 | 20 | n |  | TRUE
163 | bus_MV_340_0_node_161 | 20 | n |  | TRUE
164 | bus_MV_340_0_node_74 | 20 | n |  | TRUE
165 | bus_MV_340_0_node_75 | 20 | n |  | TRUE
166 | bus_MV_340_0_node_76 | 20 | n |  | TRUE
167 | bus_MV_340_0_node_89 | 20 | n |  | TRUE
168 | bus_MV_340_0_node_78 | 20 | n |  | TRUE
169 | bus_MV_340_0_node_79 | 20 | n |  | TRUE
170 | bus_MV_340_0_node_80 | 20 | n |  | TRUE
171 | bus_MV_340_0_node_81 | 20 | n |  | TRUE
172 | bus_MV_340_0_node_143 | 20 | n |  | TRUE
173 | bus_MV_340_0_node_82 | 20 | n |  | TRUE
174 | bus_MV_340_0_node_83 | 20 | n |  | TRUE
175 | bus_MV_340_0_node_182 | 20 | n |  | TRUE
176 | bus_MV_340_0_node_181 | 20 | n |  | TRUE
177 | bus_MV_340_0_node_178 | 20 | n |  | TRUE
178 | bus_MV_340_0_node_90 | 20 | n |  | TRUE
179 | bus_MV_340_0_node_91 | 20 | n |  | TRUE
180 | bus_MV_340_0_node_92 | 20 | n |  | TRUE
181 | bus_MV_340_0_node_94 | 20 | n |  | TRUE
182 | bus_MV_340_0_node_114 | 20 | n |  | TRUE
183 | bus_MV_340_0_node_134 | 20 | n |  | TRUE
184 | bus_MV_340_0_node_153 | 20 | n |  | TRUE
185 | bus_HV_340_0_node_133 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_340_0_load_0 | 0 | 0.11277 | 0.054616 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_340_0_load_108 | 4 | 0.20431 | 0.098953 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_340_0_load_174 | 7 | 0.068935 | 0.033387 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_340_0_load_187 | 9 | 0.15442 | 0.07479 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_340_0_load_4 | 10 | 0.070285 | 0.034041 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_340_0_load_194 | 11 | 0.12666 | 0.061343 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_340_0_load_5 | 13 | 0.082184 | 0.039803 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_340_0_load_189 | 17 | 0.089151 | 0.043178 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_340_0_load_8 | 18 | 0.12793 | 0.06196 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_340_0_load_85 | 20 | 0.14948 | 0.072394 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_340_0_load_9 | 22 | 0.068788 | 0.033316 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_340_0_load_52 | 27 | 0.13728 | 0.066489 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_340_0_load_157 | 30 | 0.15517 | 0.075154 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_340_0_load_188 | 32 | 0.11925 | 0.057754 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_340_0_load_20 | 34 | 0.15361 | 0.074399 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_340_0_load_14 | 35 | 0.089841 | 0.043512 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_340_0_load_139 | 36 | 0.13398 | 0.064888 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_340_0_load_16 | 37 | 0.066167 | 0.032046 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_340_0_load_19 | 38 | 0.15721 | 0.076139 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_340_0_load_22 | 42 | 0.15494 | 0.075039 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_340_0_load_30 | 43 | 0.13289 | 0.064362 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_340_0_load_151 | 45 | 0.099966 | 0.048416 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_340_0_load_140 | 49 | 0.14574 | 0.070583 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_340_0_load_146 | 51 | 0.14355 | 0.069522 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_340_0_load_145 | 52 | 0.14301 | 0.069265 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_340_0_load_141 | 53 | 0.51451 | 0.24919 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_340_0_load_142 | 54 | 0.1199 | 0.058071 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_340_0_load_150 | 56 | 0.093614 | 0.04534 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_340_0_load_26 | 58 | 0.14079 | 0.068185 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_340_0_load_31 | 61 | 0.091503 | 0.044317 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_340_0_load_58 | 62 | 0.083905 | 0.040637 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_340_0_load_165 | 66 | 0.53663 | 0.2599 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_340_0_load_122 | 67 | 0.070237 | 0.034017 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_340_0_load_191 | 68 | 0.08235 | 0.039884 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_340_0_load_164 | 69 | 0.1213 | 0.058748 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_340_0_load_166 | 70 | 0.063863 | 0.03093 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_340_0_load_168 | 72 | 0.11082 | 0.053672 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_340_0_load_169 | 73 | 0.094055 | 0.045553 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_340_0_load_32 | 74 | 0.12516 | 0.060619 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_340_0_load_33 | 75 | 0.11772 | 0.057013 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_340_0_load_35 | 77 | 0.084798 | 0.041069 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_340_0_load_36 | 81 | 0.13009 | 0.063006 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_340_0_load_192 | 86 | 0.15011 | 0.072703 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_340_0_load_95 | 88 | 0.086919 | 0.042097 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_340_0_load_177 | 89 | 0.099818 | 0.048344 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_340_0_load_162 | 91 | 0.11732 | 0.056819 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_340_0_load_175 | 94 | 0.2063 | 0.099916 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_340_0_load_171 | 95 | 0.080663 | 0.039067 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_340_0_load_43 | 96 | 0.098838 | 0.04787 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_340_0_load_46 | 99 | 0.12142 | 0.058809 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_340_0_load_47 | 101 | 0.064559 | 0.031267 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_340_0_load_183 | 103 | 0.15165 | 0.073447 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_340_0_load_50 | 104 | 0.17666 | 0.085559 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_340_0_load_176 | 106 | 0.10522 | 0.050959 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_340_0_load_104 | 109 | 0.10584 | 0.051259 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_340_0_load_105 | 110 | 1.384 | 0.67028 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_340_0_load_184 | 112 | 0.1355 | 0.065625 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_340_0_load_119 | 114 | 0.15016 | 0.072728 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_340_0_load_98 | 116 | 0.091569 | 0.044349 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_340_0_load_170 | 117 | 0.26415 | 0.12793 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_340_0_load_127 | 119 | 0.084464 | 0.040908 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_340_0_load_129 | 120 | 0.10062 | 0.048733 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_340_0_load_152 | 122 | 0.10773 | 0.052175 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_340_0_load_124 | 124 | 0.15478 | 0.074963 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_340_0_load_61 | 128 | 0.097062 | 0.047009 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_340_0_load_186 | 131 | 0.054101 | 0.026202 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_340_0_load_113 | 135 | 0.091402 | 0.044268 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_340_0_load_147 | 138 | 0.12274 | 0.059444 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_340_0_load_190 | 141 | 0.16345 | 0.07916 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_340_0_load_64 | 142 | 0.054535 | 0.026413 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_340_0_load_100 | 144 | 0.12568 | 0.060869 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_340_0_load_109 | 145 | 0.14231 | 0.068924 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_340_0_load_67 | 146 | 0.13144 | 0.063659 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_340_0_load_68 | 147 | 0.14311 | 0.06931 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_340_0_load_179 | 148 | 0.23445 | 0.11355 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_340_0_load_138 | 151 | 0.16661 | 0.080691 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_340_0_load_136 | 152 | 0.059108 | 0.028628 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_340_0_load_71 | 154 | 0.11038 | 0.053458 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_340_0_load_158 | 156 | 0.55242 | 0.26755 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_340_0_load_110 | 158 | 0.13201 | 0.063937 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_340_0_load_132 | 160 | 0.070265 | 0.034031 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_340_0_load_163 | 162 | 0.10392 | 0.050333 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_340_0_load_74 | 164 | 0.14816 | 0.071756 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_340_0_load_89 | 167 | 0.15265 | 0.073934 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_340_0_load_78 | 168 | 0.073341 | 0.035521 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_340_0_load_143 | 172 | 0.15904 | 0.077025 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_340_0_load_82 | 173 | 0.07544 | 0.036537 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_340_0_load_182 | 175 | 0.2521 | 0.1221 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_340_0_load_181 | 176 | 0.19002 | 0.092029 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_340_0_load_90 | 178 | 0.14976 | 0.07253 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_340_0_load_114 | 182 | 0.09682 | 0.046892 | 0 | 0 |  | 1 | TRUE | wye
91 | MV_340_0_load_134 | 183 | 0.1067 | 0.05168 | 0 | 0 |  | 1 | TRUE | wye
92 | MV_340_0_load_153 | 184 | 0.061829 | 0.029945 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 161 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_340_0_line_0 |  | 0 | 1 | 0.025726 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_340_0_line_1 |  | 1 | 2 | 0.11242 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_340_0_line_2 |  | 1 | 3 | 0.1117 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_340_0_line_3 |  | 2 | 9 | 0.053966 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_340_0_line_4 |  | 3 | 10 | 0.00776 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_340_0_line_5 |  | 4 | 5 | 0.2385 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_340_0_line_6 |  | 5 | 109 | 0.18101 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_340_0_line_7 |  | 6 | 7 | 0.027689 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_340_0_line_8 |  | 6 | 8 | 0.019689 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_340_0_line_9 |  | 8 | 117 | 0.070261 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_340_0_line_10 |  | 10 | 11 | 4.2767 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
11 | MV_340_0_line_11 |  | 11 | 12 | 5.8602 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
12 | MV_340_0_line_12 |  | 12 | 30 | 3.14 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
13 | MV_340_0_line_13 |  | 12 | 184 | 0.050444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_340_0_line_14 |  | 13 | 14 | 0.08341 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_340_0_line_15 |  | 14 | 15 | 0.15958 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_340_0_line_16 |  | 15 | 18 | 0.088014 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_340_0_line_17 |  | 16 | 17 | 0.49131 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_340_0_line_18 |  | 16 | 18 | 2.286 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_340_0_line_19 |  | 16 | 19 | 0.43706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_340_0_line_20 |  | 19 | 184 | 0.17107 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_340_0_line_21 |  | 20 | 21 | 0.005963 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_340_0_line_22 |  | 21 | 64 | 0.42221 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_340_0_line_23 |  | 22 | 23 | 0.033432 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
24 | MV_340_0_line_24 |  | 22 | 24 | 1.0124 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
25 | MV_340_0_line_25 |  | 23 | 25 | 0.13374 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
26 | MV_340_0_line_26 |  | 23 | 26 | 0.2001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_340_0_line_27 |  | 24 | 27 | 0.065569 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
28 | MV_340_0_line_28 |  | 25 | 33 | 0.091961 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
29 | MV_340_0_line_29 |  | 25 | 34 | 0.062937 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_340_0_line_30 |  | 25 | 31 | 0.079391 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_340_0_line_31 |  | 26 | 35 | 0.037525 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_340_0_line_32 |  | 27 | 28 | 0.044936 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
33 | MV_340_0_line_33 |  | 28 | 29 | 0.48054 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
34 | MV_340_0_line_34 |  | 29 | 30 | 0.021735 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
35 | MV_340_0_line_35 |  | 31 | 32 | 0.04286 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_340_0_line_36 |  | 33 | 36 | 0.030355 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
37 | MV_340_0_line_37 |  | 36 | 40 | 0.027772 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
38 | MV_340_0_line_38 |  | 37 | 38 | 0.057201 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_340_0_line_39 |  | 37 | 39 | 0.035961 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_340_0_line_40 |  | 38 | 43 | 0.010967 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_340_0_line_41 |  | 39 | 44 | 0.039965 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_340_0_line_42 |  | 40 | 41 | 0.14301 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
43 | MV_340_0_line_43 |  | 41 | 42 | 0.024155 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
44 | MV_340_0_line_44 |  | 42 | 46 | 0.026922 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
45 | MV_340_0_line_45 |  | 43 | 47 | 0.045306 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_340_0_line_46 |  | 44 | 45 | 0.10453 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_340_0_line_47 |  | 46 | 48 | 0.21267 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
48 | MV_340_0_line_48 |  | 46 | 49 | 0.10585 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_340_0_line_49 |  | 47 | 58 | 0.056147 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_340_0_line_50 |  | 48 | 50 | 0.22928 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
51 | MV_340_0_line_51 |  | 48 | 51 | 0.20644 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_340_0_line_52 |  | 49 | 53 | 0.029387 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_340_0_line_53 |  | 50 | 52 | 0.020762 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
54 | MV_340_0_line_54 |  | 51 | 56 | 0.28993 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_340_0_line_55 |  | 52 | 57 | 0.047977 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
56 | MV_340_0_line_56 |  | 53 | 54 | 0.0051143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_340_0_line_57 |  | 54 | 55 | 0.032199 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_340_0_line_58 |  | 55 | 176 | 0.016967 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_340_0_line_59 |  | 56 | 79 | 0.059139 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_340_0_line_60 |  | 57 | 165 | 0.2124 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
61 | MV_340_0_line_61 |  | 58 | 59 | 0.04461 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_340_0_line_62 |  | 59 | 60 | 0.058558 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_340_0_line_63 |  | 60 | 61 | 0.092481 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_340_0_line_64 |  | 61 | 74 | 0.24568 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_340_0_line_65 |  | 62 | 63 | 0.27743 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_340_0_line_66 |  | 62 | 64 | 0.61727 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_340_0_line_67 |  | 63 | 65 | 0.36232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_340_0_line_68 |  | 64 | 68 | 0.023489 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_340_0_line_69 |  | 65 | 66 | 0.2778 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_340_0_line_70 |  | 65 | 67 | 0.6745 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_340_0_line_71 |  | 66 | 69 | 0.10493 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_340_0_line_72 |  | 67 | 80 | 0.53636 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_340_0_line_73 |  | 69 | 70 | 0.078109 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
74 | MV_340_0_line_74 |  | 70 | 71 | 0.040173 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_340_0_line_75 |  | 70 | 72 | 0.022805 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_340_0_line_76 |  | 71 | 73 | 0.050681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_340_0_line_77 |  | 74 | 75 | 0.022767 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_340_0_line_78 |  | 75 | 76 | 0.040869 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_340_0_line_79 |  | 76 | 77 | 0.051847 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_340_0_line_80 |  | 77 | 78 | 0.067812 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_340_0_line_81 |  | 78 | 79 | 0.19646 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_340_0_line_82 |  | 79 | 80 | 0.83779 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_340_0_line_83 |  | 81 | 82 | 0.016921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_340_0_line_84 |  | 82 | 83 | 0.18606 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
85 | MV_340_0_line_85 |  | 82 | 84 | 0.19183 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
86 | MV_340_0_line_86 |  | 82 | 85 | 0.19592 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_340_0_line_87 |  | 83 | 86 | 0.053227 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_340_0_line_88 |  | 83 | 87 | 0.1152 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
89 | MV_340_0_line_89 |  | 84 | 90 | 0.19162 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
90 | MV_340_0_line_90 |  | 84 | 91 | 0.065264 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_340_0_line_91 |  | 85 | 95 | 0.046173 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_340_0_line_92 |  | 85 | 92 | 0.11508 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_340_0_line_93 |  | 87 | 88 | 0.056286 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
94 | MV_340_0_line_94 |  | 87 | 89 | 0.21863 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
95 | MV_340_0_line_95 |  | 89 | 108 | 0.12427 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_340_0_line_96 |  | 90 | 111 | 0.34525 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_340_0_line_97 |  | 90 | 112 | 0.065817 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_340_0_line_98 |  | 90 | 113 | 0.1204 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
99 | MV_340_0_line_99 |  | 92 | 93 | 0.034155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_340_0_line_100 |  | 92 | 94 | 0.072261 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_340_0_line_101 |  | 93 | 116 | 0.068134 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_340_0_line_102 |  | 95 | 117 | 0.017348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_340_0_line_103 |  | 96 | 97 | 0.035216 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_340_0_line_104 |  | 97 | 98 | 0.49252 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_340_0_line_105 |  | 98 | 118 | 0.1605 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_340_0_line_106 |  | 98 | 119 | 0.017355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_340_0_line_107 |  | 99 | 100 | 0.25189 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_340_0_line_108 |  | 99 | 101 | 0.25201 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
109 | MV_340_0_line_109 |  | 100 | 103 | 1.7824 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
110 | MV_340_0_line_110 |  | 101 | 102 | 0.1175 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_340_0_line_111 |  | 102 | 104 | 0.11993 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_340_0_line_112 |  | 102 | 105 | 0.29595 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_340_0_line_113 |  | 103 | 127 | 0.005141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_340_0_line_114 |  | 105 | 106 | 0.017051 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_340_0_line_115 |  | 105 | 107 | 0.039698 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_340_0_line_116 |  | 106 | 108 | 0.18065 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_340_0_line_117 |  | 107 | 110 | 0.13753 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_340_0_line_118 |  | 109 | 110 | 0.0185 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_340_0_line_119 |  | 111 | 114 | 0.093484 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
120 | MV_340_0_line_120 |  | 111 | 115 | 0.10476 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_340_0_line_121 |  | 112 | 143 | 0.21089 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
122 | MV_340_0_line_122 |  | 113 | 144 | 0.068194 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
123 | MV_340_0_line_123 |  | 115 | 123 | 0.49199 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_340_0_line_124 |  | 115 | 182 | 0.13882 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
125 | MV_340_0_line_125 |  | 118 | 120 | 0.003502 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_340_0_line_126 |  | 119 | 121 | 0.019454 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_340_0_line_127 |  | 120 | 126 | 0.057351 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_340_0_line_128 |  | 121 | 125 | 0.1364 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_340_0_line_129 |  | 122 | 123 | 0.12766 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_340_0_line_130 |  | 124 | 125 | 0.063735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_340_0_line_131 |  | 126 | 127 | 0.25102 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_340_0_line_132 |  | 128 | 129 | 0.33645 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_340_0_line_133 |  | 129 | 130 | 0.020756 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_340_0_line_134 |  | 130 | 133 | 1.3845 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
135 | MV_340_0_line_135 |  | 130 | 131 | 0.22151 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
136 | MV_340_0_line_136 |  | 131 | 132 | 0.04882 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
137 | MV_340_0_line_137 |  | 132 | 180 | 0.057923 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
138 | MV_340_0_line_138 |  | 133 | 135 | 0.044987 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
139 | MV_340_0_line_139 |  | 134 | 135 | 0.015889 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
140 | MV_340_0_line_140 |  | 134 | 136 | 0.10593 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
141 | MV_340_0_line_141 |  | 135 | 137 | 0.071491 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_340_0_line_142 |  | 136 | 158 | 0.071082 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
143 | MV_340_0_line_143 |  | 137 | 140 | 0.12269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_340_0_line_144 |  | 138 | 139 | 0.022478 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_340_0_line_145 |  | 139 | 140 | 0.25787 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_340_0_line_146 |  | 140 | 141 | 0.10165 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
147 | MV_340_0_line_147 |  | 142 | 143 | 0.060241 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
148 | MV_340_0_line_148 |  | 144 | 145 | 0.11484 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
149 | MV_340_0_line_149 |  | 145 | 181 | 0.093265 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
150 | MV_340_0_line_150 |  | 146 | 147 | 0.065245 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
151 | MV_340_0_line_151 |  | 146 | 148 | 0.080767 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
152 | MV_340_0_line_152 |  | 148 | 149 | 0.040107 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_340_0_line_153 |  | 149 | 177 | 0.02562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_340_0_line_154 |  | 149 | 174 | 0.075172 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_340_0_line_155 |  | 150 | 151 | 0.032755 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_340_0_line_156 |  | 150 | 152 | 0.08246 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_340_0_line_157 |  | 151 | 177 | 0.012377 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_340_0_line_158 |  | 152 | 153 | 0.036316 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_340_0_line_159 |  | 153 | 183 | 0.034002 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_340_0_line_160 |  | 154 | 155 | 0.022808 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
161 | MV_340_0_line_161 |  | 154 | 156 | 1.2337 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
162 | MV_340_0_line_162 |  | 155 | 157 | 0.59955 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
163 | MV_340_0_line_163 |  | 156 | 159 | 0.051711 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
164 | MV_340_0_line_164 |  | 157 | 164 | 0.017871 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
165 | MV_340_0_line_165 |  | 158 | 159 | 0.1253 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
166 | MV_340_0_line_166 |  | 159 | 163 | 0.097381 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
167 | MV_340_0_line_167 |  | 160 | 161 | 0.031081 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_340_0_line_168 |  | 161 | 162 | 0.73436 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
169 | MV_340_0_line_169 |  | 162 | 163 | 0.033951 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
170 | MV_340_0_line_170 |  | 164 | 165 | 0.059265 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
171 | MV_340_0_line_171 |  | 165 | 166 | 0.10094 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_340_0_line_172 |  | 166 | 167 | 0.10267 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
173 | MV_340_0_line_173 |  | 168 | 169 | 0.054985 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
174 | MV_340_0_line_174 |  | 169 | 170 | 0.16412 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_340_0_line_175 |  | 170 | 171 | 0.07741 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_340_0_line_176 |  | 170 | 172 | 0.036226 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_340_0_line_177 |  | 171 | 173 | 0.063536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
178 | MV_340_0_line_178 |  | 173 | 174 | 0.050277 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
179 | MV_340_0_line_179 |  | 174 | 175 | 0.10525 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
180 | MV_340_0_line_180 |  | 175 | 176 | 0.0044175 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
181 | MV_340_0_line_181 |  | 178 | 179 | 0.005513 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
182 | MV_340_0_line_182 |  | 178 | 180 | 0.03731 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
183 | MV_340_0_line_183 |  | 179 | 181 | 0.11746 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_340_0_trafo_133 | 25 MVA 110/20 kV | 185 | 161 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2536771.8872 | 1203639.4
1 | 2536748.6132 | 1203628.4381
2 | 2536718.3132 | 1203699.202
3 | 2536734.719 | 1203538.8208
4 | 2539158.1091 | 1198042.6495
5 | 2538962.4967 | 1197914.3347
6 | 2538578.807 | 1197713.1762
7 | 2538585.255 | 1197686.2496
8 | 2538597.8922 | 1197718.2272
9 | 2536764.0714 | 1203727.8113
10 | 2536731.8954 | 1203531.5909
11 | 2532818.2236 | 1201807.2432
12 | 2530072.7218 | 1196629.9882
13 | 2527224.9824 | 1195391.3887
14 | 2527241.8621 | 1195309.7115
15 | 2527388.7964 | 1195319.3843
16 | 2529439.4889 | 1196491.6565
17 | 2529198.0288 | 1196919.5394
18 | 2527435.1211 | 1195392.4429
19 | 2529856.384 | 1196582.4089
20 | 2532287.7867 | 1193356.7771
21 | 2532293.4266 | 1193358.7587
22 | 2534510.777 | 1195226.0077
23 | 2534544.1275 | 1195229.4329
24 | 2533641.1086 | 1195744.3168
25 | 2534606.0606 | 1195162.0923
26 | 2534531.3528 | 1195060.9849
27 | 2533581.6886 | 1195772.4053
28 | 2533539.5532 | 1195787.8945
29 | 2533106.6984 | 1195744.3143
30 | 2533084.9584 | 1195743.3685
31 | 2534595.0595 | 1195235.2336
32 | 2534590.6884 | 1195277.8622
33 | 2534619.3963 | 1195071.1038
34 | 2534668.569 | 1195169.4234
35 | 2534493.9336 | 1195056.9818
36 | 2534623.4863 | 1195041.0302
37 | 2534414.1119 | 1194983.815
38 | 2534379.5867 | 1194938.1453
39 | 2534385.6261 | 1195005.7632
40 | 2534626.8418 | 1195013.4661
41 | 2534704.8231 | 1194935.4335
42 | 2534728.042 | 1194928.5423
43 | 2534381.4781 | 1194927.3429
44 | 2534364.5432 | 1195000.3362
45 | 2534273.8054 | 1194948.4482
46 | 2534753.9509 | 1194920.9657
47 | 2534392.0852 | 1194883.5536
48 | 2534863.7732 | 1194802.5748
49 | 2534789.9003 | 1195020.5204
50 | 2535004.738 | 1194933.3933
51 | 2534757.2761 | 1194625.7225
52 | 2535023.6538 | 1194942.0703
53 | 2534810.8633 | 1195040.7975
54 | 2534814.9597 | 1195043.8595
55 | 2534837.1666 | 1195066.5981
56 | 2534684.2426 | 1194345.145
57 | 2535066.6811 | 1194963.537
58 | 2534402.0913 | 1194837.8945
59 | 2534378.3581 | 1194800.0886
60 | 2534431.0648 | 1194774.261
61 | 2534507.546 | 1194724.0365
62 | 2532823.0756 | 1193692.0187
63 | 2533069.0829 | 1193818.8535
64 | 2532436.4114 | 1193210.8633
65 | 2533360.7807 | 1193768.5729
66 | 2533103.6648 | 1193663.4109
67 | 2533906.4173 | 1193372.0427
68 | 2532412.8556 | 1193210.5852
69 | 2533006.7179 | 1193623.2782
70 | 2532998.4326 | 1193545.6103
71 | 2533014.7771 | 1193508.9131
72 | 2532977.6001 | 1193536.3318
73 | 2532985.8614 | 1193471.3036
74 | 2534372.3623 | 1194518.8891
75 | 2534388.6163 | 1194502.901
76 | 2534417.8001 | 1194474.208
77 | 2534454.8172 | 1194437.8024
78 | 2534503.2341 | 1194390.1875
79 | 2534638.0587 | 1194308.0508
80 | 2534426.4021 | 1193497.4398
81 | 2538624.2302 | 1197411.1543
82 | 2538621.6145 | 1197427.8688
83 | 2538717.153 | 1197545.9671
84 | 2538468.177 | 1197429.4053
85 | 2538624.2322 | 1197588.2357
86 | 2538676.556 | 1197574.0228
87 | 2538801.695 | 1197536.9053
88 | 2538853.0831 | 1197559.8697
89 | 2539018.8448 | 1197562.3157
90 | 2538435.842 | 1197279.4066
91 | 2538440.799 | 1197488.6492
92 | 2538520.2039 | 1197564.3592
93 | 2538488.8665 | 1197550.7742
94 | 2538520.7147 | 1197634.3746
95 | 2538610.7299 | 1197631.9639
96 | 2542145.5146 | 1199462.2786
97 | 2542134.5861 | 1199495.7596
98 | 2541897.1812 | 1199194.0249
99 | 2539808.901 | 1198122.1026
100 | 2540056.9976 | 1198134.7568
101 | 2539569.1836 | 1198044.3579
102 | 2539484.0512 | 1197964.5963
103 | 2541666.7133 | 1198900.1807
104 | 2539542.6642 | 1197859.9657
105 | 2539262.7332 | 1197770.4092
106 | 2539253.6069 | 1197755.9937
107 | 2539232.801 | 1197796.5292
108 | 2539116.4271 | 1197639.268
109 | 2539112.9442 | 1197896.4205
110 | 2539127.3017 | 1197884.7536
111 | 2538714.6844 | 1197196.01
112 | 2538396.2594 | 1197331.9903
113 | 2538357.5246 | 1197187.9615
114 | 2538687.2145 | 1197285.3666
115 | 2538724.5066 | 1197091.8483
116 | 2538447.4283 | 1197590.2135
117 | 2538608.0663 | 1197649.0931
118 | 2541906.3216 | 1199056.0333
119 | 2541911.4082 | 1199203.9633
120 | 2541908.0432 | 1199052.9814
121 | 2541929.1214 | 1199211.802
122 | 2539008.1355 | 1197214.5812
123 | 2538882.4827 | 1197211.2648
124 | 2542085.9422 | 1199132.2423
125 | 2542038.7009 | 1199175.1705
126 | 2541859.5802 | 1199022.1022
127 | 2541671.1254 | 1198902.8391
128 | 2537523.3687 | 1197208.1365
129 | 2537736.4403 | 1197108.3068
130 | 2537742.8309 | 1197088.5952
131 | 2537960.0364 | 1197132.0699
132 | 2538008.1018 | 1197135.8838
133 | 2536988.2713 | 1195927.789
134 | 2536954.8767 | 1195880.7251
135 | 2536969.5695 | 1195886.8735
136 | 2536865.4452 | 1195823.559
137 | 2536993.6727 | 1195819.5575
138 | 2537225.2958 | 1195589.7383
139 | 2537206.1464 | 1195599.6233
140 | 2537043.706 | 1195707.7197
141 | 2537134.2186 | 1195753.9817
142 | 2538157.1351 | 1197386.1619
143 | 2538205.5454 | 1197422.0148
144 | 2538395.0897 | 1197130.9847
145 | 2538298.4275 | 1197068.9804
146 | 2534984.4652 | 1195302.2865
147 | 2534949.6089 | 1195357.4405
148 | 2534917.8671 | 1195256.5924
149 | 2534878.6136 | 1195248.3862
150 | 2534846.3696 | 1195311.3751
151 | 2534861.3514 | 1195282.2469
152 | 2534807.513 | 1195384.1532
153 | 2534791.3115 | 1195416.6715
154 | 2535572.8251 | 1195207.5859
155 | 2535579.8217 | 1195185.8754
156 | 2536645.1834 | 1195817.4913
157 | 2535326.8363 | 1195090.41
158 | 2536806.3695 | 1195784.0277
159 | 2536690.6935 | 1195832.1927
160 | 2536180.7447 | 1196515.0461
161 | 2536198.7872 | 1196489.7049
162 | 2536685.7466 | 1195940.0127
163 | 2536706.487 | 1195921.2218
164 | 2535310.9518 | 1195082.2222
165 | 2535258.2639 | 1195055.088
166 | 2535300.5018 | 1194966.6671
167 | 2535324.1455 | 1194866.7523
168 | 2535176.3625 | 1195156.4474
169 | 2535123.9564 | 1195139.8068
170 | 2535028.5915 | 1195041.4416
171 | 2534978.422 | 1195100.1223
172 | 2535005.0614 | 1195016.2496
173 | 2534934.4699 | 1195146.117
174 | 2534895.5621 | 1195178.0933
175 | 2534842.1933 | 1195087.3834
176 | 2534841.1549 | 1195083.0897
177 | 2534867.007 | 1195271.2374
178 | 2538088.8276 | 1197121.9487
179 | 2538094.3465 | 1197121.6135
180 | 2538051.5652 | 1197120.5235
181 | 2538207.3643 | 1197090.2906
182 | 2538652.6514 | 1196973.0726
183 | 2534775.0355 | 1195446.5447
184 | 2530023.5189 | 1196618.8675
185 | 2536198.7872 | 1196489.7049

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98286 | -0.54735 | 0.11277 | 0.054616
1 | 0.98287 | -0.54738 | 0 | 0
2 | 0.98284 | -0.54718 | 0 | 0
3 | 0.98291 | -0.54772 | 0 | 0
4 | 0.98452 | -0.40602 | 0.20431 | 0.098953
5 | 0.98458 | -0.40658 | 0 | 0
6 | 0.98718 | -0.39309 | 0 | 0
7 | 0.98718 | -0.39306 | 0.068935 | 0.033387
8 | 0.98718 | -0.3931 | 0 | 0
9 | 0.98283 | -0.54728 | 0.15442 | 0.07479
10 | 0.98291 | -0.54774 | 0.070285 | 0.034041
11 | 0.98462 | -0.50297 | 0.12666 | 0.061343
12 | 0.98597 | -0.45511 | 0 | 0
13 | 0.98476 | -0.46097 | 0.082184 | 0.039803
14 | 0.98477 | -0.46105 | 0 | 0
15 | 0.98478 | -0.46117 | 0 | 0
16 | 0.98572 | -0.45344 | 0 | 0
17 | 0.98563 | -0.454 | 0.089151 | 0.043178
18 | 0.98479 | -0.46122 | 0.12793 | 0.06196
19 | 0.98588 | -0.4546 | 0 | 0
20 | 0.9804 | -0.41724 | 0.14948 | 0.072394
21 | 0.9804 | -0.41725 | 0 | 0
22 | 0.98789 | -0.38462 | 0.068788 | 0.033316
23 | 0.9879 | -0.38444 | 0 | 0
24 | 0.98736 | -0.40554 | 0 | 0
25 | 0.98793 | -0.38363 | 0 | 0
26 | 0.98788 | -0.38426 | 0 | 0
27 | 0.98734 | -0.40589 | 0.13728 | 0.066489
28 | 0.98733 | -0.4061 | 0 | 0
29 | 0.98723 | -0.40827 | 0 | 0
30 | 0.98723 | -0.40836 | 0.15517 | 0.075154
31 | 0.98792 | -0.38352 | 0 | 0
32 | 0.98792 | -0.38346 | 0.11925 | 0.057754
33 | 0.98796 | -0.38297 | 0 | 0
34 | 0.98792 | -0.38375 | 0.15361 | 0.074399
35 | 0.98787 | -0.38422 | 0.089841 | 0.043512
36 | 0.98797 | -0.38275 | 0.13398 | 0.064888
37 | 0.98464 | -0.3902 | 0.066167 | 0.032046
38 | 0.98465 | -0.39031 | 0.15721 | 0.076139
39 | 0.98463 | -0.39024 | 0 | 0
40 | 0.98798 | -0.38253 | 0 | 0
41 | 0.98803 | -0.38141 | 0 | 0
42 | 0.98804 | -0.38122 | 0.15494 | 0.075039
43 | 0.98466 | -0.39035 | 0.13289 | 0.064362
44 | 0.98463 | -0.3902 | 0 | 0
45 | 0.98461 | -0.39033 | 0.099966 | 0.048416
46 | 0.98805 | -0.38099 | 0 | 0
47 | 0.98468 | -0.39059 | 0 | 0
48 | 0.98825 | -0.37717 | 0 | 0
49 | 0.98756 | -0.38428 | 0.14574 | 0.070583
50 | 0.98859 | -0.37058 | 0 | 0
51 | 0.98722 | -0.38504 | 0.14355 | 0.069522
52 | 0.98862 | -0.36998 | 0.14301 | 0.069265
53 | 0.98748 | -0.38352 | 0.51451 | 0.24919
54 | 0.98747 | -0.38342 | 0.1199 | 0.058071
55 | 0.9874 | -0.38283 | 0 | 0
56 | 0.98586 | -0.3956 | 0.093614 | 0.04534
57 | 0.98869 | -0.36857 | 0 | 0
58 | 0.98472 | -0.39089 | 0.14079 | 0.068185
59 | 0.98475 | -0.39121 | 0 | 0
60 | 0.9848 | -0.39161 | 0 | 0
61 | 0.98487 | -0.39224 | 0.091503 | 0.044317
62 | 0.98076 | -0.41551 | 0.083905 | 0.040637
63 | 0.98087 | -0.41634 | 0 | 0
64 | 0.98048 | -0.4179 | 0 | 0
65 | 0.98101 | -0.41724 | 0 | 0
66 | 0.98068 | -0.4142 | 0.53663 | 0.2599
67 | 0.98264 | -0.40449 | 0.070237 | 0.034017
68 | 0.98048 | -0.41787 | 0.08235 | 0.039884
69 | 0.98063 | -0.41371 | 0.1213 | 0.058748
70 | 0.98059 | -0.414 | 0.063863 | 0.03093
71 | 0.98058 | -0.41395 | 0 | 0
72 | 0.98058 | -0.41397 | 0.11082 | 0.053672
73 | 0.98058 | -0.4139 | 0.094055 | 0.045553
74 | 0.9852 | -0.38993 | 0.12516 | 0.060619
75 | 0.98522 | -0.39014 | 0.11772 | 0.057013
76 | 0.98527 | -0.39058 | 0 | 0
77 | 0.98533 | -0.39113 | 0.084798 | 0.041069
78 | 0.98542 | -0.39192 | 0 | 0
79 | 0.98568 | -0.39417 | 0 | 0
80 | 0.98355 | -0.41166 | 0 | 0
81 | 0.98739 | -0.39496 | 0.13009 | 0.063006
82 | 0.9874 | -0.39499 | 0 | 0
83 | 0.98708 | -0.39864 | 0 | 0
84 | 0.98781 | -0.3902 | 0 | 0
85 | 0.98722 | -0.39344 | 0 | 0
86 | 0.98707 | -0.39854 | 0.15011 | 0.072703
87 | 0.9869 | -0.40078 | 0 | 0
88 | 0.98689 | -0.40085 | 0.086919 | 0.042097
89 | 0.98616 | -0.42005 | 0.099818 | 0.048344
90 | 0.98823 | -0.38525 | 0 | 0
91 | 0.9878 | -0.39011 | 0.11732 | 0.056819
92 | 0.98717 | -0.39306 | 0 | 0
93 | 0.98717 | -0.39303 | 0 | 0
94 | 0.98715 | -0.39289 | 0.2063 | 0.099916
95 | 0.98719 | -0.39322 | 0.080663 | 0.039067
96 | 0.98167 | -0.4246 | 0.098838 | 0.04787
97 | 0.98168 | -0.42465 | 0 | 0
98 | 0.98174 | -0.42504 | 0 | 0
99 | 0.9842 | -0.41018 | 0.12142 | 0.058809
100 | 0.98401 | -0.40889 | 0 | 0
101 | 0.98455 | -0.40713 | 0.064559 | 0.031267
102 | 0.98466 | -0.40797 | 0 | 0
103 | 0.98199 | -0.42671 | 0.15165 | 0.073447
104 | 0.98463 | -0.40772 | 0.17666 | 0.085559
105 | 0.98502 | -0.41057 | 0 | 0
106 | 0.98508 | -0.41105 | 0.10522 | 0.050959
107 | 0.98494 | -0.40977 | 0 | 0
108 | 0.98572 | -0.4164 | 0 | 0
109 | 0.98463 | -0.40695 | 0.10584 | 0.051259
110 | 0.98464 | -0.407 | 1.384 | 0.67028
111 | 0.98807 | -0.38423 | 0 | 0
112 | 0.98821 | -0.38541 | 0.1355 | 0.065625
113 | 0.98888 | -0.36811 | 0 | 0
114 | 0.98805 | -0.3844 | 0.15016 | 0.072728
115 | 0.98805 | -0.38407 | 0 | 0
116 | 0.98716 | -0.39296 | 0.091569 | 0.044349
117 | 0.98719 | -0.39315 | 0.26415 | 0.12793
118 | 0.98181 | -0.42551 | 0 | 0
119 | 0.98174 | -0.42499 | 0.084464 | 0.040908
120 | 0.98181 | -0.42552 | 0.10062 | 0.048733
121 | 0.98173 | -0.42496 | 0 | 0
122 | 0.98796 | -0.38355 | 0.10773 | 0.052175
123 | 0.98798 | -0.3837 | 0 | 0
124 | 0.98169 | -0.42461 | 0.15478 | 0.074963
125 | 0.9817 | -0.42473 | 0 | 0
126 | 0.98184 | -0.42575 | 0 | 0
127 | 0.98198 | -0.42669 | 0 | 0
128 | 0.99023 | -0.32955 | 0.097062 | 0.047009
129 | 0.99027 | -0.32986 | 0 | 0
130 | 0.99027 | -0.32988 | 0 | 0
131 | 0.98971 | -0.34934 | 0.054101 | 0.026202
132 | 0.98966 | -0.35036 | 0 | 0
133 | 0.99383 | -0.20623 | 0 | 0
134 | 0.99397 | -0.20187 | 0 | 0
135 | 0.99395 | -0.20223 | 0.091402 | 0.044268
136 | 0.99409 | -0.19944 | 0 | 0
137 | 0.99392 | -0.20203 | 0 | 0
138 | 0.99383 | -0.20131 | 0.12274 | 0.059444
139 | 0.99384 | -0.20135 | 0 | 0
140 | 0.99388 | -0.20167 | 0 | 0
141 | 0.99384 | -0.20187 | 0.16345 | 0.07916
142 | 0.98818 | -0.3856 | 0.054535 | 0.026413
143 | 0.98818 | -0.38555 | 0 | 0
144 | 0.98905 | -0.3661 | 0.12568 | 0.060869
145 | 0.98932 | -0.35671 | 0.14231 | 0.068924
146 | 0.98697 | -0.38339 | 0.13144 | 0.063659
147 | 0.98696 | -0.3835 | 0.14311 | 0.06931
148 | 0.98702 | -0.38311 | 0.23445 | 0.11355
149 | 0.98704 | -0.38336 | 0 | 0
150 | 0.98702 | -0.38316 | 0 | 0
151 | 0.98703 | -0.38322 | 0.16661 | 0.080691
152 | 0.987 | -0.383 | 0.059108 | 0.028628
153 | 0.987 | -0.38296 | 0 | 0
154 | 0.9901 | -0.34072 | 0.11038 | 0.053458
155 | 0.99007 | -0.34143 | 0 | 0
156 | 0.99455 | -0.18212 | 0.55242 | 0.26755
157 | 0.98913 | -0.35998 | 0 | 0
158 | 0.99429 | -0.19264 | 0.13201 | 0.063937
159 | 0.99464 | -0.1804 | 0 | 0
160 | 1 | 2.5393e-05 | 0.070265 | 0.034031
161 | 1 | 0 | -13.8887 | -6.2588
162 | 0.99503 | -0.17294 | 0.10392 | 0.050333
163 | 0.99493 | -0.17487 | 0 | 0
164 | 0.9891 | -0.36053 | 0.14816 | 0.071756
165 | 0.98901 | -0.36231 | 0 | 0
166 | 0.98899 | -0.36213 | 0 | 0
167 | 0.98896 | -0.36233 | 0.15265 | 0.073934
168 | 0.98704 | -0.38352 | 0.073341 | 0.035521
169 | 0.98705 | -0.38347 | 0 | 0
170 | 0.98706 | -0.3836 | 0 | 0
171 | 0.98709 | -0.38379 | 0 | 0
172 | 0.98706 | -0.38353 | 0.15904 | 0.077025
173 | 0.9871 | -0.38394 | 0.07544 | 0.036537
174 | 0.98712 | -0.3841 | 0 | 0
175 | 0.98736 | -0.38244 | 0.2521 | 0.1221
176 | 0.98737 | -0.38251 | 0.19002 | 0.092029
177 | 0.98703 | -0.38326 | 0 | 0
178 | 0.98955 | -0.35235 | 0.14976 | 0.07253
179 | 0.98955 | -0.35246 | 0 | 0
180 | 0.98959 | -0.35157 | 0 | 0
181 | 0.98942 | -0.35483 | 0 | 0
182 | 0.98802 | -0.38424 | 0.09682 | 0.046892
183 | 0.98699 | -0.38292 | 0.1067 | 0.05168
184 | 0.98595 | -0.45497 | 0.061829 | 0.029945
185 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.11277 | -0.054616 | 0.11277 | 0.054023 | 4.6417e-07 | -0.00059324 | 0.0036801 | 0.0036725 | 0.0036801 | 0.98286 | -0.54735 | 0.98287 | -0.54738 | 1.6728
1 | 0.15443 | 0.072137 | -0.15442 | -0.074729 | 3.7858e-06 | -0.0025919 | 0.0050061 | 0.0050388 | 0.0050388 | 0.98287 | -0.54738 | 0.98284 | -0.54718 | 2.2904
2 | -0.2672 | -0.12616 | 0.26721 | 0.12359 | 1.119e-05 | -0.0025732 | 0.0086785 | 0.0086465 | 0.0086785 | 0.98287 | -0.54738 | 0.98291 | -0.54772 | 3.9448
3 | 0.15442 | 0.074729 | -0.15442 | -0.07479 | 2.4416e-06 | -6.0703e-05 | 0.0050388 | 0.0050396 | 0.0050396 | 0.98284 | -0.54718 | 0.98283 | -0.54728 | 2.3998
4 | -0.26721 | -0.12359 | 0.26721 | 0.12341 | 7.7432e-07 | -0.00017877 | 0.0086465 | 0.0086443 | 0.0086465 | 0.98291 | -0.54772 | 0.98291 | -0.54774 | 3.9302
5 | -0.20431 | -0.098953 | 0.20433 | 0.093438 | 1.396e-05 | -0.0055157 | 0.0066564 | 0.0065875 | 0.0066564 | 0.98452 | -0.40602 | 0.98458 | -0.40658 | 3.0256
6 | -0.20433 | -0.093438 | 0.20434 | 0.089251 | 1.0406e-05 | -0.0041867 | 0.0065875 | 0.0065373 | 0.0065875 | 0.98458 | -0.40658 | 0.98463 | -0.40695 | 2.9943
7 | 0.068935 | 0.032743 | -0.068935 | -0.033387 | 1.8477e-07 | -0.0006442 | 0.0022317 | 0.0022398 | 0.0022398 | 0.98718 | -0.39309 | 0.98718 | -0.39306 | 1.0181
8 | -0.068935 | -0.032743 | 0.068935 | 0.032284 | 1.3057e-07 | -0.00045808 | 0.0022317 | 0.002226 | 0.0022317 | 0.98718 | -0.39309 | 0.98718 | -0.3931 | 1.0144
9 | -0.068935 | -0.032284 | 0.068936 | 0.03065 | 4.6058e-07 | -0.0016347 | 0.002226 | 0.0022061 | 0.002226 | 0.98718 | -0.3931 | 0.98719 | -0.39315 | 1.0118
10 | -0.33749 | -0.15745 | 0.33796 | 0.15278 | 0.00046693 | -0.0046671 | 0.010938 | 0.010874 | 0.010938 | 0.98291 | -0.54774 | 0.98462 | -0.50297 | 3.125
11 | -0.46462 | -0.21412 | 0.46508 | 0.20007 | 0.0004643 | -0.014055 | 0.014999 | 0.014823 | 0.014999 | 0.98462 | -0.50297 | 0.98597 | -0.45511 | 1.8291
12 | -0.82645 | -0.34894 | 0.82722 | 0.34214 | 0.0007694 | -0.0067981 | 0.026265 | 0.026176 | 0.026265 | 0.98597 | -0.45511 | 0.98723 | -0.40836 | 3.2031
13 | 0.36137 | 0.14887 | -0.36136 | -0.15003 | 8.828e-06 | -0.0011682 | 0.011443 | 0.011456 | 0.011456 | 0.98597 | -0.45511 | 0.98595 | -0.45497 | 5.2073
14 | -0.082184 | -0.039803 | 0.082185 | 0.037872 | 7.9063e-07 | -0.001931 | 0.0026768 | 0.0026527 | 0.0026768 | 0.98476 | -0.46097 | 0.98477 | -0.46105 | 1.2167
15 | -0.082185 | -0.037872 | 0.082186 | 0.034178 | 1.4741e-06 | -0.0036947 | 0.0026527 | 0.0026092 | 0.0026527 | 0.98477 | -0.46105 | 0.98478 | -0.46117 | 1.2058
16 | -0.082186 | -0.034178 | 0.082187 | 0.03214 | 7.9298e-07 | -0.0020378 | 0.0026092 | 0.0025868 | 0.0026092 | 0.98478 | -0.46117 | 0.98479 | -0.46122 | 1.186
17 | 0.089158 | 0.042612 | -0.089151 | -0.043178 | 7.3495e-06 | -0.00056524 | 0.002894 | 0.0029012 | 0.0029012 | 0.98572 | -0.45344 | 0.98563 | -0.454 | 1.3815
18 | 0.2103 | 0.091567 | -0.21012 | -0.0941 | 0.00018464 | -0.0025335 | 0.0067174 | 0.0067487 | 0.0067487 | 0.98572 | -0.45344 | 0.98479 | -0.46122 | 3.2137
19 | -0.29946 | -0.13418 | 0.29952 | 0.12405 | 5.3218e-05 | -0.010125 | 0.0096101 | 0.0094925 | 0.0096101 | 0.98572 | -0.45344 | 0.98588 | -0.4546 | 4.3682
20 | -0.29952 | -0.12405 | 0.29954 | 0.12009 | 2.0483e-05 | -0.0039642 | 0.0094925 | 0.0094487 | 0.0094925 | 0.98588 | -0.4546 | 0.98595 | -0.45497 | 4.3148
21 | -0.14948 | -0.072394 | 0.14948 | 0.072257 | 1.9032e-07 | -0.00013679 | 0.0048903 | 0.0048885 | 0.0048903 | 0.9804 | -0.41724 | 0.9804 | -0.41725 | 2.2229
22 | -0.14948 | -0.072257 | 0.14949 | 0.062571 | 1.3139e-05 | -0.0096862 | 0.0048885 | 0.0047713 | 0.0048885 | 0.9804 | -0.41725 | 0.98048 | -0.4179 | 2.2221
23 | -1.189 | -0.46965 | 1.189 | 0.46717 | 8.532e-06 | -0.002485 | 0.037357 | 0.03733 | 0.037357 | 0.98789 | -0.38462 | 0.9879 | -0.38444 | 4.4367
24 | 1.1202 | 0.43634 | -1.1198 | -0.43825 | 0.00044565 | -0.0019111 | 0.03513 | 0.035158 | 0.035158 | 0.98789 | -0.38462 | 0.98736 | -0.40554 | 4.2875
25 | -1.2789 | -0.50514 | 1.2789 | 0.49521 | 3.9407e-05 | -0.0099366 | 0.04018 | 0.040074 | 0.04018 | 0.9879 | -0.38444 | 0.98793 | -0.38363 | 4.772
26 | 0.089844 | 0.037976 | -0.089842 | -0.042638 | 2.2118e-06 | -0.0046619 | 0.0028502 | 0.002906 | 0.002906 | 0.9879 | -0.38444 | 0.98788 | -0.38426 | 1.3209
27 | 1.1198 | 0.43825 | -1.1198 | -0.44312 | 1.4854e-05 | -0.0048701 | 0.035158 | 0.03521 | 0.03521 | 0.98736 | -0.40554 | 0.98734 | -0.40589 | 4.1817
28 | -1.5518 | -0.62444 | 1.5518 | 0.61762 | 4.0141e-05 | -0.0068209 | 0.048877 | 0.048802 | 0.048877 | 0.98793 | -0.38363 | 0.98796 | -0.38297 | 5.8048
29 | 0.15362 | 0.074327 | -0.15361 | -0.074399 | 2.7888e-06 | -7.1584e-05 | 0.0049865 | 0.0049875 | 0.0049875 | 0.98793 | -0.38363 | 0.98792 | -0.38375 | 2.375
30 | 0.11925 | 0.054906 | -0.11925 | -0.056755 | 1.5689e-06 | -0.0018496 | 0.0038361 | 0.003859 | 0.003859 | 0.98793 | -0.38363 | 0.98792 | -0.38352 | 1.7541
31 | 0.089842 | 0.042638 | -0.089841 | -0.043512 | 4.2465e-07 | -0.00087423 | 0.002906 | 0.002917 | 0.002917 | 0.98788 | -0.38426 | 0.98787 | -0.38422 | 1.3259
32 | 0.98249 | 0.37663 | -0.98249 | -0.37997 | 7.7916e-06 | -0.0033397 | 0.030764 | 0.030799 | 0.030799 | 0.98734 | -0.40589 | 0.98733 | -0.4061 | 3.6579
33 | 0.98249 | 0.37997 | -0.9824 | -0.41568 | 8.4465e-05 | -0.03571 | 0.030799 | 0.031192 | 0.031192 | 0.98733 | -0.4061 | 0.98723 | -0.40827 | 3.7045
34 | 0.9824 | 0.41568 | -0.9824 | -0.41729 | 3.8721e-06 | -0.0016149 | 0.031192 | 0.03121 | 0.03121 | 0.98723 | -0.40827 | 0.98723 | -0.40836 | 3.7067
35 | 0.11925 | 0.056755 | -0.11925 | -0.057754 | 8.5487e-07 | -0.0009985 | 0.003859 | 0.0038716 | 0.0038716 | 0.98792 | -0.38352 | 0.98792 | -0.38346 | 1.7598
36 | -1.5518 | -0.61762 | 1.5518 | 0.61537 | 1.3223e-05 | -0.0022516 | 0.048802 | 0.048778 | 0.048802 | 0.98796 | -0.38297 | 0.98797 | -0.38275 | 5.796
37 | -1.6858 | -0.68025 | 1.6858 | 0.6782 | 1.4333e-05 | -0.002058 | 0.053117 | 0.053094 | 0.053117 | 0.98797 | -0.38275 | 0.98798 | -0.38253 | 6.3084
38 | -0.16614 | -0.079376 | 0.16614 | 0.078052 | 2.2183e-06 | -0.0013235 | 0.0053981 | 0.0053815 | 0.0053981 | 0.98464 | -0.3902 | 0.98465 | -0.39031 | 2.4537
39 | 0.099969 | 0.04733 | -0.099968 | -0.047371 | 6.7384e-07 | -4.1199e-05 | 0.0032427 | 0.0032433 | 0.0032433 | 0.98464 | -0.3902 | 0.98463 | -0.39024 | 1.5444
40 | -0.32335 | -0.15419 | 0.32335 | 0.15394 | 1.6143e-06 | -0.00025339 | 0.010502 | 0.010499 | 0.010502 | 0.98465 | -0.39031 | 0.98466 | -0.39035 | 4.7738
41 | 0.099968 | 0.047371 | -0.099968 | -0.048296 | 5.6323e-07 | -0.00092493 | 0.0032433 | 0.003255 | 0.003255 | 0.98463 | -0.39024 | 0.98463 | -0.3902 | 1.4795
42 | -1.6858 | -0.6782 | 1.6859 | 0.6676 | 7.3613e-05 | -0.010598 | 0.053094 | 0.052979 | 0.053094 | 0.98798 | -0.38253 | 0.98803 | -0.38141 | 6.3057
43 | -1.6859 | -0.6676 | 1.6859 | 0.66581 | 1.2402e-05 | -0.0017903 | 0.052979 | 0.052959 | 0.052979 | 0.98803 | -0.38141 | 0.98804 | -0.38122 | 6.292
44 | -1.8408 | -0.74085 | 1.8409 | 0.73885 | 1.6554e-05 | -0.0019929 | 0.057976 | 0.057954 | 0.057976 | 0.98804 | -0.38122 | 0.98805 | -0.38099 | 6.8855
45 | -0.45624 | -0.2183 | 0.45625 | 0.21726 | 1.3287e-05 | -0.0010449 | 0.014828 | 0.014815 | 0.014828 | 0.98466 | -0.39035 | 0.98468 | -0.39059 | 6.74
46 | 0.099968 | 0.048296 | -0.099966 | -0.048416 | 1.9741e-06 | -0.00011974 | 0.003255 | 0.0032565 | 0.0032565 | 0.98463 | -0.3902 | 0.98461 | -0.39033 | 1.5507
47 | -4.2143 | -1.8689 | 4.215 | 1.8537 | 0.00070507 | -0.015219 | 0.13469 | 0.1345 | 0.13469 | 0.98805 | -0.38099 | 0.98825 | -0.37717 | 15.9966
48 | 2.3734 | 1.1301 | -2.3723 | -1.1295 | 0.0011124 | 0.00057348 | 0.076802 | 0.076804 | 0.076804 | 0.98805 | -0.38099 | 0.98756 | -0.38428 | 36.5731
49 | -0.45625 | -0.21726 | 0.45627 | 0.21596 | 1.6433e-05 | -0.001295 | 0.014815 | 0.014798 | 0.014815 | 0.98468 | -0.39059 | 0.98472 | -0.39089 | 6.734
50 | -6.7944 | -3.032 | 6.7964 | 3.0167 | 0.00198 | -0.015296 | 0.21733 | 0.21713 | 0.21733 | 0.98825 | -0.37717 | 0.98859 | -0.37058 | 25.8117
51 | 2.5794 | 1.1783 | -2.5769 | -1.1769 | 0.002524 | 0.0013405 | 0.082836 | 0.082839 | 0.082839 | 0.98825 | -0.37717 | 0.98722 | -0.38504 | 39.447
52 | 2.2266 | 1.0589 | -2.2264 | -1.0595 | 0.0002038 | -0.00062379 | 0.07207 | 0.072079 | 0.072079 | 0.98756 | -0.38428 | 0.98748 | -0.38352 | 32.7631
53 | -6.7964 | -3.0167 | 6.7966 | 3.0153 | 0.00017911 | -0.0013859 | 0.21713 | 0.21711 | 0.21713 | 0.98859 | -0.37058 | 0.98862 | -0.36998 | 25.7876
54 | 2.4333 | 1.1074 | -2.4302 | -1.1058 | 0.0031571 | 0.0016407 | 0.078176 | 0.07818 | 0.07818 | 0.98722 | -0.38504 | 0.98586 | -0.3956 | 37.2287
55 | -6.9396 | -3.0846 | 6.94 | 3.0814 | 0.00043165 | -0.0031866 | 0.22175 | 0.22171 | 0.22175 | 0.98862 | -0.36998 | 0.98869 | -0.36857 | 26.3361
56 | 1.7119 | 0.81035 | -1.7118 | -0.81047 | 2.0931e-05 | -0.00011286 | 0.055367 | 0.055369 | 0.055369 | 0.98748 | -0.38352 | 0.98747 | -0.38342 | 25.1676
57 | 1.5919 | 0.75239 | -1.5918 | -0.75311 | 0.00011392 | -0.0007158 | 0.051474 | 0.051484 | 0.051484 | 0.98747 | -0.38342 | 0.9874 | -0.38283 | 23.4017
58 | 1.5918 | 0.75311 | -1.5918 | -0.75349 | 6.0043e-05 | -0.00037714 | 0.051484 | 0.051489 | 0.051489 | 0.9874 | -0.38283 | 0.98737 | -0.38251 | 23.4039
59 | 2.3366 | 1.0604 | -2.3361 | -1.0617 | 0.0004458 | -0.0012399 | 0.075135 | 0.075152 | 0.075152 | 0.98586 | -0.3956 | 0.98568 | -0.39417 | 34.16
60 | -6.94 | -3.0814 | 6.9419 | 3.0673 | 0.001909 | -0.014116 | 0.22171 | 0.22152 | 0.22171 | 0.98869 | -0.36857 | 0.98901 | -0.36231 | 26.3311
61 | -0.59705 | -0.28415 | 0.59708 | 0.28312 | 2.2362e-05 | -0.0010262 | 0.019384 | 0.019371 | 0.019384 | 0.98472 | -0.39089 | 0.98475 | -0.39121 | 8.8109
62 | -0.59708 | -0.28312 | 0.5971 | 0.28177 | 2.9308e-05 | -0.0013472 | 0.019371 | 0.019354 | 0.019371 | 0.98475 | -0.39121 | 0.9848 | -0.39161 | 8.805
63 | -0.5971 | -0.28177 | 0.59715 | 0.27964 | 4.6182e-05 | -0.0021279 | 0.019354 | 0.019327 | 0.019354 | 0.9848 | -0.39161 | 0.98487 | -0.39224 | 8.7973
64 | -0.68865 | -0.32396 | 0.68887 | 0.32381 | 0.00021779 | -0.00014817 | 0.022307 | 0.022304 | 0.022307 | 0.98487 | -0.39224 | 0.9852 | -0.38993 | 10.6225
65 | -0.3158 | -0.14188 | 0.31584 | 0.13552 | 3.8173e-05 | -0.0063608 | 0.01019 | 0.010115 | 0.01019 | 0.98076 | -0.41551 | 0.98087 | -0.41634 | 4.632
66 | 0.2319 | 0.10125 | -0.23184 | -0.10192 | 6.1075e-05 | -0.00067035 | 0.0074479 | 0.0074563 | 0.0074563 | 0.98076 | -0.41551 | 0.98048 | -0.4179 | 3.5506
67 | -0.31584 | -0.13552 | 0.31589 | 0.12721 | 4.9024e-05 | -0.0083098 | 0.010115 | 0.010021 | 0.010115 | 0.98087 | -0.41634 | 0.98101 | -0.41724 | 4.5977
68 | 0.08235 | 0.039345 | -0.08235 | -0.039884 | 2.27e-07 | -0.00053908 | 0.0026871 | 0.002694 | 0.002694 | 0.98048 | -0.4179 | 0.98048 | -0.41787 | 1.2245
69 | 0.92704 | 0.43743 | -0.9267 | -0.44371 | 0.00033832 | -0.0062807 | 0.030164 | 0.030244 | 0.030244 | 0.98101 | -0.41724 | 0.98068 | -0.4142 | 13.7474
70 | -1.2429 | -0.56464 | 1.2449 | 0.56508 | 0.0019389 | 0.00043826 | 0.040172 | 0.040163 | 0.040172 | 0.98101 | -0.41724 | 0.98264 | -0.40449 | 19.1295
71 | 0.39007 | 0.18381 | -0.39005 | -0.18621 | 2.2622e-05 | -0.0024025 | 0.012693 | 0.012724 | 0.012724 | 0.98068 | -0.4142 | 0.98063 | -0.41371 | 5.7834
72 | -1.3151 | -0.5991 | 1.3164 | 0.5871 | 0.001286 | -0.011995 | 0.042454 | 0.042305 | 0.042454 | 0.98264 | -0.40449 | 0.98355 | -0.41166 | 19.2975
73 | 0.26875 | 0.12746 | -0.26874 | -0.12755 | 1.0671e-05 | -8.2981e-05 | 0.0087561 | 0.0087572 | 0.0087572 | 0.98063 | -0.41371 | 0.98059 | -0.414 | 4.1701
74 | 0.094057 | 0.043468 | -0.094056 | -0.04439 | 5.0088e-07 | -0.00092213 | 0.0030503 | 0.0030618 | 0.0030618 | 0.98059 | -0.414 | 0.98058 | -0.41395 | 1.3917
75 | 0.11082 | 0.053148 | -0.11082 | -0.053672 | 3.993e-07 | -0.00052345 | 0.0036182 | 0.0036249 | 0.0036249 | 0.98059 | -0.414 | 0.98058 | -0.41397 | 1.6477
76 | 0.094056 | 0.04439 | -0.094055 | -0.045553 | 6.3733e-07 | -0.0011633 | 0.0030618 | 0.0030766 | 0.0030766 | 0.98058 | -0.41395 | 0.98058 | -0.4139 | 1.3985
77 | -0.81403 | -0.38443 | 0.81406 | 0.38391 | 2.1143e-05 | -0.00052136 | 0.026378 | 0.026372 | 0.026378 | 0.9852 | -0.38993 | 0.98522 | -0.39014 | 11.9901
78 | -0.93177 | -0.44092 | 0.93182 | 0.43999 | 4.9754e-05 | -0.00093245 | 0.030204 | 0.030192 | 0.030204 | 0.98522 | -0.39014 | 0.98527 | -0.39058 | 13.729
79 | -0.93182 | -0.43999 | 0.93188 | 0.43881 | 6.3063e-05 | -0.0011831 | 0.030192 | 0.030177 | 0.030192 | 0.98527 | -0.39058 | 0.98533 | -0.39113 | 13.7236
80 | -1.0167 | -0.47988 | 1.0168 | 0.47833 | 9.8153e-05 | -0.001543 | 0.032937 | 0.032918 | 0.032937 | 0.98533 | -0.39113 | 0.98542 | -0.39192 | 14.9715
81 | -1.0168 | -0.47833 | 1.0171 | 0.47386 | 0.0002837 | -0.004472 | 0.032918 | 0.032861 | 0.032918 | 0.98542 | -0.39192 | 0.98568 | -0.39417 | 14.9625
82 | 1.3191 | 0.58781 | -1.3164 | -0.5871 | 0.0026708 | 0.00070327 | 0.042294 | 0.042305 | 0.042305 | 0.98568 | -0.39417 | 0.98355 | -0.41166 | 20.1453
83 | -0.13009 | -0.063006 | 0.13009 | 0.062612 | 4.0294e-07 | -0.00039377 | 0.0042259 | 0.0042209 | 0.0042259 | 0.98739 | -0.39496 | 0.9874 | -0.39499 | 1.9209
84 | 3.0985 | 1.4189 | -3.0976 | -1.4245 | 0.00089278 | -0.0055723 | 0.099634 | 0.09971 | 0.09971 | 0.9874 | -0.39499 | 0.98708 | -0.39864 | 27.5442
85 | -3.9404 | -1.8107 | 3.9418 | 1.8054 | 0.0014884 | -0.0053372 | 0.12678 | 0.1267 | 0.12678 | 0.9874 | -0.39499 | 0.98781 | -0.3902 | 35.0226
86 | 0.71179 | 0.32919 | -0.71165 | -0.33371 | 0.00013783 | -0.004519 | 0.022927 | 0.022984 | 0.022984 | 0.9874 | -0.39499 | 0.98722 | -0.39344 | 10.4472
87 | 0.15011 | 0.071465 | -0.15011 | -0.072703 | 1.6853e-06 | -0.0012377 | 0.0048622 | 0.0048779 | 0.0048779 | 0.98708 | -0.39864 | 0.98707 | -0.39854 | 2.2172
88 | 2.9475 | 1.3531 | -2.947 | -1.3565 | 0.00050082 | -0.0034861 | 0.094848 | 0.094895 | 0.094895 | 0.98708 | -0.39864 | 0.9869 | -0.40078 | 26.2142
89 | -4.0592 | -1.8607 | 4.0607 | 1.8554 | 0.0015751 | -0.0052726 | 0.13049 | 0.13042 | 0.13049 | 0.98781 | -0.3902 | 0.98823 | -0.38525 | 36.0479
90 | 0.11732 | 0.055299 | -0.11732 | -0.056819 | 1.258e-06 | -0.0015201 | 0.0037903 | 0.0038094 | 0.0038094 | 0.98781 | -0.3902 | 0.9878 | -0.39011 | 1.7316
91 | 0.41376 | 0.19617 | -0.41375 | -0.19725 | 1.1063e-05 | -0.0010711 | 0.01339 | 0.013403 | 0.013403 | 0.98722 | -0.39344 | 0.98719 | -0.39322 | 6.0924
92 | 0.29789 | 0.13753 | -0.29787 | -0.1402 | 1.419e-05 | -0.0026735 | 0.0095942 | 0.0096273 | 0.0096273 | 0.98722 | -0.39344 | 0.98717 | -0.39306 | 4.376
93 | 0.08692 | 0.042032 | -0.086919 | -0.042097 | 8.0008e-07 | -6.4943e-05 | 0.0028241 | 0.002825 | 0.002825 | 0.9869 | -0.40078 | 0.98689 | -0.40085 | 1.3452
94 | 2.86 | 1.3145 | -2.8583 | -1.3128 | 0.0017015 | 0.0016787 | 0.092072 | 0.092075 | 0.092075 | 0.9869 | -0.40078 | 0.98616 | -0.42005 | 26.3071
95 | 2.7585 | 1.2645 | -2.7572 | -1.267 | 0.0013096 | -0.0024959 | 0.088829 | 0.088864 | 0.088864 | 0.98616 | -0.42005 | 0.98572 | -0.4164 | 40.3928
96 | 0.35479 | 0.14662 | -0.35473 | -0.15465 | 5.8432e-05 | -0.0080317 | 0.011214 | 0.011306 | 0.011306 | 0.98823 | -0.38525 | 0.98807 | -0.38423 | 5.1391
97 | 0.19004 | 0.091648 | -0.19004 | -0.091722 | 4.455e-06 | -7.3941e-05 | 0.0061631 | 0.0061641 | 0.0061641 | 0.98823 | -0.38525 | 0.98821 | -0.38541 | 2.9353
98 | -4.6056 | -2.0937 | 4.608 | 2.0963 | 0.0024139 | 0.0026131 | 0.14778 | 0.14778 | 0.14778 | 0.98823 | -0.38525 | 0.98888 | -0.36811 | 42.224
99 | 0.09157 | 0.041969 | -0.09157 | -0.042764 | 3.9694e-07 | -0.00079459 | 0.0029456 | 0.0029554 | 0.0029554 | 0.98717 | -0.39306 | 0.98717 | -0.39303 | 1.3433
100 | 0.2063 | 0.098235 | -0.2063 | -0.099916 | 4.3208e-06 | -0.00168 | 0.0066819 | 0.0067032 | 0.0067032 | 0.98717 | -0.39306 | 0.98715 | -0.39289 | 3.0469
101 | 0.09157 | 0.042764 | -0.091569 | -0.044349 | 7.9977e-07 | -0.001585 | 0.0029554 | 0.0029753 | 0.0029753 | 0.98717 | -0.39303 | 0.98716 | -0.39296 | 1.3524
102 | 0.33309 | 0.15818 | -0.33308 | -0.15858 | 2.6939e-06 | -0.00040286 | 0.010783 | 0.010788 | 0.010788 | 0.98719 | -0.39322 | 0.98719 | -0.39315 | 4.9035
103 | -0.098838 | -0.04787 | 0.098839 | 0.047059 | 4.8874e-07 | -0.00081014 | 0.0032294 | 0.0032191 | 0.0032294 | 0.98167 | -0.4246 | 0.98168 | -0.42465 | 1.4679
104 | -0.098839 | -0.047059 | 0.098845 | 0.035728 | 6.5286e-06 | -0.011331 | 0.0032191 | 0.0030905 | 0.0032191 | 0.98168 | -0.42465 | 0.98174 | -0.42504 | 1.4632
105 | -0.3381 | -0.14615 | 0.33812 | 0.14246 | 2.5034e-05 | -0.0036862 | 0.010831 | 0.010788 | 0.010831 | 0.98174 | -0.42504 | 0.98181 | -0.42551 | 4.923
106 | 0.23925 | 0.11042 | -0.23925 | -0.11082 | 1.3918e-06 | -0.00039895 | 0.0077481 | 0.0077531 | 0.0077531 | 0.98174 | -0.42504 | 0.98174 | -0.42499 | 3.5241
107 | 0.59173 | 0.25024 | -0.59161 | -0.25603 | 0.00011983 | -0.0057889 | 0.018844 | 0.018911 | 0.018911 | 0.9842 | -0.41018 | 0.98401 | -0.40889 | 8.5961
108 | -0.71316 | -0.30905 | 0.71339 | 0.3089 | 0.00023332 | -0.00014538 | 0.022797 | 0.022794 | 0.022797 | 0.9842 | -0.41018 | 0.98455 | -0.40713 | 10.8558
109 | 0.59161 | 0.25603 | -0.59047 | -0.25737 | 0.0011372 | -0.0013438 | 0.018911 | 0.018935 | 0.018935 | 0.98401 | -0.40889 | 0.98199 | -0.42671 | 9.0169
110 | -0.77795 | -0.34017 | 0.77804 | 0.33748 | 9.7094e-05 | -0.0026909 | 0.024895 | 0.024863 | 0.024895 | 0.98455 | -0.40713 | 0.98466 | -0.40797 | 11.316
111 | 0.17666 | 0.082784 | -0.17666 | -0.085559 | 5.2697e-06 | -0.0027746 | 0.0057197 | 0.0057547 | 0.0057547 | 0.98466 | -0.40797 | 0.98463 | -0.40772 | 2.6158
112 | -0.95471 | -0.42026 | 0.95507 | 0.41352 | 0.00036852 | -0.0067443 | 0.030581 | 0.030501 | 0.030581 | 0.98466 | -0.40797 | 0.98502 | -0.41057 | 13.9005
113 | 0.43882 | 0.18392 | -0.43882 | -0.18404 | 1.3429e-06 | -0.00011797 | 0.013987 | 0.013989 | 0.013989 | 0.98199 | -0.42671 | 0.98198 | -0.42669 | 6.3585
114 | -2.6499 | -1.22 | 2.6501 | 1.2196 | 0.00016638 | -0.00034568 | 0.085495 | 0.08549 | 0.085495 | 0.98502 | -0.41057 | 0.98508 | -0.41105 | 38.8614
115 | 1.6949 | 0.80648 | -1.6947 | -0.80735 | 0.00016039 | -0.000872 | 0.055007 | 0.055018 | 0.055018 | 0.98502 | -0.41057 | 0.98494 | -0.40977 | 25.0083
116 | -2.7553 | -1.2706 | 2.7572 | 1.267 | 0.0019056 | -0.003623 | 0.088916 | 0.088864 | 0.088916 | 0.98508 | -0.41105 | 0.98572 | -0.4164 | 40.4162
117 | 1.6947 | 0.80735 | -1.6941 | -0.81037 | 0.00055618 | -0.0030196 | 0.055018 | 0.055059 | 0.055059 | 0.98494 | -0.40977 | 0.98464 | -0.407 | 25.0266
118 | -0.31017 | -0.14051 | 0.31018 | 0.14008 | 2.4603e-06 | -0.00042751 | 0.0099833 | 0.0099782 | 0.0099833 | 0.98463 | -0.40695 | 0.98464 | -0.407 | 4.5379
119 | 0.15017 | 0.072621 | -0.15016 | -0.072728 | 3.9569e-06 | -0.00010647 | 0.0048734 | 0.0048748 | 0.0048748 | 0.98807 | -0.38423 | 0.98805 | -0.3844 | 2.3213
120 | 0.20457 | 0.082027 | -0.20456 | -0.084468 | 5.8227e-06 | -0.0024401 | 0.0064391 | 0.006466 | 0.006466 | 0.98807 | -0.38423 | 0.98805 | -0.38407 | 2.9391
121 | 0.054537 | 0.026097 | -0.054535 | -0.026343 | 1.1741e-06 | -0.00024512 | 0.0017661 | 0.0017692 | 0.0017692 | 0.98821 | -0.38541 | 0.98818 | -0.38555 | 0.8425
122 | -4.608 | -2.0963 | 4.6087 | 2.0945 | 0.00071921 | -0.0017655 | 0.14778 | 0.14775 | 0.14778 | 0.98888 | -0.36811 | 0.98905 | -0.3661 | 40.8238
123 | 0.10774 | 0.037736 | -0.10773 | -0.0492 | 7.5671e-06 | -0.011465 | 0.0033352 | 0.0034604 | 0.0034604 | 0.98805 | -0.38407 | 0.98798 | -0.3837 | 1.5729
124 | 0.096823 | 0.046732 | -0.09682 | -0.046892 | 2.4419e-06 | -0.00016025 | 0.0031411 | 0.0031432 | 0.0031432 | 0.98805 | -0.38407 | 0.98802 | -0.38424 | 1.4967
125 | -0.33812 | -0.14246 | 0.33812 | 0.14238 | 5.4408e-07 | -8.0439e-05 | 0.010788 | 0.010787 | 0.010788 | 0.98181 | -0.42551 | 0.98181 | -0.42552 | 4.9036
126 | 0.15479 | 0.069912 | -0.15479 | -0.070359 | 6.4847e-07 | -0.00044748 | 0.0049941 | 0.0049996 | 0.0049996 | 0.98174 | -0.42499 | 0.98173 | -0.42496 | 2.2725
127 | -0.43874 | -0.19111 | 0.43876 | 0.1898 | 1.5142e-05 | -0.0013155 | 0.014071 | 0.014055 | 0.014071 | 0.98181 | -0.42552 | 0.98184 | -0.42575 | 6.3958
128 | 0.15479 | 0.070359 | -0.15478 | -0.073497 | 4.5866e-06 | -0.0031373 | 0.0049996 | 0.0050385 | 0.0050385 | 0.98173 | -0.42496 | 0.9817 | -0.42473 | 2.2902
129 | -0.10773 | -0.052175 | 0.10773 | 0.0492 | 2.0624e-06 | -0.0029745 | 0.0034975 | 0.0034604 | 0.0034975 | 0.98796 | -0.38355 | 0.98798 | -0.3837 | 1.5898
130 | -0.15478 | -0.074963 | 0.15478 | 0.073497 | 2.168e-06 | -0.0014659 | 0.0050571 | 0.0050385 | 0.0050571 | 0.98169 | -0.42461 | 0.9817 | -0.42473 | 2.2987
131 | -0.43876 | -0.1898 | 0.43882 | 0.18404 | 6.5886e-05 | -0.005759 | 0.014055 | 0.013989 | 0.014055 | 0.98184 | -0.42575 | 0.98198 | -0.42669 | 6.3888
132 | -0.097062 | -0.047009 | 0.097066 | 0.039133 | 4.3044e-06 | -0.0078759 | 0.003144 | 0.0030509 | 0.003144 | 0.99023 | -0.32955 | 0.99027 | -0.32986 | 1.4291
133 | -0.097066 | -0.039133 | 0.097067 | 0.038648 | 2.5748e-07 | -0.0004859 | 0.0030509 | 0.0030456 | 0.0030509 | 0.99027 | -0.32986 | 0.99027 | -0.32988 | 1.3868
134 | -5.1823 | -2.3398 | 5.1959 | 2.3559 | 0.013553 | 0.016096 | 0.16575 | 0.16571 | 0.16575 | 0.99027 | -0.32988 | 0.99383 | -0.20623 | 20.2139
135 | 5.0852 | 2.3012 | -5.0831 | -2.2987 | 0.0020902 | 0.0024643 | 0.16271 | 0.16272 | 0.16272 | 0.99027 | -0.32988 | 0.98971 | -0.34934 | 19.8437
136 | 5.029 | 2.2725 | -5.0288 | -2.2759 | 0.00023154 | -0.0034409 | 0.16097 | 0.16101 | 0.16101 | 0.98971 | -0.34934 | 0.98966 | -0.35036 | 19.1223
137 | 5.0288 | 2.2759 | -5.0285 | -2.28 | 0.00027488 | -0.0040818 | 0.16101 | 0.16106 | 0.16106 | 0.98966 | -0.35036 | 0.98959 | -0.35157 | 19.1285
138 | -5.1959 | -2.3559 | 5.1963 | 2.3564 | 0.00044028 | 0.0005224 | 0.16571 | 0.16571 | 0.16571 | 0.99383 | -0.20623 | 0.99395 | -0.20223 | 20.2088
139 | 5.574 | 2.5269 | -5.5739 | -2.528 | 9.1868e-05 | -0.001115 | 0.17774 | 0.17776 | 0.17776 | 0.99397 | -0.20187 | 0.99395 | -0.20223 | 21.1113
140 | -5.574 | -2.5269 | 5.5746 | 2.5195 | 0.00061211 | -0.0074353 | 0.17774 | 0.17765 | 0.17774 | 0.99397 | -0.20187 | 0.99409 | -0.19944 | 21.1096
141 | 0.28621 | 0.1273 | -0.28621 | -0.12899 | 7.9169e-06 | -0.0016839 | 0.0090978 | 0.0091178 | 0.0091178 | 0.99395 | -0.20223 | 0.99392 | -0.20203 | 4.1445
142 | -5.5746 | -2.5195 | 5.5754 | 2.5204 | 0.00079948 | 0.00097562 | 0.17765 | 0.17764 | 0.17765 | 0.99409 | -0.19944 | 0.99429 | -0.19264 | 21.6642
143 | 0.28621 | 0.12899 | -0.28619 | -0.13188 | 1.3668e-05 | -0.0028896 | 0.0091178 | 0.0091527 | 0.0091527 | 0.99392 | -0.20203 | 0.99388 | -0.20167 | 4.1603
144 | -0.12274 | -0.059444 | 0.12274 | 0.058914 | 4.7006e-07 | -0.00052995 | 0.0039612 | 0.0039545 | 0.0039612 | 0.99383 | -0.20131 | 0.99384 | -0.20135 | 1.8005
145 | -0.12274 | -0.058914 | 0.12274 | 0.052834 | 5.2823e-06 | -0.00608 | 0.0039545 | 0.0038813 | 0.0039545 | 0.99384 | -0.20135 | 0.99388 | -0.20167 | 1.7975
146 | 0.16345 | 0.079043 | -0.16345 | -0.07916 | 5.038e-06 | -0.00011671 | 0.0052735 | 0.005275 | 0.005275 | 0.99388 | -0.20167 | 0.99384 | -0.20187 | 2.5119
147 | -0.054535 | -0.026413 | 0.054535 | 0.026343 | 3.3614e-07 | -7.0015e-05 | 0.0017701 | 0.0017692 | 0.0017701 | 0.98818 | -0.3856 | 0.98818 | -0.38555 | 0.84292
148 | -4.7344 | -2.1554 | 4.7353 | 2.1565 | 0.00094347 | 0.0010751 | 0.15183 | 0.15183 | 0.15183 | 0.98905 | -0.3661 | 0.98932 | -0.35671 | 18.5158
149 | -4.8776 | -2.2254 | 4.8781 | 2.2188 | 0.00041747 | -0.0065919 | 0.15644 | 0.15635 | 0.15644 | 0.98932 | -0.35671 | 0.98942 | -0.35483 | 18.5794
150 | 0.14311 | 0.069235 | -0.14311 | -0.06931 | 2.5139e-06 | -7.4298e-05 | 0.0046498 | 0.0046508 | 0.0046508 | 0.98697 | -0.38339 | 0.98696 | -0.3835 | 2.2147
151 | -0.27455 | -0.13289 | 0.27456 | 0.13281 | 1.1452e-05 | -8.6755e-05 | 0.0089214 | 0.0089202 | 0.0089214 | 0.98697 | -0.38339 | 0.98702 | -0.38311 | 4.2483
152 | -0.50901 | -0.24636 | 0.50903 | 0.24543 | 1.4636e-05 | -0.00092858 | 0.016539 | 0.016527 | 0.016539 | 0.98702 | -0.38311 | 0.98704 | -0.38336 | 7.5178
153 | 0.33243 | 0.1558 | -0.33243 | -0.1564 | 3.9459e-06 | -0.00059478 | 0.010737 | 0.010745 | 0.010745 | 0.98704 | -0.38336 | 0.98703 | -0.38326 | 4.8839
154 | -0.84146 | -0.40123 | 0.84153 | 0.39951 | 7.4537e-05 | -0.0017266 | 0.027264 | 0.027242 | 0.027264 | 0.98704 | -0.38336 | 0.98712 | -0.3841 | 12.3928
155 | -0.16582 | -0.076755 | 0.16582 | 0.075993 | 1.2466e-06 | -0.00076153 | 0.0053441 | 0.0053347 | 0.0053441 | 0.98702 | -0.38316 | 0.98703 | -0.38322 | 2.4291
156 | 0.16582 | 0.076755 | -0.16581 | -0.078672 | 3.1578e-06 | -0.0019171 | 0.0053441 | 0.0053679 | 0.0053679 | 0.98702 | -0.38316 | 0.987 | -0.383 | 2.4399
157 | -0.33242 | -0.15668 | 0.33243 | 0.1564 | 1.9083e-06 | -0.00028734 | 0.010748 | 0.010745 | 0.010748 | 0.98703 | -0.38322 | 0.98703 | -0.38326 | 4.8856
158 | 0.10671 | 0.050044 | -0.10671 | -0.050889 | 5.7784e-07 | -0.00084452 | 0.0034471 | 0.0034576 | 0.0034576 | 0.987 | -0.383 | 0.987 | -0.38296 | 1.5717
159 | 0.10671 | 0.050889 | -0.1067 | -0.05168 | 5.4425e-07 | -0.0007907 | 0.0034576 | 0.0034677 | 0.0034677 | 0.987 | -0.38296 | 0.98699 | -0.38292 | 1.5762
160 | 7.2495 | 3.1644 | -7.2493 | -3.1659 | 0.00022202 | -0.0015044 | 0.23063 | 0.23065 | 0.23065 | 0.9901 | -0.34072 | 0.99007 | -0.34143 | 27.3926
161 | -7.3599 | -3.2178 | 7.384 | 3.2496 | 0.024112 | 0.031765 | 0.2342 | 0.23416 | 0.2342 | 0.9901 | -0.34072 | 0.99455 | -0.18212 | 28.5609
162 | 7.2493 | 3.1659 | -7.2435 | -3.2054 | 0.00585 | -0.039489 | 0.23065 | 0.23117 | 0.23117 | 0.99007 | -0.34143 | 0.98913 | -0.35998 | 27.4552
163 | -7.9364 | -3.5172 | 7.937 | 3.5138 | 0.00060068 | -0.0033569 | 0.25197 | 0.25192 | 0.25197 | 0.99455 | -0.18212 | 0.99464 | -0.1804 | 29.9249
164 | 7.2435 | 3.2054 | -7.2433 | -3.2066 | 0.00017478 | -0.0011754 | 0.23117 | 0.23119 | 0.23119 | 0.98913 | -0.35998 | 0.9891 | -0.36053 | 27.4571
165 | -5.7074 | -2.5844 | 5.7089 | 2.5862 | 0.0014776 | 0.0018185 | 0.1819 | 0.1819 | 0.1819 | 0.99429 | -0.19264 | 0.99464 | -0.1804 | 22.1831
166 | -13.646 | -6.1 | 13.6493 | 6.0957 | 0.0033531 | -0.0042846 | 0.43382 | 0.43373 | 0.43382 | 0.99464 | -0.1804 | 0.99493 | -0.17487 | 51.522
167 | -0.070265 | -0.034031 | 0.070265 | 0.033289 | 2.0989e-07 | -0.00074203 | 0.0022538 | 0.0022445 | 0.0022538 | 1 | 2.5393e-05 | 1 | 0 | 1.0244
168 | 13.8044 | 6.215 | -13.7544 | -6.1446 | 0.04999 | 0.070484 | 0.43702 | 0.43705 | 0.43705 | 1 | 0 | 0.99503 | -0.17294 | 53.2983
169 | 13.6505 | 6.0942 | -13.6493 | -6.0957 | 0.0011687 | -0.0014951 | 0.4337 | 0.43373 | 0.43373 | 0.99503 | -0.17294 | 0.99493 | -0.17487 | 51.5117
170 | 7.0951 | 3.1348 | -7.0946 | -3.1387 | 0.00055597 | -0.003919 | 0.22639 | 0.22644 | 0.22644 | 0.9891 | -0.36053 | 0.98901 | -0.36231 | 26.893
171 | 0.15266 | 0.07146 | -0.15266 | -0.073817 | 3.2813e-06 | -0.0023563 | 0.00492 | 0.0049495 | 0.0049495 | 0.98901 | -0.36231 | 0.98899 | -0.36213 | 2.2498
172 | 0.15266 | 0.073817 | -0.15265 | -0.073934 | 4.4829e-06 | -0.00011708 | 0.0049495 | 0.004951 | 0.004951 | 0.98899 | -0.36213 | 0.98896 | -0.36233 | 2.3576
173 | -0.073341 | -0.035521 | 0.073341 | 0.035457 | 5.5627e-07 | -6.3603e-05 | 0.0023833 | 0.0023825 | 0.0023833 | 0.98704 | -0.38352 | 0.98705 | -0.38347 | 1.1349
174 | -0.073341 | -0.035457 | 0.073343 | 0.03164 | 1.219e-06 | -0.0038174 | 0.0023825 | 0.002336 | 0.0023825 | 0.98705 | -0.38347 | 0.98706 | -0.3836 | 1.0829
175 | -0.23238 | -0.10782 | 0.23239 | 0.10602 | 5.7837e-06 | -0.0017991 | 0.0074921 | 0.0074701 | 0.0074921 | 0.98706 | -0.3836 | 0.98709 | -0.38379 | 3.4055
176 | 0.15904 | 0.076182 | -0.15904 | -0.077025 | 1.289e-06 | -0.00084231 | 0.0051573 | 0.005168 | 0.005168 | 0.98706 | -0.3836 | 0.98706 | -0.38353 | 2.3491
177 | -0.23239 | -0.10602 | 0.23239 | 0.10455 | 4.7218e-06 | -0.0014767 | 0.0074701 | 0.0074522 | 0.0074701 | 0.98709 | -0.38379 | 0.9871 | -0.38394 | 3.3955
178 | -0.30783 | -0.14108 | 0.30784 | 0.13992 | 6.5727e-06 | -0.0011677 | 0.0099028 | 0.0098886 | 0.0099028 | 0.9871 | -0.38394 | 0.98712 | -0.3841 | 4.5013
179 | -1.1494 | -0.53942 | 1.1496 | 0.53946 | 0.0002585 | 3.9461e-05 | 0.03713 | 0.037128 | 0.03713 | 0.98712 | -0.3841 | 0.98736 | -0.38244 | 17.6809
180 | -1.4017 | -0.66156 | 1.4017 | 0.66146 | 1.2111e-05 | -9.9233e-05 | 0.045317 | 0.045316 | 0.045317 | 0.98736 | -0.38244 | 0.98737 | -0.38251 | 20.5989
181 | 4.8786 | 2.2101 | -4.8786 | -2.2105 | 2.4629e-05 | -0.00038985 | 0.15624 | 0.15625 | 0.15625 | 0.98955 | -0.35235 | 0.98955 | -0.35246 | 18.5568
182 | -5.0284 | -2.2827 | 5.0285 | 2.28 | 0.00017715 | -0.0026289 | 0.1611 | 0.16106 | 0.1611 | 0.98955 | -0.35235 | 0.98959 | -0.35157 | 19.1325
183 | 4.8786 | 2.2105 | -4.8781 | -2.2188 | 0.00052511 | -0.0083043 | 0.15625 | 0.15635 | 0.15635 | 0.98955 | -0.35246 | 0.98942 | -0.35483 | 18.5694

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 13.8887 | 6.2588

## res_load
| p_mw | q_mvar
0 | 0.11277 | 0.054616
1 | 0.20431 | 0.098953
2 | 0.068935 | 0.033387
3 | 0.15442 | 0.07479
4 | 0.070285 | 0.034041
5 | 0.12666 | 0.061343
6 | 0.082184 | 0.039803
7 | 0.089151 | 0.043178
8 | 0.12793 | 0.06196
9 | 0.14948 | 0.072394
10 | 0.068788 | 0.033316
11 | 0.13728 | 0.066489
12 | 0.15517 | 0.075154
13 | 0.11925 | 0.057754
14 | 0.15361 | 0.074399
15 | 0.089841 | 0.043512
16 | 0.13398 | 0.064888
17 | 0.066167 | 0.032046
18 | 0.15721 | 0.076139
19 | 0.15494 | 0.075039
20 | 0.13289 | 0.064362
21 | 0.099966 | 0.048416
22 | 0.14574 | 0.070583
23 | 0.14355 | 0.069522
24 | 0.14301 | 0.069265
25 | 0.51451 | 0.24919
26 | 0.1199 | 0.058071
27 | 0.093614 | 0.04534
28 | 0.14079 | 0.068185
29 | 0.091503 | 0.044317
30 | 0.083905 | 0.040637
31 | 0.53663 | 0.2599
32 | 0.070237 | 0.034017
33 | 0.08235 | 0.039884
34 | 0.1213 | 0.058748
35 | 0.063863 | 0.03093
36 | 0.11082 | 0.053672
37 | 0.094055 | 0.045553
38 | 0.12516 | 0.060619
39 | 0.11772 | 0.057013
40 | 0.084798 | 0.041069
41 | 0.13009 | 0.063006
42 | 0.15011 | 0.072703
43 | 0.086919 | 0.042097
44 | 0.099818 | 0.048344
45 | 0.11732 | 0.056819
46 | 0.2063 | 0.099916
47 | 0.080663 | 0.039067
48 | 0.098838 | 0.04787
49 | 0.12142 | 0.058809
50 | 0.064559 | 0.031267
51 | 0.15165 | 0.073447
52 | 0.17666 | 0.085559
53 | 0.10522 | 0.050959
54 | 0.10584 | 0.051259
55 | 1.384 | 0.67028
56 | 0.1355 | 0.065625
57 | 0.15016 | 0.072728
58 | 0.091569 | 0.044349
59 | 0.26415 | 0.12793
60 | 0.084464 | 0.040908
61 | 0.10062 | 0.048733
62 | 0.10773 | 0.052175
63 | 0.15478 | 0.074963
64 | 0.097062 | 0.047009
65 | 0.054101 | 0.026202
66 | 0.091402 | 0.044268
67 | 0.12274 | 0.059444
68 | 0.16345 | 0.07916
69 | 0.054535 | 0.026413
70 | 0.12568 | 0.060869
71 | 0.14231 | 0.068924
72 | 0.13144 | 0.063659
73 | 0.14311 | 0.06931
74 | 0.23445 | 0.11355
75 | 0.16661 | 0.080691
76 | 0.059108 | 0.028628
77 | 0.11038 | 0.053458
78 | 0.55242 | 0.26755
79 | 0.13201 | 0.063937
80 | 0.070265 | 0.034031
81 | 0.10392 | 0.050333
82 | 0.14816 | 0.071756
83 | 0.15265 | 0.073934
84 | 0.073341 | 0.035521
85 | 0.15904 | 0.077025
86 | 0.07544 | 0.036537
87 | 0.2521 | 0.1221
88 | 0.19002 | 0.092029
89 | 0.14976 | 0.07253
90 | 0.09682 | 0.046892
91 | 0.1067 | 0.05168
92 | 0.061829 | 0.029945

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1