## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_342_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_342_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_342_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_342_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_342_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_342_0_node_173 | 20 | n |  | TRUE
6 | bus_MV_342_0_node_5 | 20 | n |  | TRUE
7 | bus_MV_342_0_node_146 | 20 | n |  | TRUE
8 | bus_MV_342_0_node_7 | 20 | n |  | TRUE
9 | bus_MV_342_0_node_10 | 20 | n |  | TRUE
10 | bus_MV_342_0_node_6 | 20 | n |  | TRUE
11 | bus_MV_342_0_node_8 | 20 | n |  | TRUE
12 | bus_MV_342_0_node_11 | 20 | n |  | TRUE
13 | bus_MV_342_0_node_24 | 20 | n |  | TRUE
14 | bus_MV_342_0_node_14 | 20 | n |  | TRUE
15 | bus_MV_342_0_node_12 | 20 | n |  | TRUE
16 | bus_MV_342_0_node_150 | 20 | n |  | TRUE
17 | bus_MV_342_0_node_149 | 20 | n |  | TRUE
18 | bus_MV_342_0_node_151 | 20 | n |  | TRUE
19 | bus_MV_342_0_node_152 | 20 | n |  | TRUE
20 | bus_MV_342_0_node_153 | 20 | n |  | TRUE
21 | bus_MV_342_0_node_113 | 20 | n |  | TRUE
22 | bus_MV_342_0_node_154 | 20 | n |  | TRUE
23 | bus_MV_342_0_node_155 | 20 | n |  | TRUE
24 | bus_MV_342_0_node_111 | 20 | n |  | TRUE
25 | bus_MV_342_0_node_116 | 20 | n |  | TRUE
26 | bus_MV_342_0_node_29 | 20 | n |  | TRUE
27 | bus_MV_342_0_node_110 | 20 | n |  | TRUE
28 | bus_MV_342_0_node_114 | 20 | n |  | TRUE
29 | bus_MV_342_0_node_162 | 20 | n |  | TRUE
30 | bus_MV_342_0_node_115 | 20 | n |  | TRUE
31 | bus_MV_342_0_node_118 | 20 | n |  | TRUE
32 | bus_MV_342_0_node_179 | 20 | n |  | TRUE
33 | bus_MV_342_0_node_117 | 20 | n |  | TRUE
34 | bus_MV_342_0_node_15 | 20 | n |  | TRUE
35 | bus_MV_342_0_node_17 | 20 | n |  | TRUE
36 | bus_MV_342_0_node_16 | 20 | n |  | TRUE
37 | bus_MV_342_0_node_181 | 20 | n |  | TRUE
38 | bus_MV_342_0_node_19 | 20 | n |  | TRUE
39 | bus_MV_342_0_node_20 | 20 | n |  | TRUE
40 | bus_MV_342_0_node_18 | 20 | n |  | TRUE
41 | bus_MV_342_0_node_21 | 20 | n |  | TRUE
42 | bus_MV_342_0_node_23 | 20 | n |  | TRUE
43 | bus_MV_342_0_node_182 | 20 | n |  | TRUE
44 | bus_MV_342_0_node_51 | 20 | n |  | TRUE
45 | bus_MV_342_0_node_142 | 20 | n |  | TRUE
46 | bus_MV_342_0_node_140 | 20 | n |  | TRUE
47 | bus_MV_342_0_node_180 | 20 | n |  | TRUE
48 | bus_MV_342_0_node_168 | 20 | n |  | TRUE
49 | bus_MV_342_0_node_177 | 20 | n |  | TRUE
50 | bus_MV_342_0_node_141 | 20 | n |  | TRUE
51 | bus_MV_342_0_node_147 | 20 | n |  | TRUE
52 | bus_MV_342_0_node_25 | 20 | n |  | TRUE
53 | bus_MV_342_0_node_27 | 20 | n |  | TRUE
54 | bus_MV_342_0_node_156 | 20 | n |  | TRUE
55 | bus_MV_342_0_node_42 | 20 | n |  | TRUE
56 | bus_MV_342_0_node_108 | 20 | n |  | TRUE
57 | bus_MV_342_0_node_45 | 20 | n |  | TRUE
58 | bus_MV_342_0_node_28 | 20 | n |  | TRUE
59 | bus_MV_342_0_node_30 | 20 | n |  | TRUE
60 | bus_MV_342_0_node_109 | 20 | n |  | TRUE
61 | bus_MV_342_0_node_32 | 20 | n |  | TRUE
62 | bus_MV_342_0_node_36 | 20 | n |  | TRUE
63 | bus_MV_342_0_node_112 | 20 | n |  | TRUE
64 | bus_MV_342_0_node_31 | 20 | n |  | TRUE
65 | bus_MV_342_0_node_33 | 20 | n |  | TRUE
66 | bus_MV_342_0_node_34 | 20 | n |  | TRUE
67 | bus_MV_342_0_node_35 | 20 | n |  | TRUE
68 | bus_MV_342_0_node_37 | 20 | n |  | TRUE
69 | bus_MV_342_0_node_38 | 20 | n |  | TRUE
70 | bus_MV_342_0_node_39 | 20 | n |  | TRUE
71 | bus_MV_342_0_node_40 | 20 | n |  | TRUE
72 | bus_MV_342_0_node_41 | 20 | n |  | TRUE
73 | bus_MV_342_0_node_43 | 20 | n |  | TRUE
74 | bus_MV_342_0_node_44 | 20 | n |  | TRUE
75 | bus_MV_342_0_node_174 | 20 | n |  | TRUE
76 | bus_MV_342_0_node_50 | 20 | n |  | TRUE
77 | bus_MV_342_0_node_46 | 20 | n |  | TRUE
78 | bus_MV_342_0_node_48 | 20 | n |  | TRUE
79 | bus_MV_342_0_node_49 | 20 | n |  | TRUE
80 | bus_MV_342_0_node_52 | 20 | n |  | TRUE
81 | bus_MV_342_0_node_54 | 20 | n |  | TRUE
82 | bus_MV_342_0_node_53 | 20 | n |  | TRUE
83 | bus_MV_342_0_node_57 | 20 | n |  | TRUE
84 | bus_MV_342_0_node_56 | 20 | n |  | TRUE
85 | bus_MV_342_0_node_55 | 20 | n |  | TRUE
86 | bus_MV_342_0_node_157 | 20 | n |  | TRUE
87 | bus_MV_342_0_node_158 | 20 | n |  | TRUE
88 | bus_MV_342_0_node_58 | 20 | n |  | TRUE
89 | bus_MV_342_0_node_103 | 20 | n |  | TRUE
90 | bus_MV_342_0_node_59 | 20 | n |  | TRUE
91 | bus_MV_342_0_node_60 | 20 | n |  | TRUE
92 | bus_MV_342_0_node_104 | 20 | n |  | TRUE
93 | bus_MV_342_0_node_167 | 20 | n |  | TRUE
94 | bus_MV_342_0_node_81 | 20 | n |  | TRUE
95 | bus_MV_342_0_node_166 | 20 | n |  | TRUE
96 | bus_MV_342_0_node_62 | 20 | n |  | TRUE
97 | bus_MV_342_0_node_61 | 20 | n |  | TRUE
98 | bus_MV_342_0_node_172 | 20 | n |  | TRUE
99 | bus_MV_342_0_node_68 | 20 | n |  | TRUE
100 | bus_MV_342_0_node_63 | 20 | n |  | TRUE
101 | bus_MV_342_0_node_65 | 20 | n |  | TRUE
102 | bus_MV_342_0_node_64 | 20 | n |  | TRUE
103 | bus_MV_342_0_node_67 | 20 | n |  | TRUE
104 | bus_MV_342_0_node_66 | 20 | n |  | TRUE
105 | bus_MV_342_0_node_164 | 20 | n |  | TRUE
106 | bus_MV_342_0_node_163 | 20 | n |  | TRUE
107 | bus_MV_342_0_node_175 | 20 | n |  | TRUE
108 | bus_MV_342_0_node_169 | 20 | n |  | TRUE
109 | bus_MV_342_0_node_69 | 20 | n |  | TRUE
110 | bus_MV_342_0_node_71 | 20 | n |  | TRUE
111 | bus_MV_342_0_node_70 | 20 | n |  | TRUE
112 | bus_MV_342_0_node_74 | 20 | n |  | TRUE
113 | bus_MV_342_0_node_72 | 20 | n |  | TRUE
114 | bus_MV_342_0_node_73 | 20 | n |  | TRUE
115 | bus_MV_342_0_node_97 | 20 | n |  | TRUE
116 | bus_MV_342_0_node_107 | 20 | n |  | TRUE
117 | bus_MV_342_0_node_106 | 20 | n |  | TRUE
118 | bus_MV_342_0_node_143 | 20 | n |  | TRUE
119 | bus_MV_342_0_node_144 | 20 | n |  | TRUE
120 | bus_MV_342_0_node_99 | 20 | n |  | TRUE
121 | bus_MV_342_0_node_79 | 20 | n |  | TRUE
122 | bus_MV_342_0_node_75 | 20 | n |  | TRUE
123 | bus_MV_342_0_node_76 | 20 | n |  | TRUE
124 | bus_MV_342_0_node_78 | 20 | n |  | TRUE
125 | bus_MV_342_0_node_77 | 20 | n |  | TRUE
126 | bus_MV_342_0_node_161 | 20 | n |  | TRUE
127 | bus_MV_342_0_node_89 | 20 | n |  | TRUE
128 | bus_MV_342_0_node_160 | 20 | n |  | TRUE
129 | bus_MV_342_0_node_85 | 20 | n |  | TRUE
130 | bus_MV_342_0_node_80 | 20 | n |  | TRUE
131 | bus_MV_342_0_node_82 | 20 | n |  | TRUE
132 | bus_MV_342_0_node_84 | 20 | n |  | TRUE
133 | bus_MV_342_0_node_83 | 20 | n |  | TRUE
134 | bus_MV_342_0_node_88 | 20 | n |  | TRUE
135 | bus_MV_342_0_node_90 | 20 | n |  | TRUE
136 | bus_MV_342_0_node_87 | 20 | n |  | TRUE
137 | bus_MV_342_0_node_91 | 20 | n |  | TRUE
138 | bus_MV_342_0_node_92 | 20 | n |  | TRUE
139 | bus_MV_342_0_node_176 | 20 | n |  | TRUE
140 | bus_MV_342_0_node_96 | 20 | n |  | TRUE
141 | bus_MV_342_0_node_102 | 20 | n |  | TRUE
142 | bus_MV_342_0_node_93 | 20 | n |  | TRUE
143 | bus_MV_342_0_node_94 | 20 | n |  | TRUE
144 | bus_MV_342_0_node_95 | 20 | n |  | TRUE
145 | bus_MV_342_0_node_178 | 20 | n |  | TRUE
146 | bus_MV_342_0_node_98 | 20 | n |  | TRUE
147 | bus_MV_342_0_node_100 | 20 | n |  | TRUE
148 | bus_MV_342_0_node_101 | 20 | n |  | TRUE
149 | bus_MV_342_0_node_159 | 20 | n |  | TRUE
150 | bus_MV_342_0_node_105 | 20 | n |  | TRUE
151 | bus_MV_342_0_node_119 | 20 | n |  | TRUE
152 | bus_MV_342_0_node_121 | 20 | n |  | TRUE
153 | bus_MV_342_0_node_120 | 20 | n |  | TRUE
154 | bus_MV_342_0_node_123 | 20 | n |  | TRUE
155 | bus_MV_342_0_node_122 | 20 | n |  | TRUE
156 | bus_MV_342_0_node_165 | 20 | n |  | TRUE
157 | bus_MV_342_0_node_138 | 20 | n |  | TRUE
158 | bus_MV_342_0_node_135 | 20 | n |  | TRUE
159 | bus_MV_342_0_node_126 | 20 | n |  | TRUE
160 | bus_MV_342_0_node_124 | 20 | n |  | TRUE
161 | bus_MV_342_0_node_125 | 20 | n |  | TRUE
162 | bus_MV_342_0_node_127 | 20 | n |  | TRUE
163 | bus_MV_342_0_node_128 | 20 | n |  | TRUE
164 | bus_MV_342_0_node_129 | 20 | n |  | TRUE
165 | bus_MV_342_0_node_132 | 20 | n |  | TRUE
166 | bus_MV_342_0_node_136 | 20 | n |  | TRUE
167 | bus_MV_342_0_node_130 | 20 | n |  | TRUE
168 | bus_MV_342_0_node_131 | 20 | n |  | TRUE
169 | bus_MV_342_0_node_137 | 20 | n |  | TRUE
170 | bus_MV_342_0_node_133 | 20 | n |  | TRUE
171 | bus_MV_342_0_node_134 | 20 | n |  | TRUE
172 | bus_MV_342_0_node_139 | 20 | n |  | TRUE
173 | bus_MV_342_0_node_145 | 20 | n |  | TRUE
174 | bus_MV_342_0_node_171 | 20 | n |  | TRUE
175 | bus_MV_342_0_node_148 | 20 | n |  | TRUE
176 | bus_MV_342_0_node_170 | 20 | n |  | TRUE
177 | bus_HV_342_0_node_11 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_342_0_load_0 | 0 | 0.16151 | 0.078225 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_342_0_load_173 | 5 | 0.11928 | 0.057772 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_342_0_load_5 | 6 | 0.15024 | 0.072762 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_342_0_load_6 | 10 | 0.11156 | 0.054031 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_342_0_load_24 | 13 | 0.1474 | 0.07139 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_342_0_load_12 | 15 | 0.15386 | 0.074519 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_342_0_load_150 | 16 | 0.075912 | 0.036766 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_342_0_load_149 | 17 | 0.13974 | 0.067678 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_342_0_load_152 | 19 | 0.091127 | 0.044135 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_342_0_load_154 | 22 | 0.076911 | 0.03725 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_342_0_load_155 | 23 | 0.1358 | 0.065773 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_342_0_load_116 | 25 | 0.13653 | 0.066122 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_342_0_load_162 | 29 | 0.083393 | 0.040389 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_342_0_load_118 | 31 | 0.07432 | 0.035995 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_342_0_load_179 | 32 | 0.15976 | 0.077374 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_342_0_load_15 | 34 | 0.1122 | 0.054343 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_342_0_load_181 | 37 | 0.1579 | 0.076474 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_342_0_load_23 | 42 | 0.13517 | 0.065464 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_342_0_load_51 | 44 | 0.12125 | 0.058726 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_342_0_load_140 | 46 | 0.15625 | 0.075675 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_342_0_load_180 | 47 | 0.067985 | 0.032927 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_342_0_load_168 | 48 | 0.1521 | 0.073663 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_342_0_load_177 | 49 | 0.13495 | 0.065357 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_342_0_load_141 | 50 | 0.29908 | 0.14485 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_342_0_load_25 | 52 | 0.089658 | 0.043423 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_342_0_load_42 | 55 | 0.068243 | 0.033052 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_342_0_load_108 | 56 | 0.086691 | 0.041987 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_342_0_load_28 | 58 | 0.11233 | 0.054405 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_342_0_load_109 | 60 | 0.14297 | 0.069244 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_342_0_load_36 | 62 | 0.15089 | 0.073077 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_342_0_load_112 | 63 | 0.15993 | 0.077458 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_342_0_load_31 | 64 | 0.16269 | 0.078797 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_342_0_load_33 | 65 | 0.25786 | 0.12489 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_342_0_load_37 | 68 | 0.09452 | 0.045778 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_342_0_load_40 | 71 | 0.10797 | 0.052293 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_342_0_load_43 | 73 | 0.13347 | 0.064644 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_342_0_load_174 | 75 | 0.1043 | 0.050516 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_342_0_load_46 | 77 | 0.13302 | 0.064422 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_342_0_load_52 | 80 | 0.15673 | 0.075906 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_342_0_load_157 | 86 | 0.44533 | 0.21568 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_342_0_load_158 | 87 | 0.20348 | 0.098549 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_342_0_load_58 | 88 | 0.10864 | 0.052618 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_342_0_load_103 | 89 | 0.071522 | 0.03464 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_342_0_load_167 | 93 | 0.054637 | 0.026462 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_342_0_load_166 | 95 | 0.051343 | 0.024867 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_342_0_load_61 | 97 | 0.14883 | 0.072083 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_342_0_load_172 | 98 | 0.11699 | 0.056663 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_342_0_load_63 | 100 | 0.059052 | 0.0286 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_342_0_load_164 | 105 | 0.13482 | 0.065296 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_342_0_load_163 | 106 | 0.17503 | 0.084769 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_342_0_load_175 | 107 | 0.083143 | 0.040268 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_342_0_load_169 | 108 | 0.15741 | 0.076239 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_342_0_load_69 | 109 | 0.1122 | 0.054342 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_342_0_load_97 | 115 | 0.15738 | 0.076221 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_342_0_load_107 | 116 | 0.15689 | 0.075983 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_342_0_load_106 | 117 | 0.1377 | 0.066689 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_342_0_load_143 | 118 | 0.78221 | 0.37884 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_342_0_load_75 | 122 | 0.068028 | 0.032948 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_342_0_load_161 | 126 | 0.11465 | 0.055526 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_342_0_load_89 | 127 | 0.13209 | 0.063976 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_342_0_load_85 | 129 | 0.11199 | 0.054241 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_342_0_load_80 | 130 | 0.1598 | 0.077396 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_342_0_load_83 | 133 | 0.10069 | 0.048766 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_342_0_load_90 | 135 | 0.14862 | 0.071978 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_342_0_load_91 | 137 | 0.13054 | 0.063221 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_342_0_load_176 | 139 | 0.15284 | 0.074022 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_342_0_load_95 | 144 | 0.13646 | 0.066091 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_342_0_load_178 | 145 | 0.19161 | 0.092803 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_342_0_load_98 | 146 | 0.072237 | 0.034986 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_342_0_load_159 | 149 | 0.17621 | 0.085342 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_342_0_load_105 | 150 | 0.15758 | 0.076318 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_342_0_load_119 | 151 | 0.15629 | 0.075696 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_342_0_load_165 | 156 | 0.071207 | 0.034487 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_342_0_load_138 | 157 | 0.1636 | 0.079235 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_342_0_load_135 | 158 | 0.13303 | 0.064429 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_342_0_load_124 | 160 | 0.15719 | 0.076133 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_342_0_load_127 | 162 | 0.064351 | 0.031166 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_342_0_load_136 | 166 | 0.10074 | 0.04879 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_342_0_load_130 | 167 | 0.063729 | 0.030866 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_342_0_load_137 | 169 | 0.090741 | 0.043948 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_342_0_load_139 | 172 | 0.12572 | 0.06089 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_342_0_load_171 | 174 | 0.1265 | 0.061268 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_342_0_load_170 | 176 | 0.13594 | 0.065839 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_342_0_line_0 |  | 0 | 1 | 0.00817 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
1 | MV_342_0_line_1 |  | 0 | 2 | 0.061746 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
2 | MV_342_0_line_2 |  | 1 | 3 | 0.10257 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
3 | MV_342_0_line_3 |  | 2 | 4 | 0.086468 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
4 | MV_342_0_line_4 |  | 3 | 5 | 0.03627 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
5 | MV_342_0_line_5 |  | 4 | 6 | 0.094135 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
6 | MV_342_0_line_6 |  | 5 | 7 | 0.027437 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
7 | MV_342_0_line_7 |  | 6 | 8 | 0.38733 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
8 | MV_342_0_line_8 |  | 6 | 9 | 0.25167 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
9 | MV_342_0_line_9 |  | 7 | 51 | 0.27406 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
10 | MV_342_0_line_10 |  | 7 | 175 | 0.36675 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
11 | MV_342_0_line_11 |  | 8 | 10 | 0.008618 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
12 | MV_342_0_line_12 |  | 9 | 13 | 0.064332 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_342_0_line_13 |  | 10 | 11 | 0.058346 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
14 | MV_342_0_line_14 |  | 11 | 12 | 0.41943 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
15 | MV_342_0_line_15 |  | 12 | 14 | 0.21122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_342_0_line_16 |  | 12 | 15 | 0.048031 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_342_0_line_17 |  | 14 | 16 | 0.055496 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_342_0_line_18 |  | 16 | 17 | 0.039866 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_342_0_line_19 |  | 17 | 18 | 0.089212 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_342_0_line_20 |  | 18 | 19 | 0.054749 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_342_0_line_21 |  | 18 | 20 | 0.23988 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_342_0_line_22 |  | 18 | 21 | 2.3413 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_342_0_line_23 |  | 20 | 22 | 0.042899 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_342_0_line_24 |  | 21 | 28 | 0.30904 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_342_0_line_25 |  | 21 | 63 | 0.029119 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_342_0_line_26 |  | 22 | 23 | 0.0081429 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_342_0_line_27 |  | 24 | 25 | 0.068453 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_342_0_line_28 |  | 24 | 26 | 2.6446 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_342_0_line_29 |  | 24 | 27 | 0.46756 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_342_0_line_30 |  | 25 | 33 | 0.018144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_342_0_line_31 |  | 26 | 59 | 0.3588 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_342_0_line_32 |  | 26 | 58 | 0.10018 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_342_0_line_33 |  | 27 | 60 | 0.014618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_342_0_line_34 |  | 28 | 29 | 0.042888 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_342_0_line_35 |  | 28 | 30 | 0.30842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_342_0_line_36 |  | 28 | 31 | 0.023337 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_342_0_line_37 |  | 30 | 32 | 0.041534 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_342_0_line_38 |  | 31 | 33 | 0.03609 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_342_0_line_39 |  | 34 | 35 | 0.081395 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
40 | MV_342_0_line_40 |  | 34 | 36 | 0.095465 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
41 | MV_342_0_line_41 |  | 34 | 37 | 0.35152 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
42 | MV_342_0_line_42 |  | 35 | 38 | 0.19011 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
43 | MV_342_0_line_43 |  | 35 | 39 | 0.38077 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
44 | MV_342_0_line_44 |  | 36 | 40 | 0.044942 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
45 | MV_342_0_line_45 |  | 37 | 43 | 0.048889 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
46 | MV_342_0_line_46 |  | 38 | 45 | 0.17183 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
47 | MV_342_0_line_47 |  | 38 | 46 | 0.052413 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_342_0_line_48 |  | 39 | 47 | 0.02659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_342_0_line_49 |  | 40 | 41 | 0.27356 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
50 | MV_342_0_line_50 |  | 40 | 42 | 0.032553 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
51 | MV_342_0_line_51 |  | 41 | 48 | 0.030709 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
52 | MV_342_0_line_52 |  | 43 | 44 | 2.7377 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
53 | MV_342_0_line_53 |  | 44 | 79 | 0.089966 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
54 | MV_342_0_line_54 |  | 45 | 49 | 0.061857 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
55 | MV_342_0_line_55 |  | 46 | 50 | 0.061245 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_342_0_line_56 |  | 48 | 51 | 0.019936 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
57 | MV_342_0_line_57 |  | 52 | 53 | 0.099085 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_342_0_line_58 |  | 53 | 54 | 1.1804 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_342_0_line_59 |  | 54 | 55 | 0.090833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_342_0_line_60 |  | 55 | 72 | 0.061259 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_342_0_line_61 |  | 56 | 57 | 2.5216 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
62 | MV_342_0_line_62 |  | 57 | 75 | 0.0253 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
63 | MV_342_0_line_63 |  | 57 | 74 | 0.19517 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_342_0_line_64 |  | 59 | 61 | 0.31285 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_342_0_line_65 |  | 59 | 62 | 0.042293 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_342_0_line_66 |  | 61 | 64 | 0.082187 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_342_0_line_67 |  | 64 | 65 | 0.025561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_342_0_line_68 |  | 64 | 66 | 0.064194 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_342_0_line_69 |  | 66 | 67 | 0.32504 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_342_0_line_70 |  | 67 | 68 | 0.042893 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_342_0_line_71 |  | 68 | 69 | 0.012098 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_342_0_line_72 |  | 69 | 70 | 0.30526 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_342_0_line_73 |  | 70 | 71 | 0.082317 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_342_0_line_74 |  | 71 | 72 | 0.00927 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_342_0_line_75 |  | 73 | 74 | 0.032742 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_342_0_line_76 |  | 75 | 76 | 0.024107 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
77 | MV_342_0_line_77 |  | 76 | 78 | 0.29669 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
78 | MV_342_0_line_78 |  | 77 | 78 | 0.13931 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
79 | MV_342_0_line_79 |  | 77 | 79 | 0.30775 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
80 | MV_342_0_line_80 |  | 80 | 81 | 0.037963 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
81 | MV_342_0_line_81 |  | 80 | 82 | 0.16559 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
82 | MV_342_0_line_82 |  | 81 | 83 | 0.37515 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
83 | MV_342_0_line_83 |  | 82 | 84 | 0.22616 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
84 | MV_342_0_line_84 |  | 83 | 88 | 0.087048 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
85 | MV_342_0_line_85 |  | 84 | 87 | 0.078064 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
86 | MV_342_0_line_86 |  | 84 | 85 | 0.12153 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
87 | MV_342_0_line_87 |  | 85 | 86 | 0.070281 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
88 | MV_342_0_line_88 |  | 87 | 89 | 1.5383 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
89 | MV_342_0_line_89 |  | 88 | 90 | 0.16039 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
90 | MV_342_0_line_90 |  | 89 | 136 | 0.067107 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
91 | MV_342_0_line_91 |  | 90 | 91 | 0.35886 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
92 | MV_342_0_line_92 |  | 91 | 96 | 0.23983 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
93 | MV_342_0_line_93 |  | 91 | 97 | 0.069778 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_342_0_line_94 |  | 92 | 93 | 0.031129 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
95 | MV_342_0_line_95 |  | 92 | 94 | 0.93522 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
96 | MV_342_0_line_96 |  | 93 | 95 | 0.26978 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
97 | MV_342_0_line_97 |  | 94 | 133 | 0.030973 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_342_0_line_98 |  | 94 | 130 | 0.12161 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
99 | MV_342_0_line_99 |  | 96 | 98 | 0.024818 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
100 | MV_342_0_line_100 |  | 98 | 99 | 0.068335 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
101 | MV_342_0_line_101 |  | 99 | 103 | 0.25312 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
102 | MV_342_0_line_102 |  | 100 | 101 | 0.002941 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
103 | MV_342_0_line_103 |  | 100 | 102 | 0.32308 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
104 | MV_342_0_line_104 |  | 101 | 103 | 0.60514 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
105 | MV_342_0_line_105 |  | 102 | 104 | 1.0102 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
106 | MV_342_0_line_106 |  | 103 | 108 | 0.050747 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
107 | MV_342_0_line_107 |  | 104 | 105 | 0.20836 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
108 | MV_342_0_line_108 |  | 105 | 106 | 0.053527 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
109 | MV_342_0_line_109 |  | 106 | 107 | 1.8004 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
110 | MV_342_0_line_110 |  | 107 | 171 | 0.011267 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
111 | MV_342_0_line_111 |  | 109 | 110 | 0.059318 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
112 | MV_342_0_line_112 |  | 109 | 111 | 0.14361 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
113 | MV_342_0_line_113 |  | 110 | 112 | 0.37955 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
114 | MV_342_0_line_114 |  | 111 | 113 | 0.26809 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
115 | MV_342_0_line_115 |  | 111 | 114 | 0.73464 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
116 | MV_342_0_line_116 |  | 112 | 117 | 0.11839 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
117 | MV_342_0_line_117 |  | 113 | 115 | 0.080368 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
118 | MV_342_0_line_118 |  | 114 | 116 | 0.099862 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
119 | MV_342_0_line_119 |  | 115 | 121 | 0.008987 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
120 | MV_342_0_line_120 |  | 118 | 119 | 0.081269 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
121 | MV_342_0_line_121 |  | 118 | 120 | 1.1826 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
122 | MV_342_0_line_122 |  | 119 | 173 | 0.22761 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
123 | MV_342_0_line_123 |  | 120 | 147 | 0.58498 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
124 | MV_342_0_line_124 |  | 120 | 146 | 0.057943 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
125 | MV_342_0_line_125 |  | 121 | 124 | 0.24077 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
126 | MV_342_0_line_126 |  | 122 | 123 | 0.10426 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
127 | MV_342_0_line_127 |  | 123 | 124 | 0.29557 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
128 | MV_342_0_line_128 |  | 124 | 127 | 0.020187 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
129 | MV_342_0_line_129 |  | 124 | 125 | 0.15084 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
130 | MV_342_0_line_130 |  | 125 | 126 | 0.062363 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
131 | MV_342_0_line_131 |  | 126 | 128 | 0.045416 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
132 | MV_342_0_line_132 |  | 127 | 129 | 0.05606 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
133 | MV_342_0_line_133 |  | 128 | 147 | 0.10282 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
134 | MV_342_0_line_134 |  | 129 | 132 | 0.020794 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
135 | MV_342_0_line_135 |  | 130 | 131 | 0.013438 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
136 | MV_342_0_line_136 |  | 131 | 132 | 0.22601 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
137 | MV_342_0_line_137 |  | 132 | 134 | 0.025998 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
138 | MV_342_0_line_138 |  | 134 | 135 | 0.017989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_342_0_line_139 |  | 136 | 137 | 0.28812 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
140 | MV_342_0_line_140 |  | 137 | 138 | 0.059616 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
141 | MV_342_0_line_141 |  | 138 | 142 | 0.002384 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
142 | MV_342_0_line_142 |  | 138 | 143 | 0.066103 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
143 | MV_342_0_line_143 |  | 139 | 140 | 0.10641 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
144 | MV_342_0_line_144 |  | 139 | 141 | 0.044954 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
145 | MV_342_0_line_145 |  | 140 | 142 | 0.19607 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
146 | MV_342_0_line_146 |  | 141 | 147 | 0.36737 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
147 | MV_342_0_line_147 |  | 142 | 144 | 0.04993 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
148 | MV_342_0_line_148 |  | 143 | 145 | 0.020998 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
149 | MV_342_0_line_149 |  | 147 | 148 | 0.18052 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
150 | MV_342_0_line_150 |  | 147 | 149 | 0.10398 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
151 | MV_342_0_line_151 |  | 148 | 150 | 0.070106 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
152 | MV_342_0_line_152 |  | 151 | 152 | 0.18945 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
153 | MV_342_0_line_153 |  | 151 | 153 | 0.26953 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
154 | MV_342_0_line_154 |  | 152 | 154 | 1.2113 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
155 | MV_342_0_line_155 |  | 153 | 155 | 0.27091 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
156 | MV_342_0_line_156 |  | 154 | 158 | 0.02269 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
157 | MV_342_0_line_157 |  | 155 | 156 | 0.37309 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
158 | MV_342_0_line_158 |  | 156 | 157 | 0.89291 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
159 | MV_342_0_line_159 |  | 157 | 169 | 0.044537 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
160 | MV_342_0_line_160 |  | 158 | 159 | 0.070385 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
161 | MV_342_0_line_161 |  | 159 | 161 | 0.26348 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
162 | MV_342_0_line_162 |  | 160 | 161 | 0.061323 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
163 | MV_342_0_line_163 |  | 162 | 163 | 0.030546 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
164 | MV_342_0_line_164 |  | 163 | 164 | 0.22688 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
165 | MV_342_0_line_165 |  | 163 | 165 | 1.2611 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
166 | MV_342_0_line_166 |  | 164 | 166 | 0.019494 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
167 | MV_342_0_line_167 |  | 165 | 167 | 0.12463 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
168 | MV_342_0_line_168 |  | 166 | 169 | 0.16476 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
169 | MV_342_0_line_169 |  | 167 | 168 | 0.10122 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
170 | MV_342_0_line_170 |  | 168 | 170 | 1.175 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
171 | MV_342_0_line_171 |  | 168 | 171 | 1.2028 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
172 | MV_342_0_line_172 |  | 170 | 172 | 0.020496 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
173 | MV_342_0_line_173 |  | 173 | 174 | 0.04184 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
174 | MV_342_0_line_174 |  | 173 | 175 | 1.2229 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
175 | MV_342_0_line_175 |  | 175 | 176 | 0.031994 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_342_0_trafo_11 | 25 MVA 110/20 kV | 177 | 12 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2576838.3583 | 1252783.7263
1 | 2576830.2516 | 1252784.9033
2 | 2576899.7615 | 1252775.7247
3 | 2576742.9142 | 1252790.773
4 | 2576982.4073 | 1252750.8631
5 | 2576706.7488 | 1252786.8575
6 | 2576990.2358 | 1252844.6724
7 | 2576679.7834 | 1252781.5938
8 | 2577209.6121 | 1253163.8878
9 | 2576921.1323 | 1253086.6691
10 | 2577216.5131 | 1253169.0757
11 | 2577263.2903 | 1253204.0073
12 | 2577624.303 | 1253237.5938
13 | 2576903.075 | 1253147.7691
14 | 2577834.8846 | 1253221.188
15 | 2577638.5903 | 1253278.7001
16 | 2577846.7635 | 1253272.2772
17 | 2577886.3754 | 1253271.6776
18 | 2577969.5359 | 1253303.6493
19 | 2577970.4369 | 1253249.4078
20 | 2578112.5495 | 1253247.7133
21 | 2578270.983 | 1255625.4539
22 | 2578069.8076 | 1253251.3798
23 | 2578061.6946 | 1253252.0757
24 | 2578191.0418 | 1255754.2129
25 | 2578122.4162 | 1255754.9899
26 | 2578687.4996 | 1258351.7895
27 | 2578567.2246 | 1255644.5825
28 | 2578094.0906 | 1255696.3224
29 | 2578135.6989 | 1255690.4752
30 | 2577967.0023 | 1255705.402
31 | 2578098.1008 | 1255719.3119
32 | 2578007.489 | 1255696.1335
33 | 2578104.218 | 1255754.8795
34 | 2576212.0816 | 1252708.5456
35 | 2576137.9002 | 1252674.5671
36 | 2576174.9358 | 1252796.487
37 | 2576168.9503 | 1253057.4062
38 | 2576225.5323 | 1252509.4042
39 | 2575845.0008 | 1252588.7685
40 | 2576212.8436 | 1252820.7502
41 | 2576471.4905 | 1252892.5941
42 | 2576242.9067 | 1252808.2652
43 | 2576134.4588 | 1253092.0686
44 | 2574473.3389 | 1255268.238
45 | 2576307.5828 | 1252435.6699
46 | 2576174.3049 | 1252500.5791
47 | 2575855.457 | 1252564.3096
48 | 2576497.9651 | 1252877.0339
49 | 2576367.3269 | 1252419.642
50 | 2576114.6875 | 1252486.5544
51 | 2576513.6705 | 1252864.6965
52 | 2577258.2991 | 1260267.8451
53 | 2577340.7091 | 1260212.501
54 | 2577935.7157 | 1259193.0598
55 | 2577972.4981 | 1259110.4644
56 | 2574648.2336 | 1258505.7245
57 | 2574282.5685 | 1256010.7316
58 | 2578786.5247 | 1258335.7213
59 | 2578458.2601 | 1258477.3412
60 | 2578572.7566 | 1255656.0367
61 | 2578193.981 | 1258405.9869
62 | 2578500.5313 | 1258478.71
63 | 2578259.5278 | 1255652.2251
64 | 2578149.2192 | 1258474.9149
65 | 2578127.7822 | 1258460.9937
66 | 2578112.2181 | 1258526.7385
67 | 2578196.8873 | 1258706.4353
68 | 2578158.2269 | 1258725.0133
69 | 2578155.8437 | 1258736.8746
70 | 2578018.6643 | 1258969.3423
71 | 2578002.3071 | 1259049.8358
72 | 2578004.8805 | 1259058.7434
73 | 2574150.427 | 1256005.4102
74 | 2574180.9116 | 1255993.464
75 | 2574292.6254 | 1255987.5055
76 | 2574279.468 | 1255967.2826
77 | 2574372.4083 | 1255641.2368
78 | 2574449.9737 | 1255755.7106
79 | 2574489.2504 | 1255356.5283
80 | 2578771.221 | 1251075.5871
81 | 2578750.1121 | 1251046.6886
82 | 2578688.6866 | 1251219.1454
83 | 2578819.9635 | 1250806.6914
84 | 2578486.1283 | 1251220.6703
85 | 2578500.2305 | 1251300.3378
86 | 2578569.8601 | 1251309.8772
87 | 2578426.5016 | 1251254.3965
88 | 2578883.6584 | 1250747.1798
89 | 2577134.0682 | 1250420.1848
90 | 2578998.1232 | 1250634.8311
91 | 2579239.9854 | 1250876.5667
92 | 2577322.1215 | 1249560.0531
93 | 2577325.1433 | 1249529.1435
94 | 2576526.8977 | 1250052.2493
95 | 2577347.492 | 1249260.2937
96 | 2579382.8803 | 1250764.2811
97 | 2579203.6096 | 1250935.6557
98 | 2579392.643 | 1250741.4543
99 | 2579325.0928 | 1250734.0191
100 | 2579660.1292 | 1250159.713
101 | 2579658.9231 | 1250162.3966
102 | 2579806.3349 | 1249871.6119
103 | 2579314.046 | 1250567.1598
104 | 2580745.1789 | 1249842.6547
105 | 2580952.6099 | 1249861.0229
106 | 2581005.9414 | 1249865.2624
107 | 2582781.0956 | 1250165.8038
108 | 2579269.9892 | 1250541.9758
109 | 2575761.125 | 1250736.0138
110 | 2575718.5663 | 1250777.4603
111 | 2575871.9716 | 1250644.7109
112 | 2575445.1536 | 1250887.4078
113 | 2576087.1524 | 1250514.0609
114 | 2575823.3934 | 1250320.8863
115 | 2576156.8791 | 1250473.7413
116 | 2575791.5654 | 1250226.2325
117 | 2575326.4638 | 1250883.7336
118 | 2576813.1084 | 1252180.338
119 | 2576889.5906 | 1252207.7783
120 | 2576410.0139 | 1251068.6035
121 | 2576164.6354 | 1250469.1626
122 | 2576161.7173 | 1250281.2401
123 | 2576214.4742 | 1250191.3129
124 | 2576372.0727 | 1250346.9375
125 | 2576338.4611 | 1250475.3785
126 | 2576336.8542 | 1250537.7147
127 | 2576390.0693 | 1250337.7484
128 | 2576335.1869 | 1250583.0955
129 | 2576442.8028 | 1250318.7253
130 | 2576566.1636 | 1250167.3464
131 | 2576565.1599 | 1250180.7147
132 | 2576462.1565 | 1250310.9764
133 | 2576502.5987 | 1250033.5226
134 | 2576486.7135 | 1250303.796
135 | 2576504.6565 | 1250301.9122
136 | 2577072.3168 | 1250393.5402
137 | 2576842.9399 | 1250567.8942
138 | 2576826.1888 | 1250625.1085
139 | 2576670.1496 | 1250853.1393
140 | 2576714.6098 | 1250756.467
141 | 2576654.806 | 1250895.4055
142 | 2576823.8841 | 1250624.4727
143 | 2576889.9334 | 1250642.6034
144 | 2576800.5592 | 1250668.6195
145 | 2576895.349 | 1250622.3134
146 | 2576394.0317 | 1251012.9086
147 | 2576408.2908 | 1250654.7054
148 | 2576313.2368 | 1250654.5415
149 | 2576433.2432 | 1250553.8103
150 | 2576243.0311 | 1250650.6322
151 | 2581411.8767 | 1252642.1815
152 | 2581290.0565 | 1252545.5032
153 | 2581413.1645 | 1252911.7105
154 | 2580230.9502 | 1252964.5903
155 | 2581436.5973 | 1253181.5257
156 | 2581801.3706 | 1253235.8943
157 | 2582339.749 | 1252523.5512
158 | 2580209.2119 | 1252971.1119
159 | 2580139.0537 | 1252976.7404
160 | 2580008.0354 | 1253186.5883
161 | 2580024.7146 | 1253127.9931
162 | 2582798.707 | 1252595.9417
163 | 2582782.4034 | 1252570.9506
164 | 2582561.3174 | 1252560.8717
165 | 2582867.5718 | 1251312.7443
166 | 2582542.2147 | 1252556.7143
167 | 2582768.8209 | 1251239.4064
168 | 2582668.3895 | 1251226.8147
169 | 2582377.7578 | 1252546.6637
170 | 2581816.8044 | 1251330.3692
171 | 2582782.2757 | 1250177.0076
172 | 2581798.6691 | 1251320.8189
173 | 2576793.1157 | 1252413.5705
174 | 2576770.761 | 1252448.9707
175 | 2576474.9151 | 1252659.7042
176 | 2576446.2524 | 1252645.3201
177 | 2577624.303 | 1253237.5938

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99696 | -0.1107 | 0.16151 | 0.078225
1 | 0.99695 | -0.11106 | 0 | 0
2 | 0.99707 | -0.10794 | 0 | 0
3 | 0.99677 | -0.11558 | 0 | 0
4 | 0.99722 | -0.10407 | 0 | 0
5 | 0.99671 | -0.11717 | 0.11928 | 0.057772
6 | 0.99758 | -0.088472 | 0.15024 | 0.072762
7 | 0.99666 | -0.11837 | 0 | 0
8 | 0.99912 | -0.022481 | 0 | 0
9 | 0.99756 | -0.089091 | 0 | 0
10 | 0.99913 | -0.022087 | 0.11156 | 0.054031
11 | 0.99924 | -0.019396 | 0 | 0
12 | 1 | 0 | -11.6173 | -4.1772
13 | 0.99755 | -0.08898 | 0.1474 | 0.07139
14 | 0.99938 | 0.0046672 | 0 | 0
15 | 0.99999 | 8.666e-05 | 0.15386 | 0.074519
16 | 0.99921 | 0.0059057 | 0.075912 | 0.036766
17 | 0.9991 | 0.0067623 | 0.13974 | 0.067678
18 | 0.99886 | 0.008539 | 0 | 0
19 | 0.99885 | 0.0085966 | 0.091127 | 0.044135
20 | 0.99879 | 0.0090885 | 0 | 0
21 | 0.99076 | -0.058985 | 0 | 0
22 | 0.99878 | 0.009196 | 0.076911 | 0.03725
23 | 0.99878 | 0.0092092 | 0.1358 | 0.065773
24 | 0.98988 | -0.052537 | 0 | 0
25 | 0.98998 | -0.053273 | 0.13653 | 0.066122
26 | 0.98456 | -0.0974 | 0 | 0
27 | 0.98979 | -0.051898 | 0 | 0
28 | 0.99011 | -0.054248 | 0 | 0
29 | 0.99011 | -0.054206 | 0.083393 | 0.040389
30 | 0.99005 | -0.05372 | 0 | 0
31 | 0.99007 | -0.053941 | 0.07432 | 0.035995
32 | 0.99004 | -0.053802 | 0.15976 | 0.077374
33 | 0.99001 | -0.053497 | 0 | 0
34 | 0.99636 | -0.12667 | 0.1122 | 0.054343
35 | 0.99634 | -0.12692 | 0 | 0
36 | 0.99642 | -0.12409 | 0 | 0
37 | 0.99623 | -0.13136 | 0.1579 | 0.076474
38 | 0.99632 | -0.12739 | 0 | 0
39 | 0.99634 | -0.12702 | 0 | 0
40 | 0.99644 | -0.12378 | 0 | 0
41 | 0.99653 | -0.12172 | 0 | 0
42 | 0.99643 | -0.1239 | 0.13517 | 0.065464
43 | 0.99623 | -0.13149 | 0 | 0
44 | 0.99549 | -0.16049 | 0.12125 | 0.058726
45 | 0.99632 | -0.12748 | 0 | 0
46 | 0.99629 | -0.1271 | 0.15625 | 0.075675
47 | 0.99633 | -0.127 | 0.067985 | 0.032927
48 | 0.99655 | -0.1208 | 0.1521 | 0.073663
49 | 0.99631 | -0.12762 | 0.13495 | 0.065357
50 | 0.99627 | -0.12689 | 0.29908 | 0.14485
51 | 0.99656 | -0.12064 | 0 | 0
52 | 0.98311 | -0.092163 | 0.089658 | 0.043423
53 | 0.98312 | -0.092266 | 0 | 0
54 | 0.98332 | -0.090635 | 0 | 0
55 | 0.98333 | -0.090708 | 0.068243 | 0.033052
56 | 0.99528 | -0.16776 | 0.086691 | 0.041987
57 | 0.99539 | -0.164 | 0 | 0
58 | 0.98454 | -0.097269 | 0.11233 | 0.054405
59 | 0.98413 | -0.094162 | 0 | 0
60 | 0.98979 | -0.051872 | 0.14297 | 0.069244
61 | 0.98382 | -0.091759 | 0 | 0
62 | 0.98412 | -0.094242 | 0.15089 | 0.073077
63 | 0.99075 | -0.059043 | 0.15993 | 0.077458
64 | 0.98369 | -0.09275 | 0.16269 | 0.078797
65 | 0.98368 | -0.092669 | 0.25786 | 0.12489
66 | 0.98366 | -0.09257 | 0 | 0
67 | 0.98351 | -0.091558 | 0 | 0
68 | 0.98348 | -0.091814 | 0.09452 | 0.045778
69 | 0.98348 | -0.091787 | 0 | 0
70 | 0.98338 | -0.09104 | 0 | 0
71 | 0.98335 | -0.090815 | 0.10797 | 0.052293
72 | 0.98335 | -0.090801 | 0 | 0
73 | 0.99535 | -0.16367 | 0.13347 | 0.064644
74 | 0.99536 | -0.16372 | 0 | 0
75 | 0.99539 | -0.16398 | 0.1043 | 0.050516
76 | 0.99539 | -0.16394 | 0 | 0
77 | 0.99542 | -0.16328 | 0.13302 | 0.064422
78 | 0.99541 | -0.1635 | 0 | 0
79 | 0.99549 | -0.16069 | 0 | 0
80 | 0.9876 | -0.4777 | 0.15673 | 0.075906
81 | 0.98758 | -0.47823 | 0 | 0
82 | 0.98775 | -0.46957 | 0 | 0
83 | 0.98744 | -0.48336 | 0 | 0
84 | 0.98784 | -0.46629 | 0 | 0
85 | 0.98782 | -0.46637 | 0 | 0
86 | 0.98781 | -0.46641 | 0.44533 | 0.21568
87 | 0.98788 | -0.465 | 0.20348 | 0.098549
88 | 0.98741 | -0.48454 | 0.10864 | 0.052618
89 | 0.98973 | -0.3719 | 0.071522 | 0.03464
90 | 0.98728 | -0.4916 | 0 | 0
91 | 0.98715 | -0.49626 | 0 | 0
92 | 0.99058 | -0.33543 | 0 | 0
93 | 0.99058 | -0.33545 | 0.054637 | 0.026462
94 | 0.99063 | -0.33371 | 0 | 0
95 | 0.99057 | -0.33568 | 0.051343 | 0.024867
96 | 0.98707 | -0.49918 | 0 | 0
97 | 0.98714 | -0.49613 | 0.14883 | 0.072083
98 | 0.98706 | -0.49948 | 0.11699 | 0.056663
99 | 0.98704 | -0.50027 | 0 | 0
100 | 0.98679 | -0.50962 | 0.059052 | 0.0286
101 | 0.98679 | -0.50959 | 0 | 0
102 | 0.9866 | -0.52057 | 0 | 0
103 | 0.98696 | -0.50318 | 0 | 0
104 | 0.98632 | -0.53051 | 0 | 0
105 | 0.98626 | -0.53247 | 0.13482 | 0.065296
106 | 0.98625 | -0.53294 | 0.17503 | 0.084769
107 | 0.98543 | -0.58158 | 0.083143 | 0.040268
108 | 0.98696 | -0.50331 | 0.15741 | 0.076239
109 | 0.99061 | -0.33456 | 0.1122 | 0.054342
110 | 0.99061 | -0.33459 | 0 | 0
111 | 0.99063 | -0.33387 | 0 | 0
112 | 0.99059 | -0.33476 | 0 | 0
113 | 0.99065 | -0.33321 | 0 | 0
114 | 0.99061 | -0.3345 | 0 | 0
115 | 0.99065 | -0.333 | 0.15738 | 0.076221
116 | 0.9906 | -0.33476 | 0.15689 | 0.075983
117 | 0.99059 | -0.33479 | 0.1377 | 0.066689
118 | 0.99423 | -0.18303 | 0.78221 | 0.37884
119 | 0.99434 | -0.18035 | 0 | 0
120 | 0.99141 | -0.31214 | 0 | 0
121 | 0.99066 | -0.33297 | 0 | 0
122 | 0.99067 | -0.33241 | 0.068028 | 0.032948
123 | 0.99068 | -0.33229 | 0 | 0
124 | 0.99068 | -0.33218 | 0 | 0
125 | 0.99072 | -0.33111 | 0 | 0
126 | 0.99074 | -0.33066 | 0.11465 | 0.055526
127 | 0.99068 | -0.33224 | 0.13209 | 0.063976
128 | 0.99076 | -0.33032 | 0 | 0
129 | 0.99066 | -0.33286 | 0.11199 | 0.054241
130 | 0.99064 | -0.33328 | 0.1598 | 0.077396
131 | 0.99064 | -0.33326 | 0 | 0
132 | 0.99066 | -0.33291 | 0 | 0
133 | 0.99062 | -0.33367 | 0.10069 | 0.048766
134 | 0.99066 | -0.33291 | 0 | 0
135 | 0.99065 | -0.33288 | 0.14862 | 0.071978
136 | 0.98977 | -0.37073 | 0 | 0
137 | 0.99013 | -0.35295 | 0.13054 | 0.063221
138 | 0.99021 | -0.34914 | 0 | 0
139 | 0.9905 | -0.33786 | 0.15284 | 0.074022
140 | 0.99034 | -0.34528 | 0 | 0
141 | 0.99053 | -0.33696 | 0 | 0
142 | 0.99021 | -0.34909 | 0 | 0
143 | 0.9902 | -0.34916 | 0 | 0
144 | 0.99021 | -0.3491 | 0.13646 | 0.066091
145 | 0.9902 | -0.34916 | 0.19161 | 0.092803
146 | 0.99141 | -0.31221 | 0.072237 | 0.034986
147 | 0.99079 | -0.32953 | 0 | 0
148 | 0.99078 | -0.32959 | 0 | 0
149 | 0.99078 | -0.32955 | 0.17621 | 0.085342
150 | 0.99077 | -0.3296 | 0.15758 | 0.076318
151 | 0.98423 | -0.63621 | 0.15629 | 0.075696
152 | 0.98422 | -0.63658 | 0 | 0
153 | 0.98428 | -0.63365 | 0 | 0
154 | 0.98411 | -0.63815 | 0 | 0
155 | 0.9843 | -0.63288 | 0 | 0
156 | 0.98433 | -0.63174 | 0.071207 | 0.034487
157 | 0.98451 | -0.62141 | 0.1636 | 0.079235
158 | 0.98411 | -0.63817 | 0.13303 | 0.064429
159 | 0.98411 | -0.63821 | 0 | 0
160 | 0.98409 | -0.63832 | 0.15719 | 0.076133
161 | 0.98409 | -0.6383 | 0 | 0
162 | 0.98461 | -0.61737 | 0.064351 | 0.031166
163 | 0.98461 | -0.61737 | 0 | 0
164 | 0.98457 | -0.6185 | 0 | 0
165 | 0.98511 | -0.59326 | 0 | 0
166 | 0.98457 | -0.6186 | 0.10074 | 0.04879
167 | 0.98514 | -0.59259 | 0.063729 | 0.030866
168 | 0.98518 | -0.59053 | 0 | 0
169 | 0.98451 | -0.62122 | 0.090741 | 0.043948
170 | 0.98515 | -0.59156 | 0 | 0
171 | 0.98543 | -0.58167 | 0 | 0
172 | 0.98515 | -0.59161 | 0.12572 | 0.06089
173 | 0.99462 | -0.17282 | 0 | 0
174 | 0.99462 | -0.17282 | 0.1265 | 0.061268
175 | 0.99619 | -0.13121 | 0 | 0
176 | 0.99619 | -0.13122 | 0.13594 | 0.065839
177 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 8.5124 | 2.8028 | -8.5123 | -2.8034 | 0.00010068 | -0.00052799 | 0.2595 | 0.2595 | 0.2595 | 0.99696 | -0.1107 | 0.99695 | -0.11106 | 30.8199
1 | -8.6739 | -2.8811 | 8.6747 | 2.8771 | 0.00079128 | -0.0039631 | 0.26465 | 0.26461 | 0.26465 | 0.99696 | -0.1107 | 0.99707 | -0.10794 | 31.431
2 | 8.5123 | 2.8034 | -8.511 | -2.81 | 0.0012644 | -0.006627 | 0.2595 | 0.25957 | 0.25957 | 0.99695 | -0.11106 | 0.99677 | -0.11558 | 30.8282
3 | -8.6747 | -2.8771 | 8.6758 | 2.8716 | 0.0011077 | -0.0055519 | 0.26461 | 0.26455 | 0.26461 | 0.99707 | -0.10794 | 0.99722 | -0.10407 | 31.4259
4 | 8.511 | 2.81 | -8.5105 | -2.8123 | 0.00044726 | -0.0023425 | 0.25957 | 0.2596 | 0.2596 | 0.99677 | -0.11558 | 0.99671 | -0.11717 | 30.8312
5 | -8.6758 | -2.8716 | 8.6781 | 2.8747 | 0.002348 | 0.003157 | 0.26455 | 0.26454 | 0.26455 | 0.99722 | -0.10407 | 0.99758 | -0.088472 | 32.2618
6 | 8.3913 | 2.7546 | -8.3909 | -2.7564 | 0.00032855 | -0.0017808 | 0.25579 | 0.25581 | 0.25581 | 0.99671 | -0.11717 | 0.99666 | -0.11837 | 30.3816
7 | -8.9758 | -3.0167 | 8.9861 | 3.0307 | 0.010365 | 0.014007 | 0.27401 | 0.27401 | 0.27401 | 0.99758 | -0.088472 | 0.99912 | -0.022481 | 33.4164
8 | 0.14741 | 0.069217 | -0.1474 | -0.069862 | 1.9952e-06 | -0.00064544 | 0.0047124 | 0.0047204 | 0.0047204 | 0.99758 | -0.088472 | 0.99756 | -0.089091 | 0.57566
9 | 1.7953 | 0.69459 | -1.7951 | -0.71524 | 0.00015651 | -0.020654 | 0.055754 | 0.055974 | 0.055974 | 0.99666 | -0.11837 | 0.99656 | -0.12064 | 6.6478
10 | 6.5957 | 2.0618 | -6.593 | -2.0871 | 0.002692 | -0.02535 | 0.20015 | 0.2004 | 0.2004 | 0.99666 | -0.11837 | 0.99619 | -0.13121 | 23.8
11 | -8.9861 | -3.0307 | 8.9862 | 3.0302 | 0.0001184 | -0.00054859 | 0.27401 | 0.274 | 0.27401 | 0.99912 | -0.022481 | 0.99913 | -0.022087 | 32.5422
12 | 0.1474 | 0.069862 | -0.1474 | -0.07139 | 1.9214e-06 | -0.0015279 | 0.0047204 | 0.0047395 | 0.0047395 | 0.99756 | -0.089091 | 0.99755 | -0.08898 | 2.1543
13 | -9.0978 | -3.0842 | 9.0986 | 3.0805 | 0.00082241 | -0.0036956 | 0.27755 | 0.27751 | 0.27755 | 0.99913 | -0.022087 | 0.99924 | -0.019396 | 32.9635
14 | -9.0986 | -3.0805 | 9.1045 | 3.0539 | 0.0059049 | -0.026601 | 0.27751 | 0.27722 | 0.27751 | 0.99924 | -0.019396 | 1 | 0 | 32.9586
15 | 2.3449 | 1.0395 | -2.3433 | -1.0441 | 0.0015472 | -0.0045811 | 0.074044 | 0.074103 | 0.074103 | 1 | 0 | 0.99938 | 0.0046672 | 33.6831
16 | 0.15386 | 0.073373 | -0.15386 | -0.074519 | 1.5572e-06 | -0.0011463 | 0.0049209 | 0.0049352 | 0.0049352 | 1 | 0 | 0.99999 | 8.666e-05 | 2.2433
17 | 2.3433 | 1.0441 | -2.3429 | -1.0453 | 0.00040691 | -0.0012025 | 0.074103 | 0.074118 | 0.074118 | 0.99938 | 0.0046672 | 0.99921 | 0.0059057 | 33.6901
18 | 2.267 | 1.0085 | -2.2667 | -1.0094 | 0.00027352 | -0.00086911 | 0.071683 | 0.071694 | 0.071694 | 0.99921 | 0.0059057 | 0.9991 | 0.0067623 | 32.5881
19 | 2.127 | 0.94168 | -2.1265 | -0.94365 | 0.00053819 | -0.001966 | 0.06721 | 0.067235 | 0.067235 | 0.9991 | 0.0067623 | 0.99886 | 0.008539 | 30.5614
20 | 0.091127 | 0.042831 | -0.091127 | -0.044135 | 6.2238e-07 | -0.001304 | 0.00291 | 0.0029262 | 0.0029262 | 0.99886 | 0.008539 | 0.99885 | 0.0085966 | 1.3301
21 | 0.21273 | 0.096098 | -0.21272 | -0.10181 | 1.4724e-05 | -0.0057095 | 0.0067463 | 0.0068159 | 0.0068159 | 0.99886 | 0.008539 | 0.99879 | 0.0090885 | 3.0981
22 | 1.8226 | 0.80472 | -1.8088 | -0.79882 | 0.013838 | 0.0059016 | 0.05758 | 0.057612 | 0.057612 | 0.99886 | 0.008539 | 0.99076 | -0.058985 | 27.4344
23 | 0.21272 | 0.10181 | -0.21272 | -0.10283 | 2.6656e-06 | -0.001021 | 0.0068159 | 0.0068287 | 0.0068287 | 0.99879 | 0.0090885 | 0.99878 | 0.009196 | 3.104
24 | 1.6488 | 0.72139 | -1.6477 | -0.72829 | 0.0011363 | -0.0069012 | 0.052438 | 0.052523 | 0.052523 | 0.99076 | -0.058985 | 0.99011 | -0.054248 | 23.8743
25 | 0.15993 | 0.077424 | -0.15993 | -0.077458 | 1.3907e-06 | -3.3252e-05 | 0.0051772 | 0.0051776 | 0.0051776 | 0.99076 | -0.058985 | 0.99075 | -0.059043 | 2.4655
26 | 0.1358 | 0.065579 | -0.1358 | -0.065773 | 2.0664e-07 | -0.00019389 | 0.0043588 | 0.0043612 | 0.0043612 | 0.99878 | 0.009196 | 0.99878 | 0.0092092 | 1.9824
27 | -1.1934 | -0.52 | 1.1935 | 0.51844 | 0.00013163 | -0.0015626 | 0.037962 | 0.037944 | 0.037962 | 0.98988 | -0.052537 | 0.98998 | -0.053273 | 17.2555
28 | 1.0504 | 0.46203 | -1.0451 | -0.4618 | 0.0052824 | 0.00023177 | 0.033464 | 0.033501 | 0.033501 | 0.98988 | -0.052537 | 0.98456 | -0.0974 | 15.9527
29 | 0.14298 | 0.057969 | -0.14297 | -0.068902 | 1.299e-05 | -0.010934 | 0.0044995 | 0.0046288 | 0.0046288 | 0.98988 | -0.052537 | 0.98979 | -0.051898 | 2.104
30 | -1.33 | -0.58456 | 1.3301 | 0.58415 | 4.3466e-05 | -0.00041169 | 0.042364 | 0.042359 | 0.042364 | 0.98998 | -0.053273 | 0.99001 | -0.053497 | 19.2562
31 | 0.93276 | 0.40971 | -0.93233 | -0.41789 | 0.0004288 | -0.0081733 | 0.029871 | 0.02997 | 0.02997 | 0.98456 | -0.0974 | 0.98413 | -0.094162 | 13.6225
32 | 0.11233 | 0.052087 | -0.11233 | -0.054405 | 1.7768e-06 | -0.002318 | 0.0036305 | 0.0036596 | 0.0036596 | 0.98456 | -0.0974 | 0.98454 | -0.097269 | 1.6635
33 | 0.14297 | 0.068902 | -0.14297 | -0.069244 | 4.1851e-07 | -0.00034181 | 0.0046288 | 0.0046331 | 0.0046331 | 0.98979 | -0.051898 | 0.98979 | -0.051872 | 2.106
34 | 0.083393 | 0.039385 | -0.083393 | -0.040389 | 4.1591e-07 | -0.0010037 | 0.0026889 | 0.0027016 | 0.0027016 | 0.99011 | -0.054248 | 0.99011 | -0.054206 | 1.228
35 | 0.15977 | 0.070112 | -0.15976 | -0.077327 | 1.0837e-05 | -0.0072152 | 0.005087 | 0.0051752 | 0.0051752 | 0.99011 | -0.054248 | 0.99005 | -0.05372 | 2.3524
36 | 1.4045 | 0.6188 | -1.4045 | -0.61932 | 6.2393e-05 | -0.00052769 | 0.044748 | 0.044755 | 0.044755 | 0.99011 | -0.054248 | 0.99007 | -0.053941 | 20.3431
37 | 0.15976 | 0.077327 | -0.15976 | -0.077374 | 1.9822e-06 | -4.736e-05 | 0.0051752 | 0.0051758 | 0.0051758 | 0.99005 | -0.05372 | 0.99004 | -0.053802 | 2.4647
38 | 1.3301 | 0.58333 | -1.3301 | -0.58415 | 8.6427e-05 | -0.00081897 | 0.042349 | 0.042359 | 0.042359 | 0.99007 | -0.053941 | 0.99001 | -0.053497 | 19.2539
39 | 0.6583 | 0.25798 | -0.6583 | -0.26415 | 6.2709e-06 | -0.0061678 | 0.020485 | 0.020551 | 0.020551 | 0.99636 | -0.12667 | 0.99634 | -0.12692 | 2.4408
40 | -1.5076 | -0.60185 | 1.5076 | 0.60172 | 7.5254e-05 | -0.00013639 | 0.047031 | 0.047029 | 0.047031 | 0.99636 | -0.12667 | 0.99642 | -0.12409 | 5.7355
41 | 0.73707 | 0.28953 | -0.737 | -0.29034 | 6.5976e-05 | -0.00080771 | 0.022944 | 0.022953 | 0.022953 | 0.99636 | -0.12667 | 0.99623 | -0.13136 | 2.7992
42 | 0.59031 | 0.2556 | -0.5903 | -0.27001 | 1.2194e-05 | -0.014407 | 0.018638 | 0.018808 | 0.018808 | 0.99634 | -0.12692 | 0.99632 | -0.12739 | 2.2337
43 | 0.067986 | 0.0085473 | -0.067985 | -0.032297 | 4.9771e-07 | -0.023749 | 0.0019853 | 0.0021807 | 0.0021807 | 0.99634 | -0.12692 | 0.99634 | -0.12702 | 0.34181
44 | -1.5076 | -0.60172 | 1.5077 | 0.59832 | 1.8176e-05 | -0.0033926 | 0.047029 | 0.046992 | 0.047029 | 0.99642 | -0.12409 | 0.99644 | -0.12378 | 5.5853
45 | 0.5791 | 0.21387 | -0.5791 | -0.21757 | 2.8688e-06 | -0.0037046 | 0.017888 | 0.017926 | 0.017926 | 0.99623 | -0.13136 | 0.99623 | -0.13149 | 2.1289
46 | 0.13495 | 0.052167 | -0.13495 | -0.065199 | 5.7165e-07 | -0.013032 | 0.0041919 | 0.0043424 | 0.0043424 | 0.99632 | -0.12739 | 0.99632 | -0.12748 | 0.51572
47 | 0.45535 | 0.21784 | -0.45534 | -0.21908 | 1.4983e-05 | -0.0012377 | 0.014626 | 0.014641 | 0.014641 | 0.99632 | -0.12739 | 0.99629 | -0.1271 | 6.655
48 | 0.067985 | 0.032297 | -0.067985 | -0.032927 | 1.6942e-07 | -0.00063017 | 0.0021807 | 0.0021886 | 0.0021886 | 0.99634 | -0.12702 | 0.99633 | -0.127 | 0.99484
49 | -1.6428 | -0.66375 | 1.643 | 0.64312 | 0.00013134 | -0.020634 | 0.051332 | 0.05111 | 0.051332 | 0.99644 | -0.12378 | 0.99653 | -0.12172 | 6.0964
50 | 0.13517 | 0.065424 | -0.13517 | -0.065464 | 5.6566e-07 | -3.9969e-05 | 0.0043505 | 0.004351 | 0.004351 | 0.99644 | -0.12378 | 0.99643 | -0.1239 | 1.2431
51 | -1.643 | -0.64312 | 1.643 | 0.64308 | 2.8589e-05 | -3.7555e-05 | 0.05111 | 0.051109 | 0.05111 | 0.99653 | -0.12172 | 0.99655 | -0.1208 | 6.2329
52 | 0.5791 | 0.21757 | -0.57878 | -0.22414 | 0.00031479 | -0.0065727 | 0.017926 | 0.017998 | 0.017998 | 0.99623 | -0.13149 | 0.99549 | -0.16049 | 2.1949
53 | 0.45753 | 0.16542 | -0.45753 | -0.17223 | 3.2927e-06 | -0.0068088 | 0.014108 | 0.014176 | 0.014176 | 0.99549 | -0.16049 | 0.99549 | -0.16069 | 1.6837
54 | 0.13495 | 0.065199 | -0.13495 | -0.065357 | 4.159e-07 | -0.00015835 | 0.0043424 | 0.0043444 | 0.0043444 | 0.99632 | -0.12748 | 0.99631 | -0.12762 | 0.52981
55 | 0.29909 | 0.1434 | -0.29908 | -0.14485 | 7.5663e-06 | -0.0014492 | 0.0096107 | 0.009629 | 0.009629 | 0.99629 | -0.1271 | 0.99627 | -0.12689 | 4.3768
56 | -1.7951 | -0.71674 | 1.7951 | 0.71524 | 1.1434e-05 | -0.0015022 | 0.055991 | 0.055974 | 0.055991 | 0.99655 | -0.1208 | 0.99656 | -0.12064 | 6.6497
57 | -0.089658 | -0.043423 | 0.089659 | 0.041137 | 1.1207e-06 | -0.0022862 | 0.0029252 | 0.0028966 | 0.0029252 | 0.98311 | -0.092163 | 0.98312 | -0.092266 | 1.3296
58 | -0.089659 | -0.041137 | 0.089676 | 0.039786 | 1.7544e-05 | -0.0013513 | 0.0028966 | 0.0028801 | 0.0028966 | 0.98312 | -0.092266 | 0.98332 | -0.090635 | 1.3793
59 | -0.089676 | -0.039786 | 0.089677 | 0.037689 | 9.9726e-07 | -0.0020967 | 0.0028801 | 0.0028557 | 0.0028801 | 0.98332 | -0.090635 | 0.98333 | -0.090708 | 1.3091
60 | -0.15792 | -0.070741 | 0.15792 | 0.069327 | 2.1034e-06 | -0.0014137 | 0.0050799 | 0.0050631 | 0.0050799 | 0.98333 | -0.090708 | 0.98335 | -0.090801 | 2.3091
61 | -0.086691 | -0.041987 | 0.086698 | 0.035529 | 6.8174e-06 | -0.0064571 | 0.0027938 | 0.0027173 | 0.0027938 | 0.99528 | -0.16776 | 0.99539 | -0.164 | 0.34071
62 | -0.22018 | -0.094784 | 0.22018 | 0.092869 | 2.2306e-07 | -0.001915 | 0.006952 | 0.0069302 | 0.006952 | 0.99539 | -0.164 | 0.99539 | -0.16398 | 0.82565
63 | 0.13348 | 0.059254 | -0.13347 | -0.06387 | 4.7349e-06 | -0.0046155 | 0.0042353 | 0.0042914 | 0.0042914 | 0.99539 | -0.164 | 0.99536 | -0.16372 | 1.9506
64 | 0.78144 | 0.34486 | -0.78118 | -0.35201 | 0.00026309 | -0.0071542 | 0.025055 | 0.025141 | 0.025141 | 0.98413 | -0.094162 | 0.98382 | -0.091759 | 11.4279
65 | 0.15089 | 0.07303 | -0.15089 | -0.073077 | 1.8222e-06 | -4.7758e-05 | 0.0049171 | 0.0049178 | 0.0049178 | 0.98413 | -0.094162 | 0.98412 | -0.094242 | 2.3418
66 | 0.78118 | 0.35201 | -0.78109 | -0.35205 | 9.2562e-05 | -3.6975e-05 | 0.025141 | 0.025143 | 0.025143 | 0.98382 | -0.091759 | 0.98369 | -0.09275 | 11.9726
67 | 0.25786 | 0.1243 | -0.25786 | -0.12489 | 2.4102e-06 | -0.00058983 | 0.0084004 | 0.008408 | 0.008408 | 0.98369 | -0.09275 | 0.98368 | -0.092669 | 3.8218
68 | 0.36053 | 0.14895 | -0.36052 | -0.15043 | 1.1247e-05 | -0.0014797 | 0.011448 | 0.011464 | 0.011464 | 0.98369 | -0.09275 | 0.98366 | -0.09257 | 5.2111
69 | 0.36052 | 0.15043 | -0.36046 | -0.15792 | 5.7459e-05 | -0.0074911 | 0.011464 | 0.011551 | 0.011551 | 0.98366 | -0.09257 | 0.98351 | -0.091558 | 5.2504
70 | 0.36046 | 0.15792 | -0.36045 | -0.15797 | 1.0197e-05 | -4.3142e-05 | 0.011551 | 0.011552 | 0.011552 | 0.98351 | -0.091558 | 0.98348 | -0.091814 | 5.5007
71 | 0.26593 | 0.11219 | -0.26593 | -0.11247 | 1.1596e-06 | -0.00027905 | 0.008472 | 0.0084751 | 0.0084751 | 0.98348 | -0.091814 | 0.98348 | -0.091787 | 3.8523
72 | 0.26593 | 0.11247 | -0.2659 | -0.11951 | 2.9554e-05 | -0.0070401 | 0.0084751 | 0.0085579 | 0.0085579 | 0.98348 | -0.091787 | 0.98338 | -0.09104 | 3.8899
73 | 0.2659 | 0.11951 | -0.2659 | -0.12141 | 8.0698e-06 | -0.0018982 | 0.0085579 | 0.0085809 | 0.0085809 | 0.98338 | -0.09104 | 0.98335 | -0.090815 | 3.9004
74 | 0.15792 | 0.069113 | -0.15792 | -0.069327 | 3.1708e-07 | -0.00021393 | 0.0050606 | 0.0050631 | 0.0050631 | 0.98335 | -0.090815 | 0.98335 | -0.090801 | 2.3014
75 | -0.13347 | -0.064644 | 0.13347 | 0.06387 | 8.0681e-07 | -0.00077426 | 0.0043012 | 0.0042914 | 0.0043012 | 0.99535 | -0.16367 | 0.99536 | -0.16372 | 1.9551
76 | -0.32448 | -0.14339 | 0.32448 | 0.14156 | 4.6598e-07 | -0.0018245 | 0.010288 | 0.010267 | 0.010288 | 0.99539 | -0.16398 | 0.99539 | -0.16394 | 1.2219
77 | -0.32448 | -0.14156 | 0.32449 | 0.11911 | 5.5837e-06 | -0.022455 | 0.010267 | 0.010024 | 0.010267 | 0.99539 | -0.16394 | 0.99541 | -0.1635 | 1.2193
78 | 0.32449 | 0.10856 | -0.32449 | -0.11911 | 2.5354e-06 | -0.010544 | 0.009923 | 0.010024 | 0.010024 | 0.99542 | -0.16328 | 0.99541 | -0.1635 | 1.1905
79 | -0.45751 | -0.17298 | 0.45753 | 0.17223 | 2.2056e-05 | -0.00075751 | 0.014185 | 0.014176 | 0.014185 | 0.99542 | -0.16328 | 0.99549 | -0.16069 | 1.7298
80 | 2.1143 | 0.39668 | -2.1143 | -0.39948 | 2.7475e-05 | -0.0028037 | 0.06288 | 0.062895 | 0.062895 | 0.9876 | -0.4777 | 0.98758 | -0.47823 | 7.4697
81 | -2.271 | -0.47258 | 2.2713 | 0.47256 | 0.00027132 | -2.534e-05 | 0.067805 | 0.067802 | 0.067805 | 0.9876 | -0.4777 | 0.98775 | -0.46957 | 8.2689
82 | 2.1143 | 0.39948 | -2.114 | -0.42718 | 0.00027224 | -0.027702 | 0.062895 | 0.063052 | 0.063052 | 0.98758 | -0.47823 | 0.98744 | -0.48336 | 7.4884
83 | -2.2713 | -0.47256 | 2.2715 | 0.45587 | 0.00018999 | -0.016686 | 0.067802 | 0.067704 | 0.067802 | 0.98775 | -0.46957 | 0.98784 | -0.46629 | 8.0525
84 | 2.114 | 0.42718 | -2.114 | -0.43361 | 6.3367e-05 | -0.0064264 | 0.063052 | 0.06309 | 0.06309 | 0.98744 | -0.48336 | 0.98741 | -0.48454 | 7.4928
85 | -2.7168 | -0.6598 | 2.7169 | 0.65407 | 9.5313e-05 | -0.0057329 | 0.081702 | 0.081662 | 0.081702 | 0.98784 | -0.46629 | 0.98788 | -0.465 | 9.7033
86 | 0.44534 | 0.20393 | -0.44533 | -0.21138 | 7.7431e-06 | -0.007447 | 0.014314 | 0.014406 | 0.014406 | 0.98784 | -0.46629 | 0.98782 | -0.46637 | 2.2579
87 | 0.44533 | 0.21138 | -0.44533 | -0.21568 | 4.5237e-06 | -0.0043064 | 0.014406 | 0.01446 | 0.01446 | 0.98782 | -0.46637 | 0.98781 | -0.46641 | 2.2665
88 | -2.9204 | -0.75262 | 2.9247 | 0.75488 | 0.0042566 | 0.0022693 | 0.088128 | 0.0881 | 0.088128 | 0.98788 | -0.465 | 0.98973 | -0.3719 | 10.7473
89 | 2.0053 | 0.38099 | -2.0051 | -0.3811 | 0.00020357 | -0.00011001 | 0.059676 | 0.059678 | 0.059678 | 0.98741 | -0.48454 | 0.98728 | -0.4916 | 7.2778
90 | -2.9962 | -0.78952 | 2.9963 | 0.78459 | 0.00010026 | -0.0049306 | 0.090373 | 0.090336 | 0.090373 | 0.98973 | -0.3719 | 0.98977 | -0.37073 | 10.7331
91 | 2.0051 | 0.3811 | -2.0049 | -0.40761 | 0.00023446 | -0.026506 | 0.059678 | 0.059829 | 0.059829 | 0.98728 | -0.4916 | 0.98715 | -0.49626 | 7.1055
92 | 1.856 | 0.33715 | -1.8559 | -0.35488 | 0.00013379 | -0.017732 | 0.055165 | 0.055261 | 0.055261 | 0.98715 | -0.49626 | 0.98707 | -0.49918 | 6.563
93 | 0.14884 | 0.07046 | -0.14883 | -0.072083 | 2.1693e-06 | -0.0016228 | 0.0048155 | 0.004836 | 0.004836 | 0.98715 | -0.49626 | 0.98714 | -0.49613 | 2.1982
94 | 0.10598 | 0.04831 | -0.10598 | -0.050643 | 6.6182e-08 | -0.0023337 | 0.0033942 | 0.003423 | 0.003423 | 0.99058 | -0.33543 | 0.99058 | -0.33545 | 0.40653
95 | -0.10598 | -0.04831 | 0.10598 | 0.04594 | 3.8079e-06 | -0.0023702 | 0.0033942 | 0.0033661 | 0.0033942 | 0.99058 | -0.33543 | 0.99063 | -0.33371 | 0.41393
96 | 0.051343 | 0.024182 | -0.051343 | -0.024867 | 2.6436e-07 | -0.00068488 | 0.0016539 | 0.0016625 | 0.0016625 | 0.99058 | -0.33545 | 0.99057 | -0.33568 | 0.20274
97 | 0.10069 | 0.048041 | -0.10069 | -0.048766 | 4.3826e-07 | -0.00072558 | 0.003251 | 0.0032602 | 0.0032602 | 0.99063 | -0.33371 | 0.99062 | -0.33367 | 1.4819
98 | -0.20667 | -0.09398 | 0.20668 | 0.093674 | 1.8961e-06 | -0.0003062 | 0.006616 | 0.0066123 | 0.006616 | 0.99063 | -0.33371 | 0.99064 | -0.33328 | 0.80684
99 | 1.8559 | 0.35488 | -1.8559 | -0.35671 | 1.3872e-05 | -0.0018347 | 0.055261 | 0.055271 | 0.055271 | 0.98707 | -0.49918 | 0.98706 | -0.49948 | 6.5642
100 | 1.7389 | 0.30005 | -1.7389 | -0.30511 | 3.3322e-05 | -0.0050561 | 0.051607 | 0.051633 | 0.051633 | 0.98706 | -0.49948 | 0.98704 | -0.50027 | 6.1321
101 | 1.7389 | 0.30511 | -1.7387 | -0.32383 | 0.00012372 | -0.018727 | 0.051633 | 0.051731 | 0.051731 | 0.98704 | -0.50027 | 0.98696 | -0.50318 | 6.1438
102 | -1.5811 | -0.29274 | 1.5811 | 0.29253 | 1.191e-06 | -0.00021771 | 0.047039 | 0.047038 | 0.047039 | 0.98679 | -0.50962 | 0.98679 | -0.50959 | 5.5866
103 | 1.522 | 0.26414 | -1.5218 | -0.26462 | 0.00023517 | -0.00047375 | 0.045191 | 0.045195 | 0.045195 | 0.98679 | -0.50962 | 0.9866 | -0.52057 | 5.5116
104 | -1.5811 | -0.29253 | 1.5813 | 0.24772 | 0.00024382 | -0.044805 | 0.047038 | 0.046816 | 0.047038 | 0.98679 | -0.50959 | 0.98696 | -0.50318 | 5.5864
105 | 1.5218 | 0.26462 | -1.5214 | -0.33937 | 0.00038096 | -0.074755 | 0.045195 | 0.045623 | 0.045623 | 0.9866 | -0.52057 | 0.98632 | -0.53051 | 5.4184
106 | 0.15741 | 0.076112 | -0.15741 | -0.076239 | 4.7319e-07 | -0.00012728 | 0.0051142 | 0.0051158 | 0.0051158 | 0.98696 | -0.50318 | 0.98696 | -0.50331 | 0.62388
107 | 1.5214 | 0.33937 | -1.5213 | -0.35478 | 7.9539e-05 | -0.015413 | 0.045623 | 0.045724 | 0.045724 | 0.98632 | -0.53051 | 0.98626 | -0.53247 | 5.4304
108 | 1.3865 | 0.28949 | -1.3865 | -0.29345 | 1.6845e-05 | -0.0039625 | 0.041458 | 0.041482 | 0.041482 | 0.98626 | -0.53247 | 0.98625 | -0.53294 | 4.9266
109 | 1.2115 | 0.20868 | -1.2106 | -0.21201 | 0.00083129 | -0.0033261 | 0.035982 | 0.036005 | 0.036005 | 0.98625 | -0.53294 | 0.98543 | -0.58158 | 4.3908
110 | 1.1275 | 0.17174 | -1.1275 | -0.17257 | 2.3018e-06 | -0.00083382 | 0.03341 | 0.033414 | 0.033414 | 0.98543 | -0.58158 | 0.98543 | -0.58167 | 3.9684
111 | 0.1377 | 0.032333 | -0.1377 | -0.03599 | 3.133e-07 | -0.0036572 | 0.0041218 | 0.0041475 | 0.0041475 | 0.99061 | -0.33456 | 0.99061 | -0.33459 | 0.65008
112 | -0.2499 | -0.086674 | 0.2499 | 0.086314 | 3.0395e-06 | -0.00036041 | 0.007708 | 0.0077045 | 0.007708 | 0.99061 | -0.33456 | 0.99063 | -0.33387 | 0.94
113 | 0.1377 | 0.03599 | -0.1377 | -0.05939 | 2.1149e-06 | -0.0234 | 0.0041475 | 0.00437 | 0.00437 | 0.99061 | -0.33459 | 0.99059 | -0.33476 | 0.68496
114 | -0.40679 | -0.10697 | 0.4068 | 0.086872 | 7.2855e-06 | -0.020095 | 0.012257 | 0.012121 | 0.012257 | 0.99063 | -0.33387 | 0.99065 | -0.33321 | 1.4557
115 | 0.15689 | 0.020653 | -0.15689 | -0.075731 | 3.0752e-06 | -0.055078 | 0.0046113 | 0.0050766 | 0.0050766 | 0.99063 | -0.33387 | 0.99061 | -0.3345 | 0.60293
116 | 0.1377 | 0.05939 | -0.1377 | -0.066689 | 7.1253e-07 | -0.0072992 | 0.00437 | 0.0044586 | 0.0044586 | 0.99059 | -0.33476 | 0.99059 | -0.33479 | 0.69883
117 | -0.4068 | -0.086872 | 0.4068 | 0.080848 | 2.1545e-06 | -0.0060242 | 0.012121 | 0.012086 | 0.012121 | 0.99065 | -0.33321 | 0.99065 | -0.333 | 1.4396
118 | 0.15689 | 0.075731 | -0.15689 | -0.075983 | 9.1784e-07 | -0.00025234 | 0.0050766 | 0.0050799 | 0.0050799 | 0.99061 | -0.3345 | 0.9906 | -0.33476 | 0.6195
119 | -0.56418 | -0.15707 | 0.56418 | 0.1564 | 4.7884e-07 | -0.00067343 | 0.017065 | 0.01706 | 0.017065 | 0.99065 | -0.333 | 0.99066 | -0.33297 | 2.0268
120 | -6.3198 | -2.0707 | 6.3204 | 2.065 | 0.00055435 | -0.0056296 | 0.19309 | 0.19304 | 0.19309 | 0.99423 | -0.18303 | 0.99434 | -0.18035 | 22.9327
121 | 5.5376 | 1.6918 | -5.5257 | -1.6776 | 0.011914 | 0.014232 | 0.16812 | 0.16815 | 0.16815 | 0.99423 | -0.18303 | 0.99141 | -0.31214 | 20.5055
122 | -6.3204 | -2.065 | 6.3219 | 2.0492 | 0.0015509 | -0.015775 | 0.19304 | 0.19288 | 0.19304 | 0.99434 | -0.18035 | 0.99462 | -0.17282 | 22.9261
123 | 5.4534 | 1.6427 | -5.4505 | -1.6839 | 0.0029507 | -0.041194 | 0.16584 | 0.16621 | 0.16621 | 0.99141 | -0.31214 | 0.99079 | -0.32953 | 19.7401
124 | 0.072237 | 0.034838 | -0.072237 | -0.034986 | 1.127e-07 | -0.00014727 | 0.0023352 | 0.0023371 | 0.0023371 | 0.99141 | -0.31214 | 0.99141 | -0.31221 | 0.28501
125 | -0.56418 | -0.1564 | 0.56419 | 0.13835 | 1.2721e-05 | -0.018042 | 0.01706 | 0.016927 | 0.01706 | 0.99066 | -0.33297 | 0.99068 | -0.33218 | 2.0261
126 | -0.068028 | -0.032948 | 0.068029 | 0.032683 | 1.7999e-07 | -0.00026463 | 0.0022026 | 0.0021992 | 0.0022026 | 0.99067 | -0.33241 | 0.99068 | -0.33229 | 0.2686
127 | -0.068029 | -0.032683 | 0.068029 | 0.01052 | 2.3397e-07 | -0.022163 | 0.0021992 | 0.0020059 | 0.0021992 | 0.99068 | -0.33229 | 0.99068 | -0.33218 | 0.26119
128 | 0.7592 | 0.33809 | -0.7592 | -0.3396 | 2.1681e-06 | -0.0015118 | 0.024217 | 0.024235 | 0.024235 | 0.99068 | -0.33218 | 0.99068 | -0.33224 | 2.8782
129 | -1.3914 | -0.48696 | 1.3915 | 0.4757 | 5.0805e-05 | -0.011264 | 0.042956 | 0.042848 | 0.042956 | 0.99068 | -0.33218 | 0.99072 | -0.33111 | 5.1017
130 | -1.3915 | -0.4757 | 1.3915 | 0.47104 | 2.0931e-05 | -0.0046576 | 0.042848 | 0.042804 | 0.042848 | 0.99072 | -0.33111 | 0.99074 | -0.33066 | 5.0889
131 | -1.5061 | -0.52657 | 1.5062 | 0.52318 | 1.795e-05 | -0.0033896 | 0.04649 | 0.046457 | 0.04649 | 0.99074 | -0.33066 | 0.99076 | -0.33032 | 5.5213
132 | 0.6271 | 0.27563 | -0.6271 | -0.27576 | 7.961e-06 | -0.0001309 | 0.01996 | 0.019962 | 0.019962 | 0.99068 | -0.33224 | 0.99066 | -0.33286 | 2.4344
133 | -1.5062 | -0.52318 | 1.5062 | 0.5155 | 4.0546e-05 | -0.0076744 | 0.046457 | 0.046384 | 0.046457 | 0.99076 | -0.33032 | 0.99079 | -0.32953 | 5.5174
134 | 0.5151 | 0.22152 | -0.5151 | -0.22308 | 1.017e-06 | -0.0015583 | 0.016339 | 0.016357 | 0.016357 | 0.99066 | -0.33286 | 0.99066 | -0.33291 | 1.9426
135 | -0.36648 | -0.17107 | 0.36648 | 0.17006 | 3.4123e-07 | -0.0010073 | 0.011785 | 0.011773 | 0.011785 | 0.99064 | -0.33328 | 0.99064 | -0.33326 | 1.3997
136 | -0.36648 | -0.17006 | 0.36648 | 0.15312 | 5.634e-06 | -0.016941 | 0.011773 | 0.011574 | 0.011773 | 0.99064 | -0.33326 | 0.99066 | -0.33291 | 1.3982
137 | 0.14862 | 0.069954 | -0.14862 | -0.071557 | 1.8481e-07 | -0.001603 | 0.0047864 | 0.0048065 | 0.0048065 | 0.99066 | -0.33291 | 0.99066 | -0.33291 | 0.75337
138 | 0.14862 | 0.071557 | -0.14862 | -0.071978 | 5.5543e-07 | -0.00042135 | 0.0048065 | 0.0048119 | 0.0048119 | 0.99066 | -0.33291 | 0.99065 | -0.33288 | 2.1872
139 | -2.9963 | -0.78459 | 2.9971 | 0.78508 | 0.00083793 | 0.00048223 | 0.090336 | 0.09033 | 0.090336 | 0.98977 | -0.37073 | 0.99013 | -0.35295 | 11.0166
140 | -3.1277 | -0.8483 | 3.1279 | 0.84842 | 0.00018967 | 0.0001233 | 0.094483 | 0.094482 | 0.094483 | 0.99013 | -0.35295 | 0.99021 | -0.34914 | 11.5223
141 | -3.3195 | -0.93586 | 3.3195 | 0.93568 | 4.4103e-06 | -0.00017455 | 0.10055 | 0.10054 | 0.10055 | 0.99021 | -0.34914 | 0.99021 | -0.34909 | 11.9412
142 | 0.19161 | 0.087437 | -0.19161 | -0.091509 | 7.7636e-07 | -0.004072 | 0.0061402 | 0.0061905 | 0.0061905 | 0.99021 | -0.34914 | 0.9902 | -0.34916 | 0.97029
143 | 3.4568 | 0.9847 | -3.4563 | -0.98437 | 0.00041615 | 0.00033231 | 0.10475 | 0.10476 | 0.10476 | 0.9905 | -0.33786 | 0.99034 | -0.34528 | 12.775
144 | -3.6096 | -1.0587 | 3.6097 | 1.0554 | 9.8851e-05 | -0.003279 | 0.10963 | 0.1096 | 0.10963 | 0.9905 | -0.33786 | 0.99053 | -0.33696 | 13.0204
145 | 3.4563 | 0.98437 | -3.4559 | -0.9987 | 0.00039418 | -0.014328 | 0.10476 | 0.10487 | 0.10487 | 0.99034 | -0.34528 | 0.99021 | -0.34909 | 12.4553
146 | -3.6097 | -1.0554 | 3.6105 | 1.0286 | 0.00080596 | -0.026806 | 0.1096 | 0.10938 | 0.1096 | 0.99053 | -0.33696 | 0.99079 | -0.32953 | 13.0171
147 | 0.13646 | 0.063015 | -0.13646 | -0.066091 | 2.9882e-07 | -0.0030759 | 0.0043819 | 0.0044203 | 0.0044203 | 0.99021 | -0.34909 | 0.99021 | -0.3491 | 0.69283
148 | 0.19161 | 0.091509 | -0.19161 | -0.092803 | 2.4931e-07 | -0.0012935 | 0.0061905 | 0.0062068 | 0.0062068 | 0.9902 | -0.34916 | 0.9902 | -0.34916 | 0.97286
149 | 0.15758 | 0.060861 | -0.15758 | -0.071995 | 1.3848e-06 | -0.011133 | 0.0049218 | 0.0050477 | 0.0050477 | 0.99079 | -0.32953 | 0.99078 | -0.32959 | 0.79118
150 | 0.17621 | 0.07893 | -0.17621 | -0.085342 | 1.0309e-06 | -0.0064126 | 0.0056256 | 0.0057045 | 0.0057045 | 0.99079 | -0.32953 | 0.99078 | -0.32955 | 0.89413
151 | 0.15758 | 0.071995 | -0.15758 | -0.076318 | 5.5777e-07 | -0.0043237 | 0.0050477 | 0.0051014 | 0.0051014 | 0.99078 | -0.32959 | 0.99077 | -0.3296 | 0.79959
152 | 0.29026 | 0.029904 | -0.29026 | -0.041433 | 4.3069e-06 | -0.011529 | 0.0085584 | 0.0085996 | 0.0085996 | 0.98423 | -0.63621 | 0.98422 | -0.63658 | 1.3479
153 | -0.44655 | -0.1056 | 0.44657 | 0.10495 | 1.7394e-05 | -0.00065075 | 0.013459 | 0.013454 | 0.013459 | 0.98423 | -0.63621 | 0.98428 | -0.63365 | 1.6413
154 | 0.29026 | 0.041433 | -0.29023 | -0.11514 | 2.9102e-05 | -0.073703 | 0.0085996 | 0.0091588 | 0.0091588 | 0.98422 | -0.63658 | 0.98411 | -0.63815 | 1.4356
155 | -0.44657 | -0.10495 | 0.44658 | 0.084904 | 8.8886e-06 | -0.020045 | 0.013454 | 0.013332 | 0.013454 | 0.98428 | -0.63365 | 0.9843 | -0.63288 | 1.5979
156 | 0.29023 | 0.11514 | -0.29023 | -0.11652 | 5.8908e-07 | -0.0013804 | 0.0091588 | 0.0091738 | 0.0091738 | 0.98411 | -0.63815 | 0.98411 | -0.63817 | 1.4379
157 | -0.44658 | -0.084904 | 0.44659 | 0.057297 | 1.2008e-05 | -0.027607 | 0.013332 | 0.013205 | 0.013332 | 0.9843 | -0.63288 | 0.98433 | -0.63174 | 1.5834
158 | -0.5178 | -0.091784 | 0.51787 | 0.089654 | 7.5634e-05 | -0.0021305 | 0.015422 | 0.015411 | 0.015422 | 0.98433 | -0.63174 | 0.98451 | -0.62141 | 1.8808
159 | -0.68147 | -0.16889 | 0.68148 | 0.16559 | 3.4502e-06 | -0.003295 | 0.020587 | 0.020563 | 0.020587 | 0.98451 | -0.62141 | 0.98451 | -0.62122 | 2.445
160 | 0.1572 | 0.052087 | -0.1572 | -0.05637 | 5.1749e-07 | -0.0042827 | 0.0048577 | 0.0048987 | 0.0048987 | 0.98411 | -0.63817 | 0.98411 | -0.63821 | 0.76782
161 | 0.1572 | 0.05637 | -0.15719 | -0.072402 | 2.0216e-06 | -0.016032 | 0.0048987 | 0.0050768 | 0.0050768 | 0.98411 | -0.63821 | 0.98409 | -0.6383 | 0.79573
162 | -0.15719 | -0.076133 | 0.15719 | 0.072402 | 4.9284e-07 | -0.0037311 | 0.0051235 | 0.0050768 | 0.0051235 | 0.98409 | -0.63832 | 0.98409 | -0.6383 | 0.80306
163 | -0.064351 | -0.031166 | 0.064351 | 0.029306 | 4.1018e-08 | -0.0018606 | 0.0020963 | 0.0020731 | 0.0020963 | 0.98461 | -0.61737 | 0.98461 | -0.61737 | 0.32858
164 | 0.87302 | 0.23975 | -0.87299 | -0.25652 | 2.9399e-05 | -0.016777 | 0.026544 | 0.026678 | 0.026678 | 0.98461 | -0.61737 | 0.98457 | -0.6185 | 3.1684
165 | -0.93737 | -0.26905 | 0.93774 | 0.26642 | 0.00036711 | -0.0026349 | 0.028592 | 0.028567 | 0.028592 | 0.98461 | -0.61737 | 0.98511 | -0.59326 | 3.4869
166 | 0.87299 | 0.25652 | -0.87299 | -0.25796 | 2.5401e-06 | -0.0014415 | 0.026678 | 0.02669 | 0.02669 | 0.98457 | -0.6185 | 0.98457 | -0.6186 | 3.1699
167 | -0.93774 | -0.26642 | 0.93776 | 0.25719 | 1.8564e-05 | -0.0092239 | 0.028567 | 0.028494 | 0.028567 | 0.98511 | -0.59326 | 0.98514 | -0.59259 | 3.3927
168 | 0.77225 | 0.20917 | -0.77222 | -0.20954 | 3.2318e-05 | -0.00036664 | 0.023458 | 0.023461 | 0.023461 | 0.98457 | -0.6186 | 0.98451 | -0.62122 | 2.8612
169 | -1.0015 | -0.28806 | 1.0015 | 0.28785 | 3.3636e-05 | -0.0002056 | 0.030536 | 0.030534 | 0.030536 | 0.98514 | -0.59259 | 0.98518 | -0.59053 | 3.724
170 | 0.12572 | -0.026288 | -0.12572 | -0.060839 | 2.9733e-06 | -0.087127 | 0.0037636 | 0.0040926 | 0.0040926 | 0.98518 | -0.59053 | 0.98515 | -0.59156 | 0.48606
171 | -1.1272 | -0.26156 | 1.1275 | 0.17257 | 0.00024905 | -0.088991 | 0.033908 | 0.033414 | 0.033908 | 0.98518 | -0.59053 | 0.98543 | -0.58167 | 4.0271
172 | 0.12572 | 0.060839 | -0.12572 | -0.06089 | 1.2237e-07 | -5.1317e-05 | 0.0040926 | 0.0040933 | 0.0040933 | 0.98515 | -0.59156 | 0.98515 | -0.59161 | 0.49918
173 | 0.1265 | 0.058667 | -0.1265 | -0.061268 | 2.1345e-07 | -0.0026006 | 0.0040472 | 0.0040795 | 0.0040795 | 0.99462 | -0.17282 | 0.99462 | -0.17282 | 0.63942
174 | -6.4484 | -2.1079 | 6.457 | 2.0233 | 0.0086398 | -0.084643 | 0.1969 | 0.19608 | 0.1969 | 0.99462 | -0.17282 | 0.99619 | -0.13121 | 23.385
175 | 0.13594 | 0.063844 | -0.13594 | -0.065839 | 1.8831e-07 | -0.0019948 | 0.0043521 | 0.004377 | 0.004377 | 0.99619 | -0.13121 | 0.99619 | -0.13122 | 0.68605

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 11.6173 | 4.1772

## res_load
| p_mw | q_mvar
0 | 0.16151 | 0.078225
1 | 0.11928 | 0.057772
2 | 0.15024 | 0.072762
3 | 0.11156 | 0.054031
4 | 0.1474 | 0.07139
5 | 0.15386 | 0.074519
6 | 0.075912 | 0.036766
7 | 0.13974 | 0.067678
8 | 0.091127 | 0.044135
9 | 0.076911 | 0.03725
10 | 0.1358 | 0.065773
11 | 0.13653 | 0.066122
12 | 0.083393 | 0.040389
13 | 0.07432 | 0.035995
14 | 0.15976 | 0.077374
15 | 0.1122 | 0.054343
16 | 0.1579 | 0.076474
17 | 0.13517 | 0.065464
18 | 0.12125 | 0.058726
19 | 0.15625 | 0.075675
20 | 0.067985 | 0.032927
21 | 0.1521 | 0.073663
22 | 0.13495 | 0.065357
23 | 0.29908 | 0.14485
24 | 0.089658 | 0.043423
25 | 0.068243 | 0.033052
26 | 0.086691 | 0.041987
27 | 0.11233 | 0.054405
28 | 0.14297 | 0.069244
29 | 0.15089 | 0.073077
30 | 0.15993 | 0.077458
31 | 0.16269 | 0.078797
32 | 0.25786 | 0.12489
33 | 0.09452 | 0.045778
34 | 0.10797 | 0.052293
35 | 0.13347 | 0.064644
36 | 0.1043 | 0.050516
37 | 0.13302 | 0.064422
38 | 0.15673 | 0.075906
39 | 0.44533 | 0.21568
40 | 0.20348 | 0.098549
41 | 0.10864 | 0.052618
42 | 0.071522 | 0.03464
43 | 0.054637 | 0.026462
44 | 0.051343 | 0.024867
45 | 0.14883 | 0.072083
46 | 0.11699 | 0.056663
47 | 0.059052 | 0.0286
48 | 0.13482 | 0.065296
49 | 0.17503 | 0.084769
50 | 0.083143 | 0.040268
51 | 0.15741 | 0.076239
52 | 0.1122 | 0.054342
53 | 0.15738 | 0.076221
54 | 0.15689 | 0.075983
55 | 0.1377 | 0.066689
56 | 0.78221 | 0.37884
57 | 0.068028 | 0.032948
58 | 0.11465 | 0.055526
59 | 0.13209 | 0.063976
60 | 0.11199 | 0.054241
61 | 0.1598 | 0.077396
62 | 0.10069 | 0.048766
63 | 0.14862 | 0.071978
64 | 0.13054 | 0.063221
65 | 0.15284 | 0.074022
66 | 0.13646 | 0.066091
67 | 0.19161 | 0.092803
68 | 0.072237 | 0.034986
69 | 0.17621 | 0.085342
70 | 0.15758 | 0.076318
71 | 0.15629 | 0.075696
72 | 0.071207 | 0.034487
73 | 0.1636 | 0.079235
74 | 0.13303 | 0.064429
75 | 0.15719 | 0.076133
76 | 0.064351 | 0.031166
77 | 0.10074 | 0.04879
78 | 0.063729 | 0.030866
79 | 0.090741 | 0.043948
80 | 0.12572 | 0.06089
81 | 0.1265 | 0.061268
82 | 0.13594 | 0.065839

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1