## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_343_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_343_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_343_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_343_0_node_24 | 20 | n |  | TRUE
4 | bus_MV_343_0_node_52 | 20 | n |  | TRUE
5 | bus_MV_343_0_node_13 | 20 | n |  | TRUE
6 | bus_MV_343_0_node_51 | 20 | n |  | TRUE
7 | bus_MV_343_0_node_3 | 20 | n |  | TRUE
8 | bus_MV_343_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_343_0_node_4 | 20 | n |  | TRUE
10 | bus_MV_343_0_node_8 | 20 | n |  | TRUE
11 | bus_MV_343_0_node_6 | 20 | n |  | TRUE
12 | bus_MV_343_0_node_7 | 20 | n |  | TRUE
13 | bus_MV_343_0_node_9 | 20 | n |  | TRUE
14 | bus_MV_343_0_node_14 | 20 | n |  | TRUE
15 | bus_MV_343_0_node_58 | 20 | n |  | TRUE
16 | bus_MV_343_0_node_34 | 20 | n |  | TRUE
17 | bus_MV_343_0_node_12 | 20 | n |  | TRUE
18 | bus_MV_343_0_node_18 | 20 | n |  | TRUE
19 | bus_MV_343_0_node_59 | 20 | n |  | TRUE
20 | bus_MV_343_0_node_60 | 20 | n |  | TRUE
21 | bus_MV_343_0_node_55 | 20 | n |  | TRUE
22 | bus_MV_343_0_node_20 | 20 | n |  | TRUE
23 | bus_MV_343_0_node_61 | 20 | n |  | TRUE
24 | bus_MV_343_0_node_32 | 20 | n |  | TRUE
25 | bus_MV_343_0_node_33 | 20 | n |  | TRUE
26 | bus_MV_343_0_node_31 | 20 | n |  | TRUE
27 | bus_MV_343_0_node_10 | 20 | n |  | TRUE
28 | bus_MV_343_0_node_11 | 20 | n |  | TRUE
29 | bus_MV_343_0_node_15 | 20 | n |  | TRUE
30 | bus_MV_343_0_node_19 | 20 | n |  | TRUE
31 | bus_MV_343_0_node_23 | 20 | n |  | TRUE
32 | bus_MV_343_0_node_26 | 20 | n |  | TRUE
33 | bus_MV_343_0_node_16 | 20 | n |  | TRUE
34 | bus_MV_343_0_node_17 | 20 | n |  | TRUE
35 | bus_MV_343_0_node_27 | 20 | n |  | TRUE
36 | bus_MV_343_0_node_25 | 20 | n |  | TRUE
37 | bus_MV_343_0_node_49 | 20 | n |  | TRUE
38 | bus_MV_343_0_node_45 | 20 | n |  | TRUE
39 | bus_MV_343_0_node_54 | 20 | n |  | TRUE
40 | bus_MV_343_0_node_48 | 20 | n |  | TRUE
41 | bus_MV_343_0_node_42 | 20 | n |  | TRUE
42 | bus_MV_343_0_node_28 | 20 | n |  | TRUE
43 | bus_MV_343_0_node_29 | 20 | n |  | TRUE
44 | bus_MV_343_0_node_38 | 20 | n |  | TRUE
45 | bus_MV_343_0_node_39 | 20 | n |  | TRUE
46 | bus_MV_343_0_node_35 | 20 | n |  | TRUE
47 | bus_MV_343_0_node_62 | 20 | n |  | TRUE
48 | bus_MV_343_0_node_30 | 20 | n |  | TRUE
49 | bus_MV_343_0_node_56 | 20 | n |  | TRUE
50 | bus_MV_343_0_node_36 | 20 | n |  | TRUE
51 | bus_MV_343_0_node_37 | 20 | n |  | TRUE
52 | bus_MV_343_0_node_57 | 20 | n |  | TRUE
53 | bus_MV_343_0_node_40 | 20 | n |  | TRUE
54 | bus_MV_343_0_node_41 | 20 | n |  | TRUE
55 | bus_MV_343_0_node_43 | 20 | n |  | TRUE
56 | bus_MV_343_0_node_44 | 20 | n |  | TRUE
57 | bus_MV_343_0_node_46 | 20 | n |  | TRUE
58 | bus_MV_343_0_node_47 | 20 | n |  | TRUE
59 | bus_MV_343_0_node_53 | 20 | n |  | TRUE
60 | bus_MV_343_0_node_50 | 20 | n |  | TRUE
61 | bus_HV_343_0_node_10 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_343_0_load_0 | 0 | 0.12837 | 0.062171 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_343_0_load_52 | 4 | 0.19095 | 0.092482 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_343_0_load_13 | 5 | 0.14404 | 0.069761 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_343_0_load_3 | 7 | 0.11951 | 0.057879 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_343_0_load_9 | 13 | 0.08251 | 0.039961 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_343_0_load_14 | 14 | 0.056863 | 0.02754 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_343_0_load_34 | 16 | 0.16324 | 0.079059 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_343_0_load_59 | 19 | 0.092519 | 0.044809 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_343_0_load_55 | 21 | 0.086175 | 0.041737 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_343_0_load_20 | 22 | 0.084711 | 0.041027 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_343_0_load_61 | 23 | 0.11944 | 0.057847 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_343_0_load_15 | 29 | 0.16327 | 0.079075 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_343_0_load_23 | 31 | 0.068447 | 0.033151 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_343_0_load_25 | 36 | 0.1176 | 0.056956 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_343_0_load_49 | 37 | 0.088049 | 0.042644 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_343_0_load_54 | 39 | 0.2248 | 0.10888 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_343_0_load_48 | 40 | 1.2448 | 0.6029 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_343_0_load_28 | 42 | 0.077905 | 0.037731 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_343_0_load_38 | 44 | 0.14706 | 0.071222 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_343_0_load_35 | 46 | 0.056777 | 0.027498 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_343_0_load_62 | 47 | 0.07347 | 0.035583 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_343_0_load_30 | 48 | 0.14513 | 0.070289 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_343_0_load_56 | 49 | 0.12768 | 0.061836 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_343_0_load_36 | 50 | 0.16137 | 0.078154 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_343_0_load_37 | 51 | 0.071159 | 0.034464 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_343_0_load_57 | 52 | 0.15245 | 0.073835 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_343_0_load_41 | 54 | 0.54269 | 0.26284 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_343_0_load_43 | 55 | 0.18519 | 0.089693 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_343_0_load_44 | 56 | 1.3065 | 0.63275 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_343_0_load_46 | 57 | 0.81373 | 0.39411 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_343_0_load_47 | 58 | 0.26171 | 0.12675 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_343_0_load_53 | 59 | 0.15239 | 0.073805 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_343_0_load_50 | 60 | 0.57716 | 0.27953 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_343_0_line_0 |  | 0 | 1 | 0.029851 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_343_0_line_1 |  | 1 | 2 | 0.2435 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_343_0_line_2 |  | 2 | 3 | 0.29593 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
3 | MV_343_0_line_3 |  | 2 | 4 | 0.037964 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
4 | MV_343_0_line_4 |  | 3 | 5 | 0.067036 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
5 | MV_343_0_line_5 |  | 4 | 6 | 0.0060701 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
6 | MV_343_0_line_6 |  | 5 | 27 | 0.2003 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
7 | MV_343_0_line_7 |  | 5 | 28 | 0.30786 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_343_0_line_8 |  | 6 | 59 | 0.015264 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
9 | MV_343_0_line_9 |  | 6 | 60 | 0.022549 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_343_0_line_10 |  | 7 | 8 | 0.026456 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_343_0_line_11 |  | 7 | 9 | 0.21277 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_343_0_line_12 |  | 8 | 10 | 1.1579 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_343_0_line_13 |  | 9 | 11 | 0.32384 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_343_0_line_14 |  | 10 | 16 | 0.079786 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_343_0_line_15 |  | 11 | 12 | 0.38851 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_343_0_line_16 |  | 11 | 13 | 0.08979 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_343_0_line_17 |  | 12 | 14 | 0.034839 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_343_0_line_18 |  | 12 | 15 | 0.27472 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_343_0_line_19 |  | 14 | 17 | 0.14884 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_343_0_line_20 |  | 15 | 19 | 0.031456 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_343_0_line_21 |  | 16 | 24 | 0.17739 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_343_0_line_22 |  | 17 | 27 | 0.26636 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_343_0_line_23 |  | 18 | 19 | 0.063569 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_343_0_line_24 |  | 18 | 20 | 0.26639 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_343_0_line_25 |  | 20 | 23 | 0.13991 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_343_0_line_26 |  | 21 | 22 | 0.26531 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_343_0_line_27 |  | 22 | 34 | 0.006269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_343_0_line_28 |  | 24 | 25 | 0.13745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_343_0_line_29 |  | 24 | 26 | 0.31559 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_343_0_line_30 |  | 25 | 50 | 0.02728 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_343_0_line_31 |  | 26 | 48 | 0.020566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_343_0_line_32 |  | 28 | 29 | 0.06972 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_343_0_line_33 |  | 29 | 33 | 0.044255 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_343_0_line_34 |  | 30 | 31 | 0.17246 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_343_0_line_35 |  | 30 | 32 | 0.59628 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_343_0_line_36 |  | 32 | 35 | 0.16556 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_343_0_line_37 |  | 32 | 36 | 0.034055 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_343_0_line_38 |  | 33 | 34 | 0.37269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_343_0_line_39 |  | 35 | 37 | 0.026435 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
40 | MV_343_0_line_40 |  | 35 | 38 | 0.007275 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
41 | MV_343_0_line_41 |  | 37 | 39 | 0.018727 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
42 | MV_343_0_line_42 |  | 38 | 40 | 0.075966 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_343_0_line_43 |  | 38 | 41 | 0.048815 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_343_0_line_44 |  | 39 | 59 | 0.036839 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
45 | MV_343_0_line_45 |  | 40 | 58 | 0.0016279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_343_0_line_46 |  | 41 | 56 | 0.051789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_343_0_line_47 |  | 41 | 54 | 0.01815 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_343_0_line_48 |  | 42 | 43 | 0.040889 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_343_0_line_49 |  | 43 | 44 | 2.8918 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_343_0_line_50 |  | 44 | 45 | 0.055832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_343_0_line_51 |  | 45 | 53 | 0.27084 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_343_0_line_52 |  | 46 | 47 | 0.89787 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_343_0_line_53 |  | 46 | 48 | 2.0142 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_343_0_line_54 |  | 47 | 49 | 0.50557 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_343_0_line_55 |  | 50 | 51 | 0.010651 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_343_0_line_56 |  | 50 | 52 | 1.8493 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_343_0_line_57 |  | 52 | 53 | 0.079685 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_343_0_line_58 |  | 54 | 55 | 0.042293 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_343_0_line_59 |  | 55 | 57 | 0.043741 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_343_0_trafo_10 | 25 MVA 110/20 kV | 61 | 27 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2568264.0937 | 1261102.0947
1 | 2568265.523 | 1261072.2775
2 | 2568197.1106 | 1261092.6935
3 | 2568167.1231 | 1260939.4825
4 | 2568175.994 | 1261124.0083
5 | 2568143.4198 | 1260877.1451
6 | 2568173.4843 | 1261129.5353
7 | 2568266.815 | 1259901.3726
8 | 2568264.6005 | 1259875.0108
9 | 2568282.05 | 1260113.5925
10 | 2569087.6245 | 1259287.0472
11 | 2568211.6136 | 1260388.2168
12 | 2567935.1353 | 1260352.6665
13 | 2568183.5727 | 1260471.937
14 | 2567944.9781 | 1260386.0917
15 | 2567661.1011 | 1260333.2936
16 | 2569131.3098 | 1259220.7952
17 | 2567949.8036 | 1260534.8572
18 | 2567583.0243 | 1260384.4242
19 | 2567640.3795 | 1260357.0125
20 | 2567677.514 | 1260135.3558
21 | 2567218.9947 | 1260384.274
22 | 2567428.7812 | 1260546.6861
23 | 2567647.9342 | 1260004.8056
24 | 2569240.5872 | 1259081.0619
25 | 2569341.7541 | 1259024.3964
26 | 2569170.7455 | 1258859.141
27 | 2568135.8877 | 1260676.9917
28 | 2567864.3841 | 1260747.091
29 | 2567798.1476 | 1260733.3077
30 | 2567468.3053 | 1261137.8219
31 | 2567311.6253 | 1261065.7493
32 | 2568031.3119 | 1261334.2351
33 | 2567757.9515 | 1260714.7939
34 | 2567435.0241 | 1260545.94
35 | 2568122.3914 | 1261203.5403
36 | 2568059.662 | 1261353.228
37 | 2568145.9714 | 1261193.6111
38 | 2568117.4648 | 1261198.1744
39 | 2568156.6224 | 1261178.7298
40 | 2568145.6094 | 1261129.1684
41 | 2568080.9119 | 1261204.81
42 | 2574339.5023 | 1259210.1729
43 | 2574311.3979 | 1259181.22
44 | 2571431.5867 | 1259444.0699
45 | 2571396.7198 | 1259400.3867
46 | 2570486.2536 | 1257306.9657
47 | 2570037.6109 | 1256529.2213
48 | 2569182.1963 | 1258842.0361
49 | 2570523.9432 | 1256391.0675
50 | 2569350.4499 | 1258998.5425
51 | 2569340.2655 | 1258995.4232
52 | 2571172.0942 | 1259317.19
53 | 2571186.4842 | 1259238.8772
54 | 2568095.9899 | 1261194.707
55 | 2568123.144 | 1261162.9859
56 | 2568079.0744 | 1261167.4385
57 | 2568099.2843 | 1261126.3261
58 | 2568145.9561 | 1261127.5779
59 | 2568167.756 | 1261143.6766
60 | 2568194.6126 | 1261137.4118
61 | 2568135.8877 | 1260676.9917

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9975 | -0.054335 | 0.12837 | 0.062171
1 | 0.99751 | -0.054289 | 0 | 0
2 | 0.99755 | -0.054619 | 0 | 0
3 | 0.9985 | -0.044616 | 0 | 0
4 | 0.99743 | -0.055866 | 0.19095 | 0.092482
5 | 0.99871 | -0.042343 | 0.14404 | 0.069761
6 | 0.99741 | -0.056059 | 0 | 0
7 | 0.99718 | 0.0037988 | 0.11951 | 0.057879
8 | 0.99714 | 0.0040685 | 0 | 0
9 | 0.99771 | 0.0083002 | 0 | 0
10 | 0.99542 | 0.016941 | 0 | 0
11 | 0.99824 | 0.0046258 | 0 | 0
12 | 0.99891 | 0.00010189 | 0 | 0
13 | 0.99823 | 0.0047086 | 0.08251 | 0.039961
14 | 0.99898 | -0.00037013 | 0.056863 | 0.02754
15 | 0.9988 | -0.00071202 | 0 | 0
16 | 0.9953 | 0.017905 | 0.16324 | 0.079059
17 | 0.99945 | 0.0037245 | 0 | 0
18 | 0.99878 | -0.00075226 | 0 | 0
19 | 0.99879 | -0.00064029 | 0.092519 | 0.044809
20 | 0.99872 | -0.001217 | 0 | 0
21 | 0.99835 | -0.043239 | 0.086175 | 0.041737
22 | 0.9984 | -0.042958 | 0.084711 | 0.041027
23 | 0.9987 | -0.0010315 | 0.11944 | 0.057847
24 | 0.99496 | 0.015218 | 0 | 0
25 | 0.99485 | 0.016068 | 0 | 0
26 | 0.99479 | 0.01659 | 0 | 0
27 | 1 | 0 | -8.0649 | -3.7738
28 | 0.99852 | -0.043911 | 0 | 0
29 | 0.99849 | -0.043681 | 0.16327 | 0.079075
30 | 0.99704 | -0.058881 | 0 | 0
31 | 0.99702 | -0.059026 | 0.068447 | 0.033151
32 | 0.99712 | -0.058357 | 0 | 0
33 | 0.99848 | -0.043619 | 0 | 0
34 | 0.9984 | -0.042971 | 0 | 0
35 | 0.99716 | -0.058688 | 0 | 0
36 | 0.99711 | -0.058309 | 0.1176 | 0.056956
37 | 0.99722 | -0.058005 | 0.088049 | 0.042644
38 | 0.99714 | -0.058868 | 0 | 0
39 | 0.99727 | -0.057512 | 0.2248 | 0.10888
40 | 0.99699 | -0.057495 | 1.2448 | 0.6029
41 | 0.99696 | -0.057208 | 0 | 0
42 | 0.99294 | 0.0027934 | 0.077905 | 0.037731
43 | 0.99295 | 0.002756 | 0 | 0
44 | 0.99338 | 0.0061804 | 0.14706 | 0.071222
45 | 0.9934 | 0.0060463 | 0 | 0
46 | 0.99378 | 0.0098422 | 0.056777 | 0.027498
47 | 0.99343 | 0.0075447 | 0.07347 | 0.035583
48 | 0.99478 | 0.016685 | 0.14513 | 0.070289
49 | 0.9933 | 0.0067412 | 0.12768 | 0.061836
50 | 0.99483 | 0.01624 | 0.16137 | 0.078154
51 | 0.99483 | 0.016249 | 0.071159 | 0.034464
52 | 0.9935 | 0.0053123 | 0.15245 | 0.073835
53 | 0.99347 | 0.0054627 | 0 | 0
54 | 0.99693 | -0.056874 | 0.54269 | 0.26284
55 | 0.99687 | -0.056369 | 0.18519 | 0.089693
56 | 0.99688 | -0.056395 | 1.3065 | 0.63275
57 | 0.99683 | -0.055942 | 0.81373 | 0.39411
58 | 0.99699 | -0.05749 | 0.26171 | 0.12675
59 | 0.99737 | -0.056494 | 0.15239 | 0.073805
60 | 0.99739 | -0.055903 | 0.57716 | 0.27953
61 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.12837 | -0.062171 | 0.12837 | 0.062136 | 9.0607e-07 | -3.4892e-05 | 0.0041277 | 0.0041272 | 0.0041277 | 0.9975 | -0.054335 | 0.99751 | -0.054289 | 1.9656
1 | -0.12837 | -0.062136 | 0.12837 | 0.056352 | 5.4416e-06 | -0.0057834 | 0.0041272 | 0.0040571 | 0.0041272 | 0.99751 | -0.054289 | 0.99755 | -0.054619 | 1.876
2 | -5.9054 | -2.8366 | 5.9105 | 2.8302 | 0.0051339 | -0.0063812 | 0.18958 | 0.18946 | 0.18958 | 0.99755 | -0.054619 | 0.9985 | -0.044616 | 52.3714
3 | 5.777 | 2.7802 | -5.7764 | -2.7811 | 0.00063122 | -0.00083714 | 0.18553 | 0.18555 | 0.18555 | 0.99755 | -0.054619 | 0.99743 | -0.055866 | 51.2559
4 | -5.9105 | -2.8302 | 5.9117 | 2.8287 | 0.001162 | -0.0014489 | 0.18946 | 0.18943 | 0.18946 | 0.9985 | -0.044616 | 0.99871 | -0.042343 | 52.3365
5 | 5.5854 | 2.6886 | -5.5853 | -2.6887 | 9.4368e-05 | -0.00013859 | 0.17941 | 0.17941 | 0.17941 | 0.99743 | -0.055866 | 0.99741 | -0.056059 | 49.5603
6 | -6.3899 | -3.048 | 6.3959 | 3.0564 | 0.0059785 | 0.0083968 | 0.20464 | 0.20463 | 0.20464 | 0.99871 | -0.042343 | 1 | 0 | 49.9111
7 | 0.33425 | 0.14947 | -0.33419 | -0.1498 | 6.1462e-05 | -0.000328 | 0.010583 | 0.010588 | 0.010588 | 0.99871 | -0.042343 | 0.99852 | -0.043911 | 5.0418
8 | 5.0081 | 2.4097 | -5.0079 | -2.4101 | 0.00019077 | -0.0003823 | 0.16085 | 0.16086 | 0.16086 | 0.99741 | -0.056059 | 0.99737 | -0.056494 | 44.4367
9 | 0.57717 | 0.279 | -0.57716 | -0.27953 | 1.0367e-05 | -0.00053251 | 0.018554 | 0.018561 | 0.018561 | 0.99741 | -0.056059 | 0.99739 | -0.055903 | 8.4367
10 | 1.1799 | 0.50875 | -1.1799 | -0.50936 | 4.8879e-05 | -0.00061359 | 0.037198 | 0.037205 | 0.037205 | 0.99718 | 0.0037988 | 0.99714 | 0.0040685 | 16.9113
11 | -1.2994 | -0.56662 | 1.3001 | 0.56677 | 0.00063839 | 0.00014716 | 0.041038 | 0.041035 | 0.041038 | 0.99718 | 0.0037988 | 0.99771 | 0.0083002 | 19.542
12 | 1.1799 | 0.50936 | -1.1777 | -0.53616 | 0.002158 | -0.0268 | 0.037205 | 0.037527 | 0.037527 | 0.99714 | 0.0040685 | 0.99542 | 0.016941 | 17.0578
13 | -1.3001 | -0.56677 | 1.3008 | 0.55929 | 0.00072643 | -0.0074853 | 0.041035 | 0.040947 | 0.041035 | 0.99771 | 0.0083002 | 0.99824 | 0.0046258 | 18.6524
14 | 1.1777 | 0.53616 | -1.1776 | -0.538 | 0.00015009 | -0.0018428 | 0.037527 | 0.03755 | 0.03755 | 0.99542 | 0.016941 | 0.9953 | 0.017905 | 17.0681
15 | -1.3833 | -0.59711 | 1.3843 | 0.58815 | 0.00098226 | -0.0089583 | 0.043571 | 0.043466 | 0.043571 | 0.99824 | 0.0046258 | 0.99891 | 0.00010189 | 19.805
16 | 0.082511 | 0.037825 | -0.08251 | -0.039961 | 8.3411e-07 | -0.002136 | 0.0026249 | 0.0026512 | 0.0026512 | 0.99824 | 0.0046258 | 0.99823 | 0.0047086 | 1.2051
17 | -1.5963 | -0.68603 | 1.5964 | 0.68523 | 0.00011724 | -0.00079529 | 0.050211 | 0.050201 | 0.050211 | 0.99891 | 0.00010189 | 0.99898 | -0.00037013 | 22.8231
18 | 0.21199 | 0.097875 | -0.21197 | -0.098188 | 2.23e-05 | -0.00031324 | 0.0067478 | 0.0067518 | 0.0067518 | 0.99891 | 0.00010189 | 0.9988 | -0.00071202 | 3.2151
19 | -1.6533 | -0.71277 | 1.654 | 0.71305 | 0.00071775 | 0.00027217 | 0.052025 | 0.052023 | 0.052025 | 0.99898 | -0.00037013 | 0.99945 | 0.0037245 | 24.7739
20 | 0.21197 | 0.098188 | -0.21197 | -0.098937 | 1.9169e-06 | -0.00074867 | 0.0067518 | 0.0067609 | 0.0067609 | 0.9988 | -0.00071202 | 0.99879 | -0.00064029 | 3.0731
21 | 1.0143 | 0.45894 | -1.014 | -0.45895 | 0.00032958 | -3.2737e-06 | 0.032291 | 0.032293 | 0.032293 | 0.9953 | 0.017905 | 0.99496 | 0.015218 | 15.3778
22 | -1.654 | -0.71305 | 1.6549 | 0.70697 | 0.00096104 | -0.0060711 | 0.052023 | 0.051951 | 0.052023 | 0.99945 | 0.0037245 | 1 | 0 | 23.6469
23 | -0.11945 | -0.054203 | 0.11945 | 0.054128 | 1.6275e-06 | -7.4685e-05 | 0.0037912 | 0.0037903 | 0.0037912 | 0.99878 | -0.00075226 | 0.99879 | -0.00064029 | 1.8053
24 | 0.11945 | 0.054203 | -0.11944 | -0.054516 | 6.8288e-06 | -0.00031294 | 0.0037912 | 0.003795 | 0.003795 | 0.99878 | -0.00075226 | 0.99872 | -0.001217 | 1.8071
25 | 0.11944 | 0.054516 | -0.11944 | -0.057847 | 2.7189e-06 | -0.0033312 | 0.003795 | 0.003836 | 0.003836 | 0.99872 | -0.001217 | 0.9987 | -0.0010315 | 1.7436
26 | -0.086175 | -0.041737 | 0.086179 | 0.041423 | 3.6182e-06 | -0.00031343 | 0.0027686 | 0.0027647 | 0.0027686 | 0.99835 | -0.043239 | 0.9984 | -0.042958 | 1.3184
27 | -0.17089 | -0.082451 | 0.17089 | 0.082302 | 2.5179e-07 | -0.00014913 | 0.0054861 | 0.0054843 | 0.0054861 | 0.9984 | -0.042958 | 0.9984 | -0.042971 | 2.4937
28 | 0.61055 | 0.27549 | -0.61049 | -0.27871 | 6.9442e-05 | -0.0032277 | 0.019434 | 0.019473 | 0.019473 | 0.99496 | 0.015218 | 0.99485 | 0.016068 | 8.8515
29 | 0.40345 | 0.18346 | -0.40338 | -0.1909 | 7.0158e-05 | -0.0074372 | 0.012859 | 0.01295 | 0.01295 | 0.99496 | 0.015218 | 0.99479 | 0.01659 | 5.8865
30 | 0.61049 | 0.27871 | -0.61047 | -0.27935 | 1.3816e-05 | -0.00064053 | 0.019473 | 0.019481 | 0.019481 | 0.99485 | 0.016068 | 0.99483 | 0.01624 | 8.855
31 | 0.40338 | 0.1909 | -0.40338 | -0.19138 | 4.6067e-06 | -0.00048457 | 0.01295 | 0.012956 | 0.012956 | 0.99479 | 0.01659 | 0.99478 | 0.016685 | 5.8892
32 | 0.33419 | 0.1498 | -0.33418 | -0.15146 | 1.0453e-05 | -0.0016566 | 0.010588 | 0.010607 | 0.010607 | 0.99852 | -0.043911 | 0.99849 | -0.043681 | 4.8216
33 | 0.17091 | 0.072382 | -0.17091 | -0.073435 | 1.7049e-06 | -0.0010529 | 0.005366 | 0.005378 | 0.005378 | 0.99849 | -0.043681 | 0.99848 | -0.043619 | 2.4445
34 | 0.068449 | 0.032947 | -0.068447 | -0.033151 | 1.4882e-06 | -0.00020373 | 0.0021994 | 0.002202 | 0.002202 | 0.99704 | -0.058881 | 0.99702 | -0.059026 | 1.0486
35 | -0.068449 | -0.032947 | 0.068454 | 0.032242 | 5.1188e-06 | -0.00070449 | 0.0021994 | 0.0021906 | 0.0021994 | 0.99704 | -0.058881 | 0.99712 | -0.058357 | 1.0474
36 | -0.18605 | -0.08839 | 0.18606 | 0.084462 | 7.7961e-06 | -0.0039279 | 0.0059634 | 0.0059154 | 0.0059634 | 0.99712 | -0.058357 | 0.99716 | -0.058688 | 2.7106
37 | 0.1176 | 0.056147 | -0.1176 | -0.056956 | 6.4885e-07 | -0.00080822 | 0.0037728 | 0.0037829 | 0.0037829 | 0.99712 | -0.058357 | 0.99711 | -0.058309 | 1.7195
38 | 0.17091 | 0.073435 | -0.17089 | -0.082302 | 1.4669e-05 | -0.0088663 | 0.005378 | 0.0054843 | 0.0054843 | 0.99848 | -0.043619 | 0.9984 | -0.042971 | 2.4928
39 | -4.5418 | -2.1869 | 4.5421 | 2.1862 | 0.00027189 | -0.00070421 | 0.14593 | 0.14592 | 0.14593 | 0.99716 | -0.058688 | 0.99722 | -0.058005 | 40.3129
40 | 4.3557 | 2.1024 | -4.3557 | -2.1026 | 6.8891e-05 | -0.00019809 | 0.14002 | 0.14002 | 0.14002 | 0.99716 | -0.058688 | 0.99714 | -0.058868 | 38.6801
41 | -4.6301 | -2.2289 | 4.6303 | 2.2284 | 0.00020014 | -0.00049347 | 0.14875 | 0.14875 | 0.14875 | 0.99722 | -0.058005 | 0.99727 | -0.057512 | 41.0921
42 | 1.5068 | 0.72788 | -1.5065 | -0.72961 | 0.00023812 | -0.0017325 | 0.048444 | 0.048467 | 0.048467 | 0.99714 | -0.058868 | 0.99699 | -0.057495 | 22.0306
43 | 2.8489 | 1.3748 | -2.8484 | -1.3758 | 0.00054662 | -0.00099652 | 0.091578 | 0.091592 | 0.091592 | 0.99714 | -0.058868 | 0.99696 | -0.057208 | 41.6328
44 | -4.8551 | -2.3372 | 4.8556 | 2.3363 | 0.00043284 | -0.0009425 | 0.15598 | 0.15596 | 0.15598 | 0.99727 | -0.057512 | 0.99737 | -0.056494 | 43.0872
45 | 0.26171 | 0.12671 | -0.26171 | -0.12675 | 1.5405e-07 | -3.8588e-05 | 0.0084191 | 0.0084196 | 0.0084196 | 0.99699 | -0.057495 | 0.99699 | -0.05749 | 3.8271
46 | 1.3066 | 0.63156 | -1.3065 | -0.63275 | 0.00012213 | -0.0011927 | 0.042021 | 0.042036 | 0.042036 | 0.99696 | -0.057208 | 0.99688 | -0.056395 | 19.1074
47 | 1.5418 | 0.74421 | -1.5417 | -0.74462 | 5.9548e-05 | -0.00041304 | 0.049571 | 0.049577 | 0.049577 | 0.99696 | -0.057208 | 0.99693 | -0.056874 | 22.5349
48 | -0.077905 | -0.037731 | 0.077906 | 0.036769 | 3.4404e-07 | -0.00096244 | 0.0025166 | 0.0025045 | 0.0025166 | 0.99294 | 0.0027934 | 0.99295 | 0.002756 | 1.1439
49 | -0.077906 | -0.036769 | 0.077937 | 0.033384 | 3.1785e-05 | -0.0033853 | 0.0025045 | 0.0024639 | 0.0025045 | 0.99295 | 0.002756 | 0.99338 | 0.0061804 | 1.1926
50 | -0.22499 | -0.10461 | 0.225 | 0.10329 | 3.8664e-06 | -0.0013143 | 0.0072104 | 0.0071943 | 0.0072104 | 0.99338 | 0.0061804 | 0.9934 | 0.0060463 | 3.2774
51 | -0.225 | -0.10329 | 0.22502 | 0.096915 | 1.8516e-05 | -0.0063765 | 0.0071943 | 0.007119 | 0.0071943 | 0.9934 | 0.0060463 | 0.99347 | 0.0054627 | 3.2702
52 | 0.20123 | 0.095817 | -0.20116 | -0.096833 | 6.7189e-05 | -0.0010161 | 0.0064741 | 0.0064874 | 0.0064874 | 0.99378 | 0.0098422 | 0.99343 | 0.0075447 | 3.0892
53 | -0.258 | -0.12332 | 0.25825 | 0.12109 | 0.00024674 | -0.0022226 | 0.0083066 | 0.0082771 | 0.0083066 | 0.99378 | 0.0098422 | 0.99478 | 0.016685 | 3.9555
54 | 0.12769 | 0.06125 | -0.12768 | -0.061836 | 1.5283e-05 | -0.000586 | 0.0041153 | 0.0041228 | 0.0041228 | 0.99343 | 0.0075447 | 0.9933 | 0.0067412 | 1.9632
55 | 0.071159 | 0.034212 | -0.071159 | -0.034464 | 7.4748e-08 | -0.00025167 | 0.0022911 | 0.0022943 | 0.0022943 | 0.99483 | 0.01624 | 0.99483 | 0.016249 | 1.0429
56 | 0.37794 | 0.16699 | -0.37747 | -0.16887 | 0.00047468 | -0.0018847 | 0.01199 | 0.012016 | 0.012016 | 0.99483 | 0.01624 | 0.9935 | 0.0053123 | 5.7217
57 | 0.22502 | 0.095039 | -0.22502 | -0.096915 | 5.375e-06 | -0.0018763 | 0.0070976 | 0.007119 | 0.007119 | 0.9935 | 0.0053123 | 0.99347 | 0.0054627 | 3.2359
58 | 0.99902 | 0.48179 | -0.99896 | -0.48277 | 5.8261e-05 | -0.00098627 | 0.032116 | 0.032129 | 0.032129 | 0.99693 | -0.056874 | 0.99687 | -0.056369 | 14.6041
59 | 0.81377 | 0.39308 | -0.81373 | -0.39411 | 4.0013e-05 | -0.0010259 | 0.02617 | 0.026183 | 0.026183 | 0.99687 | -0.056369 | 0.99683 | -0.055942 | 11.9015

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 8.0649 | 3.7738

## res_load
| p_mw | q_mvar
0 | 0.12837 | 0.062171
1 | 0.19095 | 0.092482
2 | 0.14404 | 0.069761
3 | 0.11951 | 0.057879
4 | 0.08251 | 0.039961
5 | 0.056863 | 0.02754
6 | 0.16324 | 0.079059
7 | 0.092519 | 0.044809
8 | 0.086175 | 0.041737
9 | 0.084711 | 0.041027
10 | 0.11944 | 0.057847
11 | 0.16327 | 0.079075
12 | 0.068447 | 0.033151
13 | 0.1176 | 0.056956
14 | 0.088049 | 0.042644
15 | 0.2248 | 0.10888
16 | 1.2448 | 0.6029
17 | 0.077905 | 0.037731
18 | 0.14706 | 0.071222
19 | 0.056777 | 0.027498
20 | 0.07347 | 0.035583
21 | 0.14513 | 0.070289
22 | 0.12768 | 0.061836
23 | 0.16137 | 0.078154
24 | 0.071159 | 0.034464
25 | 0.15245 | 0.073835
26 | 0.54269 | 0.26284
27 | 0.18519 | 0.089693
28 | 1.3065 | 0.63275
29 | 0.81373 | 0.39411
30 | 0.26171 | 0.12675
31 | 0.15239 | 0.073805
32 | 0.57716 | 0.27953

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1