## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_344_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_344_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_344_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_344_0_node_2 | 20 | n |  | TRUE
4 | bus_MV_344_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_344_0_node_5 | 20 | n |  | TRUE
6 | bus_MV_344_0_node_8 | 20 | n |  | TRUE
7 | bus_MV_344_0_node_38 | 20 | n |  | TRUE
8 | bus_MV_344_0_node_6 | 20 | n |  | TRUE
9 | bus_MV_344_0_node_7 | 20 | n |  | TRUE
10 | bus_MV_344_0_node_10 | 20 | n |  | TRUE
11 | bus_MV_344_0_node_9 | 20 | n |  | TRUE
12 | bus_MV_344_0_node_11 | 20 | n |  | TRUE
13 | bus_MV_344_0_node_12 | 20 | n |  | TRUE
14 | bus_MV_344_0_node_183 | 20 | n |  | TRUE
15 | bus_MV_344_0_node_39 | 20 | n |  | TRUE
16 | bus_MV_344_0_node_42 | 20 | n |  | TRUE
17 | bus_MV_344_0_node_34 | 20 | n |  | TRUE
18 | bus_MV_344_0_node_35 | 20 | n |  | TRUE
19 | bus_MV_344_0_node_36 | 20 | n |  | TRUE
20 | bus_MV_344_0_node_187 | 20 | n |  | TRUE
21 | bus_MV_344_0_node_37 | 20 | n |  | TRUE
22 | bus_MV_344_0_node_40 | 20 | n |  | TRUE
23 | bus_MV_344_0_node_41 | 20 | n |  | TRUE
24 | bus_MV_344_0_node_48 | 20 | n |  | TRUE
25 | bus_MV_344_0_node_43 | 20 | n |  | TRUE
26 | bus_MV_344_0_node_51 | 20 | n |  | TRUE
27 | bus_MV_344_0_node_50 | 20 | n |  | TRUE
28 | bus_MV_344_0_node_49 | 20 | n |  | TRUE
29 | bus_MV_344_0_node_52 | 20 | n |  | TRUE
30 | bus_MV_344_0_node_53 | 20 | n |  | TRUE
31 | bus_MV_344_0_node_54 | 20 | n |  | TRUE
32 | bus_MV_344_0_node_55 | 20 | n |  | TRUE
33 | bus_MV_344_0_node_57 | 20 | n |  | TRUE
34 | bus_MV_344_0_node_56 | 20 | n |  | TRUE
35 | bus_MV_344_0_node_59 | 20 | n |  | TRUE
36 | bus_MV_344_0_node_58 | 20 | n |  | TRUE
37 | bus_MV_344_0_node_65 | 20 | n |  | TRUE
38 | bus_MV_344_0_node_61 | 20 | n |  | TRUE
39 | bus_MV_344_0_node_62 | 20 | n |  | TRUE
40 | bus_MV_344_0_node_63 | 20 | n |  | TRUE
41 | bus_MV_344_0_node_64 | 20 | n |  | TRUE
42 | bus_MV_344_0_node_185 | 20 | n |  | TRUE
43 | bus_HV_344_0_node_65 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_344_0_load_0 | 0 | 0.11977 | 0.058005 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_344_0_load_4 | 4 | 0.09139 | 0.044262 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_344_0_load_5 | 5 | 0.073303 | 0.035502 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_344_0_load_8 | 6 | 0.15967 | 0.07733 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_344_0_load_10 | 10 | 0.087612 | 0.042432 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_344_0_load_9 | 11 | 0.087829 | 0.042538 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_344_0_load_11 | 12 | 0.14177 | 0.06866 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_344_0_load_12 | 13 | 0.14119 | 0.068382 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_344_0_load_183 | 14 | 0.12646 | 0.061249 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_344_0_load_34 | 17 | 0.064592 | 0.031283 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_344_0_load_187 | 20 | 0.097125 | 0.04704 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_344_0_load_37 | 21 | 0.08875 | 0.042984 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_344_0_load_40 | 22 | 0.13608 | 0.065907 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_344_0_load_48 | 24 | 0.14483 | 0.070142 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_344_0_load_51 | 26 | 0.10565 | 0.051168 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_344_0_load_49 | 28 | 0.079062 | 0.038291 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_344_0_load_53 | 30 | 0.11285 | 0.054653 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_344_0_load_59 | 35 | 0.099558 | 0.048218 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_344_0_load_58 | 36 | 0.15228 | 0.073752 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_344_0_load_65 | 37 | 0.087539 | 0.042397 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_344_0_load_62 | 39 | 0.10605 | 0.051361 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_344_0_load_64 | 41 | 0.78745 | 0.38138 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_344_0_load_185 | 42 | 0.32256 | 0.15622 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 37 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_344_0_line_0 |  | 0 | 1 | 0.086368 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_344_0_line_1 |  | 1 | 2 | 0.14226 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_344_0_line_2 |  | 2 | 6 | 0.018497 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_344_0_line_3 |  | 3 | 4 | 0.034943 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
4 | MV_344_0_line_4 |  | 3 | 5 | 0.25923 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
5 | MV_344_0_line_5 |  | 4 | 7 | 4.6548 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
6 | MV_344_0_line_6 |  | 5 | 8 | 0.1239 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
7 | MV_344_0_line_7 |  | 6 | 11 | 0.017735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_344_0_line_8 |  | 6 | 10 | 0.06509 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_344_0_line_9 |  | 7 | 15 | 0.27373 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
10 | MV_344_0_line_10 |  | 7 | 21 | 0.020337 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_344_0_line_11 |  | 8 | 9 | 0.1111 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
12 | MV_344_0_line_12 |  | 9 | 10 | 0.044373 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
13 | MV_344_0_line_13 |  | 10 | 12 | 0.076037 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
14 | MV_344_0_line_14 |  | 12 | 13 | 0.14123 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_344_0_line_15 |  | 14 | 15 | 2.8751 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
16 | MV_344_0_line_16 |  | 14 | 16 | 0.13327 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
17 | MV_344_0_line_17 |  | 15 | 20 | 0.069012 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_344_0_line_18 |  | 16 | 23 | 0.15497 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
19 | MV_344_0_line_19 |  | 17 | 18 | 0.034751 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_344_0_line_20 |  | 18 | 19 | 0.55446 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_344_0_line_21 |  | 19 | 20 | 0.03788 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_344_0_line_22 |  | 22 | 23 | 0.039695 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_344_0_line_23 |  | 22 | 24 | 2.1942 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_344_0_line_24 |  | 23 | 25 | 1.3961 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
25 | MV_344_0_line_25 |  | 24 | 27 | 2.1136 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_344_0_line_26 |  | 25 | 26 | 0.077353 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
27 | MV_344_0_line_27 |  | 26 | 29 | 0.037426 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
28 | MV_344_0_line_28 |  | 27 | 28 | 0.030991 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_344_0_line_29 |  | 29 | 30 | 2.9593 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
30 | MV_344_0_line_30 |  | 30 | 31 | 0.10089 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
31 | MV_344_0_line_31 |  | 31 | 32 | 0.26053 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_344_0_line_32 |  | 31 | 33 | 0.50789 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
33 | MV_344_0_line_33 |  | 32 | 34 | 0.12084 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_344_0_line_34 |  | 32 | 35 | 0.060114 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_344_0_line_35 |  | 33 | 37 | 0.082325 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
36 | MV_344_0_line_36 |  | 34 | 36 | 0.01958 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_344_0_line_37 |  | 35 | 38 | 0.29855 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_344_0_line_38 |  | 38 | 39 | 0.020391 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_344_0_line_39 |  | 39 | 40 | 0.11631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_344_0_line_40 |  | 40 | 41 | 0.029572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_344_0_line_41 |  | 41 | 42 | 2.4621 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_344_0_trafo_65 | 25 MVA 110/20 kV | 43 | 37 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2567189.0736 | 1254727.716
1 | 2567268.0101 | 1254692.1427
2 | 2567389.3993 | 1254627.7276
3 | 2567506.6179 | 1254276.6894
4 | 2567486.3872 | 1254248.1593
5 | 2567647.0448 | 1254494.5872
6 | 2567407.5641 | 1254624.2389
7 | 2563392.6144 | 1252032.646
8 | 2567571.3671 | 1254592.8352
9 | 2567501.7777 | 1254670.2811
10 | 2567467.0839 | 1254642.7925
11 | 2567404.1901 | 1254606.8274
12 | 2567437.7157 | 1254712.9295
13 | 2567485.3284 | 1254845.8902
14 | 2562185.1942 | 1249319.0481
15 | 2563130.2855 | 1252034.4005
16 | 2562246.7285 | 1249201.1765
17 | 2562602.5113 | 1252428.7491
18 | 2562631.5194 | 1252448.0118
19 | 2563069.3494 | 1252115.58
20 | 2563102.8269 | 1252097.7144
21 | 2563399.9316 | 1252013.9215
22 | 2562242.591 | 1249081.8682
23 | 2562281.563 | 1249080.2628
24 | 2561096.4516 | 1247210.8269
25 | 2563572.5187 | 1248957.5746
26 | 2563649.9646 | 1248957.7535
27 | 2558994.1752 | 1246992.4179
28 | 2558963.11 | 1246991.3771
29 | 2563665.3133 | 1248991.904
30 | 2566624.3118 | 1249033.1938
31 | 2566721.9706 | 1249059.227
32 | 2566962.0744 | 1249099.3508
33 | 2566786.7058 | 1249381.3197
34 | 2566940.9397 | 1248989.7857
35 | 2567014.3227 | 1249129.2453
36 | 2566947.0495 | 1248971.1837
37 | 2566761.7915 | 1249445.7467
38 | 2567190.5236 | 1249370.2567
39 | 2567190.3719 | 1249390.5265
40 | 2567290.6608 | 1249449.9319
41 | 2567315.3291 | 1249466.2399
42 | 2569656.9879 | 1248705.7298
43 | 2566761.7915 | 1249445.7467

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98482 | -0.49687 | 0.11977 | 0.058005
1 | 0.98483 | -0.49699 | 0 | 0
2 | 0.98485 | -0.49717 | 0 | 0
3 | 0.98525 | -0.48967 | 0 | 0
4 | 0.98527 | -0.48949 | 0.09139 | 0.044262
5 | 0.985 | -0.49613 | 0.073303 | 0.035502
6 | 0.98486 | -0.49713 | 0.15967 | 0.07733
7 | 0.98949 | -0.34472 | 0 | 0
8 | 0.98495 | -0.4967 | 0 | 0
9 | 0.98491 | -0.4972 | 0 | 0
10 | 0.98489 | -0.4974 | 0.087612 | 0.042432
11 | 0.98485 | -0.49711 | 0.087829 | 0.042538
12 | 0.98486 | -0.49804 | 0.14177 | 0.06866
13 | 0.98482 | -0.49829 | 0.14119 | 0.068382
14 | 0.99289 | -0.22671 | 0.12646 | 0.061249
15 | 0.98961 | -0.34248 | 0 | 0
16 | 0.99296 | -0.22527 | 0 | 0
17 | 0.98954 | -0.34251 | 0.064592 | 0.031283
18 | 0.98954 | -0.34254 | 0 | 0
19 | 0.98959 | -0.34271 | 0 | 0
20 | 0.98959 | -0.34271 | 0.097125 | 0.04704
21 | 0.98949 | -0.3447 | 0.08875 | 0.042984
22 | 0.99303 | -0.22343 | 0.13608 | 0.065907
23 | 0.99305 | -0.22359 | 0 | 0
24 | 0.99208 | -0.23031 | 0.14483 | 0.070142
25 | 0.99403 | -0.20369 | 0 | 0
26 | 0.99408 | -0.20255 | 0.10565 | 0.051168
27 | 0.99176 | -0.23272 | 0 | 0
28 | 0.99175 | -0.23269 | 0.079062 | 0.038291
29 | 0.99411 | -0.20197 | 0 | 0
30 | 0.99908 | -0.018183 | 0.11285 | 0.054653
31 | 0.99916 | -0.016535 | 0 | 0
32 | 0.99867 | -0.012186 | 0 | 0
33 | 0.99988 | -0.0023186 | 0 | 0
34 | 0.99865 | -0.011977 | 0 | 0
35 | 0.99857 | -0.011266 | 0.099558 | 0.048218
36 | 0.99864 | -0.012013 | 0.15228 | 0.073752
37 | 1 | 0 | -3.3591 | -1.4684
38 | 0.99787 | -0.015851 | 0 | 0
39 | 0.99783 | -0.015562 | 0.10605 | 0.051361
40 | 0.99767 | -0.014046 | 0 | 0
41 | 0.99763 | -0.013658 | 0.78745 | 0.38138
42 | 0.99609 | -0.023622 | 0.32256 | 0.15622
43 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.11977 | -0.058005 | 0.11977 | 0.056006 | 1.743e-06 | -0.0019995 | 0.0039007 | 0.0038755 | 0.0039007 | 0.98482 | -0.49687 | 0.98483 | -0.49699 | 1.7731
1 | -0.11977 | -0.056006 | 0.11977 | 0.052712 | 2.8228e-06 | -0.0032935 | 0.0038755 | 0.0038356 | 0.0038755 | 0.98483 | -0.49699 | 0.98485 | -0.49717 | 1.7616
2 | -0.11977 | -0.052712 | 0.11977 | 0.052691 | 4.8481e-07 | -2.1114e-05 | 0.0038356 | 0.0038354 | 0.0038356 | 0.98485 | -0.49717 | 0.98486 | -0.49713 | 1.8265
3 | -0.8114 | -0.376 | 0.81141 | 0.37485 | 1.1581e-05 | -0.0011553 | 0.026202 | 0.026188 | 0.026202 | 0.98525 | -0.48967 | 0.98527 | -0.48949 | 7.2382
4 | 0.8114 | 0.376 | -0.81124 | -0.37613 | 0.00016341 | -0.00012923 | 0.026202 | 0.026206 | 0.026206 | 0.98525 | -0.48967 | 0.985 | -0.49613 | 7.4875
5 | -0.9028 | -0.41911 | 0.90562 | 0.41731 | 0.0028149 | -0.0017985 | 0.029163 | 0.029091 | 0.029163 | 0.98527 | -0.48949 | 0.98949 | -0.34472 | 7.1129
6 | 0.73793 | 0.34063 | -0.7379 | -0.34473 | 3.4027e-05 | -0.0040991 | 0.02382 | 0.023871 | 0.023871 | 0.985 | -0.49613 | 0.98495 | -0.4967 | 6.5941
7 | 0.08783 | 0.042127 | -0.087829 | -0.042538 | 1.9338e-07 | -0.00041067 | 0.0028552 | 0.0028605 | 0.0028605 | 0.98486 | -0.49713 | 0.98485 | -0.49711 | 1.3002
8 | -0.36727 | -0.17215 | 0.36728 | 0.17064 | 1.2263e-05 | -0.0015038 | 0.011889 | 0.01187 | 0.011889 | 0.98486 | -0.49713 | 0.98489 | -0.4974 | 5.4041
9 | -0.99437 | -0.45982 | 0.99447 | 0.44967 | 0.00010194 | -0.010146 | 0.031961 | 0.031837 | 0.031961 | 0.98949 | -0.34472 | 0.98961 | -0.34248 | 7.5917
10 | 0.08875 | 0.042508 | -0.08875 | -0.042984 | 2.2424e-07 | -0.00047535 | 0.0028709 | 0.0028769 | 0.0028769 | 0.98949 | -0.34472 | 0.98949 | -0.3447 | 1.3077
11 | 0.7379 | 0.34473 | -0.73787 | -0.3484 | 3.0635e-05 | -0.0036751 | 0.023871 | 0.023917 | 0.023917 | 0.98495 | -0.4967 | 0.98491 | -0.4972 | 6.6068
12 | 0.73787 | 0.3484 | -0.73786 | -0.34987 | 1.2269e-05 | -0.0014677 | 0.023917 | 0.023935 | 0.023935 | 0.98491 | -0.4972 | 0.98489 | -0.4974 | 6.6119
13 | 0.28297 | 0.1368 | -0.28296 | -0.13688 | 5.9245e-06 | -8.5906e-05 | 0.0092122 | 0.0092134 | 0.0092134 | 0.98489 | -0.4974 | 0.98486 | -0.49804 | 2.6324
14 | 0.1412 | 0.068221 | -0.14119 | -0.068382 | 5.3185e-06 | -0.0001602 | 0.0045964 | 0.0045985 | 0.0045985 | 0.98486 | -0.49804 | 0.98482 | -0.49829 | 2.1897
15 | 1.159 | 0.51364 | -1.1562 | -0.51326 | 0.0027873 | 0.00037894 | 0.036857 | 0.036901 | 0.036901 | 0.99289 | -0.22671 | 0.98961 | -0.34248 | 9.0001
16 | -1.2854 | -0.57488 | 1.2855 | 0.56994 | 8.1637e-05 | -0.0049444 | 0.040941 | 0.040881 | 0.040941 | 0.99289 | -0.22671 | 0.99296 | -0.22527 | 9.7246
17 | 0.16172 | 0.063584 | -0.16172 | -0.063662 | 3.16e-06 | -7.8703e-05 | 0.0050691 | 0.0050699 | 0.0050699 | 0.98961 | -0.34248 | 0.98959 | -0.34271 | 2.4143
18 | -1.2855 | -0.56994 | 1.2856 | 0.56419 | 9.4635e-05 | -0.0057508 | 0.040881 | 0.040813 | 0.040881 | 0.99296 | -0.22527 | 0.99305 | -0.22359 | 9.7105
19 | -0.064592 | -0.031283 | 0.064592 | 0.030471 | 2.0237e-07 | -0.0008124 | 0.0020937 | 0.0020835 | 0.0020937 | 0.98954 | -0.34251 | 0.98954 | -0.34254 | 0.95167
20 | -0.064592 | -0.030471 | 0.064595 | 0.017508 | 2.9907e-06 | -0.012963 | 0.0020835 | 0.0019523 | 0.0020835 | 0.98954 | -0.34254 | 0.98959 | -0.34271 | 0.94703
21 | -0.064595 | -0.017508 | 0.064595 | 0.016623 | 1.9209e-07 | -0.00088564 | 0.0019523 | 0.0019457 | 0.0019523 | 0.98959 | -0.34271 | 0.98959 | -0.34271 | 0.88741
22 | -0.36019 | -0.16869 | 0.3602 | 0.16776 | 7.0774e-06 | -0.00093251 | 0.011562 | 0.011551 | 0.011562 | 0.99303 | -0.22343 | 0.99305 | -0.22359 | 5.2556
23 | 0.22411 | 0.10278 | -0.22391 | -0.10524 | 0.00020172 | -0.0024542 | 0.0071675 | 0.0071991 | 0.0071991 | 0.99303 | -0.22343 | 0.99208 | -0.23031 | 3.4281
24 | -1.6458 | -0.73195 | 1.6472 | 0.68057 | 0.0013846 | -0.051375 | 0.052361 | 0.051758 | 0.052361 | 0.99305 | -0.22359 | 0.99403 | -0.20369 | 12.4374
25 | 0.079086 | 0.035096 | -0.079062 | -0.037564 | 2.4153e-05 | -0.0024675 | 0.0025177 | 0.0025478 | 0.0025478 | 0.99208 | -0.23031 | 0.99176 | -0.23272 | 1.2132
26 | -1.6472 | -0.68057 | 1.6473 | 0.67772 | 7.5796e-05 | -0.0028504 | 0.051758 | 0.051726 | 0.051758 | 0.99403 | -0.20369 | 0.99408 | -0.20255 | 12.2942
27 | -1.7529 | -0.72889 | 1.753 | 0.72752 | 4.1619e-05 | -0.0013747 | 0.055129 | 0.055113 | 0.055129 | 0.99408 | -0.20255 | 0.99411 | -0.20197 | 13.0948
28 | 0.079062 | 0.037564 | -0.079062 | -0.038291 | 2.6953e-07 | -0.00072772 | 0.0025478 | 0.002557 | 0.002557 | 0.99176 | -0.23272 | 0.99175 | -0.23269 | 1.1623
29 | -1.753 | -0.72752 | 1.7594 | 0.73298 | 0.0064023 | 0.005465 | 0.055113 | 0.055071 | 0.055113 | 0.99411 | -0.20197 | 0.99908 | -0.018183 | 13.4423
30 | -1.8722 | -0.78763 | 1.8723 | 0.7839 | 0.00012709 | -0.0037306 | 0.058688 | 0.058645 | 0.058688 | 0.99908 | -0.018183 | 0.99916 | -0.016535 | 13.9403
31 | 1.4704 | 0.69433 | -1.4696 | -0.70031 | 0.00076891 | -0.0059787 | 0.046981 | 0.047057 | 0.047057 | 0.99916 | -0.016535 | 0.99867 | -0.012186 | 21.3897
32 | -3.3427 | -1.4782 | 3.3448 | 1.4607 | 0.0020685 | -0.017485 | 0.1056 | 0.10537 | 0.1056 | 0.99916 | -0.016535 | 0.99988 | -0.0023186 | 25.0831
33 | 0.15228 | 0.070852 | -0.15228 | -0.073729 | 3.8303e-06 | -0.0028763 | 0.004855 | 0.0048907 | 0.0048907 | 0.99867 | -0.012186 | 0.99865 | -0.011977 | 2.223
34 | 1.3173 | 0.62946 | -1.3172 | -0.63084 | 0.00014299 | -0.0013889 | 0.042203 | 0.04222 | 0.04222 | 0.99867 | -0.012186 | 0.99857 | -0.011266 | 19.1911
35 | -3.3448 | -1.4607 | 3.3451 | 1.4579 | 0.00033445 | -0.0028376 | 0.10537 | 0.10534 | 0.10537 | 0.99988 | -0.0023186 | 1 | 0 | 25.0296
36 | 0.15228 | 0.073729 | -0.15228 | -0.073752 | 8.3446e-07 | -2.2788e-05 | 0.0048907 | 0.004891 | 0.004891 | 0.99865 | -0.011977 | 0.99864 | -0.012013 | 2.329
37 | 1.2176 | 0.58263 | -1.2168 | -0.58247 | 0.00081009 | 0.00015227 | 0.039023 | 0.039027 | 0.039027 | 0.99857 | -0.011266 | 0.99787 | -0.015851 | 18.5843
38 | 1.2168 | 0.58247 | -1.2168 | -0.58295 | 4.1468e-05 | -0.00047247 | 0.039027 | 0.039033 | 0.039033 | 0.99787 | -0.015851 | 0.99783 | -0.015562 | 17.7423
39 | 1.1107 | 0.53159 | -1.1105 | -0.53429 | 0.00019725 | -0.0027061 | 0.035624 | 0.035659 | 0.035659 | 0.99783 | -0.015562 | 0.99767 | -0.014046 | 16.2086
40 | 1.1105 | 0.53429 | -1.1105 | -0.53498 | 5.0211e-05 | -0.00068784 | 0.035659 | 0.035668 | 0.035668 | 0.99767 | -0.014046 | 0.99763 | -0.013658 | 16.2126
41 | 0.32304 | 0.1536 | -0.32256 | -0.15622 | 0.00047159 | -0.0026254 | 0.01035 | 0.010387 | 0.010387 | 0.99763 | -0.013658 | 0.99609 | -0.023622 | 4.9461

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 3.4467 | 1.5108

## res_load
| p_mw | q_mvar
0 | 0.11977 | 0.058005
1 | 0.09139 | 0.044262
2 | 0.073303 | 0.035502
3 | 0.15967 | 0.07733
4 | 0.087612 | 0.042432
5 | 0.087829 | 0.042538
6 | 0.14177 | 0.06866
7 | 0.14119 | 0.068382
8 | 0.12646 | 0.061249
9 | 0.064592 | 0.031283
10 | 0.097125 | 0.04704
11 | 0.08875 | 0.042984
12 | 0.13608 | 0.065907
13 | 0.14483 | 0.070142
14 | 0.10565 | 0.051168
15 | 0.079062 | 0.038291
16 | 0.11285 | 0.054653
17 | 0.099558 | 0.048218
18 | 0.15228 | 0.073752
19 | 0.087539 | 0.042397
20 | 0.10605 | 0.051361
21 | 0.78745 | 0.38138
22 | 0.32256 | 0.15622

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1