## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_347_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_347_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_347_0_node_6 | 20 | n |  | TRUE
3 | bus_MV_347_0_node_9 | 20 | n |  | TRUE
4 | bus_MV_347_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_347_0_node_3 | 20 | n |  | TRUE
6 | bus_MV_347_0_node_5 | 20 | n |  | TRUE
7 | bus_MV_347_0_node_8 | 20 | n |  | TRUE
8 | bus_MV_347_0_node_7 | 20 | n |  | TRUE
9 | bus_MV_347_0_node_184 | 20 | n |  | TRUE
10 | bus_MV_347_0_node_129 | 20 | n |  | TRUE
11 | bus_MV_347_0_node_112 | 20 | n |  | TRUE
12 | bus_MV_347_0_node_113 | 20 | n |  | TRUE
13 | bus_MV_347_0_node_114 | 20 | n |  | TRUE
14 | bus_MV_347_0_node_118 | 20 | n |  | TRUE
15 | bus_MV_347_0_node_117 | 20 | n |  | TRUE
16 | bus_MV_347_0_node_131 | 20 | n |  | TRUE
17 | bus_MV_347_0_node_127 | 20 | n |  | TRUE
18 | bus_MV_347_0_node_10 | 20 | n |  | TRUE
19 | bus_MV_347_0_node_11 | 20 | n |  | TRUE
20 | bus_MV_347_0_node_12 | 20 | n |  | TRUE
21 | bus_MV_347_0_node_14 | 20 | n |  | TRUE
22 | bus_MV_347_0_node_65 | 20 | n |  | TRUE
23 | bus_MV_347_0_node_52 | 20 | n |  | TRUE
24 | bus_MV_347_0_node_163 | 20 | n |  | TRUE
25 | bus_MV_347_0_node_16 | 20 | n |  | TRUE
26 | bus_MV_347_0_node_13 | 20 | n |  | TRUE
27 | bus_MV_347_0_node_55 | 20 | n |  | TRUE
28 | bus_MV_347_0_node_180 | 20 | n |  | TRUE
29 | bus_MV_347_0_node_15 | 20 | n |  | TRUE
30 | bus_MV_347_0_node_56 | 20 | n |  | TRUE
31 | bus_MV_347_0_node_166 | 20 | n |  | TRUE
32 | bus_MV_347_0_node_60 | 20 | n |  | TRUE
33 | bus_MV_347_0_node_63 | 20 | n |  | TRUE
34 | bus_MV_347_0_node_34 | 20 | n |  | TRUE
35 | bus_MV_347_0_node_39 | 20 | n |  | TRUE
36 | bus_MV_347_0_node_40 | 20 | n |  | TRUE
37 | bus_MV_347_0_node_61 | 20 | n |  | TRUE
38 | bus_MV_347_0_node_32 | 20 | n |  | TRUE
39 | bus_MV_347_0_node_17 | 20 | n |  | TRUE
40 | bus_MV_347_0_node_18 | 20 | n |  | TRUE
41 | bus_MV_347_0_node_53 | 20 | n |  | TRUE
42 | bus_MV_347_0_node_20 | 20 | n |  | TRUE
43 | bus_MV_347_0_node_19 | 20 | n |  | TRUE
44 | bus_MV_347_0_node_164 | 20 | n |  | TRUE
45 | bus_MV_347_0_node_165 | 20 | n |  | TRUE
46 | bus_MV_347_0_node_183 | 20 | n |  | TRUE
47 | bus_MV_347_0_node_87 | 20 | n |  | TRUE
48 | bus_MV_347_0_node_68 | 20 | n |  | TRUE
49 | bus_MV_347_0_node_21 | 20 | n |  | TRUE
50 | bus_MV_347_0_node_23 | 20 | n |  | TRUE
51 | bus_MV_347_0_node_22 | 20 | n |  | TRUE
52 | bus_MV_347_0_node_25 | 20 | n |  | TRUE
53 | bus_MV_347_0_node_58 | 20 | n |  | TRUE
54 | bus_MV_347_0_node_24 | 20 | n |  | TRUE
55 | bus_MV_347_0_node_171 | 20 | n |  | TRUE
56 | bus_MV_347_0_node_43 | 20 | n |  | TRUE
57 | bus_MV_347_0_node_29 | 20 | n |  | TRUE
58 | bus_MV_347_0_node_37 | 20 | n |  | TRUE
59 | bus_MV_347_0_node_35 | 20 | n |  | TRUE
60 | bus_MV_347_0_node_44 | 20 | n |  | TRUE
61 | bus_MV_347_0_node_42 | 20 | n |  | TRUE
62 | bus_MV_347_0_node_30 | 20 | n |  | TRUE
63 | bus_MV_347_0_node_36 | 20 | n |  | TRUE
64 | bus_MV_347_0_node_59 | 20 | n |  | TRUE
65 | bus_MV_347_0_node_26 | 20 | n |  | TRUE
66 | bus_MV_347_0_node_27 | 20 | n |  | TRUE
67 | bus_MV_347_0_node_28 | 20 | n |  | TRUE
68 | bus_MV_347_0_node_169 | 20 | n |  | TRUE
69 | bus_MV_347_0_node_170 | 20 | n |  | TRUE
70 | bus_MV_347_0_node_186 | 20 | n |  | TRUE
71 | bus_MV_347_0_node_174 | 20 | n |  | TRUE
72 | bus_MV_347_0_node_41 | 20 | n |  | TRUE
73 | bus_MV_347_0_node_31 | 20 | n |  | TRUE
74 | bus_MV_347_0_node_160 | 20 | n |  | TRUE
75 | bus_MV_347_0_node_62 | 20 | n |  | TRUE
76 | bus_MV_347_0_node_173 | 20 | n |  | TRUE
77 | bus_MV_347_0_node_90 | 20 | n |  | TRUE
78 | bus_MV_347_0_node_185 | 20 | n |  | TRUE
79 | bus_MV_347_0_node_89 | 20 | n |  | TRUE
80 | bus_MV_347_0_node_84 | 20 | n |  | TRUE
81 | bus_MV_347_0_node_45 | 20 | n |  | TRUE
82 | bus_MV_347_0_node_78 | 20 | n |  | TRUE
83 | bus_MV_347_0_node_132 | 20 | n |  | TRUE
84 | bus_MV_347_0_node_172 | 20 | n |  | TRUE
85 | bus_MV_347_0_node_77 | 20 | n |  | TRUE
86 | bus_MV_347_0_node_50 | 20 | n |  | TRUE
87 | bus_MV_347_0_node_46 | 20 | n |  | TRUE
88 | bus_MV_347_0_node_47 | 20 | n |  | TRUE
89 | bus_MV_347_0_node_48 | 20 | n |  | TRUE
90 | bus_MV_347_0_node_49 | 20 | n |  | TRUE
91 | bus_MV_347_0_node_51 | 20 | n |  | TRUE
92 | bus_MV_347_0_node_54 | 20 | n |  | TRUE
93 | bus_MV_347_0_node_162 | 20 | n |  | TRUE
94 | bus_MV_347_0_node_70 | 20 | n |  | TRUE
95 | bus_MV_347_0_node_66 | 20 | n |  | TRUE
96 | bus_MV_347_0_node_179 | 20 | n |  | TRUE
97 | bus_MV_347_0_node_64 | 20 | n |  | TRUE
98 | bus_MV_347_0_node_178 | 20 | n |  | TRUE
99 | bus_MV_347_0_node_67 | 20 | n |  | TRUE
100 | bus_MV_347_0_node_177 | 20 | n |  | TRUE
101 | bus_MV_347_0_node_69 | 20 | n |  | TRUE
102 | bus_MV_347_0_node_79 | 20 | n |  | TRUE
103 | bus_MV_347_0_node_82 | 20 | n |  | TRUE
104 | bus_MV_347_0_node_86 | 20 | n |  | TRUE
105 | bus_MV_347_0_node_76 | 20 | n |  | TRUE
106 | bus_MV_347_0_node_71 | 20 | n |  | TRUE
107 | bus_MV_347_0_node_72 | 20 | n |  | TRUE
108 | bus_MV_347_0_node_73 | 20 | n |  | TRUE
109 | bus_MV_347_0_node_81 | 20 | n |  | TRUE
110 | bus_MV_347_0_node_83 | 20 | n |  | TRUE
111 | bus_MV_347_0_node_75 | 20 | n |  | TRUE
112 | bus_MV_347_0_node_80 | 20 | n |  | TRUE
113 | bus_MV_347_0_node_74 | 20 | n |  | TRUE
114 | bus_MV_347_0_node_88 | 20 | n |  | TRUE
115 | bus_MV_347_0_node_115 | 20 | n |  | TRUE
116 | bus_MV_347_0_node_116 | 20 | n |  | TRUE
117 | bus_MV_347_0_node_128 | 20 | n |  | TRUE
118 | bus_MV_347_0_node_119 | 20 | n |  | TRUE
119 | bus_MV_347_0_node_120 | 20 | n |  | TRUE
120 | bus_MV_347_0_node_121 | 20 | n |  | TRUE
121 | bus_MV_347_0_node_130 | 20 | n |  | TRUE
122 | bus_MV_347_0_node_125 | 20 | n |  | TRUE
123 | bus_MV_347_0_node_123 | 20 | n |  | TRUE
124 | bus_MV_347_0_node_122 | 20 | n |  | TRUE
125 | bus_MV_347_0_node_124 | 20 | n |  | TRUE
126 | bus_MV_347_0_node_126 | 20 | n |  | TRUE
127 | bus_HV_347_0_node_173 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_347_0_load_0 | 0 | 0.23501 | 0.11382 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_347_0_load_9 | 3 | 0.3406 | 0.16496 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_347_0_load_3 | 5 | 0.40097 | 0.1942 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_347_0_load_184 | 9 | 0.098006 | 0.047467 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_347_0_load_112 | 11 | 0.13398 | 0.064892 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_347_0_load_118 | 14 | 0.087917 | 0.04258 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_347_0_load_131 | 16 | 0.10203 | 0.049417 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_347_0_load_10 | 18 | 0.11997 | 0.058103 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_347_0_load_65 | 22 | 0.34972 | 0.16938 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_347_0_load_163 | 24 | 0.25346 | 0.12276 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_347_0_load_55 | 27 | 0.12633 | 0.061185 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_347_0_load_180 | 28 | 0.23552 | 0.11407 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_347_0_load_15 | 29 | 0.10445 | 0.050588 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_347_0_load_166 | 31 | 0.15361 | 0.074398 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_347_0_load_63 | 33 | 0.21714 | 0.10516 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_347_0_load_61 | 37 | 0.39028 | 0.18902 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_347_0_load_32 | 38 | 0.21721 | 0.1052 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_347_0_load_164 | 44 | 0.09545 | 0.046228 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_347_0_load_165 | 45 | 0.094576 | 0.045805 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_347_0_load_183 | 46 | 0.11581 | 0.056089 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_347_0_load_87 | 47 | 0.30259 | 0.14655 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_347_0_load_21 | 49 | 0.26725 | 0.12943 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_347_0_load_58 | 53 | 0.1316 | 0.063735 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_347_0_load_171 | 55 | 0.13961 | 0.067616 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_347_0_load_29 | 57 | 0.27633 | 0.13383 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_347_0_load_42 | 61 | 0.36548 | 0.17701 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_347_0_load_59 | 64 | 0.18911 | 0.091588 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_347_0_load_26 | 65 | 0.41038 | 0.19876 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_347_0_load_169 | 68 | 0.3161 | 0.1531 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_347_0_load_186 | 70 | 0.26207 | 0.12693 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_347_0_load_174 | 71 | 0.34783 | 0.16846 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_347_0_load_41 | 72 | 0.29822 | 0.14444 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_347_0_load_160 | 74 | 0.34202 | 0.16565 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_347_0_load_173 | 76 | 0.34789 | 0.16849 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_347_0_load_185 | 78 | 0.14157 | 0.068564 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_347_0_load_84 | 80 | 0.17586 | 0.085171 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_347_0_load_78 | 82 | 0.074831 | 0.036242 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_347_0_load_132 | 83 | 0.15308 | 0.074139 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_347_0_load_172 | 84 | 0.35988 | 0.1743 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_347_0_load_77 | 85 | 0.26079 | 0.12631 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_347_0_load_50 | 86 | 0.076316 | 0.036962 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_347_0_load_46 | 87 | 0.39587 | 0.19173 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_347_0_load_162 | 93 | 0.23956 | 0.11602 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_347_0_load_66 | 95 | 0.28391 | 0.13751 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_347_0_load_179 | 96 | 0.31303 | 0.15161 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_347_0_load_64 | 97 | 0.25621 | 0.12409 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_347_0_load_178 | 98 | 0.3158 | 0.15295 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_347_0_load_177 | 100 | 0.26422 | 0.12797 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_347_0_load_79 | 102 | 0.20376 | 0.098687 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_347_0_load_86 | 104 | 0.31187 | 0.15105 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_347_0_load_71 | 106 | 0.377 | 0.18259 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_347_0_load_83 | 110 | 0.20741 | 0.10045 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_347_0_load_80 | 112 | 0.20913 | 0.10128 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_347_0_load_74 | 113 | 0.32006 | 0.15501 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_347_0_load_88 | 114 | 0.38641 | 0.18715 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_347_0_load_115 | 115 | 0.08278 | 0.040092 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_347_0_load_128 | 117 | 0.12684 | 0.061431 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_347_0_load_119 | 118 | 1.2011 | 0.58174 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_347_0_load_130 | 121 | 0.1009 | 0.048867 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_347_0_load_125 | 122 | 0.10078 | 0.04881 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_347_0_load_122 | 124 | 0.10072 | 0.04878 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_347_0_load_124 | 125 | 0.10052 | 0.048684 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_347_0_load_126 | 126 | 0.10032 | 0.048585 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 76 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_347_0_line_0 |  | 0 | 1 | 0.006351 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_347_0_line_1 |  | 1 | 2 | 0.26587 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_347_0_line_2 |  | 2 | 3 | 0.098187 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_347_0_line_3 |  | 2 | 4 | 0.41484 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_347_0_line_4 |  | 4 | 5 | 0.10075 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_347_0_line_5 |  | 5 | 6 | 0.053753 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_347_0_line_6 |  | 6 | 7 | 0.36104 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_347_0_line_7 |  | 7 | 11 | 0.031443 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_347_0_line_8 |  | 8 | 9 | 0.011293 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_347_0_line_9 |  | 8 | 10 | 0.015366 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_347_0_line_10 |  | 10 | 16 | 0.009344 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_347_0_line_11 |  | 10 | 17 | 0.021412 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_347_0_line_12 |  | 11 | 12 | 0.0043659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_347_0_line_13 |  | 12 | 13 | 0.037331 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_347_0_line_14 |  | 13 | 14 | 0.029955 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_347_0_line_15 |  | 14 | 15 | 0.033085 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_347_0_line_16 |  | 15 | 71 | 0.38315 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_347_0_line_17 |  | 15 | 116 | 0.062092 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_347_0_line_18 |  | 17 | 117 | 0.018343 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_347_0_line_19 |  | 17 | 126 | 0.015966 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_347_0_line_20 |  | 18 | 19 | 0.067308 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_347_0_line_21 |  | 19 | 20 | 0.60554 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_347_0_line_22 |  | 19 | 21 | 0.87982 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_347_0_line_23 |  | 20 | 24 | 0.022883 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_347_0_line_24 |  | 20 | 25 | 0.54057 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_347_0_line_25 |  | 21 | 28 | 0.043905 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_347_0_line_26 |  | 21 | 26 | 0.74385 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_347_0_line_27 |  | 22 | 23 | 0.028175 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_347_0_line_28 |  | 23 | 41 | 0.63241 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_347_0_line_29 |  | 25 | 29 | 0.03887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_347_0_line_30 |  | 26 | 27 | 0.11335 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_347_0_line_31 |  | 27 | 33 | 0.44651 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_347_0_line_32 |  | 29 | 39 | 0.042972 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_347_0_line_33 |  | 30 | 31 | 0.098268 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
34 | MV_347_0_line_34 |  | 30 | 32 | 0.082771 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
35 | MV_347_0_line_35 |  | 31 | 75 | 0.24735 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
36 | MV_347_0_line_36 |  | 32 | 64 | 0.059299 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
37 | MV_347_0_line_37 |  | 33 | 75 | 0.34989 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_347_0_line_38 |  | 34 | 35 | 0.65192 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
39 | MV_347_0_line_39 |  | 34 | 36 | 0.34719 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_347_0_line_40 |  | 34 | 37 | 0.36854 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
41 | MV_347_0_line_41 |  | 34 | 38 | 0.006429 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_347_0_line_42 |  | 35 | 69 | 1.0106 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_347_0_line_43 |  | 35 | 70 | 0.032679 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_347_0_line_44 |  | 35 | 67 | 0.48485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_347_0_line_45 |  | 36 | 72 | 0.016619 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_347_0_line_46 |  | 37 | 75 | 0.033599 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
47 | MV_347_0_line_47 |  | 39 | 40 | 0.95525 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_347_0_line_48 |  | 40 | 42 | 0.38469 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_347_0_line_49 |  | 40 | 43 | 0.51088 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_347_0_line_50 |  | 40 | 44 | 0.16784 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_347_0_line_51 |  | 41 | 96 | 0.014866 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_347_0_line_52 |  | 41 | 91 | 0.62805 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_347_0_line_53 |  | 42 | 46 | 0.002482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_347_0_line_54 |  | 43 | 45 | 0.014597 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_347_0_line_55 |  | 47 | 48 | 0.028141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_347_0_line_56 |  | 48 | 98 | 0.52371 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_347_0_line_57 |  | 49 | 50 | 0.071461 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
58 | MV_347_0_line_58 |  | 49 | 51 | 0.089923 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
59 | MV_347_0_line_59 |  | 50 | 52 | 0.089126 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_347_0_line_60 |  | 50 | 53 | 0.3746 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
61 | MV_347_0_line_61 |  | 51 | 54 | 0.51995 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
62 | MV_347_0_line_62 |  | 52 | 57 | 0.16799 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_347_0_line_63 |  | 53 | 58 | 0.005442 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
64 | MV_347_0_line_64 |  | 54 | 55 | 0.035587 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_347_0_line_65 |  | 54 | 56 | 0.20078 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
66 | MV_347_0_line_66 |  | 56 | 60 | 0.2615 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
67 | MV_347_0_line_67 |  | 56 | 61 | 0.056097 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
68 | MV_347_0_line_68 |  | 57 | 62 | 0.067636 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_347_0_line_69 |  | 58 | 59 | 0.23996 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
70 | MV_347_0_line_70 |  | 59 | 63 | 0.24871 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
71 | MV_347_0_line_71 |  | 59 | 64 | 0.076563 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
72 | MV_347_0_line_72 |  | 60 | 81 | 0.23297 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_347_0_line_73 |  | 60 | 82 | 0.024758 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_347_0_line_74 |  | 60 | 83 | 0.020225 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
75 | MV_347_0_line_75 |  | 62 | 73 | 0.29614 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_347_0_line_76 |  | 63 | 76 | 0.021159 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
77 | MV_347_0_line_77 |  | 65 | 66 | 0.034284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_347_0_line_78 |  | 66 | 67 | 0.33867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_347_0_line_79 |  | 67 | 68 | 0.038262 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_347_0_line_80 |  | 69 | 71 | 0.068373 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_347_0_line_81 |  | 70 | 80 | 0.42645 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
82 | MV_347_0_line_82 |  | 73 | 74 | 0.026114 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_347_0_line_83 |  | 76 | 77 | 0.37797 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
84 | MV_347_0_line_84 |  | 77 | 78 | 0.009826 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_347_0_line_85 |  | 77 | 79 | 0.35621 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_347_0_line_86 |  | 79 | 114 | 0.073936 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
87 | MV_347_0_line_87 |  | 81 | 84 | 0.005394 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_347_0_line_88 |  | 82 | 85 | 0.019318 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_347_0_line_89 |  | 83 | 86 | 0.02967 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
90 | MV_347_0_line_90 |  | 86 | 89 | 0.020068 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
91 | MV_347_0_line_91 |  | 87 | 88 | 0.005527 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_347_0_line_92 |  | 87 | 89 | 0.037194 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_347_0_line_93 |  | 88 | 90 | 0.43548 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_347_0_line_94 |  | 89 | 91 | 0.59555 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_347_0_line_95 |  | 89 | 92 | 0.47845 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_347_0_line_96 |  | 90 | 93 | 0.022365 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
97 | MV_347_0_line_97 |  | 91 | 94 | 0.49336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_347_0_line_98 |  | 91 | 95 | 0.074063 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_347_0_line_99 |  | 92 | 97 | 0.06259 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_347_0_line_100 |  | 94 | 98 | 0.005995 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_347_0_line_101 |  | 95 | 99 | 0.07094 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
102 | MV_347_0_line_102 |  | 96 | 100 | 0.32036 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
103 | MV_347_0_line_103 |  | 99 | 101 | 1.0353 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_347_0_line_104 |  | 101 | 102 | 0.044663 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_347_0_line_105 |  | 101 | 103 | 0.33377 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
106 | MV_347_0_line_106 |  | 103 | 104 | 0.040722 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_347_0_line_107 |  | 103 | 105 | 0.52253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_347_0_line_108 |  | 105 | 109 | 0.41522 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_347_0_line_109 |  | 105 | 111 | 0.076072 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_347_0_line_110 |  | 106 | 107 | 0.078692 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
111 | MV_347_0_line_111 |  | 107 | 108 | 0.44796 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_347_0_line_112 |  | 108 | 109 | 0.2986 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_347_0_line_113 |  | 108 | 110 | 0.084291 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_347_0_line_114 |  | 109 | 112 | 0.074491 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_347_0_line_115 |  | 111 | 113 | 0.072446 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_347_0_line_116 |  | 115 | 116 | 0.025817 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_347_0_line_117 |  | 115 | 117 | 0.40406 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
118 | MV_347_0_line_118 |  | 118 | 119 | 0.0053842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_347_0_line_119 |  | 119 | 120 | 0.078487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_347_0_line_120 |  | 120 | 121 | 0.011528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_347_0_line_121 |  | 120 | 122 | 0.022968 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_347_0_line_122 |  | 122 | 123 | 0.05318 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_347_0_line_123 |  | 123 | 124 | 0.018147 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_347_0_line_124 |  | 124 | 125 | 0.01859 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_347_0_line_125 |  | 125 | 126 | 0.018665 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_347_0_trafo_173 | 25 MVA 110/20 kV | 127 | 76 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2613569.013 | 1268362.4884
1 | 2613563.7987 | 1268358.8406
2 | 2613500.1339 | 1268100.7028
3 | 2613445.8607 | 1268182.526
4 | 2613837.0147 | 1268295.5822
5 | 2613918.6787 | 1268354.5925
6 | 2613950.9663 | 1268311.5491
7 | 2614148.2698 | 1268488.3296
8 | 2614097.2411 | 1268086.1473
9 | 2614101.5556 | 1268075.7057
10 | 2614111.534 | 1268091.8964
11 | 2614129.3777 | 1268513.4641
12 | 2614126.7545 | 1268516.9541
13 | 2614116.0022 | 1268544.8926
14 | 2614140.9108 | 1268561.5315
15 | 2614168.4219 | 1268579.9089
16 | 2614115.2044 | 1268083.2991
17 | 2614131.6628 | 1268099.3384
18 | 2616766.7864 | 1268801.9189
19 | 2616707.3927 | 1268833.8405
20 | 2617110.184 | 1268982.1941
21 | 2616486.4122 | 1269287.4206
22 | 2616476.6269 | 1270057.1062
23 | 2616500.358 | 1270072.4053
24 | 2617095.0999 | 1268999.4406
25 | 2617508.3212 | 1268702.4476
26 | 2616099.3649 | 1268973.8686
27 | 2615996.4117 | 1268929.4475
28 | 2616495.5233 | 1269244.4711
29 | 2617507.8704 | 1268663.9857
30 | 2615693.0152 | 1269204.8317
31 | 2615681.2569 | 1269107.276
32 | 2615703.2113 | 1269286.9724
33 | 2615658.7512 | 1268637.2846
34 | 2615135.1246 | 1269123.5021
35 | 2614788.1357 | 1268974.7107
36 | 2614990.1099 | 1268952.0794
37 | 2615460.4234 | 1268950.2964
38 | 2615135.5221 | 1269129.9188
39 | 2617549.6686 | 1268672.8489
40 | 2618293.4987 | 1268972.8545
41 | 2616196.8095 | 1270052.8432
42 | 2618522.967 | 1268822.8276
43 | 2618365.1958 | 1269207.6648
44 | 2618127.6735 | 1268946.9489
45 | 2618353.4076 | 1269204.426
46 | 2618525.2576 | 1268821.8563
47 | 2617003.9613 | 1270515.5646
48 | 2616981.0872 | 1270531.9566
49 | 2615607.9379 | 1269941.5738
50 | 2615543.6351 | 1269910.0047
51 | 2615688.9599 | 1269980.582
52 | 2615463.0237 | 1269871.4778
53 | 2615672.7652 | 1269558.3618
54 | 2615758.4177 | 1270209.0173
55 | 2615789.7058 | 1270226.1461
56 | 2615819.5951 | 1270369.8168
57 | 2615390.5622 | 1270023.0413
58 | 2615671.0107 | 1269553.2091
59 | 2615635.5999 | 1269360.468
60 | 2615943.8598 | 1270531.3869
61 | 2615764.2178 | 1270378.7757
62 | 2615349.4358 | 1270076.8285
63 | 2615469.0685 | 1269400.3262
64 | 2615710.956 | 1269345.7567
65 | 2614579.8748 | 1269238.1481
66 | 2614549.5155 | 1269222.2624
67 | 2614602.5239 | 1269008.675
68 | 2614620.6805 | 1269042.3546
69 | 2614368.5319 | 1268924.3442
70 | 2614819.9983 | 1268967.4518
71 | 2614414.4884 | 1268873.5976
72 | 2615006.1238 | 1268947.6354
73 | 2615229.2852 | 1269861.7438
74 | 2615255.3423 | 1269863.4676
75 | 2615493.8296 | 1268945.8694
76 | 2615448.3948 | 1269405.109
77 | 2615087.7657 | 1269291.934
78 | 2615078.0626 | 1269293.6549
79 | 2615019.9222 | 1269495.7394
80 | 2614857.2716 | 1268542.6341
81 | 2615789.8069 | 1270532.5977
82 | 2615949.8165 | 1270555.4174
83 | 2615963.7896 | 1270529.1831
84 | 2615788.2786 | 1270527.4233
85 | 2615954.4644 | 1270574.1681
86 | 2615992.9037 | 1270523.7116
87 | 2616018.0657 | 1270558.4395
88 | 2616018.8408 | 1270563.9122
89 | 2616012.8618 | 1270521.6103
90 | 2616239.6177 | 1270746.9766
91 | 2616214.1578 | 1270391.1423
92 | 2616036.6262 | 1270229.7002
93 | 2616257.8692 | 1270759.9025
94 | 2616462.1749 | 1270449.6008
95 | 2616238.7015 | 1270461.0037
96 | 2616186.5438 | 1270046.0103
97 | 2615996.462 | 1270181.7798
98 | 2616462.9859 | 1270455.5406
99 | 2616277.4611 | 1270520.4189
100 | 2616069.8012 | 1269747.681
101 | 2616940.5906 | 1270882.435
102 | 2616955.4016 | 1270924.5853
103 | 2616610.0313 | 1270928.6214
104 | 2616591.8319 | 1270892.1666
105 | 2616262.2823 | 1270793.7276
106 | 2616232.4754 | 1271453.7283
107 | 2616305.9255 | 1271425.4875
108 | 2616191.5432 | 1271203.3597
109 | 2616259.9859 | 1270997.2665
110 | 2616115.8187 | 1271226.2697
111 | 2616329.96 | 1270758.5997
112 | 2616188.3329 | 1271018.3743
113 | 2616395.5437 | 1270727.4696
114 | 2615031.6927 | 1269568.732
115 | 2614220.4689 | 1268509.0676
116 | 2614205.4598 | 1268530.0734
117 | 2614125.0294 | 1268116.4458
118 | 2614127.3327 | 1267992.9254
119 | 2614132.333 | 1267994.9222
120 | 2614183.3253 | 1268015.1803
121 | 2614172.2946 | 1268012.0596
122 | 2614185.4502 | 1268038.0424
123 | 2614200.1496 | 1268088.9946
124 | 2614183.994 | 1268097.1802
125 | 2614166.0151 | 1268101.4972
126 | 2614147.4035 | 1268101.8479
127 | 2615448.3948 | 1269405.109

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98487 | -0.099375 | 0.23501 | 0.11382
1 | 0.98487 | -0.099393 | 0 | 0
2 | 0.985 | -0.098608 | 0 | 0
3 | 0.98493 | -0.099025 | 0.3406 | 0.16496
4 | 0.9853 | -0.10141 | 0 | 0
5 | 0.98542 | -0.10059 | 0.40097 | 0.1942
6 | 0.98549 | -0.1012 | 0 | 0
7 | 0.98594 | -0.10517 | 0 | 0
8 | 0.98423 | -0.11459 | 0 | 0
9 | 0.98423 | -0.11457 | 0.098006 | 0.047467
10 | 0.98423 | -0.11461 | 0 | 0
11 | 0.98598 | -0.10551 | 0.13398 | 0.064892
12 | 0.98598 | -0.10556 | 0 | 0
13 | 0.98604 | -0.10602 | 0 | 0
14 | 0.98608 | -0.10639 | 0.087917 | 0.04258
15 | 0.98613 | -0.10682 | 0 | 0
16 | 0.98423 | -0.11459 | 0.10203 | 0.049417
17 | 0.98423 | -0.11466 | 0 | 0
18 | 0.994 | -0.067224 | 0.11997 | 0.058103
19 | 0.99401 | -0.067318 | 0 | 0
20 | 0.99351 | -0.065048 | 0 | 0
21 | 0.99487 | -0.070805 | 0 | 0
22 | 0.99228 | -0.072306 | 0.34972 | 0.16938
23 | 0.9923 | -0.072425 | 0 | 0
24 | 0.9935 | -0.064978 | 0.25346 | 0.12276
25 | 0.99323 | -0.064191 | 0 | 0
26 | 0.99581 | -0.074943 | 0 | 0
27 | 0.99595 | -0.075499 | 0.12633 | 0.061185
28 | 0.99485 | -0.070931 | 0.23552 | 0.11407
29 | 0.99321 | -0.064112 | 0.10445 | 0.050588
30 | 0.99882 | -0.022489 | 0 | 0
31 | 0.99866 | -0.025411 | 0.15361 | 0.074398
32 | 0.99895 | -0.020024 | 0 | 0
33 | 0.9969 | -0.064781 | 0.21714 | 0.10516
34 | 0.99542 | -0.11577 | 0 | 0
35 | 0.9937 | -0.13509 | 0 | 0
36 | 0.99528 | -0.11462 | 0 | 0
37 | 0.99775 | -0.056233 | 0.39028 | 0.18902
38 | 0.99541 | -0.11576 | 0.21721 | 0.1052
39 | 0.9932 | -0.064077 | 0 | 0
40 | 0.99283 | -0.062565 | 0 | 0
41 | 0.99258 | -0.07478 | 0 | 0
42 | 0.99278 | -0.062138 | 0 | 0
43 | 0.99277 | -0.062188 | 0 | 0
44 | 0.9928 | -0.062763 | 0.09545 | 0.046228
45 | 0.99277 | -0.062172 | 0.094576 | 0.045805
46 | 0.99277 | -0.062135 | 0.11581 | 0.056089
47 | 0.99261 | -0.079253 | 0.30259 | 0.14655
48 | 0.99262 | -0.079356 | 0 | 0
49 | 0.99749 | -0.067567 | 0.26725 | 0.12943
50 | 0.99758 | -0.06576 | 0 | 0
51 | 0.99723 | -0.076546 | 0 | 0
52 | 0.99751 | -0.065154 | 0 | 0
53 | 0.99881 | -0.022845 | 0.1316 | 0.063735
54 | 0.99658 | -0.089081 | 0 | 0
55 | 0.99657 | -0.089022 | 0.13961 | 0.067616
56 | 0.99633 | -0.093769 | 0 | 0
57 | 0.99731 | -0.066542 | 0.27633 | 0.13383
58 | 0.99881 | -0.022692 | 0 | 0
59 | 0.99917 | -0.015913 | 0 | 0
60 | 0.99603 | -0.099472 | 0 | 0
61 | 0.99629 | -0.094019 | 0.36548 | 0.17701
62 | 0.99728 | -0.066297 | 0 | 0
63 | 0.99993 | -0.0012485 | 0 | 0
64 | 0.99904 | -0.018255 | 0.18911 | 0.091588
65 | 0.99305 | -0.12953 | 0.41038 | 0.19876
66 | 0.99307 | -0.1297 | 0 | 0
67 | 0.99325 | -0.13128 | 0 | 0
68 | 0.99323 | -0.13142 | 0.3161 | 0.1531
69 | 0.98894 | -0.092885 | 0 | 0
70 | 0.99367 | -0.13527 | 0.26207 | 0.12693
71 | 0.98861 | -0.089959 | 0.34783 | 0.16846
72 | 0.99528 | -0.11456 | 0.29822 | 0.14444
73 | 0.99715 | -0.065146 | 0 | 0
74 | 0.99713 | -0.065255 | 0.34202 | 0.16565
75 | 0.99779 | -0.055462 | 0 | 0
76 | 1 | 0 | -14.8843 | -6.6703
77 | 0.99962 | -0.0027041 | 0 | 0
78 | 0.99962 | -0.0026875 | 0.14157 | 0.068564
79 | 0.99944 | -0.0011542 | 0 | 0
80 | 0.99353 | -0.13619 | 0.17586 | 0.085171
81 | 0.99593 | -0.098505 | 0 | 0
82 | 0.99602 | -0.099373 | 0.074831 | 0.036242
83 | 0.99601 | -0.099857 | 0.15308 | 0.074139
84 | 0.99593 | -0.098481 | 0.35988 | 0.1743
85 | 0.99602 | -0.099313 | 0.26079 | 0.12631
86 | 0.99599 | -0.1004 | 0.076316 | 0.036962
87 | 0.99591 | -0.10071 | 0.39587 | 0.19173
88 | 0.99591 | -0.1007 | 0 | 0
89 | 0.99594 | -0.10097 | 0 | 0
90 | 0.99577 | -0.099587 | 0 | 0
91 | 0.99332 | -0.080885 | 0 | 0
92 | 0.99578 | -0.099713 | 0 | 0
93 | 0.99576 | -0.099653 | 0.23956 | 0.11602
94 | 0.99293 | -0.077413 | 0 | 0
95 | 0.99314 | -0.079519 | 0.28391 | 0.13751
96 | 0.99257 | -0.074676 | 0.31303 | 0.15161
97 | 0.99576 | -0.099522 | 0.25621 | 0.12409
98 | 0.99292 | -0.077369 | 0.3158 | 0.15295
99 | 0.99292 | -0.081395 | 0 | 0
100 | 0.9924 | -0.07572 | 0.26422 | 0.12797
101 | 0.99077 | -0.064953 | 0 | 0
102 | 0.99076 | -0.064844 | 0.20376 | 0.098687
103 | 0.98985 | -0.072212 | 0 | 0
104 | 0.98984 | -0.072058 | 0.31187 | 0.15105
105 | 0.98911 | -0.066478 | 0 | 0
106 | 0.98819 | -0.059782 | 0.377 | 0.18259
107 | 0.98825 | -0.059414 | 0 | 0
108 | 0.98847 | -0.061327 | 0 | 0
109 | 0.98869 | -0.063152 | 0 | 0
110 | 0.98845 | -0.061119 | 0.20741 | 0.10045
111 | 0.98908 | -0.066193 | 0 | 0
112 | 0.98867 | -0.062966 | 0.20913 | 0.10128
113 | 0.98905 | -0.065914 | 0.32006 | 0.15501
114 | 0.99939 | -0.0015001 | 0.38641 | 0.18715
115 | 0.98589 | -0.10458 | 0.08278 | 0.040092
116 | 0.98596 | -0.10524 | 0 | 0
117 | 0.98428 | -0.11508 | 0.12684 | 0.061431
118 | 0.98383 | -0.1108 | 1.2011 | 0.58174
119 | 0.98383 | -0.11088 | 0 | 0
120 | 0.98396 | -0.11204 | 0 | 0
121 | 0.98396 | -0.11202 | 0.1009 | 0.048867
122 | 0.984 | -0.1124 | 0.10078 | 0.04881
123 | 0.98409 | -0.11331 | 0 | 0
124 | 0.98412 | -0.11362 | 0.10072 | 0.04878
125 | 0.98416 | -0.11396 | 0.10052 | 0.048684
126 | 0.9842 | -0.11433 | 0.10032 | 0.048585
127 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.23501 | -0.11382 | 0.23501 | 0.11367 | 4.9655e-07 | -0.00014694 | 0.0076538 | 0.0076519 | 0.0076538 | 0.98487 | -0.099375 | 0.98487 | -0.099393 | 3.479
1 | -0.23501 | -0.11367 | 0.23504 | 0.11338 | 2.7722e-05 | -0.00029055 | 0.0076519 | 0.007648 | 0.0076519 | 0.98487 | -0.099393 | 0.985 | -0.098608 | 3.6438
2 | 0.34063 | 0.16486 | -0.3406 | -0.16496 | 2.152e-05 | -0.00010024 | 0.011091 | 0.011092 | 0.011092 | 0.985 | -0.098608 | 0.98493 | -0.099025 | 5.2819
3 | -0.57566 | -0.27825 | 0.57586 | 0.26869 | 0.0001932 | -0.0095556 | 0.018739 | 0.018618 | 0.018739 | 0.985 | -0.098608 | 0.9853 | -0.10141 | 8.5175
4 | -0.57586 | -0.26869 | 0.57592 | 0.26861 | 6.2217e-05 | -7.7813e-05 | 0.018618 | 0.018616 | 0.018618 | 0.9853 | -0.10141 | 0.98542 | -0.10059 | 8.8656
5 | -0.97689 | -0.46281 | 0.97696 | 0.46159 | 7.1925e-05 | -0.001225 | 0.031667 | 0.031651 | 0.031667 | 0.98542 | -0.10059 | 0.98549 | -0.1012 | 14.394
6 | -0.97696 | -0.46159 | 0.97744 | 0.45335 | 0.00048126 | -0.0082328 | 0.031651 | 0.031547 | 0.031651 | 0.98549 | -0.1012 | 0.98594 | -0.10517 | 14.3869
7 | -0.97744 | -0.45335 | 0.97748 | 0.45264 | 4.1764e-05 | -0.00071741 | 0.031547 | 0.031538 | 0.031547 | 0.98594 | -0.10517 | 0.98598 | -0.10551 | 14.3396
8 | 0.098007 | 0.047205 | -0.098006 | -0.047467 | 1.5365e-07 | -0.00026115 | 0.0031906 | 0.0031939 | 0.0031939 | 0.98423 | -0.11459 | 0.98423 | -0.11457 | 1.4518
9 | -0.098007 | -0.047205 | 0.098007 | 0.04685 | 2.0853e-07 | -0.00035534 | 0.0031906 | 0.0031861 | 0.0031906 | 0.98423 | -0.11459 | 0.98423 | -0.11461 | 1.4503
10 | 0.10203 | 0.049201 | -0.10203 | -0.049417 | 1.3781e-07 | -0.00021608 | 0.0033224 | 0.0033252 | 0.0033252 | 0.98423 | -0.11461 | 0.98423 | -0.11459 | 1.5114
11 | -0.20004 | -0.096051 | 0.20004 | 0.095557 | 1.2097e-06 | -0.00049488 | 0.0065085 | 0.0065022 | 0.0065085 | 0.98423 | -0.11461 | 0.98423 | -0.11466 | 2.9584
12 | -1.1115 | -0.51753 | 1.1115 | 0.51743 | 7.51e-06 | -9.9111e-05 | 0.035896 | 0.035895 | 0.035896 | 0.98598 | -0.10551 | 0.98598 | -0.10556 | 16.3165
13 | -1.1115 | -0.51743 | 1.1115 | 0.51658 | 6.4194e-05 | -0.00084752 | 0.035895 | 0.035884 | 0.035895 | 0.98598 | -0.10556 | 0.98604 | -0.10602 | 16.3159
14 | -1.1115 | -0.51658 | 1.1116 | 0.5159 | 5.1482e-05 | -0.00068013 | 0.035884 | 0.035876 | 0.035884 | 0.98604 | -0.10602 | 0.98608 | -0.10639 | 16.3111
15 | -1.1995 | -0.55848 | 1.1996 | 0.55773 | 6.6254e-05 | -0.00074848 | 0.038735 | 0.038726 | 0.038735 | 0.98608 | -0.10639 | 0.98613 | -0.10682 | 17.6069
16 | -3.318 | -1.5741 | 3.3259 | 1.5786 | 0.0078894 | 0.0044957 | 0.10751 | 0.1075 | 0.10751 | 0.98613 | -0.10682 | 0.98861 | -0.089959 | 51.1933
17 | 2.1184 | 1.0163 | -2.1181 | -1.0177 | 0.00039227 | -0.0013251 | 0.068782 | 0.0688 | 0.0688 | 0.98613 | -0.10682 | 0.98596 | -0.10524 | 31.2728
18 | -1.905 | -0.91559 | 1.9051 | 0.91519 | 9.4101e-05 | -0.00039637 | 0.061993 | 0.061987 | 0.061993 | 0.98423 | -0.11466 | 0.98428 | -0.11508 | 28.1785
19 | 1.705 | 0.82003 | -1.7049 | -0.82038 | 6.5636e-05 | -0.00034979 | 0.05549 | 0.055495 | 0.055495 | 0.98423 | -0.11466 | 0.9842 | -0.11433 | 25.2251
20 | -0.11997 | -0.058103 | 0.11997 | 0.056516 | 1.3397e-06 | -0.0015874 | 0.0038712 | 0.0038513 | 0.0038712 | 0.994 | -0.067224 | 0.99401 | -0.067318 | 1.7596
21 | 0.66435 | 0.248 | -0.66401 | -0.26218 | 0.00034531 | -0.014176 | 0.020594 | 0.020743 | 0.020743 | 0.99401 | -0.067318 | 0.99351 | -0.065048 | 9.4286
22 | -0.78432 | -0.30452 | 0.78502 | 0.28395 | 0.00069511 | -0.020567 | 0.024434 | 0.024223 | 0.024434 | 0.99401 | -0.067318 | 0.99487 | -0.070805 | 11.1066
23 | 0.25346 | 0.12222 | -0.25346 | -0.12276 | 2.0438e-06 | -0.00053867 | 0.0081761 | 0.0081829 | 0.0081829 | 0.99351 | -0.065048 | 0.9935 | -0.064978 | 3.7195
24 | 0.41055 | 0.13996 | -0.41043 | -0.15266 | 0.00011574 | -0.012702 | 0.012603 | 0.012727 | 0.012727 | 0.99351 | -0.065048 | 0.99323 | -0.064191 | 5.7851
25 | 0.23553 | 0.11402 | -0.23552 | -0.11407 | 4.5103e-06 | -4.9051e-05 | 0.0075929 | 0.0075936 | 0.0075936 | 0.99487 | -0.070805 | 0.99485 | -0.070931 | 3.616
26 | -1.0205 | -0.39797 | 1.0215 | 0.38067 | 0.00099744 | -0.017299 | 0.031785 | 0.031603 | 0.031785 | 0.99487 | -0.070805 | 0.99581 | -0.074943 | 14.4475
27 | -0.34972 | -0.16938 | 0.34973 | 0.16872 | 4.8032e-06 | -0.00066095 | 0.011305 | 0.011296 | 0.011305 | 0.99228 | -0.072306 | 0.9923 | -0.072425 | 5.1384
28 | -0.34973 | -0.16872 | 0.34983 | 0.15388 | 0.00010598 | -0.014841 | 0.011296 | 0.011115 | 0.011296 | 0.9923 | -0.072425 | 0.99258 | -0.07478 | 5.1346
29 | 0.41043 | 0.15266 | -0.41042 | -0.15357 | 8.4117e-06 | -0.00091303 | 0.012727 | 0.012737 | 0.012737 | 0.99323 | -0.064191 | 0.99321 | -0.064112 | 5.7894
30 | -1.0215 | -0.38067 | 1.0217 | 0.37803 | 0.000151 | -0.0026393 | 0.031603 | 0.031576 | 0.031603 | 0.99581 | -0.074943 | 0.99595 | -0.075499 | 14.3649
31 | -1.148 | -0.43922 | 1.149 | 0.43932 | 0.0010096 | 0.00010316 | 0.035627 | 0.035622 | 0.035627 | 0.99595 | -0.075499 | 0.9969 | -0.064781 | 16.9654
32 | 0.30597 | 0.10299 | -0.30597 | -0.104 | 5.056e-06 | -0.0010106 | 0.0093832 | 0.0093926 | 0.0093926 | 0.99321 | -0.064112 | 0.9932 | -0.064077 | 4.2694
33 | 7.3089 | 3.3115 | -7.308 | -3.3181 | 0.00096755 | -0.0066009 | 0.23191 | 0.232 | 0.232 | 0.99882 | -0.022489 | 0.99866 | -0.025411 | 27.5535
34 | -7.3089 | -3.3115 | 7.3098 | 3.306 | 0.00081439 | -0.0055623 | 0.23191 | 0.23184 | 0.23191 | 0.99882 | -0.022489 | 0.99895 | -0.020024 | 27.5429
35 | 7.1544 | 3.2437 | -7.1498 | -3.2378 | 0.0045454 | 0.0059429 | 0.22707 | 0.22708 | 0.22708 | 0.99866 | -0.025411 | 0.99779 | -0.055462 | 27.6922
36 | -7.3098 | -3.306 | 7.3103 | 3.302 | 0.00058312 | -0.0039862 | 0.23184 | 0.23178 | 0.23184 | 0.99895 | -0.020024 | 0.99904 | -0.018255 | 27.534
37 | -1.3662 | -0.54448 | 1.3673 | 0.54478 | 0.0011305 | 0.00029262 | 0.042587 | 0.042582 | 0.042587 | 0.9969 | -0.064781 | 0.99779 | -0.055462 | 20.2794
38 | 4.8665 | 2.2545 | -4.8589 | -2.271 | 0.007631 | -0.016577 | 0.15554 | 0.15581 | 0.15581 | 0.99542 | -0.11577 | 0.9937 | -0.13509 | 43.0418
39 | 0.29827 | 0.13584 | -0.29823 | -0.14404 | 4.2314e-05 | -0.0082001 | 0.0095048 | 0.009606 | 0.009606 | 0.99542 | -0.11577 | 0.99528 | -0.11462 | 4.3664
40 | -5.382 | -2.4954 | 5.392 | 2.5064 | 0.010013 | 0.010993 | 0.17204 | 0.17204 | 0.17204 | 0.99542 | -0.11577 | 0.99775 | -0.056233 | 49.1546
41 | 0.21721 | 0.10505 | -0.21721 | -0.1052 | 4.2031e-07 | -0.00015197 | 0.006997 | 0.006999 | 0.006999 | 0.99542 | -0.11577 | 0.99541 | -0.11576 | 3.1813
42 | 3.694 | 1.7277 | -3.675 | -1.7458 | 0.018982 | -0.01808 | 0.11847 | 0.11876 | 0.11876 | 0.9937 | -0.13509 | 0.98894 | -0.092885 | 53.9841
43 | 0.43797 | 0.21158 | -0.43795 | -0.21161 | 1.1625e-05 | -3.1239e-05 | 0.01413 | 0.014131 | 0.014131 | 0.9937 | -0.13509 | 0.99367 | -0.13527 | 6.7288
44 | 0.72693 | 0.33173 | -0.72658 | -0.34305 | 0.00035086 | -0.011322 | 0.023213 | 0.023353 | 0.023353 | 0.9937 | -0.13509 | 0.99325 | -0.13128 | 10.6148
45 | 0.29823 | 0.14404 | -0.29822 | -0.14444 | 2.0483e-06 | -0.00039246 | 0.009606 | 0.0096109 | 0.0096109 | 0.99528 | -0.11462 | 0.99528 | -0.11456 | 4.3686
46 | -5.7823 | -2.6954 | 5.7825 | 2.693 | 0.00020945 | -0.0023634 | 0.18458 | 0.18455 | 0.18458 | 0.99775 | -0.056233 | 0.99779 | -0.055462 | 21.9217
47 | 0.30597 | 0.104 | -0.30585 | -0.12645 | 0.00011516 | -0.022456 | 0.0093926 | 0.009623 | 0.009623 | 0.9932 | -0.064077 | 0.99283 | -0.062565 | 4.3741
48 | 0.11582 | 0.046979 | -0.11581 | -0.05603 | 6.9754e-06 | -0.0090512 | 0.0036339 | 0.0037408 | 0.0037408 | 0.99283 | -0.062565 | 0.99278 | -0.062138 | 1.7004
49 | 0.094583 | 0.033441 | -0.094576 | -0.045462 | 6.0556e-06 | -0.012021 | 0.0029169 | 0.0030513 | 0.0030513 | 0.99283 | -0.062565 | 0.99277 | -0.062188 | 1.387
50 | 0.095452 | 0.046033 | -0.09545 | -0.046228 | 2.8414e-06 | -0.00019572 | 0.0030812 | 0.0030837 | 0.0030837 | 0.99283 | -0.062565 | 0.9928 | -0.062763 | 1.4685
51 | 0.5773 | 0.27888 | -0.57729 | -0.27922 | 6.9017e-06 | -0.00034764 | 0.018646 | 0.018651 | 0.018651 | 0.99258 | -0.07478 | 0.99257 | -0.074676 | 8.4776
52 | -0.92713 | -0.43275 | 0.92787 | 0.41819 | 0.00073793 | -0.014566 | 0.029757 | 0.029578 | 0.029757 | 0.99258 | -0.07478 | 0.99332 | -0.080885 | 13.5258
53 | 0.11581 | 0.05603 | -0.11581 | -0.056089 | 4.6371e-08 | -5.8394e-05 | 0.0037408 | 0.0037416 | 0.0037416 | 0.99278 | -0.062138 | 0.99277 | -0.062135 | 1.7007
54 | 0.094576 | 0.045462 | -0.094576 | -0.045805 | 1.8169e-07 | -0.00034344 | 0.0030513 | 0.0030556 | 0.0030556 | 0.99277 | -0.062188 | 0.99277 | -0.062172 | 1.3889
55 | -0.30259 | -0.14655 | 0.30259 | 0.14589 | 3.5887e-06 | -0.00066094 | 0.0097778 | 0.0097694 | 0.0097778 | 0.99261 | -0.079253 | 0.99262 | -0.079356 | 4.4444
56 | -0.30259 | -0.14589 | 0.30268 | 0.14533 | 8.8984e-05 | -0.00056046 | 0.0097694 | 0.0097616 | 0.0097694 | 0.99262 | -0.079356 | 0.99292 | -0.077369 | 4.6521
57 | -6.0729 | -2.6978 | 6.0734 | 2.6928 | 0.0004835 | -0.0049891 | 0.19231 | 0.19225 | 0.19231 | 0.99749 | -0.067567 | 0.99758 | -0.06576 | 22.8401
58 | 5.8057 | 2.5683 | -5.8046 | -2.567 | 0.0010818 | 0.0013347 | 0.18372 | 0.18373 | 0.18373 | 0.99749 | -0.067567 | 0.99723 | -0.076546 | 22.4058
59 | 0.61857 | 0.2886 | -0.61853 | -0.29071 | 4.6483e-05 | -0.0021038 | 0.019752 | 0.019778 | 0.019778 | 0.99758 | -0.06576 | 0.99751 | -0.065154 | 8.9902
60 | -6.692 | -2.9814 | 6.698 | 2.9891 | 0.006 | 0.0077207 | 0.212 | 0.21199 | 0.212 | 0.99758 | -0.06576 | 0.99881 | -0.022845 | 25.8535
61 | 5.8046 | 2.567 | -5.8014 | -2.6035 | 0.00322 | -0.036524 | 0.18373 | 0.18419 | 0.18419 | 0.99723 | -0.076546 | 0.99658 | -0.089081 | 21.8756
62 | 0.61853 | 0.29071 | -0.61841 | -0.29083 | 0.0001171 | -0.00012617 | 0.019778 | 0.019781 | 0.019781 | 0.99751 | -0.065154 | 0.99731 | -0.066542 | 9.4195
63 | -6.8296 | -3.0528 | 6.8296 | 3.0525 | 4.6554e-05 | -0.00037206 | 0.21621 | 0.21621 | 0.21621 | 0.99881 | -0.022845 | 0.99881 | -0.022692 | 25.6783
64 | 0.13961 | 0.066773 | -0.13961 | -0.067616 | 9.5696e-07 | -0.00084359 | 0.0044828 | 0.0044934 | 0.0044934 | 0.99658 | -0.089081 | 0.99657 | -0.089022 | 2.0424
65 | 5.6618 | 2.5368 | -5.6606 | -2.5509 | 0.0011878 | -0.014141 | 0.17971 | 0.17989 | 0.17989 | 0.99658 | -0.089081 | 0.99633 | -0.093769 | 21.3649
66 | 5.2951 | 2.374 | -5.2937 | -2.3925 | 0.0013546 | -0.018584 | 0.16813 | 0.16837 | 0.16837 | 0.99633 | -0.093769 | 0.99603 | -0.099472 | 19.9961
67 | 0.36549 | 0.17695 | -0.36548 | -0.17701 | 1.3836e-05 | -5.781e-05 | 0.011765 | 0.011766 | 0.011766 | 0.99633 | -0.093769 | 0.99629 | -0.094019 | 5.603
68 | 0.34209 | 0.157 | -0.34207 | -0.1586 | 1.0737e-05 | -0.001603 | 0.010895 | 0.010914 | 0.010914 | 0.99731 | -0.066542 | 0.99728 | -0.066297 | 4.9611
69 | -6.8296 | -3.0525 | 6.8317 | 3.0361 | 0.0020507 | -0.016414 | 0.21621 | 0.21599 | 0.21621 | 0.99881 | -0.022692 | 0.99917 | -0.015913 | 25.6777
70 | -14.3319 | -6.4245 | 14.3413 | 6.4141 | 0.0093672 | -0.010386 | 0.45377 | 0.45355 | 0.45377 | 0.99917 | -0.015913 | 0.99993 | -0.0012485 | 53.892
71 | 7.5002 | 3.3885 | -7.4994 | -3.3936 | 0.00079242 | -0.0051118 | 0.23778 | 0.23785 | 0.23785 | 0.99917 | -0.015913 | 0.99904 | -0.018255 | 28.2484
72 | 0.35992 | 0.16866 | -0.35988 | -0.17417 | 4.1519e-05 | -0.0055055 | 0.01152 | 0.011589 | 0.011589 | 0.99603 | -0.099472 | 0.99593 | -0.098505 | 5.2676
73 | 0.33563 | 0.16151 | -0.33562 | -0.16209 | 3.8541e-06 | -0.00058529 | 0.010795 | 0.010802 | 0.010802 | 0.99603 | -0.099472 | 0.99602 | -0.099373 | 4.9101
74 | 4.5982 | 2.0624 | -4.5981 | -2.0638 | 7.8966e-05 | -0.0014605 | 0.14606 | 0.14608 | 0.14608 | 0.99603 | -0.099472 | 0.99601 | -0.099857 | 17.3486
75 | 0.34207 | 0.1586 | -0.34203 | -0.16562 | 4.7468e-05 | -0.0070172 | 0.010914 | 0.011002 | 0.011002 | 0.99728 | -0.066297 | 0.99715 | -0.065146 | 5.0007
76 | -14.3413 | -6.4141 | 14.3421 | 6.4133 | 0.00079648 | -0.00088533 | 0.45355 | 0.45353 | 0.45355 | 0.99993 | -0.0012485 | 1 | 0 | 53.8654
77 | -0.41038 | -0.19876 | 0.41039 | 0.19795 | 8.0352e-06 | -0.00080487 | 0.013255 | 0.013245 | 0.013255 | 0.99305 | -0.12953 | 0.99307 | -0.1297 | 6.025
78 | -0.41039 | -0.19795 | 0.41047 | 0.19 | 7.8718e-05 | -0.0079527 | 0.013245 | 0.013146 | 0.013245 | 0.99307 | -0.1297 | 0.99325 | -0.13128 | 6.0204
79 | 0.31611 | 0.15306 | -0.3161 | -0.1531 | 7.1035e-06 | -4.0612e-05 | 0.010208 | 0.010208 | 0.010208 | 0.99325 | -0.13128 | 0.99323 | -0.13142 | 4.861
80 | 3.675 | 1.7458 | -3.6737 | -1.747 | 0.0012877 | -0.0012141 | 0.11876 | 0.11878 | 0.11878 | 0.98894 | -0.092885 | 0.98861 | -0.089959 | 53.9931
81 | 0.17588 | 0.084684 | -0.17586 | -0.085171 | 2.4463e-05 | -0.00048728 | 0.005671 | 0.0056773 | 0.0056773 | 0.99367 | -0.13527 | 0.99353 | -0.13619 | 2.7035
82 | 0.34203 | 0.16562 | -0.34202 | -0.16565 | 5.6316e-06 | -2.747e-05 | 0.011002 | 0.011002 | 0.011002 | 0.99715 | -0.065146 | 0.99713 | -0.065255 | 5.239
83 | 0.52826 | 0.2466 | -0.52807 | -0.24693 | 0.0001908 | -0.00033154 | 0.016829 | 0.016835 | 0.016835 | 1 | 0 | 0.99962 | -0.0027041 | 8.0166
84 | 0.14157 | 0.06833 | -0.14157 | -0.068564 | 2.7051e-07 | -0.00023435 | 0.0045396 | 0.0045425 | 0.0045425 | 0.99962 | -0.0027041 | 0.99962 | -0.0026875 | 2.0648
85 | 0.38651 | 0.1786 | -0.38643 | -0.18707 | 7.2503e-05 | -0.0084753 | 0.012296 | 0.012401 | 0.012401 | 0.99962 | -0.0027041 | 0.99944 | -0.0011542 | 5.6367
86 | 0.38643 | 0.18707 | -0.38641 | -0.18715 | 2.0259e-05 | -7.5472e-05 | 0.012401 | 0.012402 | 0.012402 | 0.99944 | -0.0011542 | 0.99939 | -0.0015001 | 5.9056
87 | 0.35988 | 0.17417 | -0.35988 | -0.1743 | 9.6721e-07 | -0.00012745 | 0.011589 | 0.01159 | 0.01159 | 0.99593 | -0.098505 | 0.99593 | -0.098481 | 5.2683
88 | 0.26079 | 0.12585 | -0.26079 | -0.12631 | 1.8177e-06 | -0.00045704 | 0.0083925 | 0.0083983 | 0.0083983 | 0.99602 | -0.099373 | 0.99602 | -0.099313 | 3.8174
89 | 4.445 | 1.9897 | -4.4449 | -1.9918 | 0.00010819 | -0.0021495 | 0.14115 | 0.14117 | 0.14117 | 0.99601 | -0.099857 | 0.99599 | -0.1004 | 16.7666
90 | 4.3686 | 1.9549 | -4.3684 | -1.9554 | 0.00018653 | -0.00054737 | 0.13872 | 0.13873 | 0.13873 | 0.99599 | -0.1004 | 0.99594 | -0.10097 | 38.3221
91 | 0.2396 | 0.10557 | -0.2396 | -0.1057 | 4.2506e-07 | -0.00013076 | 0.0075892 | 0.0075908 | 0.0075908 | 0.99591 | -0.10071 | 0.99591 | -0.1007 | 3.4503
92 | -0.63547 | -0.2973 | 0.63549 | 0.29642 | 2.0523e-05 | -0.00087474 | 0.020336 | 0.020325 | 0.020336 | 0.99591 | -0.10071 | 0.99594 | -0.10097 | 9.2436
93 | 0.2396 | 0.1057 | -0.23956 | -0.116 | 3.4043e-05 | -0.010301 | 0.0075908 | 0.0077163 | 0.0077163 | 0.99591 | -0.1007 | 0.99577 | -0.099587 | 3.5074
94 | 3.4767 | 1.5477 | -3.467 | -1.5589 | 0.0096886 | -0.011193 | 0.11031 | 0.11047 | 0.11047 | 0.99594 | -0.10097 | 0.99332 | -0.080885 | 50.2151
95 | 0.25626 | 0.11129 | -0.25621 | -0.12261 | 4.2579e-05 | -0.011316 | 0.0080979 | 0.0082342 | 0.0082342 | 0.99594 | -0.10097 | 0.99578 | -0.099713 | 3.7428
96 | 0.23956 | 0.116 | -0.23956 | -0.11602 | 2.3727e-06 | -2.4988e-05 | 0.0077163 | 0.0077166 | 0.0077166 | 0.99577 | -0.099587 | 0.99576 | -0.099653 | 3.6746
97 | 0.61874 | 0.2866 | -0.61848 | -0.29814 | 0.00026052 | -0.011541 | 0.019817 | 0.019961 | 0.019961 | 0.99332 | -0.080885 | 0.99293 | -0.077413 | 9.0733
98 | 1.9204 | 0.85412 | -1.92 | -0.85576 | 0.00036901 | -0.001635 | 0.06108 | 0.061101 | 0.061101 | 0.99332 | -0.080885 | 0.99314 | -0.079519 | 27.7732
99 | 0.25621 | 0.12261 | -0.25621 | -0.12409 | 5.6782e-06 | -0.0014801 | 0.0082342 | 0.0082528 | 0.0082528 | 0.99578 | -0.099713 | 0.99576 | -0.099522 | 3.7513
100 | 0.61848 | 0.29814 | -0.61848 | -0.29828 | 3.1892e-06 | -0.00014017 | 0.019961 | 0.019963 | 0.019963 | 0.99293 | -0.077413 | 0.99292 | -0.077369 | 9.0741
101 | 1.6361 | 0.71825 | -1.6358 | -0.71812 | 0.00034095 | 0.00013005 | 0.051937 | 0.051938 | 0.051938 | 0.99314 | -0.079519 | 0.99292 | -0.081395 | 24.7324
102 | 0.26426 | 0.12762 | -0.26422 | -0.12797 | 4.1603e-05 | -0.00035066 | 0.008535 | 0.0085398 | 0.0085398 | 0.99257 | -0.074676 | 0.9924 | -0.07572 | 4.0666
103 | 1.6358 | 0.71812 | -1.632 | -0.74133 | 0.0037491 | -0.023206 | 0.051938 | 0.052227 | 0.052227 | 0.99292 | -0.081395 | 0.99077 | -0.064953 | 23.7394
104 | 0.20377 | 0.097641 | -0.20376 | -0.098687 | 2.5894e-06 | -0.001046 | 0.0065834 | 0.0065967 | 0.0065967 | 0.99077 | -0.064953 | 0.99076 | -0.064844 | 2.9985
105 | 1.4282 | 0.64369 | -1.427 | -0.6433 | 0.0012391 | 0.00038537 | 0.045645 | 0.045649 | 0.045649 | 0.99077 | -0.064953 | 0.98985 | -0.072212 | 21.7378
106 | 0.31188 | 0.1501 | -0.31187 | -0.15105 | 5.5456e-06 | -0.00095099 | 0.010094 | 0.010106 | 0.010106 | 0.98985 | -0.072212 | 0.98984 | -0.072058 | 4.5936
107 | 1.1151 | 0.49321 | -1.1142 | -0.50516 | 0.00088568 | -0.011952 | 0.03556 | 0.035705 | 0.035705 | 0.98985 | -0.072212 | 0.98911 | -0.066478 | 16.2297
108 | 0.79415 | 0.35361 | -0.79379 | -0.3632 | 0.00035845 | -0.0095887 | 0.025371 | 0.025488 | 0.025488 | 0.98911 | -0.066478 | 0.98869 | -0.063152 | 11.5854
109 | 0.32008 | 0.15155 | -0.32007 | -0.15332 | 1.0873e-05 | -0.0017737 | 0.010336 | 0.010358 | 0.010358 | 0.98911 | -0.066478 | 0.98908 | -0.066193 | 4.7083
110 | -0.377 | -0.18259 | 0.37702 | 0.18251 | 2.0992e-05 | -7.8594e-05 | 0.012237 | 0.012236 | 0.012237 | 0.98819 | -0.059782 | 0.98825 | -0.059414 | 5.827
111 | -0.37702 | -0.18251 | 0.37711 | 0.17209 | 8.857e-05 | -0.010422 | 0.012236 | 0.012106 | 0.012236 | 0.98825 | -0.059414 | 0.98847 | -0.061327 | 5.5616
112 | -0.58452 | -0.27058 | 0.58466 | 0.26365 | 0.00014042 | -0.0069259 | 0.018811 | 0.018726 | 0.018811 | 0.98847 | -0.061327 | 0.98869 | -0.063152 | 8.5504
113 | 0.20741 | 0.098488 | -0.20741 | -0.10045 | 5.0785e-06 | -0.0019648 | 0.0067056 | 0.0067304 | 0.0067304 | 0.98847 | -0.061327 | 0.98845 | -0.061119 | 3.0593
114 | 0.20913 | 0.099547 | -0.20913 | -0.10128 | 4.5627e-06 | -0.0017372 | 0.0067626 | 0.0067846 | 0.0067846 | 0.98869 | -0.063152 | 0.98867 | -0.062966 | 3.0839
115 | 0.32007 | 0.15332 | -0.32006 | -0.15501 | 1.0398e-05 | -0.001689 | 0.010358 | 0.01038 | 0.01038 | 0.98908 | -0.066193 | 0.98905 | -0.065914 | 4.718
116 | -2.1179 | -1.0182 | 2.1181 | 1.0177 | 0.00016316 | -0.00055078 | 0.068808 | 0.0688 | 0.068808 | 0.98589 | -0.10458 | 0.98596 | -0.10524 | 31.2763
117 | 2.0351 | 0.97813 | -2.032 | -0.97662 | 0.0031471 | 0.0015032 | 0.066115 | 0.066121 | 0.066121 | 0.98589 | -0.10458 | 0.98428 | -0.11508 | 31.486
118 | -1.2011 | -0.58174 | 1.2011 | 0.58162 | 1.1022e-05 | -0.00012116 | 0.03916 | 0.039158 | 0.03916 | 0.98383 | -0.1108 | 0.98383 | -0.11088 | 17.7999
119 | -1.2011 | -0.58162 | 1.2013 | 0.57985 | 0.00016057 | -0.0017665 | 0.039158 | 0.039135 | 0.039158 | 0.98383 | -0.11088 | 0.98396 | -0.11204 | 17.7992
120 | 0.1009 | 0.048601 | -0.1009 | -0.048867 | 1.6631e-07 | -0.00026642 | 0.0032857 | 0.0032891 | 0.0032891 | 0.98396 | -0.11204 | 0.98396 | -0.11202 | 1.495
121 | -1.3022 | -0.62845 | 1.3023 | 0.62794 | 5.5169e-05 | -0.00051459 | 0.042421 | 0.042414 | 0.042421 | 0.98396 | -0.11204 | 0.984 | -0.1124 | 19.2822
122 | -1.403 | -0.67675 | 1.4032 | 0.67556 | 0.00014822 | -0.0011856 | 0.045699 | 0.045683 | 0.045699 | 0.984 | -0.1124 | 0.98409 | -0.11331 | 20.7723
123 | -1.4032 | -0.67556 | 1.4032 | 0.67516 | 5.0553e-05 | -0.00040462 | 0.045683 | 0.045678 | 0.045683 | 0.98409 | -0.11331 | 0.98412 | -0.11362 | 20.7652
124 | -1.504 | -0.72394 | 1.504 | 0.72352 | 5.9487e-05 | -0.00041226 | 0.048961 | 0.048955 | 0.048961 | 0.98412 | -0.11362 | 0.98416 | -0.11396 | 22.2549
125 | -1.6045 | -0.77221 | 1.6046 | 0.7718 | 6.797e-05 | -0.00041149 | 0.052231 | 0.052226 | 0.052231 | 0.98416 | -0.11396 | 0.9842 | -0.11433 | 23.7415

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 15.2322 | 6.8388

## res_load
| p_mw | q_mvar
0 | 0.23501 | 0.11382
1 | 0.3406 | 0.16496
2 | 0.40097 | 0.1942
3 | 0.098006 | 0.047467
4 | 0.13398 | 0.064892
5 | 0.087917 | 0.04258
6 | 0.10203 | 0.049417
7 | 0.11997 | 0.058103
8 | 0.34972 | 0.16938
9 | 0.25346 | 0.12276
10 | 0.12633 | 0.061185
11 | 0.23552 | 0.11407
12 | 0.10445 | 0.050588
13 | 0.15361 | 0.074398
14 | 0.21714 | 0.10516
15 | 0.39028 | 0.18902
16 | 0.21721 | 0.1052
17 | 0.09545 | 0.046228
18 | 0.094576 | 0.045805
19 | 0.11581 | 0.056089
20 | 0.30259 | 0.14655
21 | 0.26725 | 0.12943
22 | 0.1316 | 0.063735
23 | 0.13961 | 0.067616
24 | 0.27633 | 0.13383
25 | 0.36548 | 0.17701
26 | 0.18911 | 0.091588
27 | 0.41038 | 0.19876
28 | 0.3161 | 0.1531
29 | 0.26207 | 0.12693
30 | 0.34783 | 0.16846
31 | 0.29822 | 0.14444
32 | 0.34202 | 0.16565
33 | 0.34789 | 0.16849
34 | 0.14157 | 0.068564
35 | 0.17586 | 0.085171
36 | 0.074831 | 0.036242
37 | 0.15308 | 0.074139
38 | 0.35988 | 0.1743
39 | 0.26079 | 0.12631
40 | 0.076316 | 0.036962
41 | 0.39587 | 0.19173
42 | 0.23956 | 0.11602
43 | 0.28391 | 0.13751
44 | 0.31303 | 0.15161
45 | 0.25621 | 0.12409
46 | 0.3158 | 0.15295
47 | 0.26422 | 0.12797
48 | 0.20376 | 0.098687
49 | 0.31187 | 0.15105
50 | 0.377 | 0.18259
51 | 0.20741 | 0.10045
52 | 0.20913 | 0.10128
53 | 0.32006 | 0.15501
54 | 0.38641 | 0.18715
55 | 0.08278 | 0.040092
56 | 0.12684 | 0.061431
57 | 1.2011 | 0.58174
58 | 0.1009 | 0.048867
59 | 0.10078 | 0.04881
60 | 0.10072 | 0.04878
61 | 0.10052 | 0.048684
62 | 0.10032 | 0.048585

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1