## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_347_1_node_133 | 20 | n |  | TRUE
1 | bus_MV_347_1_node_97 | 20 | n |  | TRUE
2 | bus_MV_347_1_node_134 | 20 | n |  | TRUE
3 | bus_MV_347_1_node_136 | 20 | n |  | TRUE
4 | bus_MV_347_1_node_99 | 20 | n |  | TRUE
5 | bus_MV_347_1_node_137 | 20 | n |  | TRUE
6 | bus_MV_347_1_node_138 | 20 | n |  | TRUE
7 | bus_MV_347_1_node_139 | 20 | n |  | TRUE
8 | bus_MV_347_1_node_142 | 20 | n |  | TRUE
9 | bus_MV_347_1_node_144 | 20 | n |  | TRUE
10 | bus_MV_347_1_node_151 | 20 | n |  | TRUE
11 | bus_MV_347_1_node_153 | 20 | n |  | TRUE
12 | bus_MV_347_1_node_140 | 20 | n |  | TRUE
13 | bus_MV_347_1_node_141 | 20 | n |  | TRUE
14 | bus_MV_347_1_node_156 | 20 | n |  | TRUE
15 | bus_MV_347_1_node_182 | 20 | n |  | TRUE
16 | bus_MV_347_1_node_109 | 20 | n |  | TRUE
17 | bus_MV_347_1_node_143 | 20 | n |  | TRUE
18 | bus_MV_347_1_node_145 | 20 | n |  | TRUE
19 | bus_MV_347_1_node_167 | 20 | n |  | TRUE
20 | bus_MV_347_1_node_146 | 20 | n |  | TRUE
21 | bus_MV_347_1_node_147 | 20 | n |  | TRUE
22 | bus_MV_347_1_node_148 | 20 | n |  | TRUE
23 | bus_MV_347_1_node_149 | 20 | n |  | TRUE
24 | bus_MV_347_1_node_150 | 20 | n |  | TRUE
25 | bus_MV_347_1_node_152 | 20 | n |  | TRUE
26 | bus_MV_347_1_node_181 | 20 | n |  | TRUE
27 | bus_MV_347_1_node_154 | 20 | n |  | TRUE
28 | bus_MV_347_1_node_104 | 20 | n |  | TRUE
29 | bus_MV_347_1_node_155 | 20 | n |  | TRUE
30 | bus_MV_347_1_node_157 | 20 | n |  | TRUE
31 | bus_MV_347_1_node_158 | 20 | n |  | TRUE
32 | bus_MV_347_1_node_159 | 20 | n |  | TRUE
33 | bus_MV_347_1_node_161 | 20 | n |  | TRUE
34 | bus_MV_347_1_node_98 | 20 | n |  | TRUE
35 | bus_MV_347_1_node_168 | 20 | n |  | TRUE
36 | bus_MV_347_1_node_102 | 20 | n |  | TRUE
37 | bus_MV_347_1_node_175 | 20 | n |  | TRUE
38 | bus_MV_347_1_node_91 | 20 | n |  | TRUE
39 | bus_MV_347_1_node_176 | 20 | n |  | TRUE
40 | bus_MV_347_1_node_92 | 20 | n |  | TRUE
41 | bus_MV_347_1_node_93 | 20 | n |  | TRUE
42 | bus_MV_347_1_node_94 | 20 | n |  | TRUE
43 | bus_MV_347_1_node_95 | 20 | n |  | TRUE
44 | bus_MV_347_1_node_96 | 20 | n |  | TRUE
45 | bus_MV_347_1_node_100 | 20 | n |  | TRUE
46 | bus_MV_347_1_node_101 | 20 | n |  | TRUE
47 | bus_MV_347_1_node_103 | 20 | n |  | TRUE
48 | bus_MV_347_1_node_111 | 20 | n |  | TRUE
49 | bus_MV_347_1_node_106 | 20 | n |  | TRUE
50 | bus_MV_347_1_node_105 | 20 | n |  | TRUE
51 | bus_MV_347_1_node_110 | 20 | n |  | TRUE
52 | bus_MV_347_1_node_107 | 20 | n |  | TRUE
53 | bus_MV_347_1_node_108 | 20 | n |  | TRUE
54 | bus_HV_347_1_node_110 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_347_1_load_133 | 0 | 0.084367 | 0.040861 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_347_1_load_134 | 2 | 0.10531 | 0.051002 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_347_1_load_136 | 3 | 0.39217 | 0.18994 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_347_1_load_137 | 5 | 0.19769 | 0.095744 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_347_1_load_153 | 11 | 0.090298 | 0.043733 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_347_1_load_156 | 14 | 0.086326 | 0.04181 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_347_1_load_182 | 15 | 0.14711 | 0.07125 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_347_1_load_145 | 18 | 0.12401 | 0.060059 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_347_1_load_167 | 19 | 0.41236 | 0.19972 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_347_1_load_146 | 20 | 0.11124 | 0.053875 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_347_1_load_147 | 21 | 0.091354 | 0.044245 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_347_1_load_150 | 24 | 0.074828 | 0.036241 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_347_1_load_181 | 26 | 0.28393 | 0.13751 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_347_1_load_154 | 27 | 0.31793 | 0.15398 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_347_1_load_155 | 29 | 0.08985 | 0.043516 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_347_1_load_159 | 32 | 0.072349 | 0.03504 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_347_1_load_161 | 33 | 0.06954 | 0.03368 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_347_1_load_168 | 35 | 0.20639 | 0.099958 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_347_1_load_91 | 38 | 0.12948 | 0.062711 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_347_1_load_176 | 39 | 0.12897 | 0.062463 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_347_1_load_94 | 42 | 0.2123 | 0.10282 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_347_1_load_100 | 45 | 0.1397 | 0.067661 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_347_1_load_111 | 48 | 0.3672 | 0.17784 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_347_1_load_106 | 49 | 0.20375 | 0.098681 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_347_1_load_110 | 51 | 0.32065 | 0.1553 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_347_1_load_107 | 52 | 0.2361 | 0.11435 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 51 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_347_1_line_0 |  | 0 | 1 | 0.00091009 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_347_1_line_1 |  | 1 | 34 | 0.1517 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_347_1_line_2 |  | 2 | 3 | 0.07896 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_347_1_line_3 |  | 3 | 4 | 0.030344 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_347_1_line_4 |  | 4 | 43 | 0.33162 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_347_1_line_5 |  | 5 | 6 | 0.020534 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_347_1_line_6 |  | 6 | 7 | 0.038115 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_347_1_line_7 |  | 6 | 8 | 0.31625 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_347_1_line_8 |  | 6 | 9 | 0.18778 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_347_1_line_9 |  | 7 | 10 | 0.18054 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_347_1_line_10 |  | 7 | 11 | 0.055472 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_347_1_line_11 |  | 8 | 16 | 0.35548 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_347_1_line_12 |  | 8 | 17 | 0.24385 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_347_1_line_13 |  | 8 | 18 | 0.021961 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_347_1_line_14 |  | 8 | 12 | 0.72592 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_347_1_line_15 |  | 9 | 20 | 0.089803 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_347_1_line_16 |  | 10 | 25 | 0.11113 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_347_1_line_17 |  | 10 | 24 | 0.052109 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_347_1_line_18 |  | 12 | 13 | 0.34001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_347_1_line_19 |  | 12 | 14 | 0.1288 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_347_1_line_20 |  | 13 | 15 | 0.035975 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_347_1_line_21 |  | 14 | 30 | 0.053947 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_347_1_line_22 |  | 16 | 29 | 0.084492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_347_1_line_23 |  | 16 | 53 | 0.089389 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_347_1_line_24 |  | 17 | 19 | 0.033272 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_347_1_line_25 |  | 21 | 22 | 0.059023 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_347_1_line_26 |  | 22 | 23 | 0.034447 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_347_1_line_27 |  | 23 | 24 | 0.050379 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_347_1_line_28 |  | 25 | 26 | 0.037319 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_347_1_line_29 |  | 26 | 37 | 1.5399 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_347_1_line_30 |  | 27 | 28 | 0.026692 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_347_1_line_31 |  | 28 | 50 | 0.38541 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
32 | MV_347_1_line_32 |  | 28 | 44 | 0.44332 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
33 | MV_347_1_line_33 |  | 30 | 31 | 0.41913 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_347_1_line_34 |  | 31 | 32 | 0.10393 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_347_1_line_35 |  | 33 | 34 | 0.037288 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_347_1_line_36 |  | 34 | 43 | 0.25495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_347_1_line_37 |  | 35 | 36 | 0.082209 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_347_1_line_38 |  | 36 | 47 | 0.30412 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_347_1_line_39 |  | 36 | 44 | 0.36265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_347_1_line_40 |  | 37 | 38 | 1.2618 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_347_1_line_41 |  | 37 | 39 | 0.1091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_347_1_line_42 |  | 38 | 40 | 0.048639 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_347_1_line_43 |  | 40 | 41 | 0.3144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_347_1_line_44 |  | 41 | 42 | 0.1057 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_347_1_line_45 |  | 42 | 43 | 0.044262 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_347_1_line_46 |  | 43 | 44 | 0.22766 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_347_1_line_47 |  | 44 | 45 | 0.023543 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_347_1_line_48 |  | 46 | 47 | 0.095791 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_347_1_line_49 |  | 46 | 48 | 0.04075 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_347_1_line_50 |  | 47 | 49 | 0.045971 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_347_1_line_51 |  | 50 | 51 | 0.035925 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
52 | MV_347_1_line_52 |  | 52 | 53 | 0.017587 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_347_1_trafo_110 | 25 MVA 110/20 kV | 54 | 51 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2621461.9282 | 1265076.8552
1 | 2621462.6109 | 1265077.4569
2 | 2620763.9172 | 1264916.2987
3 | 2620805.4034 | 1264983.4817
4 | 2620835.8381 | 1264983.6998
5 | 2621991.9315 | 1264977.6075
6 | 2621982.4402 | 1264995.8162
7 | 2621964.1919 | 1265029.2719
8 | 2621984.5505 | 1265244.82
9 | 2622097.1209 | 1264977.1741
10 | 2621844.6085 | 1264942.3916
11 | 2621936.6281 | 1265077.4109
12 | 2621904.9641 | 1265548.0705
13 | 2621758.6063 | 1265566.4442
14 | 2622026.2955 | 1265591.0523
15 | 2621733.7857 | 1265584.1655
16 | 2622199.9664 | 1265331.8949
17 | 2622021.7699 | 1265135.1483
18 | 2621983.3998 | 1265265.2851
19 | 2621991.7802 | 1265120.738
20 | 2622146.4931 | 1264910.5911
21 | 2621718.8051 | 1265035.3274
22 | 2621772.4593 | 1265042.218
23 | 2621793.5371 | 1265025.3058
24 | 2621817.6855 | 1264981.0918
25 | 2621922.4258 | 1264929.1919
26 | 2621939.6113 | 1264896.0435
27 | 2621565.134 | 1265363.8462
28 | 2621541.1329 | 1265352.1668
29 | 2622242.4446 | 1265284.6949
30 | 2622077.6784 | 1265607.4863
31 | 2622366.8436 | 1265516.3179
32 | 2622267.1134 | 1265486.0768
33 | 2621415.8885 | 1265085.9939
34 | 2621385.7704 | 1265064.9482
35 | 2621175.6509 | 1265398.5822
36 | 2621250.7029 | 1265432.1298
37 | 2621441.4562 | 1263438.9199
38 | 2621495.0422 | 1264699.5556
39 | 2621536.9882 | 1263389.5097
40 | 2621458.1496 | 1264731.3774
41 | 2621210.7364 | 1264894.1781
42 | 2621178.7957 | 1264994.9341
43 | 2621162.8893 | 1265035.9503
44 | 2621302.054 | 1265184.6191
45 | 2621278.4886 | 1265186.1244
46 | 2621496.3105 | 1265586.6679
47 | 2621452.516 | 1265536.2295
48 | 2621537.1332 | 1265588.673
49 | 2621465.2347 | 1265492.0447
50 | 2621636.7739 | 1265223.4809
51 | 2621665.8922 | 1265202.4392
52 | 2622215.5568 | 1265412.9433
53 | 2622214.8847 | 1265395.4285
54 | 2621665.8922 | 1265202.4392

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99697 | -0.020302 | 0.084367 | 0.040861
1 | 0.99697 | -0.020303 | 0 | 0
2 | 0.99679 | -0.018824 | 0.10531 | 0.051002
3 | 0.9968 | -0.018722 | 0.39217 | 0.18994
4 | 0.99682 | -0.018903 | 0 | 0
5 | 0.9834 | -0.10456 | 0.19769 | 0.095744
6 | 0.98341 | -0.10461 | 0 | 0
7 | 0.98348 | -0.10512 | 0 | 0
8 | 0.98294 | -0.10137 | 0 | 0
9 | 0.98338 | -0.1044 | 0 | 0
10 | 0.98384 | -0.10768 | 0 | 0
11 | 0.98347 | -0.10506 | 0.090298 | 0.043733
12 | 0.98266 | -0.10022 | 0 | 0
13 | 0.98259 | -0.099708 | 0 | 0
14 | 0.98263 | -0.10009 | 0.086326 | 0.04181
15 | 0.98259 | -0.099643 | 0.14711 | 0.07125
16 | 0.98279 | -0.10014 | 0 | 0
17 | 0.98281 | -0.10018 | 0 | 0
18 | 0.98293 | -0.10134 | 0.12401 | 0.060059
19 | 0.98278 | -0.10035 | 0.41236 | 0.19972
20 | 0.98337 | -0.10429 | 0.11124 | 0.053875
21 | 0.98381 | -0.10744 | 0.091354 | 0.044245
22 | 0.98382 | -0.1075 | 0 | 0
23 | 0.98382 | -0.10754 | 0 | 0
24 | 0.98383 | -0.10758 | 0.074828 | 0.036241
25 | 0.98409 | -0.10942 | 0 | 0
26 | 0.98417 | -0.11001 | 0.28393 | 0.13751
27 | 0.9989 | -0.015785 | 0.31793 | 0.15398
28 | 0.99891 | -0.015886 | 0 | 0
29 | 0.98278 | -0.10005 | 0.08985 | 0.043516
30 | 0.98263 | -0.10009 | 0 | 0
31 | 0.98259 | -0.099914 | 0 | 0
32 | 0.98258 | -0.099829 | 0.072349 | 0.03504
33 | 0.99698 | -0.020409 | 0.06954 | 0.03368
34 | 0.99698 | -0.020439 | 0 | 0
35 | 0.99755 | -0.024838 | 0.20639 | 0.099958
36 | 0.99758 | -0.024632 | 0 | 0
37 | 0.99015 | -0.05931 | 0 | 0
38 | 0.99537 | -0.015787 | 0.12948 | 0.062711
39 | 0.99014 | -0.059148 | 0.12897 | 0.062463
40 | 0.99551 | -0.016848 | 0 | 0
41 | 0.99643 | -0.023613 | 0 | 0
42 | 0.99689 | -0.019736 | 0.2123 | 0.10282
43 | 0.99703 | -0.020788 | 0 | 0
44 | 0.99794 | -0.027649 | 0 | 0
45 | 0.99794 | -0.02761 | 0.1397 | 0.067661
46 | 0.99732 | -0.022289 | 0 | 0
47 | 0.99736 | -0.022699 | 0 | 0
48 | 0.9973 | -0.02211 | 0.3672 | 0.17784
49 | 0.99735 | -0.022588 | 0.20375 | 0.098681
50 | 0.99982 | -0.0048608 | 0 | 0
51 | 1 | 0 | -4.4283 | -1.9732
52 | 0.98276 | -0.099835 | 0.2361 | 0.11435
53 | 0.98276 | -0.099887 | 0 | 0
54 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.084367 | -0.040861 | 0.084367 | 0.040839 | 8.9576e-09 | -2.1595e-05 | 0.0027143 | 0.002714 | 0.0027143 | 0.99697 | -0.020302 | 0.99697 | -0.020303 | 1.2338
1 | -0.084367 | -0.040839 | 0.084369 | 0.03724 | 1.4674e-06 | -0.0035997 | 0.002714 | 0.0026703 | 0.002714 | 0.99697 | -0.020303 | 0.99698 | -0.020439 | 1.2337
2 | -0.10531 | -0.051002 | 0.10531 | 0.05091 | 1.6148e-06 | -9.2648e-05 | 0.0033886 | 0.0033874 | 0.0033886 | 0.99679 | -0.018824 | 0.9968 | -0.018722 | 1.6136
3 | -0.49748 | -0.24085 | 0.49749 | 0.24013 | 1.0373e-05 | -0.00071681 | 0.016007 | 0.015998 | 0.016007 | 0.9968 | -0.018722 | 0.99682 | -0.018903 | 7.2758
4 | -0.49749 | -0.24013 | 0.4976 | 0.2323 | 0.00011261 | -0.0078358 | 0.015998 | 0.0159 | 0.015998 | 0.99682 | -0.018903 | 0.99703 | -0.020788 | 7.2717
5 | -0.19769 | -0.095744 | 0.19769 | 0.09527 | 1.1386e-06 | -0.0004738 | 0.0064478 | 0.0064417 | 0.0064478 | 0.9834 | -0.10456 | 0.98341 | -0.10461 | 2.9308
6 | -1.4779 | -0.64096 | 1.478 | 0.64011 | 0.00011375 | -0.00084642 | 0.047286 | 0.047276 | 0.047286 | 0.98341 | -0.10461 | 0.98348 | -0.10512 | 21.4938
7 | 1.1689 | 0.49822 | -1.1683 | -0.50535 | 0.00058872 | -0.0071241 | 0.0373 | 0.037385 | 0.037385 | 0.98341 | -0.10461 | 0.98294 | -0.10137 | 16.9931
8 | 0.11124 | 0.047467 | -0.11124 | -0.051802 | 3.2053e-06 | -0.0043348 | 0.0035503 | 0.0036022 | 0.0036022 | 0.98341 | -0.10461 | 0.98338 | -0.1044 | 1.6374
9 | -1.5683 | -0.68257 | 1.5689 | 0.67858 | 0.00060687 | -0.0039908 | 0.050204 | 0.050155 | 0.050204 | 0.98348 | -0.10512 | 0.98384 | -0.10768 | 22.8198
10 | 0.090299 | 0.042452 | -0.090298 | -0.043733 | 6.3873e-07 | -0.0012809 | 0.0029288 | 0.002945 | 0.002945 | 0.98348 | -0.10512 | 0.98347 | -0.10506 | 1.3386
11 | 0.32601 | 0.14527 | -0.32595 | -0.15345 | 5.2636e-05 | -0.0081835 | 0.010482 | 0.010582 | 0.010582 | 0.98294 | -0.10137 | 0.98279 | -0.10014 | 4.8101
12 | 0.41243 | 0.19408 | -0.41237 | -0.19968 | 5.8646e-05 | -0.0056071 | 0.013387 | 0.013458 | 0.013458 | 0.98294 | -0.10137 | 0.98281 | -0.10018 | 6.1171
13 | 0.12401 | 0.059553 | -0.12401 | -0.060059 | 4.793e-07 | -0.00050646 | 0.0040401 | 0.0040466 | 0.0040466 | 0.98294 | -0.10137 | 0.98293 | -0.10134 | 1.8394
14 | 0.3059 | 0.10645 | -0.30581 | -0.12317 | 8.9235e-05 | -0.016715 | 0.0095122 | 0.009685 | 0.009685 | 0.98294 | -0.10137 | 0.98266 | -0.10022 | 4.4023
15 | 0.11124 | 0.051802 | -0.11124 | -0.053875 | 1.5668e-06 | -0.002073 | 0.0036022 | 0.0036283 | 0.0036283 | 0.98338 | -0.1044 | 0.98337 | -0.10429 | 1.6492
16 | -1.7351 | -0.75453 | 1.7355 | 0.7521 | 0.000457 | -0.0024335 | 0.055515 | 0.055485 | 0.055515 | 0.98384 | -0.10768 | 0.98409 | -0.10942 | 25.2342
17 | 0.16619 | 0.075958 | -0.16618 | -0.077162 | 2.0051e-06 | -0.0012037 | 0.0053614 | 0.0053761 | 0.0053761 | 0.98384 | -0.10768 | 0.98383 | -0.10758 | 2.4437
18 | 0.14712 | 0.062586 | -0.14711 | -0.070421 | 1.0212e-05 | -0.0078355 | 0.0046969 | 0.0047917 | 0.0047917 | 0.98266 | -0.10022 | 0.98259 | -0.099708 | 2.178
19 | 0.15868 | 0.060581 | -0.15868 | -0.063549 | 4.3082e-06 | -0.0029681 | 0.0049898 | 0.0050216 | 0.0050216 | 0.98266 | -0.10022 | 0.98263 | -0.10009 | 2.2825
20 | 0.14711 | 0.070421 | -0.14711 | -0.07125 | 1.1051e-06 | -0.00082897 | 0.0047917 | 0.0048023 | 0.0048023 | 0.98259 | -0.099708 | 0.98259 | -0.099643 | 2.1829
21 | 0.072353 | 0.02174 | -0.072352 | -0.022983 | 3.5646e-07 | -0.0012436 | 0.0022194 | 0.0022302 | 0.0022302 | 0.98263 | -0.10009 | 0.98263 | -0.10009 | 1.0137
22 | 0.089851 | 0.041568 | -0.08985 | -0.043516 | 9.618e-07 | -0.0019482 | 0.0029079 | 0.0029324 | 0.0029324 | 0.98279 | -0.10014 | 0.98278 | -0.10005 | 1.3329
23 | 0.2361 | 0.11188 | -0.2361 | -0.11394 | 7.0521e-06 | -0.0020593 | 0.0076743 | 0.0077005 | 0.0077005 | 0.98279 | -0.10014 | 0.98276 | -0.099887 | 3.5002
24 | 0.41237 | 0.19968 | -0.41236 | -0.19972 | 1.0737e-05 | -3.164e-05 | 0.013458 | 0.013458 | 0.013458 | 0.98281 | -0.10018 | 0.98278 | -0.10035 | 6.4087
25 | -0.091354 | -0.044245 | 0.091354 | 0.042881 | 6.9491e-07 | -0.0013638 | 0.0029784 | 0.0029611 | 0.0029784 | 0.98381 | -0.10744 | 0.98382 | -0.1075 | 1.3538
26 | -0.091354 | -0.042881 | 0.091355 | 0.042085 | 4.0188e-07 | -0.00079595 | 0.0029611 | 0.0029513 | 0.0029611 | 0.98382 | -0.1075 | 0.98382 | -0.10754 | 1.346
27 | -0.091355 | -0.042085 | 0.091355 | 0.040921 | 5.8299e-07 | -0.0011641 | 0.0029513 | 0.0029372 | 0.0029513 | 0.98382 | -0.10754 | 0.98383 | -0.10758 | 1.3415
28 | -1.7355 | -0.7521 | 1.7357 | 0.75128 | 0.00015335 | -0.00081749 | 0.055485 | 0.055475 | 0.055485 | 0.98409 | -0.10942 | 0.98417 | -0.11001 | 25.2205
29 | -2.0196 | -0.88879 | 2.0311 | 0.8942 | 0.011489 | 0.0054049 | 0.064721 | 0.0647 | 0.064721 | 0.98417 | -0.11001 | 0.99015 | -0.05931 | 30.8197
30 | -0.31793 | -0.15398 | 0.31794 | 0.15335 | 3.7109e-06 | -0.0006348 | 0.010209 | 0.010201 | 0.010209 | 0.9989 | -0.015785 | 0.99891 | -0.015886 | 4.6404
31 | -4.4101 | -1.9726 | 4.4137 | 1.962 | 0.0036245 | -0.010571 | 0.13961 | 0.13946 | 0.13961 | 0.99891 | -0.015886 | 0.99982 | -0.0048608 | 38.5677
32 | 4.0921 | 1.8192 | -4.0885 | -1.8318 | 0.0035914 | -0.012551 | 0.12942 | 0.1296 | 0.1296 | 0.99891 | -0.015886 | 0.99794 | -0.027649 | 35.8003
33 | 0.072352 | 0.022983 | -0.072349 | -0.032645 | 2.9016e-06 | -0.0096612 | 0.0022302 | 0.0023319 | 0.0023319 | 0.98263 | -0.10009 | 0.98259 | -0.099914 | 1.06
34 | 0.072349 | 0.032645 | -0.072349 | -0.03504 | 7.64e-07 | -0.0023955 | 0.0023319 | 0.0023617 | 0.0023617 | 0.98259 | -0.099914 | 0.98258 | -0.099829 | 1.0735
35 | -0.06954 | -0.03368 | 0.06954 | 0.032795 | 2.4792e-07 | -0.00088485 | 0.0022373 | 0.0022262 | 0.0022373 | 0.99698 | -0.020409 | 0.99698 | -0.020439 | 1.0169
36 | -0.15391 | -0.070035 | 0.15392 | 0.063986 | 8.0407e-06 | -0.0060484 | 0.0048961 | 0.0048262 | 0.0048961 | 0.99698 | -0.020439 | 0.99703 | -0.020788 | 2.2255
37 | -0.20639 | -0.099958 | 0.20639 | 0.099864 | 6.4491e-06 | -9.3625e-05 | 0.0066361 | 0.0066349 | 0.0066361 | 0.99755 | -0.024838 | 0.99758 | -0.024632 | 3.1601
38 | 0.57112 | 0.26502 | -0.57098 | -0.2722 | 0.00013542 | -0.0071843 | 0.018219 | 0.018308 | 0.018308 | 0.99758 | -0.024632 | 0.99736 | -0.022699 | 8.3219
39 | -0.77751 | -0.36488 | 0.77781 | 0.35635 | 0.00029779 | -0.0085317 | 0.024854 | 0.024749 | 0.024854 | 0.99758 | -0.024632 | 0.99794 | -0.027649 | 11.2971
40 | -2.1601 | -0.95411 | 2.1707 | 0.9593 | 0.010653 | 0.0051879 | 0.068845 | 0.068828 | 0.068845 | 0.99015 | -0.05931 | 0.99537 | -0.015787 | 32.7835
41 | 0.12897 | 0.05991 | -0.12897 | -0.062463 | 2.5228e-06 | -0.0025531 | 0.004146 | 0.0041779 | 0.0041779 | 0.99015 | -0.05931 | 0.99014 | -0.059148 | 1.899
42 | -2.3002 | -1.022 | 2.3005 | 1.021 | 0.00034595 | -0.0010481 | 0.072998 | 0.072984 | 0.072998 | 0.99537 | -0.015787 | 0.99551 | -0.016848 | 33.1809
43 | -2.3005 | -1.021 | 2.3028 | 1.0142 | 0.0022331 | -0.0067839 | 0.072984 | 0.072897 | 0.072984 | 0.99551 | -0.016848 | 0.99643 | -0.023613 | 33.1748
44 | -2.3028 | -1.0142 | 2.3038 | 1.0147 | 0.0010007 | 0.00050148 | 0.072897 | 0.072896 | 0.072897 | 0.99643 | -0.023613 | 0.99689 | -0.019736 | 34.713
45 | -2.5161 | -1.1175 | 2.5164 | 1.1166 | 0.0003755 | -0.00093901 | 0.079722 | 0.07971 | 0.079722 | 0.99689 | -0.019736 | 0.99703 | -0.020788 | 36.2374
46 | -3.168 | -1.4128 | 3.171 | 1.4083 | 0.0030636 | -0.0044995 | 0.10043 | 0.10037 | 0.10043 | 0.99703 | -0.020788 | 0.99794 | -0.027649 | 45.6509
47 | 0.1397 | 0.067101 | -0.1397 | -0.067661 | 6.3269e-07 | -0.00055961 | 0.0044832 | 0.0044902 | 0.0044902 | 0.99794 | -0.027649 | 0.99794 | -0.02761 | 2.041
48 | -0.36721 | -0.17688 | 0.36723 | 0.17461 | 1.7756e-05 | -0.0022697 | 0.011798 | 0.011769 | 0.011798 | 0.99732 | -0.022289 | 0.99736 | -0.022699 | 5.3626
49 | 0.36721 | 0.17688 | -0.3672 | -0.17784 | 7.5798e-06 | -0.00096547 | 0.011798 | 0.01181 | 0.01181 | 0.99732 | -0.022289 | 0.9973 | -0.02211 | 5.3682
50 | 0.20375 | 0.09759 | -0.20375 | -0.098681 | 2.6296e-06 | -0.001091 | 0.006539 | 0.0065527 | 0.0065527 | 0.99736 | -0.022699 | 0.99735 | -0.022588 | 2.9785
51 | -4.4137 | -1.962 | 4.4143 | 1.9627 | 0.00064141 | 0.00068851 | 0.13946 | 0.13946 | 0.13946 | 0.99982 | -0.0048608 | 1 | 0 | 39.8456
52 | -0.2361 | -0.11435 | 0.2361 | 0.11394 | 1.3932e-06 | -0.00040514 | 0.0077056 | 0.0077005 | 0.0077056 | 0.98276 | -0.099835 | 0.98276 | -0.099887 | 3.5026

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 4.749 | 2.1285

## res_load
| p_mw | q_mvar
0 | 0.084367 | 0.040861
1 | 0.10531 | 0.051002
2 | 0.39217 | 0.18994
3 | 0.19769 | 0.095744
4 | 0.090298 | 0.043733
5 | 0.086326 | 0.04181
6 | 0.14711 | 0.07125
7 | 0.12401 | 0.060059
8 | 0.41236 | 0.19972
9 | 0.11124 | 0.053875
10 | 0.091354 | 0.044245
11 | 0.074828 | 0.036241
12 | 0.28393 | 0.13751
13 | 0.31793 | 0.15398
14 | 0.08985 | 0.043516
15 | 0.072349 | 0.03504
16 | 0.06954 | 0.03368
17 | 0.20639 | 0.099958
18 | 0.12948 | 0.062711
19 | 0.12897 | 0.062463
20 | 0.2123 | 0.10282
21 | 0.1397 | 0.067661
22 | 0.3672 | 0.17784
23 | 0.20375 | 0.098681
24 | 0.32065 | 0.1553
25 | 0.2361 | 0.11435

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1