## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_356_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_356_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_356_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_356_0_node_7 | 20 | n |  | TRUE
4 | bus_MV_356_0_node_3 | 20 | n |  | TRUE
5 | bus_MV_356_0_node_4 | 20 | n |  | TRUE
6 | bus_MV_356_0_node_5 | 20 | n |  | TRUE
7 | bus_MV_356_0_node_6 | 20 | n |  | TRUE
8 | bus_MV_356_0_node_21 | 20 | n |  | TRUE
9 | bus_MV_356_0_node_22 | 20 | n |  | TRUE
10 | bus_MV_356_0_node_28 | 20 | n |  | TRUE
11 | bus_MV_356_0_node_29 | 20 | n |  | TRUE
12 | bus_MV_356_0_node_19 | 20 | n |  | TRUE
13 | bus_MV_356_0_node_131 | 20 | n |  | TRUE
14 | bus_MV_356_0_node_135 | 20 | n |  | TRUE
15 | bus_MV_356_0_node_25 | 20 | n |  | TRUE
16 | bus_MV_356_0_node_27 | 20 | n |  | TRUE
17 | bus_MV_356_0_node_23 | 20 | n |  | TRUE
18 | bus_MV_356_0_node_8 | 20 | n |  | TRUE
19 | bus_MV_356_0_node_9 | 20 | n |  | TRUE
20 | bus_MV_356_0_node_17 | 20 | n |  | TRUE
21 | bus_MV_356_0_node_16 | 20 | n |  | TRUE
22 | bus_MV_356_0_node_18 | 20 | n |  | TRUE
23 | bus_MV_356_0_node_10 | 20 | n |  | TRUE
24 | bus_MV_356_0_node_15 | 20 | n |  | TRUE
25 | bus_MV_356_0_node_14 | 20 | n |  | TRUE
26 | bus_MV_356_0_node_13 | 20 | n |  | TRUE
27 | bus_MV_356_0_node_12 | 20 | n |  | TRUE
28 | bus_MV_356_0_node_36 | 20 | n |  | TRUE
29 | bus_MV_356_0_node_139 | 20 | n |  | TRUE
30 | bus_MV_356_0_node_34 | 20 | n |  | TRUE
31 | bus_MV_356_0_node_20 | 20 | n |  | TRUE
32 | bus_MV_356_0_node_136 | 20 | n |  | TRUE
33 | bus_MV_356_0_node_30 | 20 | n |  | TRUE
34 | bus_MV_356_0_node_31 | 20 | n |  | TRUE
35 | bus_MV_356_0_node_32 | 20 | n |  | TRUE
36 | bus_MV_356_0_node_40 | 20 | n |  | TRUE
37 | bus_MV_356_0_node_39 | 20 | n |  | TRUE
38 | bus_MV_356_0_node_33 | 20 | n |  | TRUE
39 | bus_MV_356_0_node_35 | 20 | n |  | TRUE
40 | bus_MV_356_0_node_37 | 20 | n |  | TRUE
41 | bus_MV_356_0_node_130 | 20 | n |  | TRUE
42 | bus_MV_356_0_node_24 | 20 | n |  | TRUE
43 | bus_MV_356_0_node_26 | 20 | n |  | TRUE
44 | bus_MV_356_0_node_111 | 20 | n |  | TRUE
45 | bus_MV_356_0_node_113 | 20 | n |  | TRUE
46 | bus_MV_356_0_node_112 | 20 | n |  | TRUE
47 | bus_MV_356_0_node_123 | 20 | n |  | TRUE
48 | bus_MV_356_0_node_92 | 20 | n |  | TRUE
49 | bus_MV_356_0_node_124 | 20 | n |  | TRUE
50 | bus_MV_356_0_node_43 | 20 | n |  | TRUE
51 | bus_MV_356_0_node_41 | 20 | n |  | TRUE
52 | bus_MV_356_0_node_42 | 20 | n |  | TRUE
53 | bus_MV_356_0_node_44 | 20 | n |  | TRUE
54 | bus_MV_356_0_node_83 | 20 | n |  | TRUE
55 | bus_MV_356_0_node_121 | 20 | n |  | TRUE
56 | bus_MV_356_0_node_120 | 20 | n |  | TRUE
57 | bus_MV_356_0_node_45 | 20 | n |  | TRUE
58 | bus_MV_356_0_node_46 | 20 | n |  | TRUE
59 | bus_MV_356_0_node_47 | 20 | n |  | TRUE
60 | bus_MV_356_0_node_48 | 20 | n |  | TRUE
61 | bus_MV_356_0_node_51 | 20 | n |  | TRUE
62 | bus_MV_356_0_node_49 | 20 | n |  | TRUE
63 | bus_MV_356_0_node_50 | 20 | n |  | TRUE
64 | bus_MV_356_0_node_63 | 20 | n |  | TRUE
65 | bus_MV_356_0_node_52 | 20 | n |  | TRUE
66 | bus_MV_356_0_node_64 | 20 | n |  | TRUE
67 | bus_MV_356_0_node_66 | 20 | n |  | TRUE
68 | bus_MV_356_0_node_134 | 20 | n |  | TRUE
69 | bus_MV_356_0_node_132 | 20 | n |  | TRUE
70 | bus_MV_356_0_node_54 | 20 | n |  | TRUE
71 | bus_MV_356_0_node_69 | 20 | n |  | TRUE
72 | bus_MV_356_0_node_116 | 20 | n |  | TRUE
73 | bus_MV_356_0_node_62 | 20 | n |  | TRUE
74 | bus_MV_356_0_node_61 | 20 | n |  | TRUE
75 | bus_MV_356_0_node_81 | 20 | n |  | TRUE
76 | bus_MV_356_0_node_96 | 20 | n |  | TRUE
77 | bus_MV_356_0_node_97 | 20 | n |  | TRUE
78 | bus_MV_356_0_node_91 | 20 | n |  | TRUE
79 | bus_MV_356_0_node_99 | 20 | n |  | TRUE
80 | bus_MV_356_0_node_67 | 20 | n |  | TRUE
81 | bus_MV_356_0_node_82 | 20 | n |  | TRUE
82 | bus_MV_356_0_node_55 | 20 | n |  | TRUE
83 | bus_MV_356_0_node_56 | 20 | n |  | TRUE
84 | bus_MV_356_0_node_57 | 20 | n |  | TRUE
85 | bus_MV_356_0_node_58 | 20 | n |  | TRUE
86 | bus_MV_356_0_node_59 | 20 | n |  | TRUE
87 | bus_MV_356_0_node_60 | 20 | n |  | TRUE
88 | bus_MV_356_0_node_72 | 20 | n |  | TRUE
89 | bus_MV_356_0_node_133 | 20 | n |  | TRUE
90 | bus_MV_356_0_node_70 | 20 | n |  | TRUE
91 | bus_MV_356_0_node_68 | 20 | n |  | TRUE
92 | bus_MV_356_0_node_127 | 20 | n |  | TRUE
93 | bus_MV_356_0_node_95 | 20 | n |  | TRUE
94 | bus_MV_356_0_node_125 | 20 | n |  | TRUE
95 | bus_MV_356_0_node_93 | 20 | n |  | TRUE
96 | bus_MV_356_0_node_117 | 20 | n |  | TRUE
97 | bus_MV_356_0_node_118 | 20 | n |  | TRUE
98 | bus_MV_356_0_node_138 | 20 | n |  | TRUE
99 | bus_MV_356_0_node_119 | 20 | n |  | TRUE
100 | bus_MV_356_0_node_126 | 20 | n |  | TRUE
101 | bus_MV_356_0_node_73 | 20 | n |  | TRUE
102 | bus_MV_356_0_node_71 | 20 | n |  | TRUE
103 | bus_MV_356_0_node_75 | 20 | n |  | TRUE
104 | bus_MV_356_0_node_129 | 20 | n |  | TRUE
105 | bus_MV_356_0_node_86 | 20 | n |  | TRUE
106 | bus_MV_356_0_node_76 | 20 | n |  | TRUE
107 | bus_MV_356_0_node_77 | 20 | n |  | TRUE
108 | bus_MV_356_0_node_78 | 20 | n |  | TRUE
109 | bus_MV_356_0_node_80 | 20 | n |  | TRUE
110 | bus_MV_356_0_node_79 | 20 | n |  | TRUE
111 | bus_MV_356_0_node_128 | 20 | n |  | TRUE
112 | bus_MV_356_0_node_89 | 20 | n |  | TRUE
113 | bus_MV_356_0_node_102 | 20 | n |  | TRUE
114 | bus_MV_356_0_node_88 | 20 | n |  | TRUE
115 | bus_MV_356_0_node_90 | 20 | n |  | TRUE
116 | bus_MV_356_0_node_100 | 20 | n |  | TRUE
117 | bus_MV_356_0_node_98 | 20 | n |  | TRUE
118 | bus_MV_356_0_node_137 | 20 | n |  | TRUE
119 | bus_MV_356_0_node_94 | 20 | n |  | TRUE
120 | bus_MV_356_0_node_110 | 20 | n |  | TRUE
121 | bus_MV_356_0_node_103 | 20 | n |  | TRUE
122 | bus_MV_356_0_node_104 | 20 | n |  | TRUE
123 | bus_MV_356_0_node_105 | 20 | n |  | TRUE
124 | bus_MV_356_0_node_106 | 20 | n |  | TRUE
125 | bus_MV_356_0_node_107 | 20 | n |  | TRUE
126 | bus_MV_356_0_node_109 | 20 | n |  | TRUE
127 | bus_MV_356_0_node_108 | 20 | n |  | TRUE
128 | bus_MV_356_0_node_114 | 20 | n |  | TRUE
129 | bus_MV_356_0_node_115 | 20 | n |  | TRUE
130 | bus_HV_356_0_node_89 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_356_0_load_0 | 0 | 0.359 | 0.17387 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_356_0_load_7 | 3 | 0.15829 | 0.076663 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_356_0_load_6 | 7 | 0.32593 | 0.15786 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_356_0_load_21 | 8 | 0.20948 | 0.10145 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_356_0_load_22 | 9 | 0.16793 | 0.081333 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_356_0_load_29 | 11 | 0.29122 | 0.14104 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_356_0_load_131 | 13 | 0.29125 | 0.14106 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_356_0_load_135 | 14 | 0.24492 | 0.11862 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_356_0_load_27 | 16 | 0.138 | 0.066838 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_356_0_load_23 | 17 | 0.34551 | 0.16734 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_356_0_load_8 | 18 | 0.26781 | 0.12971 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_356_0_load_17 | 20 | 0.28099 | 0.13609 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_356_0_load_16 | 21 | 0.17112 | 0.082876 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_356_0_load_15 | 24 | 0.35711 | 0.17295 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_356_0_load_12 | 27 | 0.14713 | 0.07126 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_356_0_load_139 | 29 | 0.3407 | 0.16501 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_356_0_load_136 | 32 | 0.36187 | 0.17526 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_356_0_load_30 | 33 | 0.40419 | 0.19576 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_356_0_load_31 | 34 | 0.21682 | 0.10501 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_356_0_load_39 | 37 | 0.077491 | 0.037531 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_356_0_load_33 | 38 | 0.18986 | 0.091952 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_356_0_load_35 | 39 | 0.088346 | 0.042788 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_356_0_load_130 | 41 | 0.41288 | 0.19997 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_356_0_load_111 | 44 | 0.14767 | 0.071521 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_356_0_load_113 | 45 | 0.12463 | 0.060359 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_356_0_load_123 | 47 | 0.10484 | 0.050778 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_356_0_load_92 | 48 | 0.39554 | 0.19157 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_356_0_load_124 | 49 | 0.16741 | 0.081081 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_356_0_load_41 | 51 | 0.40047 | 0.19396 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_356_0_load_83 | 54 | 0.2209 | 0.10699 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_356_0_load_121 | 55 | 0.30276 | 0.14663 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_356_0_load_120 | 56 | 0.12752 | 0.061761 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_356_0_load_45 | 57 | 0.26464 | 0.12817 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_356_0_load_46 | 58 | 0.068645 | 0.033246 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_356_0_load_47 | 59 | 0.31593 | 0.15301 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_356_0_load_64 | 66 | 0.28983 | 0.14037 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_356_0_load_134 | 68 | 0.10465 | 0.050686 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_356_0_load_116 | 72 | 0.093984 | 0.045518 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_356_0_load_61 | 74 | 0.41015 | 0.19864 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_356_0_load_81 | 75 | 0.40439 | 0.19586 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_356_0_load_96 | 76 | 0.23606 | 0.11433 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_356_0_load_67 | 80 | 0.28413 | 0.13761 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_356_0_load_82 | 81 | 0.27144 | 0.13146 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_356_0_load_55 | 82 | 0.34997 | 0.1695 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_356_0_load_72 | 88 | 0.13331 | 0.064565 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_356_0_load_133 | 89 | 0.11959 | 0.057922 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_356_0_load_68 | 91 | 0.33872 | 0.16405 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_356_0_load_127 | 92 | 0.31068 | 0.15047 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_356_0_load_125 | 94 | 0.4153 | 0.20114 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_356_0_load_117 | 96 | 0.80106 | 0.38797 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_356_0_load_138 | 98 | 0.17397 | 0.084257 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_356_0_load_126 | 100 | 0.23213 | 0.11242 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_356_0_load_73 | 101 | 0.18264 | 0.088457 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_356_0_load_71 | 102 | 0.15526 | 0.075195 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_356_0_load_129 | 104 | 0.10462 | 0.050669 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_356_0_load_86 | 105 | 0.077175 | 0.037378 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_356_0_load_77 | 107 | 0.16642 | 0.080601 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_356_0_load_128 | 111 | 0.41466 | 0.20083 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_356_0_load_102 | 113 | 0.20956 | 0.10149 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_356_0_load_88 | 114 | 0.30882 | 0.14957 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_356_0_load_100 | 116 | 0.27096 | 0.13123 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_356_0_load_137 | 118 | 0.22822 | 0.11053 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_356_0_load_110 | 120 | 0.31983 | 0.1549 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_356_0_load_103 | 121 | 0.077742 | 0.037652 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_356_0_load_109 | 126 | 0.24861 | 0.12041 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_356_0_load_108 | 127 | 0.12585 | 0.060953 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_356_0_load_114 | 128 | 0.10449 | 0.050609 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_356_0_load_115 | 129 | 0.11871 | 0.057496 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 112 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_356_0_line_0 |  | 0 | 1 | 0.08008 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_356_0_line_1 |  | 1 | 2 | 0.52253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_356_0_line_2 |  | 2 | 3 | 0.045505 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_356_0_line_3 |  | 2 | 4 | 0.2298 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
4 | MV_356_0_line_4 |  | 2 | 5 | 0.62893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_356_0_line_5 |  | 2 | 6 | 0.77601 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
6 | MV_356_0_line_6 |  | 2 | 7 | 0.079526 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_356_0_line_7 |  | 4 | 8 | 0.068548 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
8 | MV_356_0_line_8 |  | 5 | 9 | 0.062239 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_356_0_line_9 |  | 6 | 10 | 0.30796 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
10 | MV_356_0_line_10 |  | 6 | 11 | 0.018514 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_356_0_line_11 |  | 8 | 12 | 0.062068 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
12 | MV_356_0_line_12 |  | 9 | 13 | 1.1445 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_356_0_line_13 |  | 10 | 14 | 0.004885 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_356_0_line_14 |  | 10 | 15 | 0.32739 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
15 | MV_356_0_line_15 |  | 12 | 22 | 0.25124 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
16 | MV_356_0_line_16 |  | 12 | 31 | 0.42858 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_356_0_line_17 |  | 15 | 16 | 0.048181 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_356_0_line_18 |  | 15 | 17 | 0.024206 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
19 | MV_356_0_line_19 |  | 16 | 45 | 0.019 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_356_0_line_20 |  | 17 | 42 | 0.015476 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
21 | MV_356_0_line_21 |  | 18 | 19 | 0.031253 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
22 | MV_356_0_line_22 |  | 18 | 20 | 0.40507 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
23 | MV_356_0_line_23 |  | 19 | 21 | 1.1867 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
24 | MV_356_0_line_24 |  | 20 | 22 | 0.055671 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
25 | MV_356_0_line_25 |  | 21 | 25 | 0.047589 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
26 | MV_356_0_line_26 |  | 22 | 23 | 0.41453 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_356_0_line_27 |  | 23 | 24 | 0.049623 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_356_0_line_28 |  | 25 | 26 | 1.1289 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
29 | MV_356_0_line_29 |  | 26 | 28 | 1.0175 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
30 | MV_356_0_line_30 |  | 26 | 27 | 0.045854 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_356_0_line_31 |  | 28 | 29 | 0.012523 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_356_0_line_32 |  | 28 | 30 | 0.45581 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
33 | MV_356_0_line_33 |  | 30 | 40 | 0.7498 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
34 | MV_356_0_line_34 |  | 30 | 38 | 0.033663 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_356_0_line_35 |  | 31 | 32 | 0.15591 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_356_0_line_36 |  | 33 | 34 | 0.10466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_356_0_line_37 |  | 34 | 35 | 0.068451 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_356_0_line_38 |  | 35 | 36 | 0.13647 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_356_0_line_39 |  | 35 | 37 | 0.12413 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_356_0_line_40 |  | 36 | 41 | 0.086852 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_356_0_line_41 |  | 38 | 39 | 0.029645 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_356_0_line_42 |  | 40 | 41 | 0.006219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_356_0_line_43 |  | 42 | 43 | 0.14184 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
44 | MV_356_0_line_44 |  | 43 | 44 | 0.021674 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
45 | MV_356_0_line_45 |  | 44 | 46 | 0.026608 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
46 | MV_356_0_line_46 |  | 46 | 118 | 1.9029 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
47 | MV_356_0_line_47 |  | 46 | 120 | 0.040853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_356_0_line_48 |  | 47 | 48 | 0.49215 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_356_0_line_49 |  | 48 | 95 | 0.037311 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_356_0_line_50 |  | 49 | 50 | 0.11494 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_356_0_line_51 |  | 50 | 57 | 0.4552 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_356_0_line_52 |  | 50 | 52 | 1.0003 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_356_0_line_53 |  | 51 | 52 | 0.048681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_356_0_line_54 |  | 52 | 53 | 0.67576 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_356_0_line_55 |  | 53 | 56 | 0.005469 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_356_0_line_56 |  | 54 | 55 | 0.34648 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_356_0_line_57 |  | 54 | 56 | 0.82917 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_356_0_line_58 |  | 55 | 109 | 0.006027 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_356_0_line_59 |  | 57 | 58 | 0.11203 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_356_0_line_60 |  | 59 | 60 | 0.031731 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_356_0_line_61 |  | 60 | 61 | 0.52783 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_356_0_line_62 |  | 61 | 70 | 0.2178 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_356_0_line_63 |  | 61 | 71 | 1.4883 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_356_0_line_64 |  | 61 | 72 | 0.041023 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_356_0_line_65 |  | 61 | 63 | 0.37616 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_356_0_line_66 |  | 62 | 63 | 0.28052 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_356_0_line_67 |  | 62 | 64 | 0.96701 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_356_0_line_68 |  | 62 | 65 | 0.81432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_356_0_line_69 |  | 62 | 66 | 0.097623 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
70 | MV_356_0_line_70 |  | 62 | 67 | 0.37012 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_356_0_line_71 |  | 63 | 68 | 0.005706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_356_0_line_72 |  | 63 | 69 | 0.039217 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_356_0_line_73 |  | 64 | 81 | 0.059548 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_356_0_line_74 |  | 65 | 73 | 0.49289 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_356_0_line_75 |  | 65 | 74 | 0.092239 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_356_0_line_76 |  | 67 | 88 | 0.021163 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_356_0_line_77 |  | 69 | 89 | 0.05099 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_356_0_line_78 |  | 70 | 75 | 0.011138 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_356_0_line_79 |  | 71 | 90 | 1.1932 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_356_0_line_80 |  | 71 | 91 | 0.025124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_356_0_line_81 |  | 73 | 80 | 0.049541 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_356_0_line_82 |  | 76 | 77 | 0.027325 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_356_0_line_83 |  | 76 | 78 | 0.11151 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
84 | MV_356_0_line_84 |  | 77 | 79 | 0.27052 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_356_0_line_85 |  | 78 | 117 | 0.96255 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
86 | MV_356_0_line_86 |  | 78 | 112 | 1.4142 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
87 | MV_356_0_line_87 |  | 78 | 115 | 0.2422 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_356_0_line_88 |  | 79 | 113 | 0.064087 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
89 | MV_356_0_line_89 |  | 82 | 83 | 0.017583 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_356_0_line_90 |  | 82 | 84 | 0.051863 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_356_0_line_91 |  | 83 | 85 | 0.376 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_356_0_line_92 |  | 84 | 86 | 0.31581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_356_0_line_93 |  | 85 | 100 | 0.040043 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
94 | MV_356_0_line_94 |  | 85 | 101 | 0.31319 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
95 | MV_356_0_line_95 |  | 86 | 87 | 0.29469 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_356_0_line_96 |  | 86 | 88 | 0.00527 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_356_0_line_97 |  | 87 | 102 | 0.078451 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_356_0_line_98 |  | 87 | 92 | 0.41041 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_356_0_line_99 |  | 90 | 104 | 0.12238 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_356_0_line_100 |  | 93 | 94 | 0.048971 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
101 | MV_356_0_line_101 |  | 93 | 95 | 0.41119 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_356_0_line_102 |  | 94 | 99 | 0.056073 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_356_0_line_103 |  | 95 | 119 | 0.14497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_356_0_line_104 |  | 96 | 97 | 0.029002 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_356_0_line_105 |  | 96 | 98 | 0.22884 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
106 | MV_356_0_line_106 |  | 97 | 99 | 0.043607 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_356_0_line_107 |  | 101 | 103 | 0.014063 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
108 | MV_356_0_line_108 |  | 103 | 106 | 1.3774 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
109 | MV_356_0_line_109 |  | 104 | 105 | 1.7196 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
110 | MV_356_0_line_110 |  | 106 | 107 | 0.083479 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
111 | MV_356_0_line_111 |  | 107 | 108 | 0.061045 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
112 | MV_356_0_line_112 |  | 108 | 109 | 0.58004 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
113 | MV_356_0_line_113 |  | 109 | 110 | 0.6041 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
114 | MV_356_0_line_114 |  | 110 | 111 | 0.002992 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
115 | MV_356_0_line_115 |  | 111 | 112 | 1.4411 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
116 | MV_356_0_line_116 |  | 112 | 114 | 0.036177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_356_0_line_117 |  | 115 | 116 | 0.040628 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_356_0_line_118 |  | 116 | 119 | 0.077387 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
119 | MV_356_0_line_119 |  | 117 | 118 | 0.002702 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
120 | MV_356_0_line_120 |  | 120 | 124 | 0.03196 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_356_0_line_121 |  | 121 | 122 | 0.005589 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_356_0_line_122 |  | 121 | 123 | 0.022007 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_356_0_line_123 |  | 122 | 124 | 0.015387 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_356_0_line_124 |  | 123 | 125 | 0.014822 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_356_0_line_125 |  | 124 | 126 | 0.079921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_356_0_line_126 |  | 125 | 127 | 0.026381 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_356_0_line_127 |  | 127 | 128 | 0.00079951 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_356_0_line_128 |  | 128 | 129 | 0.028214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_356_0_trafo_89 | 25 MVA 110/20 kV | 130 | 112 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2700016.1465 | 1240339.1108
1 | 2700089.6969 | 1240307.4373
2 | 2699779.8313 | 1240250.5229
3 | 2699748.3887 | 1240283.4182
4 | 2699883.3974 | 1240121.5663
5 | 2700024.1203 | 1240679.8933
6 | 2699618.1801 | 1240465.2937
7 | 2699716.5176 | 1240202.4004
8 | 2699935.5664 | 1240076.9325
9 | 2699972.9282 | 1240715.2914
10 | 2699437.2921 | 1240264.9982
11 | 2699619.337 | 1240483.7716
12 | 2699983.4319 | 1240037.2638
13 | 2699614.0536 | 1241802.1089
14 | 2699441.1673 | 1240267.9876
15 | 2699214.4548 | 1240233.2128
16 | 2699255.2758 | 1240207.619
17 | 2699192.9606 | 1240244.4622
18 | 2700547.599 | 1239881.5836
19 | 2700571.0271 | 1239860.8979
20 | 2700142.5952 | 1239888.9001
21 | 2701230.8045 | 1238874.5368
22 | 2700121.0796 | 1239940.2318
23 | 2700487.6965 | 1240133.6835
24 | 2700527.2352 | 1240103.5521
25 | 2701229.9601 | 1238828.6875
26 | 2700675.5 | 1238808.2799
27 | 2700721.079 | 1238813.2899
28 | 2700293.1373 | 1237865.364
29 | 2700304.2149 | 1237859.5244
30 | 2699994.1891 | 1237695.4399
31 | 2699977.0814 | 1239767.7634
32 | 2699852.4606 | 1239861.4596
33 | 2699641.858 | 1237714.6445
34 | 2699720.2509 | 1237646.4866
35 | 2699677.5286 | 1237592.907
36 | 2699795.4224 | 1237529.2609
37 | 2699667.6432 | 1237469.1703
38 | 2699972.2725 | 1237669.8884
39 | 2699999.194 | 1237657.4759
40 | 2699838.9093 | 1237447.8304
41 | 2699833.7504 | 1237451.3241
42 | 2699184.5329 | 1240231.4671
43 | 2699092.0751 | 1240182.2749
44 | 2699080.5286 | 1240163.9329
45 | 2699271.3738 | 1240197.526
46 | 2699066.3533 | 1240141.4147
47 | 2697469.9653 | 1241216.8265
48 | 2697065.5141 | 1240936.4103
49 | 2697486.7021 | 1237360.1174
50 | 2697455.5341 | 1237249.479
51 | 2696922.139 | 1236966.0858
52 | 2696875.1316 | 1236952.9982
53 | 2696779.6856 | 1237235.9639
54 | 2696352.4864 | 1237949.0048
55 | 2696216.478 | 1238267.6705
56 | 2696774.2662 | 1237235.1194
57 | 2697507.4873 | 1236797.2502
58 | 2697537.2786 | 1236717.1399
59 | 2694889.5507 | 1239749.8458
60 | 2694913.097 | 1239771.1158
61 | 2694804.1298 | 1239854.1479
62 | 2694645.1732 | 1239599.8562
63 | 2694562.682 | 1239777.7076
64 | 2694278.443 | 1239752.936
65 | 2694550.7201 | 1239917.9548
66 | 2694672.7706 | 1239506.2154
67 | 2694707.371 | 1239234.9988
68 | 2694557.4781 | 1239775.334
69 | 2694581.2125 | 1239743.1214
70 | 2694788.95 | 1240004.1951
71 | 2694020.2238 | 1240204.8442
72 | 2694834.5084 | 1239852.9625
73 | 2694386.9735 | 1240002.7126
74 | 2694565.1823 | 1240000.0129
75 | 2694779.616 | 1239998.0749
76 | 2696805.0275 | 1240585.5484
77 | 2696777.6315 | 1240584.8234
78 | 2696916.5413 | 1240586.0348
79 | 2696675.2214 | 1240364.4671
80 | 2694352.6631 | 1240038.5384
81 | 2694299.6001 | 1239698.1312
82 | 2694923.8642 | 1239247.9207
83 | 2694934.2346 | 1239262.1415
84 | 2694881.456 | 1239219.1771
85 | 2695081.1163 | 1239079.2777
86 | 2694682.7239 | 1239226.1214
87 | 2694641.2518 | 1239053.2208
88 | 2694687.8309 | 1239227.4817
89 | 2694552.1869 | 1239714.8381
90 | 2693555.254 | 1240843.5743
91 | 2694000.6042 | 1240189.133
92 | 2694285.0657 | 1239257.1063
93 | 2696817.043 | 1241193.1352
94 | 2696781.8159 | 1241227.1531
95 | 2697033.0803 | 1240917.8327
96 | 2696724.3191 | 1241124.3607
97 | 2696734.5924 | 1241151.4819
98 | 2696682.6664 | 1240899.3461
99 | 2696748.1069 | 1241188.0519
100 | 2695119.4822 | 1239090.745
101 | 2695134.8247 | 1238770.7307
102 | 2694713.4199 | 1239083.9831
103 | 2695142.9224 | 1238759.2185
104 | 2693454.6295 | 1240913.1412
105 | 2694065.395 | 1242520.667
106 | 2695977.6864 | 1238593.3048
107 | 2696010.4201 | 1238516.7102
108 | 2696043.3336 | 1238466.9275
109 | 2696210.4336 | 1238267.6281
110 | 2696341.9549 | 1238572.0981
111 | 2696344.8643 | 1238571.367
112 | 2696942.9966 | 1239882.449
113 | 2696671.4537 | 1240300.4911
114 | 2696956.3328 | 1239914.7688
115 | 2696980.1985 | 1240732.6513
116 | 2697020.4233 | 1240738.7242
117 | 2697217.8457 | 1240600.3385
118 | 2697220.051 | 1240601.9091
119 | 2697024.9528 | 1240815.9787
120 | 2699100.706 | 1240119.3041
121 | 2699139.1495 | 1240119.5194
122 | 2699136.0331 | 1240114.8799
123 | 2699151.4203 | 1240137.7875
124 | 2699127.5804 | 1240102.0068
125 | 2699159.4102 | 1240150.286
126 | 2699084.6879 | 1240034.4953
127 | 2699181.4788 | 1240135.8307
128 | 2699182.1476 | 1240135.3926
129 | 2699205.7488 | 1240119.9333
130 | 2696942.9966 | 1239882.449

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99071 | -0.2996 | 0.359 | 0.17387
1 | 0.99077 | -0.29925 | 0 | 0
2 | 0.99101 | -0.30132 | 0 | 0
3 | 0.991 | -0.30124 | 0.15829 | 0.076663
4 | 0.99088 | -0.3023 | 0 | 0
5 | 0.99064 | -0.29816 | 0 | 0
6 | 0.99161 | -0.29689 | 0 | 0
7 | 0.99096 | -0.30164 | 0.32593 | 0.15786
8 | 0.99084 | -0.30259 | 0.20948 | 0.10145
9 | 0.99058 | -0.29852 | 0.16793 | 0.081333
10 | 0.99186 | -0.29492 | 0 | 0
11 | 0.9916 | -0.29695 | 0.29122 | 0.14104
12 | 0.99081 | -0.30283 | 0 | 0
13 | 0.98993 | -0.30269 | 0.29125 | 0.14106
14 | 0.99186 | -0.29491 | 0.24492 | 0.11862
15 | 0.99214 | -0.29269 | 0 | 0
16 | 0.99212 | -0.29253 | 0.138 | 0.066838
17 | 0.99216 | -0.29251 | 0.34551 | 0.16734
18 | 0.99037 | -0.32262 | 0.26781 | 0.12971
19 | 0.99035 | -0.3239 | 0 | 0
20 | 0.99067 | -0.30389 | 0.28099 | 0.13609
21 | 0.98961 | -0.37272 | 0.17112 | 0.082876
22 | 0.99069 | -0.30371 | 0 | 0
23 | 0.9904 | -0.30558 | 0 | 0
24 | 0.99038 | -0.30537 | 0.35711 | 0.17295
25 | 0.9896 | -0.37284 | 0 | 0
26 | 0.98926 | -0.37523 | 0 | 0
27 | 0.98924 | -0.37531 | 0.14713 | 0.07126
28 | 0.98867 | -0.40963 | 0 | 0
29 | 0.98867 | -0.40968 | 0.3407 | 0.16501
30 | 0.98847 | -0.41071 | 0 | 0
31 | 0.99061 | -0.30108 | 0 | 0
32 | 0.9905 | -0.30178 | 0.36187 | 0.17526
33 | 0.98765 | -0.41443 | 0.40419 | 0.19576
34 | 0.98771 | -0.41494 | 0.21682 | 0.10501
35 | 0.98776 | -0.41545 | 0 | 0
36 | 0.98788 | -0.41656 | 0 | 0
37 | 0.98774 | -0.41557 | 0.077491 | 0.037531
38 | 0.98845 | -0.41083 | 0.18986 | 0.091952
39 | 0.98844 | -0.4108 | 0.088346 | 0.042788
40 | 0.98801 | -0.41584 | 0 | 0
41 | 0.988 | -0.41576 | 0.41288 | 0.19997
42 | 0.99217 | -0.2924 | 0 | 0
43 | 0.99231 | -0.29134 | 0 | 0
44 | 0.99233 | -0.29118 | 0.14767 | 0.071521
45 | 0.99212 | -0.29251 | 0.12463 | 0.060359
46 | 0.99235 | -0.29098 | 0 | 0
47 | 0.99622 | -0.0082969 | 0.10484 | 0.050778
48 | 0.99632 | -0.0076564 | 0.39554 | 0.19157
49 | 0.98906 | -0.37353 | 0.16741 | 0.081081
50 | 0.98908 | -0.37375 | 0 | 0
51 | 0.9897 | -0.3785 | 0.40047 | 0.19396
52 | 0.98972 | -0.37873 | 0 | 0
53 | 0.99049 | -0.38449 | 0 | 0
54 | 0.99213 | -0.37066 | 0.2209 | 0.10699
55 | 0.99296 | -0.36392 | 0.30276 | 0.14663
56 | 0.9905 | -0.38453 | 0.12752 | 0.061761
57 | 0.98879 | -0.37574 | 0.26464 | 0.12817
58 | 0.98878 | -0.37566 | 0.068645 | 0.033246
59 | 0.98223 | -0.41538 | 0.31593 | 0.15301
60 | 0.98225 | -0.41525 | 0 | 0
61 | 0.98247 | -0.41711 | 0 | 0
62 | 0.98366 | -0.42467 | 0 | 0
63 | 0.98311 | -0.4211 | 0 | 0
64 | 0.98333 | -0.42222 | 0 | 0
65 | 0.98294 | -0.41896 | 0 | 0
66 | 0.98361 | -0.42502 | 0.28983 | 0.14037
67 | 0.98566 | -0.40644 | 0 | 0
68 | 0.98311 | -0.42109 | 0.10465 | 0.050686
69 | 0.9831 | -0.42104 | 0 | 0
70 | 0.98235 | -0.41606 | 0 | 0
71 | 0.98149 | -0.41241 | 0 | 0
72 | 0.98246 | -0.41706 | 0.093984 | 0.045518
73 | 0.98276 | -0.41745 | 0 | 0
74 | 0.98289 | -0.4185 | 0.41015 | 0.19864
75 | 0.98235 | -0.416 | 0.40439 | 0.19586
76 | 0.99766 | -0.016767 | 0.23606 | 0.11433
77 | 0.99765 | -0.016711 | 0 | 0
78 | 0.99776 | -0.016095 | 0 | 0
79 | 0.99758 | -0.016086 | 0 | 0
80 | 0.98274 | -0.41728 | 0.28413 | 0.13761
81 | 0.98331 | -0.42202 | 0.27144 | 0.13146
82 | 0.98736 | -0.4184 | 0.34997 | 0.1695
83 | 0.98744 | -0.41901 | 0 | 0
84 | 0.98713 | -0.41682 | 0 | 0
85 | 0.98925 | -0.43193 | 0 | 0
86 | 0.98575 | -0.40709 | 0 | 0
87 | 0.98558 | -0.40548 | 0 | 0
88 | 0.98573 | -0.40695 | 0.13331 | 0.064565
89 | 0.98309 | -0.42097 | 0.11959 | 0.057922
90 | 0.98121 | -0.41117 | 0 | 0
91 | 0.98148 | -0.4123 | 0.33872 | 0.16405
92 | 0.98533 | -0.40707 | 0.31068 | 0.15047
93 | 0.99561 | -0.0012001 | 0 | 0
94 | 0.99548 | -0.0020445 | 0.4153 | 0.20114
95 | 0.99634 | -0.0078789 | 0 | 0
96 | 0.99532 | -0.00054428 | 0.80106 | 0.38797
97 | 0.99536 | -0.00088463 | 0 | 0
98 | 0.99525 | -0.0010326 | 0.17397 | 0.084257
99 | 0.99541 | -0.0013939 | 0 | 0
100 | 0.98923 | -0.43204 | 0.23213 | 0.11242
101 | 0.99007 | -0.3826 | 0.18264 | 0.088457
102 | 0.98555 | -0.40563 | 0.15526 | 0.075195
103 | 0.99009 | -0.38249 | 0 | 0
104 | 0.98118 | -0.41092 | 0.10462 | 0.050669
105 | 0.98092 | -0.41274 | 0.077175 | 0.037378
106 | 0.99196 | -0.37092 | 0 | 0
107 | 0.99208 | -0.37016 | 0.16642 | 0.080601
108 | 0.99216 | -0.36959 | 0 | 0
109 | 0.99298 | -0.36401 | 0 | 0
110 | 0.99413 | -0.35635 | 0 | 0
111 | 0.99413 | -0.35631 | 0.41466 | 0.20083
112 | 1 | 0 | -16.716 | -6.9034
113 | 0.99756 | -0.016249 | 0.20956 | 0.10149
114 | 0.99999 | 0.00013267 | 0.30882 | 0.14957
115 | 0.99709 | -0.010136 | 0 | 0
116 | 0.99698 | -0.0091269 | 0.27096 | 0.13123
117 | 0.99663 | -0.024323 | 0 | 0
118 | 0.99663 | -0.024344 | 0.22822 | 0.11053
119 | 0.99669 | -0.01103 | 0 | 0
120 | 0.9923 | -0.2905 | 0.31983 | 0.1549
121 | 0.99226 | -0.29014 | 0.077742 | 0.037652
122 | 0.99227 | -0.29017 | 0 | 0
123 | 0.99225 | -0.29005 | 0 | 0
124 | 0.99227 | -0.29025 | 0 | 0
125 | 0.99225 | -0.28999 | 0 | 0
126 | 0.99225 | -0.29001 | 0.24861 | 0.12041
127 | 0.99223 | -0.28988 | 0.12585 | 0.060953
128 | 0.99223 | -0.28988 | 0.10449 | 0.050609
129 | 0.99223 | -0.28984 | 0.11871 | 0.057496
130 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.359 | -0.17387 | 0.35902 | 0.17379 | 1.9273e-05 | -8.1766e-05 | 0.011623 | 0.011622 | 0.011623 | 0.99071 | -0.2996 | 0.99077 | -0.29925 | 5.5347
1 | -0.35902 | -0.17379 | 0.35911 | 0.16157 | 9.2978e-05 | -0.012222 | 0.011622 | 0.011471 | 0.011622 | 0.99077 | -0.29925 | 0.99101 | -0.30132 | 5.2826
2 | 0.15829 | 0.075597 | -0.15829 | -0.076663 | 1.5903e-06 | -0.0010666 | 0.0051098 | 0.0051233 | 0.0051233 | 0.99101 | -0.30132 | 0.991 | -0.30124 | 2.3288
3 | 3.5306 | 1.4066 | -3.5301 | -1.4347 | 0.00043634 | -0.028112 | 0.1107 | 0.11101 | 0.11101 | 0.99101 | -0.30132 | 0.99088 | -0.3023 | 8.7001
4 | 0.45957 | 0.20642 | -0.45938 | -0.22111 | 0.00018303 | -0.014688 | 0.014675 | 0.014856 | 0.014856 | 0.99101 | -0.30132 | 0.99064 | -0.29816 | 6.7529
5 | -4.8335 | -2.008 | 4.8362 | 1.9137 | 0.0027676 | -0.094269 | 0.15246 | 0.15141 | 0.15246 | 0.99101 | -0.30132 | 0.99161 | -0.29689 | 11.9485
6 | 0.32595 | 0.15777 | -0.32593 | -0.15786 | 1.5768e-05 | -8.3357e-05 | 0.010549 | 0.01055 | 0.01055 | 0.99101 | -0.30132 | 0.99096 | -0.30164 | 5.0237
7 | 3.5301 | 1.4347 | -3.53 | -1.4431 | 0.00013063 | -0.0083837 | 0.11101 | 0.11111 | 0.11111 | 0.99088 | -0.3023 | 0.99084 | -0.30259 | 8.7074
8 | 0.45938 | 0.22111 | -0.45936 | -0.22116 | 2.4477e-05 | -5.7581e-05 | 0.014856 | 0.014857 | 0.014857 | 0.99064 | -0.29816 | 0.99058 | -0.29852 | 7.0749
9 | -5.1275 | -2.0547 | 5.1287 | 2.0174 | 0.0012273 | -0.037371 | 0.16081 | 0.1604 | 0.16081 | 0.99161 | -0.29689 | 0.99186 | -0.29492 | 12.6026
10 | 0.29122 | 0.14102 | -0.29122 | -0.14104 | 2.927e-06 | -1.9899e-05 | 0.0094197 | 0.0094199 | 0.0094199 | 0.99161 | -0.29689 | 0.9916 | -0.29695 | 4.4857
11 | 3.3205 | 1.3417 | -3.3204 | -1.3493 | 0.00010448 | -0.0075984 | 0.10434 | 0.10442 | 0.10442 | 0.99084 | -0.30259 | 0.99081 | -0.30283 | 8.1836
12 | 0.29143 | 0.13983 | -0.29125 | -0.14106 | 0.00018127 | -0.0012263 | 0.0094197 | 0.0094367 | 0.0094367 | 0.99058 | -0.29852 | 0.98993 | -0.30269 | 4.4937
13 | 0.24492 | 0.1185 | -0.24492 | -0.11862 | 4.0901e-07 | -0.00011462 | 0.0079188 | 0.0079203 | 0.0079203 | 0.99186 | -0.29492 | 0.99186 | -0.29491 | 3.6001
14 | -5.3736 | -2.1359 | 5.375 | 2.0962 | 0.001429 | -0.03968 | 0.1683 | 0.16787 | 0.1683 | 0.99186 | -0.29492 | 0.99214 | -0.29269 | 13.1894
15 | 2.9584 | 1.1842 | -2.9581 | -1.215 | 0.0003358 | -0.030801 | 0.092843 | 0.093182 | 0.093182 | 0.99081 | -0.30283 | 0.99069 | -0.30371 | 7.3027
16 | 0.36199 | 0.16508 | -0.36191 | -0.1751 | 7.7697e-05 | -0.010021 | 0.011592 | 0.011716 | 0.011716 | 0.99081 | -0.30283 | 0.99061 | -0.30108 | 5.3255
17 | 0.26263 | 0.12562 | -0.26263 | -0.12675 | 4.6232e-06 | -0.001131 | 0.0084709 | 0.0084851 | 0.0084851 | 0.99214 | -0.29269 | 0.99212 | -0.29253 | 3.8569
18 | -5.6377 | -2.2218 | 5.6378 | 2.2189 | 0.00011624 | -0.0029288 | 0.17631 | 0.17628 | 0.17631 | 0.99214 | -0.29269 | 0.99216 | -0.29251 | 13.8177
19 | 0.12463 | 0.059913 | -0.12463 | -0.060359 | 4.112e-07 | -0.00044641 | 0.0040235 | 0.0040291 | 0.0040291 | 0.99212 | -0.29253 | 0.99212 | -0.29251 | 1.8314
20 | -5.9833 | -2.3862 | 5.9834 | 2.3843 | 8.3981e-05 | -0.0018671 | 0.18742 | 0.1874 | 0.18742 | 0.99216 | -0.29251 | 0.99217 | -0.2924 | 14.6882
21 | 2.0516 | 0.78471 | -2.0516 | -0.78474 | 2.2869e-05 | -2.3249e-05 | 0.064026 | 0.064027 | 0.064027 | 0.99037 | -0.32262 | 0.99035 | -0.3239 | 4.9633
22 | -2.3194 | -0.91442 | 2.3198 | 0.91435 | 0.00038179 | -7.2061e-05 | 0.072671 | 0.07266 | 0.072671 | 0.99037 | -0.32262 | 0.99067 | -0.30389 | 5.6334
23 | 2.0516 | 0.78474 | -2.0507 | -0.78562 | 0.00086881 | -0.00087902 | 0.064027 | 0.06406 | 0.06406 | 0.99035 | -0.3239 | 0.98961 | -0.37272 | 4.9659
24 | -2.6008 | -1.0504 | 2.6009 | 1.0436 | 5.7407e-05 | -0.0068337 | 0.081734 | 0.08166 | 0.081734 | 0.99067 | -0.30389 | 0.99069 | -0.30371 | 6.4055
25 | 1.8796 | 0.70274 | -1.8796 | -0.70858 | 2.5219e-05 | -0.0058423 | 0.058536 | 0.058596 | 0.058596 | 0.98961 | -0.37272 | 0.9896 | -0.37284 | 4.5922
26 | 0.35721 | 0.17137 | -0.35711 | -0.17179 | 9.8486e-05 | -0.00042386 | 0.011545 | 0.011551 | 0.011551 | 0.99069 | -0.30371 | 0.9904 | -0.30558 | 5.5003
27 | 0.35711 | 0.17179 | -0.35711 | -0.17295 | 8.8498e-06 | -0.0011595 | 0.011551 | 0.011565 | 0.011565 | 0.9904 | -0.30558 | 0.99038 | -0.30537 | 5.257
28 | 1.8796 | 0.70858 | -1.879 | -0.84711 | 0.00061417 | -0.13853 | 0.058596 | 0.060145 | 0.060145 | 0.9896 | -0.37284 | 0.98926 | -0.37523 | 4.7136
29 | 1.7318 | 0.77591 | -1.7313 | -0.77716 | 0.0005573 | -0.0012526 | 0.055377 | 0.05541 | 0.05541 | 0.98926 | -0.37523 | 0.98867 | -0.40963 | 4.2953
30 | 0.14714 | 0.071208 | -0.14713 | -0.07126 | 1.8591e-06 | -5.2405e-05 | 0.0047699 | 0.0047706 | 0.0047706 | 0.98926 | -0.37523 | 0.98924 | -0.37531 | 2.2717
31 | 0.3407 | 0.165 | -0.3407 | -0.16501 | 2.7259e-06 | -1.2905e-05 | 0.011053 | 0.011053 | 0.011053 | 0.98867 | -0.40963 | 0.98867 | -0.40968 | 5.2635
32 | 1.3906 | 0.61216 | -1.3903 | -0.63999 | 0.00027927 | -0.027831 | 0.044363 | 0.044698 | 0.044698 | 0.98867 | -0.40963 | 0.98847 | -0.41071 | 7.006
33 | 1.1121 | 0.50598 | -1.1116 | -0.53076 | 0.00046506 | -0.024783 | 0.035682 | 0.035992 | 0.035992 | 0.98847 | -0.41071 | 0.98801 | -0.41584 | 9.9424
34 | 0.27821 | 0.13401 | -0.2782 | -0.13405 | 4.8783e-06 | -3.6209e-05 | 0.0090184 | 0.0090189 | 0.0090189 | 0.98847 | -0.41071 | 0.98845 | -0.41083 | 4.2947
35 | 0.36191 | 0.1751 | -0.36187 | -0.17526 | 3.814e-05 | -0.00015874 | 0.011716 | 0.011718 | 0.011718 | 0.99061 | -0.30108 | 0.9905 | -0.30178 | 5.5802
36 | -0.40419 | -0.19576 | 0.40421 | 0.19333 | 2.4018e-05 | -0.0024306 | 0.013126 | 0.013096 | 0.013126 | 0.98765 | -0.41443 | 0.98771 | -0.41494 | 5.9666
37 | -0.62103 | -0.29834 | 0.62107 | 0.29675 | 3.7017e-05 | -0.0015835 | 0.020137 | 0.020116 | 0.020137 | 0.98771 | -0.41494 | 0.98776 | -0.41545 | 9.153
38 | -0.69856 | -0.33414 | 0.69866 | 0.33099 | 9.3146e-05 | -0.003152 | 0.022631 | 0.022591 | 0.022631 | 0.98776 | -0.41545 | 0.98788 | -0.41656 | 10.2868
39 | 0.077493 | 0.037387 | -0.077491 | -0.037531 | 1.3994e-06 | -0.0001437 | 0.0025145 | 0.0025164 | 0.0025164 | 0.98776 | -0.41545 | 0.98774 | -0.41557 | 1.1983
40 | -0.69866 | -0.33099 | 0.69873 | 0.33094 | 7.8969e-05 | -5.1735e-05 | 0.022591 | 0.02259 | 0.022591 | 0.98788 | -0.41656 | 0.988 | -0.41576 | 10.7576
41 | 0.088346 | 0.042096 | -0.088346 | -0.042788 | 3.2427e-07 | -0.00069145 | 0.0028581 | 0.0028668 | 0.0028668 | 0.98845 | -0.41083 | 0.98844 | -0.4108 | 1.3031
42 | 1.1116 | 0.53076 | -1.1116 | -0.53091 | 1.0755e-05 | -0.00014176 | 0.035992 | 0.035993 | 0.035993 | 0.98801 | -0.41584 | 0.988 | -0.41576 | 16.3607
43 | -5.9834 | -2.3843 | 5.9841 | 2.3672 | 0.00076885 | -0.017116 | 0.1874 | 0.18721 | 0.1874 | 0.99217 | -0.2924 | 0.99231 | -0.29134 | 14.6866
44 | -5.9841 | -2.3672 | 5.9843 | 2.3646 | 0.00011735 | -0.0026158 | 0.18721 | 0.18718 | 0.18721 | 0.99231 | -0.29134 | 0.99233 | -0.29118 | 14.6719
45 | -6.1319 | -2.4361 | 6.1321 | 2.4329 | 0.00015143 | -0.0032074 | 0.19194 | 0.19191 | 0.19194 | 0.99233 | -0.29118 | 0.99235 | -0.29098 | 15.0427
46 | -7.1274 | -2.9087 | 7.1445 | 2.9493 | 0.017029 | 0.040589 | 0.22394 | 0.22388 | 0.22394 | 0.99235 | -0.29098 | 0.99663 | -0.024344 | 17.3595
47 | 0.99534 | 0.47579 | -0.99528 | -0.47674 | 5.6192e-05 | -0.00094384 | 0.032092 | 0.032105 | 0.032105 | 0.99235 | -0.29098 | 0.9923 | -0.2905 | 14.593
48 | -0.10484 | -0.050778 | 0.10485 | 0.050201 | 9.9698e-06 | -0.00057692 | 0.0033756 | 0.0033683 | 0.0033756 | 0.99622 | -0.0082969 | 0.99632 | -0.0076564 | 1.6074
49 | -0.5004 | -0.24177 | 0.50041 | 0.24089 | 1.2906e-05 | -0.00088049 | 0.016102 | 0.016091 | 0.016102 | 0.99632 | -0.0076564 | 0.99634 | -0.0078789 | 7.3192
50 | -0.16741 | -0.081081 | 0.16742 | 0.078398 | 4.4945e-06 | -0.0026832 | 0.0054291 | 0.0053954 | 0.0054291 | 0.98906 | -0.37353 | 0.98908 | -0.37375 | 2.4678
51 | 0.33338 | 0.15833 | -0.33329 | -0.1588 | 9.4161e-05 | -0.00047248 | 0.010772 | 0.010778 | 0.010778 | 0.98908 | -0.37375 | 0.98879 | -0.37574 | 5.1325
52 | -0.5008 | -0.23673 | 0.50114 | 0.21345 | 0.00034289 | -0.023278 | 0.016167 | 0.015888 | 0.016167 | 0.98908 | -0.37375 | 0.98972 | -0.37873 | 7.3486
53 | -0.40047 | -0.19396 | 0.40048 | 0.19282 | 1.0935e-05 | -0.0011353 | 0.012979 | 0.012964 | 0.012979 | 0.9897 | -0.3785 | 0.98972 | -0.37873 | 5.8995
54 | -0.90162 | -0.40627 | 0.90236 | 0.39068 | 0.00074569 | -0.015596 | 0.028844 | 0.028658 | 0.028844 | 0.98972 | -0.37873 | 0.99049 | -0.38449 | 13.1111
55 | -0.90236 | -0.39068 | 0.90237 | 0.39055 | 5.9959e-06 | -0.00012633 | 0.028658 | 0.028656 | 0.028658 | 0.99049 | -0.38449 | 0.9905 | -0.38453 | 13.0264
56 | -1.2524 | -0.55932 | 1.2534 | 0.55953 | 0.00098308 | 0.00020828 | 0.039909 | 0.039904 | 0.039909 | 0.99213 | -0.37066 | 0.99296 | -0.36392 | 19.0041
57 | 1.0315 | 0.45233 | -1.0299 | -0.45231 | 0.0015871 | 2.1381e-05 | 0.032771 | 0.032783 | 0.032783 | 0.99213 | -0.37066 | 0.9905 | -0.38453 | 15.6108
58 | -1.5561 | -0.70616 | 1.5561 | 0.70602 | 1.9858e-05 | -0.00013599 | 0.04968 | 0.049678 | 0.04968 | 0.99296 | -0.36392 | 0.99298 | -0.36401 | 22.5817
59 | 0.068646 | 0.030632 | -0.068645 | -0.033246 | 7.3073e-07 | -0.0026149 | 0.0021946 | 0.0022268 | 0.0022268 | 0.98879 | -0.37574 | 0.98878 | -0.37566 | 1.0122
60 | -0.31593 | -0.15301 | 0.31594 | 0.15298 | 6.0172e-06 | -3.2778e-05 | 0.010317 | 0.010316 | 0.010317 | 0.98223 | -0.41538 | 0.98225 | -0.41525 | 4.9128
61 | -0.31594 | -0.15298 | 0.31601 | 0.14084 | 7.3885e-05 | -0.01214 | 0.010316 | 0.010166 | 0.010316 | 0.98225 | -0.41525 | 0.98247 | -0.41711 | 4.6893
62 | 0.40445 | 0.1906 | -0.4044 | -0.1956 | 5.0423e-05 | -0.0050039 | 0.013137 | 0.013201 | 0.013201 | 0.98247 | -0.41711 | 0.98235 | -0.41606 | 6.0003
63 | 0.52113 | 0.18522 | -0.52059 | -0.21932 | 0.00053608 | -0.034106 | 0.016251 | 0.016615 | 0.016615 | 0.98247 | -0.41711 | 0.98149 | -0.41241 | 7.5523
64 | 0.093984 | 0.044573 | -0.093984 | -0.045518 | 5.1358e-07 | -0.00094527 | 0.0030563 | 0.0030683 | 0.0030683 | 0.98247 | -0.41711 | 0.98246 | -0.41706 | 1.3947
65 | -1.3356 | -0.56123 | 1.3365 | 0.55282 | 0.00090781 | -0.0084055 | 0.042567 | 0.042469 | 0.042567 | 0.98247 | -0.41711 | 0.98311 | -0.4211 | 19.3485
66 | 1.5617 | 0.65302 | -1.5607 | -0.65922 | 0.00092549 | -0.0062025 | 0.049675 | 0.049749 | 0.049749 | 0.98366 | -0.42467 | 0.98311 | -0.4211 | 22.6132
67 | 0.27154 | 0.10779 | -0.27144 | -0.13009 | 9.7713e-05 | -0.022304 | 0.0085737 | 0.0088366 | 0.0088366 | 0.98366 | -0.42467 | 0.98333 | -0.42222 | 4.0166
68 | 0.69491 | 0.30301 | -0.69437 | -0.32164 | 0.00054351 | -0.018638 | 0.022248 | 0.022474 | 0.022474 | 0.98366 | -0.42467 | 0.98294 | -0.41896 | 10.2155
69 | 0.28984 | 0.14027 | -0.28983 | -0.14037 | 1.5534e-05 | -0.00010303 | 0.0094497 | 0.0094512 | 0.0094512 | 0.98366 | -0.42467 | 0.98361 | -0.42502 | 4.5006
70 | -2.818 | -1.2041 | 2.8233 | 1.207 | 0.005333 | 0.002912 | 0.089931 | 0.089926 | 0.089931 | 0.98366 | -0.42467 | 0.98566 | -0.40644 | 42.8244
71 | 0.10465 | 0.050554 | -0.10465 | -0.050686 | 8.8741e-08 | -0.00013165 | 0.0034128 | 0.0034145 | 0.0034145 | 0.98311 | -0.4211 | 0.98311 | -0.42109 | 1.552
72 | 0.1196 | 0.055841 | -0.1196 | -0.056746 | 7.8872e-07 | -0.00090474 | 0.0038757 | 0.003887 | 0.003887 | 0.98311 | -0.4211 | 0.9831 | -0.42104 | 1.7668
73 | 0.27144 | 0.13009 | -0.27144 | -0.13146 | 6.2198e-06 | -0.0013729 | 0.0088366 | 0.0088541 | 0.0088541 | 0.98333 | -0.42222 | 0.98331 | -0.42202 | 4.0246
74 | 0.28419 | 0.12512 | -0.28414 | -0.13647 | 5.5548e-05 | -0.011352 | 0.0091195 | 0.0092591 | 0.0092591 | 0.98294 | -0.41896 | 0.98276 | -0.41745 | 4.2087
75 | 0.41017 | 0.19652 | -0.41015 | -0.19864 | 2.2015e-05 | -0.0021212 | 0.013357 | 0.013385 | 0.013385 | 0.98294 | -0.41896 | 0.98289 | -0.4185 | 6.0839
76 | -2.8233 | -1.207 | 2.8235 | 1.2066 | 0.00022846 | -0.00042317 | 0.089926 | 0.089921 | 0.089926 | 0.98566 | -0.40644 | 0.98573 | -0.40695 | 40.8756
77 | 0.1196 | 0.056746 | -0.11959 | -0.057922 | 1.0324e-06 | -0.0011763 | 0.003887 | 0.003902 | 0.003902 | 0.9831 | -0.42104 | 0.98309 | -0.42097 | 1.7736
78 | 0.4044 | 0.1956 | -0.40439 | -0.19586 | 2.5917e-06 | -0.00025586 | 0.013201 | 0.013204 | 0.013204 | 0.98235 | -0.41606 | 0.98235 | -0.416 | 6.0018
79 | 0.18187 | 0.05585 | -0.18182 | -0.083271 | 5.225e-05 | -0.027421 | 0.0055957 | 0.0058834 | 0.0058834 | 0.98149 | -0.41241 | 0.98121 | -0.41117 | 2.6743
80 | 0.33872 | 0.16347 | -0.33872 | -0.16405 | 4.1071e-06 | -0.00057663 | 0.011062 | 0.011069 | 0.011069 | 0.98149 | -0.41241 | 0.98148 | -0.4123 | 5.0316
81 | 0.28414 | 0.13647 | -0.28413 | -0.13761 | 5.6789e-06 | -0.0011407 | 0.0092591 | 0.0092736 | 0.0092736 | 0.98276 | -0.41745 | 0.98274 | -0.41728 | 4.2153
82 | 0.20958 | 0.094349 | -0.20958 | -0.094998 | 1.6153e-06 | -0.00064888 | 0.0066505 | 0.0066582 | 0.0066582 | 0.99766 | -0.016767 | 0.99765 | -0.016711 | 3.0265
83 | -0.44564 | -0.20868 | 0.44568 | 0.20857 | 4.0275e-05 | -0.00010729 | 0.014238 | 0.014237 | 0.014238 | 0.99766 | -0.016767 | 0.99776 | -0.016095 | 6.7802
84 | 0.20958 | 0.094998 | -0.20956 | -0.10142 | 1.6198e-05 | -0.0064233 | 0.0066582 | 0.0067371 | 0.0067371 | 0.99765 | -0.016711 | 0.99758 | -0.016086 | 3.0623
85 | 7.3806 | 2.9437 | -7.3727 | -3.0595 | 0.0079045 | -0.11583 | 0.2299 | 0.23121 | 0.23121 | 0.99776 | -0.016095 | 0.99663 | -0.024323 | 18.1198
86 | -9.9925 | -4.176 | 10.0138 | 4.0106 | 0.021319 | -0.16531 | 0.31334 | 0.3114 | 0.31334 | 0.99776 | -0.016095 | 1 | 0 | 24.5562
87 | 2.1662 | 1.0237 | -2.1646 | -1.029 | 0.0015553 | -0.0052918 | 0.069319 | 0.069391 | 0.069391 | 0.99776 | -0.016095 | 0.99709 | -0.010136 | 31.5412
88 | 0.20956 | 0.10142 | -0.20956 | -0.10149 | 5.1834e-06 | -7.2889e-05 | 0.0067371 | 0.0067381 | 0.0067381 | 0.99758 | -0.016086 | 0.99756 | -0.016249 | 3.2086
89 | -3.7788 | -1.6521 | 3.7792 | 1.6517 | 0.00034127 | -0.00030807 | 0.12058 | 0.12057 | 0.12058 | 0.98736 | -0.4184 | 0.98744 | -0.41901 | 54.8086
90 | 3.4289 | 1.4826 | -3.428 | -1.4835 | 0.00082603 | -0.00096187 | 0.10922 | 0.10923 | 0.10923 | 0.98736 | -0.4184 | 0.98713 | -0.41682 | 49.6515
91 | -3.7792 | -1.6517 | 3.7865 | 1.6451 | 0.0072913 | -0.0066066 | 0.12057 | 0.12047 | 0.12057 | 0.98744 | -0.41901 | 0.98925 | -0.43193 | 54.8064
92 | 3.428 | 1.4835 | -3.423 | -1.4894 | 0.0050344 | -0.0058438 | 0.10923 | 0.10932 | 0.10932 | 0.98713 | -0.41682 | 0.98575 | -0.40709 | 49.6904
93 | 0.23213 | 0.11238 | -0.23213 | -0.11242 | 4.0412e-06 | -4.4249e-05 | 0.0075259 | 0.0075265 | 0.0075265 | 0.98925 | -0.43193 | 0.98923 | -0.43204 | 3.5841
94 | -4.0186 | -1.7575 | 4.0204 | 1.762 | 0.0018315 | 0.0045012 | 0.12799 | 0.12799 | 0.12799 | 0.98925 | -0.43193 | 0.99007 | -0.3826 | 19.8437
95 | 0.46611 | 0.21834 | -0.46602 | -0.22515 | 8.989e-05 | -0.0068091 | 0.015073 | 0.015159 | 0.015159 | 0.98575 | -0.40709 | 0.98558 | -0.40548 | 6.8905
96 | 2.9569 | 1.271 | -2.9568 | -1.2711 | 6.25e-05 | -0.00010373 | 0.094252 | 0.094254 | 0.094254 | 0.98575 | -0.40709 | 0.98573 | -0.40695 | 42.8426
97 | 0.15526 | 0.075106 | -0.15526 | -0.075195 | 3.5679e-06 | -8.8736e-05 | 0.0050517 | 0.0050529 | 0.0050529 | 0.98558 | -0.40548 | 0.98555 | -0.40563 | 2.4061
98 | 0.31076 | 0.15004 | -0.31068 | -0.15047 | 7.4747e-05 | -0.00042898 | 0.010107 | 0.010113 | 0.010113 | 0.98558 | -0.40548 | 0.98533 | -0.40707 | 4.8159
99 | 0.18182 | 0.083271 | -0.18181 | -0.086083 | 5.6886e-06 | -0.0028114 | 0.0058834 | 0.0059184 | 0.0059184 | 0.98121 | -0.41117 | 0.98118 | -0.41092 | 2.6902
100 | 1.3907 | 0.67016 | -1.3905 | -0.67011 | 0.00017481 | 5.1553e-05 | 0.04476 | 0.044761 | 0.044761 | 0.99561 | -0.0012001 | 0.99548 | -0.0020445 | 21.3148
101 | -1.3907 | -0.67016 | 1.3918 | 0.66075 | 0.0010968 | -0.0094134 | 0.04476 | 0.044639 | 0.04476 | 0.99561 | -0.0012001 | 0.99634 | -0.0078789 | 20.3456
102 | 0.97521 | 0.46897 | -0.97514 | -0.47028 | 7.3751e-05 | -0.0013048 | 0.03138 | 0.031397 | 0.031397 | 0.99548 | -0.0020445 | 0.99541 | -0.0013939 | 14.2711
103 | -1.8922 | -0.90164 | 1.8929 | 0.89842 | 0.00071329 | -0.0032258 | 0.060729 | 0.060687 | 0.060729 | 0.99634 | -0.0078789 | 0.99669 | -0.01103 | 27.6043
104 | -0.97505 | -0.47197 | 0.97508 | 0.47129 | 3.8207e-05 | -0.00067468 | 0.031418 | 0.03141 | 0.031418 | 0.99532 | -0.00054428 | 0.99536 | -0.00088463 | 14.281
105 | 0.17398 | 0.083994 | -0.17397 | -0.084257 | 1.2809e-05 | -0.00026259 | 0.0056033 | 0.0056067 | 0.0056067 | 0.99532 | -0.00054428 | 0.99525 | -0.0010326 | 2.6699
106 | -0.97508 | -0.47129 | 0.97514 | 0.47028 | 5.7409e-05 | -0.0010146 | 0.03141 | 0.031397 | 0.03141 | 0.99536 | -0.00088463 | 0.99541 | -0.0013939 | 14.2771
107 | -4.2031 | -1.8505 | 4.2031 | 1.8497 | 7.7904e-05 | -0.0008223 | 0.1339 | 0.13389 | 0.1339 | 0.99007 | -0.3826 | 0.99009 | -0.38249 | 20.9874
108 | -4.2031 | -1.8497 | 4.2107 | 1.7689 | 0.0075737 | -0.080735 | 0.13389 | 0.13291 | 0.13389 | 0.99009 | -0.38249 | 0.99196 | -0.37092 | 20.9858
109 | 0.077195 | 0.035414 | -0.077175 | -0.037378 | 1.9318e-05 | -0.0019638 | 0.0024987 | 0.0025235 | 0.0025235 | 0.98118 | -0.41092 | 0.98092 | -0.41274 | 1.2017
110 | -4.2107 | -1.7689 | 4.2112 | 1.764 | 0.00045548 | -0.0049053 | 0.13291 | 0.13285 | 0.13291 | 0.99196 | -0.37092 | 0.99208 | -0.37016 | 20.8325
111 | -4.3776 | -1.8446 | 4.3779 | 1.841 | 0.00036029 | -0.0035725 | 0.13823 | 0.13818 | 0.13823 | 0.99208 | -0.37016 | 0.99216 | -0.36959 | 21.6655
112 | -4.3779 | -1.841 | 4.3814 | 1.8071 | 0.0034124 | -0.033984 | 0.13818 | 0.13778 | 0.13818 | 0.99216 | -0.36959 | 0.99298 | -0.36401 | 21.6588
113 | -5.9375 | -2.5131 | 5.944 | 2.4793 | 0.0065434 | -0.033784 | 0.18744 | 0.18702 | 0.18744 | 0.99298 | -0.36401 | 0.99413 | -0.35635 | 29.379
114 | -5.944 | -2.4793 | 5.9441 | 2.4791 | 3.2335e-05 | -0.00016758 | 0.18702 | 0.18701 | 0.18702 | 0.99413 | -0.35635 | 0.99413 | -0.35631 | 29.3129
115 | -6.3587 | -2.68 | 6.3794 | 2.7335 | 0.020653 | 0.053558 | 0.20037 | 0.20035 | 0.20037 | 0.99413 | -0.35631 | 1 | 0 | 31.0656
116 | 0.30882 | 0.14871 | -0.30882 | -0.14957 | 4.7336e-06 | -0.00086235 | 0.0098947 | 0.0099055 | 0.0099055 | 1 | 0 | 0.99999 | 0.00013267 | 4.5025
117 | 2.1646 | 1.029 | -2.1644 | -1.0299 | 0.00026121 | -0.00088681 | 0.069391 | 0.069403 | 0.069403 | 0.99709 | -0.010136 | 0.99698 | -0.0091269 | 31.5466
118 | 1.8934 | 0.89864 | -1.8929 | -0.89842 | 0.00050779 | 0.00022626 | 0.060685 | 0.060687 | 0.060687 | 0.99698 | -0.0091269 | 0.99669 | -0.01103 | 28.8984
119 | 7.3727 | 3.0595 | -7.3727 | -3.0598 | 2.2316e-05 | -0.00032469 | 0.23121 | 0.23121 | 0.23121 | 0.99663 | -0.024323 | 0.99663 | -0.024344 | 18.1201
120 | 0.67545 | 0.32184 | -0.67543 | -0.32258 | 2.0223e-05 | -0.00074535 | 0.021767 | 0.021776 | 0.021776 | 0.9923 | -0.2905 | 0.99227 | -0.29025 | 9.8981
121 | -0.42681 | -0.20454 | 0.42681 | 0.20441 | 1.4145e-06 | -0.00013097 | 0.013769 | 0.013768 | 0.013769 | 0.99226 | -0.29014 | 0.99227 | -0.29017 | 6.2588
122 | 0.34907 | 0.16689 | -0.34907 | -0.16741 | 3.7246e-06 | -0.00051622 | 0.011256 | 0.011263 | 0.011263 | 0.99226 | -0.29014 | 0.99225 | -0.29005 | 5.1195
123 | -0.42681 | -0.20441 | 0.42682 | 0.20405 | 3.8924e-06 | -0.00036057 | 0.013768 | 0.013763 | 0.013768 | 0.99227 | -0.29017 | 0.99227 | -0.29025 | 6.2581
124 | 0.34907 | 0.16741 | -0.34906 | -0.16776 | 2.5111e-06 | -0.00034768 | 0.011263 | 0.011267 | 0.011267 | 0.99225 | -0.29005 | 0.99225 | -0.28999 | 5.1215
125 | 0.24862 | 0.11853 | -0.24861 | -0.12041 | 6.8704e-06 | -0.0018767 | 0.0080128 | 0.0080364 | 0.0080364 | 0.99227 | -0.29025 | 0.99225 | -0.29001 | 3.6529
126 | 0.34906 | 0.16776 | -0.34906 | -0.16838 | 4.4742e-06 | -0.00061882 | 0.011267 | 0.011275 | 0.011275 | 0.99225 | -0.28999 | 0.99223 | -0.28988 | 5.125
127 | 0.22321 | 0.10742 | -0.22321 | -0.10744 | 5.5536e-08 | -1.8777e-05 | 0.0072068 | 0.007207 | 0.007207 | 0.99223 | -0.28988 | 0.99223 | -0.28988 | 3.2759
128 | 0.11871 | 0.056833 | -0.11871 | -0.057496 | 5.5347e-07 | -0.00066304 | 0.0038292 | 0.0038376 | 0.0038376 | 0.99223 | -0.28988 | 0.99223 | -0.28984 | 1.7443

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 16.716 | 6.9034

## res_load
| p_mw | q_mvar
0 | 0.359 | 0.17387
1 | 0.15829 | 0.076663
2 | 0.32593 | 0.15786
3 | 0.20948 | 0.10145
4 | 0.16793 | 0.081333
5 | 0.29122 | 0.14104
6 | 0.29125 | 0.14106
7 | 0.24492 | 0.11862
8 | 0.138 | 0.066838
9 | 0.34551 | 0.16734
10 | 0.26781 | 0.12971
11 | 0.28099 | 0.13609
12 | 0.17112 | 0.082876
13 | 0.35711 | 0.17295
14 | 0.14713 | 0.07126
15 | 0.3407 | 0.16501
16 | 0.36187 | 0.17526
17 | 0.40419 | 0.19576
18 | 0.21682 | 0.10501
19 | 0.077491 | 0.037531
20 | 0.18986 | 0.091952
21 | 0.088346 | 0.042788
22 | 0.41288 | 0.19997
23 | 0.14767 | 0.071521
24 | 0.12463 | 0.060359
25 | 0.10484 | 0.050778
26 | 0.39554 | 0.19157
27 | 0.16741 | 0.081081
28 | 0.40047 | 0.19396
29 | 0.2209 | 0.10699
30 | 0.30276 | 0.14663
31 | 0.12752 | 0.061761
32 | 0.26464 | 0.12817
33 | 0.068645 | 0.033246
34 | 0.31593 | 0.15301
35 | 0.28983 | 0.14037
36 | 0.10465 | 0.050686
37 | 0.093984 | 0.045518
38 | 0.41015 | 0.19864
39 | 0.40439 | 0.19586
40 | 0.23606 | 0.11433
41 | 0.28413 | 0.13761
42 | 0.27144 | 0.13146
43 | 0.34997 | 0.1695
44 | 0.13331 | 0.064565
45 | 0.11959 | 0.057922
46 | 0.33872 | 0.16405
47 | 0.31068 | 0.15047
48 | 0.4153 | 0.20114
49 | 0.80106 | 0.38797
50 | 0.17397 | 0.084257
51 | 0.23213 | 0.11242
52 | 0.18264 | 0.088457
53 | 0.15526 | 0.075195
54 | 0.10462 | 0.050669
55 | 0.077175 | 0.037378
56 | 0.16642 | 0.080601
57 | 0.41466 | 0.20083
58 | 0.20956 | 0.10149
59 | 0.30882 | 0.14957
60 | 0.27096 | 0.13123
61 | 0.22822 | 0.11053
62 | 0.31983 | 0.1549
63 | 0.077742 | 0.037652
64 | 0.24861 | 0.12041
65 | 0.12585 | 0.060953
66 | 0.10449 | 0.050609
67 | 0.11871 | 0.057496

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1