## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_359_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_359_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_359_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_359_0_node_135 | 20 | n |  | TRUE
4 | bus_MV_359_0_node_170 | 20 | n |  | TRUE
5 | bus_MV_359_0_node_168 | 20 | n |  | TRUE
6 | bus_MV_359_0_node_116 | 20 | n |  | TRUE
7 | bus_MV_359_0_node_3 | 20 | n |  | TRUE
8 | bus_MV_359_0_node_4 | 20 | n |  | TRUE
9 | bus_MV_359_0_node_88 | 20 | n |  | TRUE
10 | bus_MV_359_0_node_5 | 20 | n |  | TRUE
11 | bus_MV_359_0_node_83 | 20 | n |  | TRUE
12 | bus_MV_359_0_node_84 | 20 | n |  | TRUE
13 | bus_MV_359_0_node_85 | 20 | n |  | TRUE
14 | bus_MV_359_0_node_86 | 20 | n |  | TRUE
15 | bus_MV_359_0_node_87 | 20 | n |  | TRUE
16 | bus_MV_359_0_node_169 | 20 | n |  | TRUE
17 | bus_MV_359_0_node_114 | 20 | n |  | TRUE
18 | bus_MV_359_0_node_115 | 20 | n |  | TRUE
19 | bus_MV_359_0_node_136 | 20 | n |  | TRUE
20 | bus_MV_359_0_node_133 | 20 | n |  | TRUE
21 | bus_MV_359_0_node_134 | 20 | n |  | TRUE
22 | bus_MV_359_0_node_137 | 20 | n |  | TRUE
23 | bus_MV_359_0_node_174 | 20 | n |  | TRUE
24 | bus_MV_359_0_node_132 | 20 | n |  | TRUE
25 | bus_MV_359_0_node_6 | 20 | n |  | TRUE
26 | bus_MV_359_0_node_17 | 20 | n |  | TRUE
27 | bus_MV_359_0_node_18 | 20 | n |  | TRUE
28 | bus_MV_359_0_node_21 | 20 | n |  | TRUE
29 | bus_MV_359_0_node_160 | 20 | n |  | TRUE
30 | bus_MV_359_0_node_155 | 20 | n |  | TRUE
31 | bus_MV_359_0_node_22 | 20 | n |  | TRUE
32 | bus_MV_359_0_node_45 | 20 | n |  | TRUE
33 | bus_MV_359_0_node_61 | 20 | n |  | TRUE
34 | bus_MV_359_0_node_19 | 20 | n |  | TRUE
35 | bus_MV_359_0_node_163 | 20 | n |  | TRUE
36 | bus_MV_359_0_node_41 | 20 | n |  | TRUE
37 | bus_MV_359_0_node_171 | 20 | n |  | TRUE
38 | bus_MV_359_0_node_14 | 20 | n |  | TRUE
39 | bus_MV_359_0_node_16 | 20 | n |  | TRUE
40 | bus_MV_359_0_node_13 | 20 | n |  | TRUE
41 | bus_MV_359_0_node_15 | 20 | n |  | TRUE
42 | bus_MV_359_0_node_7 | 20 | n |  | TRUE
43 | bus_MV_359_0_node_8 | 20 | n |  | TRUE
44 | bus_MV_359_0_node_11 | 20 | n |  | TRUE
45 | bus_MV_359_0_node_12 | 20 | n |  | TRUE
46 | bus_MV_359_0_node_10 | 20 | n |  | TRUE
47 | bus_MV_359_0_node_20 | 20 | n |  | TRUE
48 | bus_MV_359_0_node_124 | 20 | n |  | TRUE
49 | bus_MV_359_0_node_154 | 20 | n |  | TRUE
50 | bus_MV_359_0_node_62 | 20 | n |  | TRUE
51 | bus_MV_359_0_node_162 | 20 | n |  | TRUE
52 | bus_MV_359_0_node_27 | 20 | n |  | TRUE
53 | bus_MV_359_0_node_161 | 20 | n |  | TRUE
54 | bus_MV_359_0_node_40 | 20 | n |  | TRUE
55 | bus_MV_359_0_node_42 | 20 | n |  | TRUE
56 | bus_MV_359_0_node_43 | 20 | n |  | TRUE
57 | bus_MV_359_0_node_44 | 20 | n |  | TRUE
58 | bus_MV_359_0_node_146 | 20 | n |  | TRUE
59 | bus_MV_359_0_node_165 | 20 | n |  | TRUE
60 | bus_MV_359_0_node_23 | 20 | n |  | TRUE
61 | bus_MV_359_0_node_24 | 20 | n |  | TRUE
62 | bus_MV_359_0_node_30 | 20 | n |  | TRUE
63 | bus_MV_359_0_node_106 | 20 | n |  | TRUE
64 | bus_MV_359_0_node_156 | 20 | n |  | TRUE
65 | bus_MV_359_0_node_107 | 20 | n |  | TRUE
66 | bus_MV_359_0_node_26 | 20 | n |  | TRUE
67 | bus_MV_359_0_node_166 | 20 | n |  | TRUE
68 | bus_MV_359_0_node_123 | 20 | n |  | TRUE
69 | bus_MV_359_0_node_29 | 20 | n |  | TRUE
70 | bus_MV_359_0_node_145 | 20 | n |  | TRUE
71 | bus_MV_359_0_node_39 | 20 | n |  | TRUE
72 | bus_MV_359_0_node_38 | 20 | n |  | TRUE
73 | bus_MV_359_0_node_175 | 20 | n |  | TRUE
74 | bus_MV_359_0_node_122 | 20 | n |  | TRUE
75 | bus_MV_359_0_node_37 | 20 | n |  | TRUE
76 | bus_MV_359_0_node_108 | 20 | n |  | TRUE
77 | bus_MV_359_0_node_128 | 20 | n |  | TRUE
78 | bus_MV_359_0_node_150 | 20 | n |  | TRUE
79 | bus_MV_359_0_node_33 | 20 | n |  | TRUE
80 | bus_MV_359_0_node_143 | 20 | n |  | TRUE
81 | bus_MV_359_0_node_131 | 20 | n |  | TRUE
82 | bus_MV_359_0_node_104 | 20 | n |  | TRUE
83 | bus_MV_359_0_node_159 | 20 | n |  | TRUE
84 | bus_MV_359_0_node_103 | 20 | n |  | TRUE
85 | bus_MV_359_0_node_31 | 20 | n |  | TRUE
86 | bus_MV_359_0_node_32 | 20 | n |  | TRUE
87 | bus_MV_359_0_node_34 | 20 | n |  | TRUE
88 | bus_MV_359_0_node_158 | 20 | n |  | TRUE
89 | bus_MV_359_0_node_36 | 20 | n |  | TRUE
90 | bus_MV_359_0_node_126 | 20 | n |  | TRUE
91 | bus_MV_359_0_node_35 | 20 | n |  | TRUE
92 | bus_MV_359_0_node_153 | 20 | n |  | TRUE
93 | bus_MV_359_0_node_138 | 20 | n |  | TRUE
94 | bus_MV_359_0_node_94 | 20 | n |  | TRUE
95 | bus_MV_359_0_node_125 | 20 | n |  | TRUE
96 | bus_MV_359_0_node_80 | 20 | n |  | TRUE
97 | bus_MV_359_0_node_60 | 20 | n |  | TRUE
98 | bus_MV_359_0_node_120 | 20 | n |  | TRUE
99 | bus_MV_359_0_node_147 | 20 | n |  | TRUE
100 | bus_MV_359_0_node_57 | 20 | n |  | TRUE
101 | bus_MV_359_0_node_177 | 20 | n |  | TRUE
102 | bus_MV_359_0_node_119 | 20 | n |  | TRUE
103 | bus_MV_359_0_node_56 | 20 | n |  | TRUE
104 | bus_MV_359_0_node_151 | 20 | n |  | TRUE
105 | bus_MV_359_0_node_55 | 20 | n |  | TRUE
106 | bus_MV_359_0_node_58 | 20 | n |  | TRUE
107 | bus_MV_359_0_node_172 | 20 | n |  | TRUE
108 | bus_MV_359_0_node_59 | 20 | n |  | TRUE
109 | bus_MV_359_0_node_121 | 20 | n |  | TRUE
110 | bus_MV_359_0_node_46 | 20 | n |  | TRUE
111 | bus_MV_359_0_node_47 | 20 | n |  | TRUE
112 | bus_MV_359_0_node_48 | 20 | n |  | TRUE
113 | bus_MV_359_0_node_49 | 20 | n |  | TRUE
114 | bus_MV_359_0_node_69 | 20 | n |  | TRUE
115 | bus_MV_359_0_node_73 | 20 | n |  | TRUE
116 | bus_MV_359_0_node_68 | 20 | n |  | TRUE
117 | bus_MV_359_0_node_50 | 20 | n |  | TRUE
118 | bus_MV_359_0_node_149 | 20 | n |  | TRUE
119 | bus_MV_359_0_node_176 | 20 | n |  | TRUE
120 | bus_MV_359_0_node_72 | 20 | n |  | TRUE
121 | bus_MV_359_0_node_70 | 20 | n |  | TRUE
122 | bus_MV_359_0_node_71 | 20 | n |  | TRUE
123 | bus_MV_359_0_node_148 | 20 | n |  | TRUE
124 | bus_MV_359_0_node_51 | 20 | n |  | TRUE
125 | bus_MV_359_0_node_52 | 20 | n |  | TRUE
126 | bus_MV_359_0_node_53 | 20 | n |  | TRUE
127 | bus_MV_359_0_node_54 | 20 | n |  | TRUE
128 | bus_MV_359_0_node_118 | 20 | n |  | TRUE
129 | bus_MV_359_0_node_105 | 20 | n |  | TRUE
130 | bus_MV_359_0_node_113 | 20 | n |  | TRUE
131 | bus_MV_359_0_node_167 | 20 | n |  | TRUE
132 | bus_MV_359_0_node_173 | 20 | n |  | TRUE
133 | bus_MV_359_0_node_63 | 20 | n |  | TRUE
134 | bus_MV_359_0_node_64 | 20 | n |  | TRUE
135 | bus_MV_359_0_node_65 | 20 | n |  | TRUE
136 | bus_MV_359_0_node_66 | 20 | n |  | TRUE
137 | bus_MV_359_0_node_67 | 20 | n |  | TRUE
138 | bus_MV_359_0_node_99 | 20 | n |  | TRUE
139 | bus_MV_359_0_node_127 | 20 | n |  | TRUE
140 | bus_MV_359_0_node_98 | 20 | n |  | TRUE
141 | bus_MV_359_0_node_129 | 20 | n |  | TRUE
142 | bus_MV_359_0_node_77 | 20 | n |  | TRUE
143 | bus_MV_359_0_node_82 | 20 | n |  | TRUE
144 | bus_MV_359_0_node_78 | 20 | n |  | TRUE
145 | bus_MV_359_0_node_81 | 20 | n |  | TRUE
146 | bus_MV_359_0_node_74 | 20 | n |  | TRUE
147 | bus_MV_359_0_node_75 | 20 | n |  | TRUE
148 | bus_MV_359_0_node_76 | 20 | n |  | TRUE
149 | bus_MV_359_0_node_79 | 20 | n |  | TRUE
150 | bus_MV_359_0_node_117 | 20 | n |  | TRUE
151 | bus_MV_359_0_node_89 | 20 | n |  | TRUE
152 | bus_MV_359_0_node_90 | 20 | n |  | TRUE
153 | bus_MV_359_0_node_91 | 20 | n |  | TRUE
154 | bus_MV_359_0_node_93 | 20 | n |  | TRUE
155 | bus_MV_359_0_node_130 | 20 | n |  | TRUE
156 | bus_MV_359_0_node_92 | 20 | n |  | TRUE
157 | bus_MV_359_0_node_101 | 20 | n |  | TRUE
158 | bus_MV_359_0_node_109 | 20 | n |  | TRUE
159 | bus_MV_359_0_node_95 | 20 | n |  | TRUE
160 | bus_MV_359_0_node_144 | 20 | n |  | TRUE
161 | bus_MV_359_0_node_96 | 20 | n |  | TRUE
162 | bus_MV_359_0_node_139 | 20 | n |  | TRUE
163 | bus_MV_359_0_node_152 | 20 | n |  | TRUE
164 | bus_MV_359_0_node_111 | 20 | n |  | TRUE
165 | bus_MV_359_0_node_110 | 20 | n |  | TRUE
166 | bus_MV_359_0_node_100 | 20 | n |  | TRUE
167 | bus_MV_359_0_node_97 | 20 | n |  | TRUE
168 | bus_MV_359_0_node_102 | 20 | n |  | TRUE
169 | bus_MV_359_0_node_164 | 20 | n |  | TRUE
170 | bus_MV_359_0_node_142 | 20 | n |  | TRUE
171 | bus_MV_359_0_node_112 | 20 | n |  | TRUE
172 | bus_MV_359_0_node_157 | 20 | n |  | TRUE
173 | bus_MV_359_0_node_140 | 20 | n |  | TRUE
174 | bus_MV_359_0_node_141 | 20 | n |  | TRUE
175 | bus_HV_359_0_node_156 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_359_0_load_0 | 0 | 0.21418 | 0.10373 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_359_0_load_170 | 4 | 0.21343 | 0.10337 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_359_0_load_168 | 5 | 0.08264 | 0.040024 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_359_0_load_3 | 7 | 0.25385 | 0.12294 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_359_0_load_83 | 11 | 0.2597 | 0.12578 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_359_0_load_86 | 14 | 0.24256 | 0.11748 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_359_0_load_169 | 16 | 0.21984 | 0.10647 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_359_0_load_114 | 17 | 0.25763 | 0.12478 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_359_0_load_133 | 20 | 0.069149 | 0.033491 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_359_0_load_174 | 23 | 0.22438 | 0.10867 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_359_0_load_132 | 24 | 0.078113 | 0.037832 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_359_0_load_21 | 28 | 0.27815 | 0.13471 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_359_0_load_160 | 29 | 0.28209 | 0.13662 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_359_0_load_61 | 33 | 0.27231 | 0.13189 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_359_0_load_163 | 35 | 0.2536 | 0.12283 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_359_0_load_171 | 37 | 0.24867 | 0.12044 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_359_0_load_13 | 40 | 0.40498 | 0.19614 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_359_0_load_7 | 42 | 0.39351 | 0.19059 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_359_0_load_12 | 45 | 0.08791 | 0.042577 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_359_0_load_10 | 46 | 0.22937 | 0.11109 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_359_0_load_20 | 47 | 0.13703 | 0.066368 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_359_0_load_154 | 49 | 0.34082 | 0.16506 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_359_0_load_62 | 50 | 0.17008 | 0.082374 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_359_0_load_161 | 53 | 0.34846 | 0.16877 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_359_0_load_40 | 54 | 0.41502 | 0.201 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_359_0_load_146 | 58 | 0.43987 | 0.21304 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_359_0_load_165 | 59 | 0.19273 | 0.093342 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_359_0_load_23 | 60 | 0.37248 | 0.1804 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_359_0_load_156 | 64 | 0.31794 | 0.15399 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_359_0_load_166 | 67 | 0.13285 | 0.064341 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_359_0_load_145 | 70 | 0.078629 | 0.038082 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_359_0_load_38 | 72 | 0.4106 | 0.19887 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_359_0_load_175 | 73 | 0.21667 | 0.10494 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_359_0_load_122 | 74 | 0.095759 | 0.046378 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_359_0_load_37 | 75 | 0.16534 | 0.080079 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_359_0_load_150 | 78 | 0.095963 | 0.046477 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_359_0_load_143 | 80 | 0.068296 | 0.033077 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_359_0_load_131 | 81 | 0.12841 | 0.062192 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_359_0_load_159 | 83 | 0.39946 | 0.19347 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_359_0_load_31 | 85 | 0.12791 | 0.061949 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_359_0_load_158 | 88 | 0.29548 | 0.14311 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_359_0_load_153 | 92 | 0.35095 | 0.16997 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_359_0_load_138 | 93 | 0.091168 | 0.044155 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_359_0_load_125 | 95 | 0.37031 | 0.17935 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_359_0_load_120 | 98 | 0.3174 | 0.15372 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_359_0_load_147 | 99 | 0.074075 | 0.035876 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_359_0_load_177 | 101 | 0.35704 | 0.17292 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_359_0_load_151 | 104 | 0.13036 | 0.063134 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_359_0_load_172 | 107 | 0.19731 | 0.095564 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_359_0_load_59 | 108 | 0.18173 | 0.088016 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_359_0_load_121 | 109 | 0.35008 | 0.16955 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_359_0_load_46 | 110 | 0.32186 | 0.15588 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_359_0_load_69 | 114 | 0.41527 | 0.20113 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_359_0_load_73 | 115 | 0.39818 | 0.19285 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_359_0_load_68 | 116 | 0.40188 | 0.19464 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_359_0_load_176 | 119 | 0.078236 | 0.037891 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_359_0_load_148 | 123 | 0.11042 | 0.053478 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_359_0_load_51 | 124 | 0.18849 | 0.091289 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_359_0_load_118 | 128 | 0.27609 | 0.13372 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_359_0_load_113 | 130 | 0.33044 | 0.16004 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_359_0_load_167 | 131 | 0.21584 | 0.10453 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_359_0_load_173 | 132 | 0.2216 | 0.10733 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_359_0_load_63 | 133 | 0.34534 | 0.16725 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_359_0_load_127 | 139 | 0.39768 | 0.1926 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_359_0_load_98 | 140 | 0.087549 | 0.042402 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_359_0_load_77 | 142 | 0.17026 | 0.082463 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_359_0_load_82 | 143 | 0.09858 | 0.047745 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_359_0_load_78 | 144 | 0.56006 | 0.27125 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_359_0_load_81 | 145 | 0.20352 | 0.098571 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_359_0_load_117 | 150 | 0.18992 | 0.091984 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_359_0_load_89 | 151 | 0.16887 | 0.081789 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_359_0_load_130 | 155 | 0.25725 | 0.12459 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_359_0_load_109 | 158 | 0.36172 | 0.17519 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_359_0_load_144 | 160 | 0.077055 | 0.037319 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_359_0_load_139 | 162 | 0.1297 | 0.062816 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_359_0_load_152 | 163 | 0.080618 | 0.039045 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_359_0_load_110 | 165 | 0.16338 | 0.079126 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_359_0_load_100 | 166 | 0.26637 | 0.12901 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_359_0_load_97 | 167 | 0.31285 | 0.15152 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_359_0_load_102 | 168 | 0.38852 | 0.18817 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_359_0_load_164 | 169 | 0.33341 | 0.16148 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_359_0_load_157 | 172 | 0.27053 | 0.13102 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_359_0_load_140 | 173 | 0.077464 | 0.037518 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 64 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_359_0_line_0 |  | 0 | 1 | 0.036548 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_359_0_line_1 |  | 1 | 2 | 0.39054 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_359_0_line_2 |  | 2 | 5 | 0.020851 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_359_0_line_3 |  | 3 | 4 | 0.027852 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_359_0_line_4 |  | 3 | 5 | 1.3723 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_359_0_line_5 |  | 3 | 6 | 0.45746 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_359_0_line_6 |  | 6 | 19 | 0.14293 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_359_0_line_7 |  | 6 | 20 | 0.027792 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_359_0_line_8 |  | 6 | 18 | 0.22395 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_359_0_line_9 |  | 7 | 8 | 0.003449 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_359_0_line_10 |  | 7 | 9 | 0.89589 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_359_0_line_11 |  | 8 | 10 | 0.050173 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_359_0_line_12 |  | 9 | 16 | 0.060254 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_359_0_line_13 |  | 9 | 15 | 0.72064 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_359_0_line_14 |  | 10 | 24 | 0.040619 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_359_0_line_15 |  | 11 | 12 | 0.046534 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_359_0_line_16 |  | 12 | 13 | 0.48549 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_359_0_line_17 |  | 12 | 126 | 0.35305 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_359_0_line_18 |  | 13 | 14 | 0.003327 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_359_0_line_19 |  | 14 | 15 | 0.052768 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_359_0_line_20 |  | 16 | 22 | 0.052495 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_359_0_line_21 |  | 17 | 18 | 0.057587 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_359_0_line_22 |  | 19 | 23 | 0.005444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_359_0_line_23 |  | 20 | 21 | 0.039328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_359_0_line_24 |  | 21 | 22 | 0.24483 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_359_0_line_25 |  | 25 | 26 | 0.72892 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
26 | MV_359_0_line_26 |  | 25 | 27 | 0.58475 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_359_0_line_27 |  | 25 | 28 | 0.003488 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_359_0_line_28 |  | 26 | 29 | 0.053105 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
29 | MV_359_0_line_29 |  | 26 | 30 | 0.44197 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_359_0_line_30 |  | 27 | 37 | 0.039997 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_359_0_line_31 |  | 27 | 38 | 1.0334 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_359_0_line_32 |  | 29 | 48 | 0.052981 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
33 | MV_359_0_line_33 |  | 30 | 49 | 0.09044 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_359_0_line_34 |  | 31 | 32 | 0.25381 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
35 | MV_359_0_line_35 |  | 31 | 33 | 0.070311 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
36 | MV_359_0_line_36 |  | 32 | 59 | 0.039194 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
37 | MV_359_0_line_37 |  | 33 | 55 | 0.03196 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
38 | MV_359_0_line_38 |  | 34 | 35 | 0.011406 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
39 | MV_359_0_line_39 |  | 34 | 36 | 0.22253 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
40 | MV_359_0_line_40 |  | 35 | 50 | 0.32489 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
41 | MV_359_0_line_41 |  | 36 | 55 | 0.18241 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
42 | MV_359_0_line_42 |  | 36 | 54 | 0.029965 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_359_0_line_43 |  | 38 | 39 | 0.50408 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_359_0_line_44 |  | 38 | 40 | 0.072026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_359_0_line_45 |  | 39 | 41 | 0.7474 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_359_0_line_46 |  | 41 | 45 | 0.062599 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_359_0_line_47 |  | 42 | 43 | 0.028265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_359_0_line_48 |  | 43 | 44 | 0.085821 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_359_0_line_49 |  | 44 | 45 | 0.014962 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_359_0_line_50 |  | 44 | 46 | 0.052828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_359_0_line_51 |  | 46 | 47 | 0.057585 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_359_0_line_52 |  | 48 | 68 | 0.30101 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
53 | MV_359_0_line_53 |  | 50 | 52 | 0.088825 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
54 | MV_359_0_line_54 |  | 51 | 52 | 0.27749 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
55 | MV_359_0_line_55 |  | 51 | 53 | 0.025398 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
56 | MV_359_0_line_56 |  | 52 | 61 | 0.56424 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
57 | MV_359_0_line_57 |  | 52 | 66 | 0.47963 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
58 | MV_359_0_line_58 |  | 53 | 76 | 0.007851 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
59 | MV_359_0_line_59 |  | 53 | 75 | 0.46273 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
60 | MV_359_0_line_60 |  | 56 | 57 | 0.12928 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
61 | MV_359_0_line_61 |  | 56 | 58 | 0.0048723 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
62 | MV_359_0_line_62 |  | 57 | 97 | 0.046551 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
63 | MV_359_0_line_63 |  | 57 | 98 | 0.046175 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
64 | MV_359_0_line_64 |  | 60 | 61 | 0.023239 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_359_0_line_65 |  | 61 | 62 | 0.36686 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
66 | MV_359_0_line_66 |  | 61 | 63 | 0.29658 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
67 | MV_359_0_line_67 |  | 62 | 71 | 0.10281 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
68 | MV_359_0_line_68 |  | 62 | 72 | 0.002735 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
69 | MV_359_0_line_69 |  | 62 | 69 | 0.14132 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
70 | MV_359_0_line_70 |  | 63 | 64 | 0.048955 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
71 | MV_359_0_line_71 |  | 63 | 65 | 0.21064 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
72 | MV_359_0_line_72 |  | 64 | 170 | 0.056611 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_359_0_line_73 |  | 65 | 169 | 0.004599 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_359_0_line_74 |  | 65 | 129 | 0.43762 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_359_0_line_75 |  | 66 | 67 | 0.004561 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
76 | MV_359_0_line_76 |  | 66 | 68 | 0.18284 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
77 | MV_359_0_line_77 |  | 68 | 74 | 0.005284 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
78 | MV_359_0_line_78 |  | 69 | 70 | 0.041825 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
79 | MV_359_0_line_79 |  | 70 | 77 | 0.058886 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
80 | MV_359_0_line_80 |  | 71 | 81 | 0.036392 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
81 | MV_359_0_line_81 |  | 73 | 74 | 0.22911 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
82 | MV_359_0_line_82 |  | 76 | 102 | 0.33831 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
83 | MV_359_0_line_83 |  | 77 | 141 | 0.01428 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
84 | MV_359_0_line_84 |  | 77 | 138 | 0.1852 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
85 | MV_359_0_line_85 |  | 78 | 79 | 0.045413 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
86 | MV_359_0_line_86 |  | 78 | 80 | 0.19617 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
87 | MV_359_0_line_87 |  | 79 | 86 | 0.17308 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
88 | MV_359_0_line_88 |  | 80 | 141 | 0.052232 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
89 | MV_359_0_line_89 |  | 82 | 83 | 0.051748 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
90 | MV_359_0_line_90 |  | 82 | 84 | 0.3812 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
91 | MV_359_0_line_91 |  | 83 | 137 | 0.028223 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
92 | MV_359_0_line_92 |  | 84 | 168 | 0.009133 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
93 | MV_359_0_line_93 |  | 85 | 86 | 0.014267 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
94 | MV_359_0_line_94 |  | 87 | 88 | 0.018073 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
95 | MV_359_0_line_95 |  | 87 | 89 | 0.49747 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
96 | MV_359_0_line_96 |  | 87 | 90 | 0.16605 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
97 | MV_359_0_line_97 |  | 89 | 93 | 0.0076975 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
98 | MV_359_0_line_98 |  | 89 | 91 | 0.020441 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
99 | MV_359_0_line_99 |  | 90 | 94 | 0.10142 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
100 | MV_359_0_line_100 |  | 90 | 95 | 0.056983 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
101 | MV_359_0_line_101 |  | 91 | 92 | 0.016909 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
102 | MV_359_0_line_102 |  | 93 | 96 | 0.042168 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
103 | MV_359_0_line_103 |  | 94 | 159 | 0.18182 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
104 | MV_359_0_line_104 |  | 94 | 160 | 0.019704 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
105 | MV_359_0_line_105 |  | 95 | 167 | 0.18055 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
106 | MV_359_0_line_106 |  | 96 | 149 | 0.1281 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
107 | MV_359_0_line_107 |  | 97 | 99 | 0.0054743 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
108 | MV_359_0_line_108 |  | 98 | 102 | 0.30194 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
109 | MV_359_0_line_109 |  | 100 | 101 | 0.002201 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_359_0_line_110 |  | 100 | 102 | 0.28652 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
111 | MV_359_0_line_111 |  | 102 | 109 | 0.04004 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
112 | MV_359_0_line_112 |  | 103 | 104 | 0.0017798 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_359_0_line_113 |  | 103 | 105 | 0.1282 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_359_0_line_114 |  | 105 | 108 | 0.029588 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_359_0_line_115 |  | 105 | 106 | 0.094223 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_359_0_line_116 |  | 106 | 107 | 0.040408 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_359_0_line_117 |  | 107 | 132 | 0.028282 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_359_0_line_118 |  | 108 | 128 | 0.51616 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
119 | MV_359_0_line_119 |  | 110 | 111 | 0.003537 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
120 | MV_359_0_line_120 |  | 111 | 112 | 0.52321 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
121 | MV_359_0_line_121 |  | 111 | 113 | 0.36185 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
122 | MV_359_0_line_122 |  | 111 | 114 | 0.13153 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
123 | MV_359_0_line_123 |  | 112 | 115 | 0.004693 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
124 | MV_359_0_line_124 |  | 113 | 116 | 0.004076 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
125 | MV_359_0_line_125 |  | 114 | 121 | 0.019706 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
126 | MV_359_0_line_126 |  | 117 | 118 | 0.012919 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
127 | MV_359_0_line_127 |  | 117 | 119 | 0.006383 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_359_0_line_128 |  | 117 | 120 | 0.014259 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
129 | MV_359_0_line_129 |  | 118 | 123 | 0.00036397 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
130 | MV_359_0_line_130 |  | 120 | 122 | 0.34688 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
131 | MV_359_0_line_131 |  | 121 | 122 | 0.094293 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
132 | MV_359_0_line_132 |  | 122 | 142 | 0.049956 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
133 | MV_359_0_line_133 |  | 124 | 125 | 0.004113 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_359_0_line_134 |  | 125 | 126 | 0.67605 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_359_0_line_135 |  | 125 | 127 | 0.42143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_359_0_line_136 |  | 125 | 128 | 0.80318 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
137 | MV_359_0_line_137 |  | 126 | 130 | 0.048827 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
138 | MV_359_0_line_138 |  | 127 | 131 | 0.011509 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_359_0_line_139 |  | 128 | 129 | 0.007443 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_359_0_line_140 |  | 133 | 134 | 0.00645 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
141 | MV_359_0_line_141 |  | 133 | 135 | 0.006966 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
142 | MV_359_0_line_142 |  | 134 | 136 | 0.14524 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
143 | MV_359_0_line_143 |  | 135 | 137 | 0.026229 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
144 | MV_359_0_line_144 |  | 136 | 138 | 0.10264 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
145 | MV_359_0_line_145 |  | 136 | 139 | 0.008827 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
146 | MV_359_0_line_146 |  | 138 | 140 | 0.031965 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
147 | MV_359_0_line_147 |  | 140 | 167 | 0.027121 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
148 | MV_359_0_line_148 |  | 142 | 143 | 0.12089 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
149 | MV_359_0_line_149 |  | 143 | 144 | 0.05764 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
150 | MV_359_0_line_150 |  | 143 | 145 | 0.023648 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
151 | MV_359_0_line_151 |  | 144 | 149 | 0.050386 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
152 | MV_359_0_line_152 |  | 146 | 147 | 0.29139 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
153 | MV_359_0_line_153 |  | 146 | 148 | 0.5011 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
154 | MV_359_0_line_154 |  | 147 | 149 | 0.077803 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
155 | MV_359_0_line_155 |  | 148 | 150 | 0.003477 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
156 | MV_359_0_line_156 |  | 151 | 152 | 0.007276 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
157 | MV_359_0_line_157 |  | 152 | 153 | 0.93271 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
158 | MV_359_0_line_158 |  | 153 | 154 | 1.0858 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
159 | MV_359_0_line_159 |  | 153 | 155 | 0.007219 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
160 | MV_359_0_line_160 |  | 154 | 159 | 0.21425 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
161 | MV_359_0_line_161 |  | 154 | 156 | 0.40157 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
162 | MV_359_0_line_162 |  | 156 | 157 | 0.31253 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
163 | MV_359_0_line_163 |  | 156 | 158 | 0.01935 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
164 | MV_359_0_line_164 |  | 157 | 163 | 0.083585 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
165 | MV_359_0_line_165 |  | 158 | 164 | 0.014311 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
166 | MV_359_0_line_166 |  | 158 | 165 | 0.016827 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
167 | MV_359_0_line_167 |  | 159 | 161 | 0.12968 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
168 | MV_359_0_line_168 |  | 160 | 166 | 0.069254 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
169 | MV_359_0_line_169 |  | 161 | 162 | 0.052582 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
170 | MV_359_0_line_170 |  | 164 | 171 | 0.18278 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
171 | MV_359_0_line_171 |  | 170 | 174 | 0.084686 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_359_0_line_172 |  | 171 | 172 | 0.055637 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
173 | MV_359_0_line_173 |  | 173 | 174 | 0.036856 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_359_0_trafo_156 | 25 MVA 110/20 kV | 175 | 64 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2679555.0661 | 1241721.9365
1 | 2679518.5047 | 1241719.5005
2 | 2679621.5558 | 1242008.043
3 | 2680993.5572 | 1242082.2907
4 | 2681021.4503 | 1242083.728
5 | 2679622.5989 | 1242021.0218
6 | 2681310.786 | 1242239.1513
7 | 2682456.2138 | 1242234.6489
8 | 2682459.6706 | 1242234.5191
9 | 2681573.1978 | 1242386.0016
10 | 2682477.9958 | 1242269.9103
11 | 2681247.6725 | 1242834.1812
12 | 2681270.9627 | 1242874.4734
13 | 2681328.6205 | 1242610.7514
14 | 2681330.5252 | 1242608.0199
15 | 2681330.8708 | 1242555.2534
16 | 2681560.9987 | 1242329.7268
17 | 2681388.0438 | 1242052.3093
18 | 2681334.5783 | 1242073.7029
19 | 2681231.7115 | 1242312.2322
20 | 2681308.0584 | 1242266.8089
21 | 2681307.2153 | 1242299.4345
22 | 2681515.8632 | 1242302.9209
23 | 2681237.1659 | 1242311.9733
24 | 2682518.6065 | 1242269.0946
25 | 2682905.7024 | 1242859.0053
26 | 2683355.6347 | 1242993.2378
27 | 2683051.3766 | 1242472.1512
28 | 2682904.3797 | 1242862.2336
29 | 2683328.4751 | 1243038.9117
30 | 2683613.8035 | 1242951.6058
31 | 2682633.8907 | 1243119.8254
32 | 2682393.5259 | 1243038.3247
33 | 2682593.3302 | 1243177.2579
34 | 2682759.5024 | 1243218.7695
35 | 2682770.3204 | 1243222.4786
36 | 2682573.3439 | 1243340.6869
37 | 2683061.8923 | 1242436.5281
38 | 2683221.433 | 1242601.7379
39 | 2683438.815 | 1242629.054
40 | 2683199.1535 | 1242670.2417
41 | 2683517.1647 | 1242471.6976
42 | 2683637.635 | 1242579.2607
43 | 2683609.2864 | 1242579.2168
44 | 2683543.7293 | 1242523.8314
45 | 2683529.4196 | 1242519.4602
46 | 2683519.0848 | 1242570.4961
47 | 2683461.5065 | 1242569.6189
48 | 2683299.6102 | 1243082.7827
49 | 2683698.4196 | 1242919.6753
50 | 2682960.4464 | 1243485.9241
51 | 2682645.2003 | 1243601.387
52 | 2682920.3132 | 1243565.1651
53 | 2682639.6547 | 1243626.1722
54 | 2682579.0721 | 1243370.099
55 | 2682591.14 | 1243209.1394
56 | 2682254.6633 | 1243233.4951
57 | 2682276.2436 | 1243304.3566
58 | 2682254.5722 | 1243228.6237
59 | 2682382.4525 | 1243000.7216
60 | 2682811.5681 | 1244052.0904
61 | 2682791.4329 | 1244040.4882
62 | 2682903.3293 | 1244189.025
63 | 2682514.8134 | 1243933.5244
64 | 2682502.5335 | 1243886.1304
65 | 2682397.5167 | 1244060.5199
66 | 2683159.3812 | 1243219.6709
67 | 2683156.1918 | 1243216.4017
68 | 2683321.1787 | 1243304.8242
69 | 2682852.6239 | 1244291.3022
70 | 2682833.3906 | 1244328.4426
71 | 2682994.3819 | 1244236.7436
72 | 2682902.1386 | 1244191.4879
73 | 2683181.7928 | 1243487.0122
74 | 2683325.1663 | 1243308.305
75 | 2683024.1684 | 1243883.5926
76 | 2682631.8958 | 1243624.8298
77 | 2682816.8153 | 1244382.8022
78 | 2682833.5988 | 1244631.9705
79 | 2682846.1083 | 1244664.0379
80 | 2682800.7919 | 1244438.5586
81 | 2682984.4291 | 1244271.2629
82 | 2682499.171 | 1244299.4612
83 | 2682550.9185 | 1244299.392
84 | 2682301.2937 | 1244409.282
85 | 2682791.5054 | 1244781.6725
86 | 2682791.2156 | 1244795.9343
87 | 2682579.9796 | 1244759.9088
88 | 2682585.6045 | 1244777.0885
89 | 2682616.4206 | 1245083.5739
90 | 2682616.5674 | 1244613.7007
91 | 2682608.3888 | 1245072.1204
92 | 2682610.3231 | 1245055.324
93 | 2682616.2287 | 1245091.269
94 | 2682527.7288 | 1244585.2215
95 | 2682672.5133 | 1244624.5212
96 | 2682615.4462 | 1245133.43
97 | 2682234.1126 | 1243297.6789
98 | 2682319.1682 | 1243321.3752
99 | 2682237.6462 | 1243293.4978
100 | 2682124.7948 | 1243510.1521
101 | 2682124.447 | 1243507.979
102 | 2682391.6438 | 1243614.493
103 | 2681642.9611 | 1243639.6529
104 | 2681642.9186 | 1243641.4322
105 | 2681636.7219 | 1243718.424
106 | 2681574.3009 | 1243716.0305
107 | 2681574.9322 | 1243675.6323
108 | 2681641.679 | 1243745.4117
109 | 2682387.4399 | 1243654.3079
110 | 2682411.7345 | 1245456.0318
111 | 2682411.7534 | 1245459.568
112 | 2682332.6498 | 1245201.0481
113 | 2682206.926 | 1245447.9289
114 | 2682541.5579 | 1245480.8325
115 | 2682327.9595 | 1245201.4388
116 | 2682206.3035 | 1245451.9565
117 | 2682674.8346 | 1245659.4187
118 | 2682664.1511 | 1245653.9658
119 | 2682680.786 | 1245661.77
120 | 2682669.7977 | 1245672.7582
121 | 2682554.4616 | 1245467.9582
122 | 2682608.135 | 1245436.8605
123 | 2682664.1597 | 1245653.6019
124 | 2681667.4221 | 1243244.8601
125 | 2681664.8694 | 1243247.9939
126 | 2681420.4494 | 1243089.7105
127 | 2681461.3516 | 1243431.9963
128 | 2682134.213 | 1243899.7754
129 | 2682132.8645 | 1243907.0954
130 | 2681409.8701 | 1243137.3775
131 | 2681450.2756 | 1243429.4313
132 | 2681547.6722 | 1243668.0966
133 | 2682565.1808 | 1244259.1501
134 | 2682571.5513 | 1244260.2729
135 | 2682563.8763 | 1244265.9925
136 | 2682689.6881 | 1244312.0334
137 | 2682556.3827 | 1244271.7035
138 | 2682725.1352 | 1244390.9626
139 | 2682694.9639 | 1244304.9462
140 | 2682719.7686 | 1244422.3313
141 | 2682807.5323 | 1244386.7644
142 | 2682599.1403 | 1245387.7216
143 | 2682534.8085 | 1245285.3672
144 | 2682546.5114 | 1245228.9281
145 | 2682511.5308 | 1245289.534
146 | 2682324.7099 | 1245139.4264
147 | 2682486.9401 | 1245150.2876
148 | 2682078.1468 | 1245246.5993
149 | 2682527.428 | 1245182.2962
150 | 2682081.2591 | 1245245.0301
151 | 2682011.6418 | 1244658.3633
152 | 2682016.5154 | 1244652.949
153 | 2682061.5357 | 1244190.7918
154 | 2682283.5185 | 1244468.6563
155 | 2682061.8244 | 1244183.5795
156 | 2682308.3688 | 1244781.5505
157 | 2682227.0265 | 1244716.1195
158 | 2682295.4948 | 1244796.0269
159 | 2682395.8761 | 1244519.041
160 | 2682534.1988 | 1244566.6243
161 | 2682411.2028 | 1244638.0736
162 | 2682392.7126 | 1244594.5882
163 | 2682216.1565 | 1244751.9041
164 | 2682306.1991 | 1244805.56
165 | 2682278.8511 | 1244793.5498
166 | 2682466.9434 | 1244550.1064
167 | 2682712.3401 | 1244448.4148
168 | 2682296.92 | 1244417.3049
169 | 2682393.5358 | 1244058.1963
170 | 2682506.0103 | 1243829.6267
171 | 2682296.7635 | 1244970.3045
172 | 2682282.182 | 1245023.9969
173 | 2682525.6041 | 1243783.2433
174 | 2682501.0795 | 1243801.0374
175 | 2682502.5335 | 1243886.1304

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98507 | 0.017955 | 0.21418 | 0.10373
1 | 0.98508 | 0.01786 | 0 | 0
2 | 0.98519 | 0.016966 | 0 | 0
3 | 0.98598 | 0.023336 | 0 | 0
4 | 0.98597 | 0.023409 | 0.21343 | 0.10337
5 | 0.9852 | 0.016925 | 0.08264 | 0.040024
6 | 0.98628 | 0.021 | 0 | 0
7 | 0.98633 | 0.013856 | 0.25385 | 0.12294
8 | 0.98633 | 0.013859 | 0 | 0
9 | 0.98691 | 0.01776 | 0 | 0
10 | 0.98632 | 0.013902 | 0 | 0
11 | 0.9897 | -0.0015472 | 0.2597 | 0.12578
12 | 0.98972 | -0.0016932 | 0 | 0
13 | 0.98857 | 0.0072291 | 0 | 0
14 | 0.98856 | 0.0072916 | 0.24256 | 0.11748
15 | 0.9884 | 0.0059547 | 0 | 0
16 | 0.98681 | 0.018551 | 0.21984 | 0.10647
17 | 0.98618 | 0.021486 | 0.25763 | 0.12478
18 | 0.98621 | 0.021671 | 0 | 0
19 | 0.98624 | 0.021378 | 0 | 0
20 | 0.98632 | 0.02072 | 0.069149 | 0.033491
21 | 0.98637 | 0.020291 | 0 | 0
22 | 0.9867 | 0.017679 | 0 | 0
23 | 0.98624 | 0.021393 | 0.22438 | 0.10867
24 | 0.98632 | 0.01394 | 0.078113 | 0.037832
25 | 0.99667 | -0.11485 | 0 | 0
26 | 0.99737 | -0.10605 | 0 | 0
27 | 0.99556 | -0.10679 | 0 | 0
28 | 0.99667 | -0.11484 | 0.27815 | 0.13471
29 | 0.9974 | -0.10583 | 0.28209 | 0.13662
30 | 0.99717 | -0.10439 | 0 | 0
31 | 0.99767 | -0.10723 | 0 | 0
32 | 0.99765 | -0.10817 | 0 | 0
33 | 0.99767 | -0.10697 | 0.27231 | 0.13189
34 | 0.99775 | -0.10313 | 0 | 0
35 | 0.99776 | -0.10312 | 0.2536 | 0.12283
36 | 0.99769 | -0.10688 | 0 | 0
37 | 0.99555 | -0.10667 | 0.24867 | 0.12044
38 | 0.99392 | -0.094287 | 0 | 0
39 | 0.99338 | -0.09 | 0 | 0
40 | 0.99388 | -0.093937 | 0.40498 | 0.19614
41 | 0.99257 | -0.082924 | 0 | 0
42 | 0.9924 | -0.082442 | 0.39351 | 0.19059
43 | 0.99242 | -0.082576 | 0 | 0
44 | 0.99248 | -0.082157 | 0 | 0
45 | 0.9925 | -0.082293 | 0.08791 | 0.042577
46 | 0.99246 | -0.081924 | 0.22937 | 0.11109
47 | 0.99244 | -0.082021 | 0.13703 | 0.066368
48 | 0.99742 | -0.10571 | 0 | 0
49 | 0.99711 | -0.10476 | 0.34082 | 0.16506
50 | 0.99788 | -0.096067 | 0.17008 | 0.082374
51 | 0.99773 | -0.10479 | 0 | 0
52 | 0.99792 | -0.093855 | 0 | 0
53 | 0.99772 | -0.10483 | 0.34846 | 0.16877
54 | 0.99767 | -0.10704 | 0.41502 | 0.201
55 | 0.99768 | -0.10696 | 0 | 0
56 | 0.99753 | -0.11058 | 0 | 0
57 | 0.99754 | -0.11053 | 0 | 0
58 | 0.99753 | -0.11058 | 0.43987 | 0.21304
59 | 0.99765 | -0.10817 | 0.19273 | 0.093342
60 | 0.99847 | -0.09017 | 0.37248 | 0.1804
61 | 0.99848 | -0.090273 | 0 | 0
62 | 0.99798 | -0.095123 | 0 | 0
63 | 0.99985 | -0.0011486 | 0 | 0
64 | 1 | 0 | -19.6069 | -7.8513
65 | 0.99937 | -0.0067784 | 0 | 0
66 | 0.9977 | -0.095328 | 0 | 0
67 | 0.9977 | -0.095328 | 0.13285 | 0.064341
68 | 0.99754 | -0.10497 | 0 | 0
69 | 0.9978 | -0.096896 | 0 | 0
70 | 0.99775 | -0.097417 | 0.078629 | 0.038082
71 | 0.99798 | -0.095139 | 0 | 0
72 | 0.99798 | -0.095124 | 0.4106 | 0.19887
73 | 0.99749 | -0.10661 | 0.21667 | 0.10494
74 | 0.99754 | -0.10497 | 0.095759 | 0.046378
75 | 0.99769 | -0.10628 | 0.16534 | 0.080079
76 | 0.99772 | -0.10484 | 0 | 0
77 | 0.99768 | -0.098146 | 0 | 0
78 | 0.99766 | -0.099053 | 0.095963 | 0.046477
79 | 0.99766 | -0.099065 | 0 | 0
80 | 0.99768 | -0.098174 | 0.068296 | 0.033077
81 | 0.99798 | -0.095142 | 0.12841 | 0.062192
82 | 0.99739 | -0.10112 | 0 | 0
83 | 0.99739 | -0.10072 | 0.39946 | 0.19347
84 | 0.99737 | -0.10127 | 0 | 0
85 | 0.99766 | -0.099095 | 0.12791 | 0.061949
86 | 0.99766 | -0.099094 | 0 | 0
87 | 0.99692 | -0.12935 | 0 | 0
88 | 0.99692 | -0.12937 | 0.29548 | 0.14311
89 | 0.99665 | -0.13164 | 0 | 0
90 | 0.99701 | -0.1285 | 0 | 0
91 | 0.99665 | -0.13165 | 0 | 0
92 | 0.99665 | -0.13165 | 0.35095 | 0.16997
93 | 0.99665 | -0.13167 | 0.091168 | 0.044155
94 | 0.99699 | -0.12895 | 0 | 0
95 | 0.9971 | -0.12219 | 0.37031 | 0.17935
96 | 0.99663 | -0.13185 | 0 | 0
97 | 0.99754 | -0.11054 | 0 | 0
98 | 0.99755 | -0.11008 | 0.3174 | 0.15372
99 | 0.99754 | -0.11054 | 0.074075 | 0.035876
100 | 0.99744 | -0.10652 | 0 | 0
101 | 0.99743 | -0.10651 | 0.35704 | 0.17292
102 | 0.99763 | -0.10528 | 0 | 0
103 | 0.99641 | 0.0059061 | 0 | 0
104 | 0.99641 | 0.0059089 | 0.13036 | 0.063134
105 | 0.99644 | 0.0057176 | 0 | 0
106 | 0.99639 | 0.0061766 | 0 | 0
107 | 0.99636 | 0.0063777 | 0.19731 | 0.095564
108 | 0.99646 | 0.0055356 | 0.18173 | 0.088016
109 | 0.99763 | -0.10528 | 0.35008 | 0.16955
110 | 0.99635 | -0.14276 | 0.32186 | 0.15588
111 | 0.99635 | -0.14275 | 0 | 0
112 | 0.99632 | -0.14301 | 0 | 0
113 | 0.99633 | -0.1429 | 0 | 0
114 | 0.9964 | -0.13983 | 0.41527 | 0.20113
115 | 0.99632 | -0.14301 | 0.39818 | 0.19285
116 | 0.99633 | -0.1429 | 0.40188 | 0.19464
117 | 0.99641 | -0.13978 | 0 | 0
118 | 0.99641 | -0.13978 | 0 | 0
119 | 0.99641 | -0.13978 | 0.078236 | 0.037891
120 | 0.99642 | -0.13973 | 0 | 0
121 | 0.9964 | -0.1398 | 0 | 0
122 | 0.99643 | -0.13963 | 0 | 0
123 | 0.99641 | -0.13978 | 0.11042 | 0.053478
124 | 0.99278 | -0.025232 | 0.18849 | 0.091289
125 | 0.99278 | -0.025241 | 0 | 0
126 | 0.99067 | -0.0090363 | 0 | 0
127 | 0.99267 | -0.024279 | 0 | 0
128 | 0.99719 | 0.010476 | 0.27609 | 0.13372
129 | 0.99722 | 0.010185 | 0 | 0
130 | 0.99064 | -0.0092351 | 0.33044 | 0.16004
131 | 0.99266 | -0.024249 | 0.21584 | 0.10453
132 | 0.99636 | 0.0064526 | 0.2216 | 0.10733
133 | 0.9974 | -0.10066 | 0.34534 | 0.16725
134 | 0.9974 | -0.10066 | 0 | 0
135 | 0.9974 | -0.10067 | 0 | 0
136 | 0.99743 | -0.10049 | 0 | 0
137 | 0.9974 | -0.10069 | 0 | 0
138 | 0.99746 | -0.10033 | 0 | 0
139 | 0.99743 | -0.10049 | 0.39768 | 0.1926
140 | 0.99742 | -0.10066 | 0.087549 | 0.042402
141 | 0.99768 | -0.098152 | 0 | 0
142 | 0.99644 | -0.13952 | 0.17026 | 0.082463
143 | 0.99651 | -0.13499 | 0.09858 | 0.047745
144 | 0.99655 | -0.13251 | 0.56006 | 0.27125
145 | 0.99651 | -0.135 | 0.20352 | 0.098571
146 | 0.99656 | -0.13263 | 0 | 0
147 | 0.99657 | -0.13242 | 0 | 0
148 | 0.99655 | -0.13281 | 0 | 0
149 | 0.99657 | -0.13236 | 0 | 0
150 | 0.99655 | -0.13281 | 0.18992 | 0.091984
151 | 0.99683 | -0.13276 | 0.16887 | 0.081789
152 | 0.99683 | -0.13276 | 0 | 0
153 | 0.99685 | -0.13226 | 0 | 0
154 | 0.99691 | -0.13049 | 0 | 0
155 | 0.99685 | -0.13226 | 0.25725 | 0.12459
156 | 0.99686 | -0.131 | 0 | 0
157 | 0.99685 | -0.13108 | 0 | 0
158 | 0.99685 | -0.13101 | 0.36172 | 0.17519
159 | 0.99695 | -0.1297 | 0 | 0
160 | 0.99699 | -0.12896 | 0.077055 | 0.037319
161 | 0.99695 | -0.12972 | 0 | 0
162 | 0.99695 | -0.12973 | 0.1297 | 0.062816
163 | 0.99685 | -0.13109 | 0.080618 | 0.039045
164 | 0.99685 | -0.13102 | 0 | 0
165 | 0.99685 | -0.13106 | 0.16338 | 0.079126
166 | 0.99696 | -0.12949 | 0.26637 | 0.12901
167 | 0.9974 | -0.10093 | 0.31285 | 0.15152
168 | 0.99736 | -0.10128 | 0.38852 | 0.18817
169 | 0.99937 | -0.00676 | 0.33341 | 0.16148
170 | 0.99999 | -6.7131e-05 | 0 | 0
171 | 0.99684 | -0.13106 | 0 | 0
172 | 0.99682 | -0.13124 | 0.27053 | 0.13102
173 | 0.99998 | 3.4272e-05 | 0.077464 | 0.037518
174 | 0.99998 | 1.1478e-06 | 0 | 0
175 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.21418 | -0.10373 | 0.21418 | 0.10289 | 2.3694e-06 | -0.00084607 | 0.006974 | 0.0069632 | 0.006974 | 0.98507 | 0.017955 | 0.98508 | 0.01786 | 3.17
1 | -0.21418 | -0.10289 | 0.21421 | 0.093845 | 2.4872e-05 | -0.009042 | 0.0069632 | 0.0068526 | 0.0069632 | 0.98508 | 0.01786 | 0.98519 | 0.016966 | 3.1651
2 | -0.21421 | -0.093845 | 0.21421 | 0.093362 | 1.306e-06 | -0.00048282 | 0.0068526 | 0.0068469 | 0.0068526 | 0.98519 | 0.016966 | 0.9852 | 0.016925 | 3.1148
3 | 0.21343 | 0.10272 | -0.21343 | -0.10337 | 1.7903e-06 | -0.00064595 | 0.0069349 | 0.0069431 | 0.0069431 | 0.98598 | 0.023336 | 0.98597 | 0.023409 | 3.1559
4 | 0.29707 | 0.13193 | -0.29685 | -0.13339 | 0.00022189 | -0.0014524 | 0.0095169 | 0.0095359 | 0.0095359 | 0.98598 | 0.023336 | 0.9852 | 0.016925 | 4.5409
5 | -0.5105 | -0.23466 | 0.51067 | 0.22408 | 0.00016396 | -0.010573 | 0.01645 | 0.016322 | 0.01645 | 0.98598 | 0.023336 | 0.98628 | 0.021 | 7.4772
6 | 0.2244 | 0.10523 | -0.22439 | -0.10855 | 1.0098e-05 | -0.0033164 | 0.0072542 | 0.007296 | 0.007296 | 0.98628 | 0.021 | 0.98624 | 0.021378 | 3.3163
7 | -0.99272 | -0.44883 | 0.99276 | 0.4482 | 3.7717e-05 | -0.00063432 | 0.031888 | 0.03188 | 0.031888 | 0.98628 | 0.021 | 0.98632 | 0.02072 | 14.4944
8 | 0.25766 | 0.11952 | -0.25764 | -0.12471 | 2.0823e-05 | -0.0051948 | 0.0083132 | 0.0083784 | 0.0083784 | 0.98628 | 0.021 | 0.98621 | 0.021671 | 3.8084
9 | 0.078114 | 0.035643 | -0.078114 | -0.035723 | 2.9087e-08 | -8.0104e-05 | 0.002513 | 0.0025139 | 0.0025139 | 0.98633 | 0.013856 | 0.98633 | 0.013859 | 1.1427
10 | -0.33196 | -0.15859 | 0.33215 | 0.15766 | 0.00018484 | -0.00092531 | 0.010768 | 0.010754 | 0.010768 | 0.98633 | 0.013856 | 0.98691 | 0.01776 | 5.1274
11 | 0.078114 | 0.035723 | -0.078113 | -0.036888 | 4.2572e-07 | -0.0011653 | 0.0025139 | 0.0025283 | 0.0025283 | 0.98633 | 0.013859 | 0.98632 | 0.013902 | 1.1492
12 | 1.2824 | 0.58034 | -1.2823 | -0.5817 | 0.00013642 | -0.0013606 | 0.041174 | 0.041191 | 0.041191 | 0.98691 | 0.01776 | 0.98681 | 0.018551 | 18.723
13 | -1.6146 | -0.738 | 1.6172 | 0.72198 | 0.002584 | -0.016017 | 0.051927 | 0.051725 | 0.051927 | 0.98691 | 0.01776 | 0.9884 | 0.0059547 | 23.6031
14 | 0.078113 | 0.036888 | -0.078113 | -0.037832 | 3.4826e-07 | -0.00094336 | 0.0025283 | 0.0025402 | 0.0025402 | 0.98632 | 0.013902 | 0.98632 | 0.01394 | 1.1546
15 | -0.2597 | -0.12578 | 0.2597 | 0.12469 | 4.3934e-06 | -0.001087 | 0.0084165 | 0.0084027 | 0.0084165 | 0.9897 | -0.0015472 | 0.98972 | -0.0016932 | 3.8257
16 | 1.8623 | 0.82882 | -1.86 | -0.83948 | 0.0022963 | -0.01066 | 0.059455 | 0.05959 | 0.05959 | 0.98972 | -0.0016932 | 0.98857 | 0.0072291 | 27.0864
17 | -2.122 | -0.95351 | 2.1242 | 0.94589 | 0.0021669 | -0.0076221 | 0.067854 | 0.067756 | 0.067854 | 0.98972 | -0.0016932 | 0.99067 | -0.0090363 | 30.8429
18 | 1.86 | 0.83948 | -1.86 | -0.83956 | 1.5772e-05 | -7.2951e-05 | 0.05959 | 0.059591 | 0.059591 | 0.98857 | 0.0072291 | 0.98856 | 0.0072916 | 27.0868
19 | 1.6174 | 0.72208 | -1.6172 | -0.72198 | 0.00025153 | 9.6001e-05 | 0.051724 | 0.051725 | 0.051725 | 0.98856 | 0.0072916 | 0.9884 | 0.0059547 | 24.6308
20 | 1.0625 | 0.47522 | -1.0623 | -0.47522 | 0.00010843 | 6.896e-06 | 0.034048 | 0.034049 | 0.034049 | 0.98681 | 0.018551 | 0.9867 | 0.017679 | 16.2136
21 | -0.25763 | -0.12478 | 0.25764 | 0.12471 | 7.2032e-06 | -6.235e-05 | 0.0083793 | 0.0083784 | 0.0083793 | 0.98618 | 0.021486 | 0.98621 | 0.021671 | 3.9901
22 | 0.22439 | 0.10855 | -0.22438 | -0.10867 | 3.8693e-07 | -0.00012631 | 0.007296 | 0.0072976 | 0.0072976 | 0.98624 | 0.021378 | 0.98624 | 0.021393 | 3.3171
23 | -1.0619 | -0.48169 | 1.062 | 0.48079 | 6.1131e-05 | -0.00089539 | 0.034128 | 0.034117 | 0.034128 | 0.98632 | 0.02072 | 0.98637 | 0.020291 | 15.5127
24 | -1.062 | -0.48079 | 1.0623 | 0.47522 | 0.00037967 | -0.0055765 | 0.034117 | 0.034049 | 0.034117 | 0.98637 | 0.020291 | 0.9867 | 0.017679 | 15.5077
25 | -1.785 | -0.78913 | 1.7861 | 0.76508 | 0.0011192 | -0.024044 | 0.056526 | 0.056239 | 0.056526 | 0.99667 | -0.11485 | 0.99737 | -0.10605 | 15.615
26 | 1.5068 | 0.65449 | -1.505 | -0.66782 | 0.0017734 | -0.013327 | 0.047582 | 0.047744 | 0.047744 | 0.99667 | -0.11485 | 0.99556 | -0.10679 | 21.7016
27 | 0.27815 | 0.13463 | -0.27815 | -0.13471 | 3.7306e-07 | -8.2616e-05 | 0.0089504 | 0.0089515 | 0.0089515 | 0.99667 | -0.11485 | 0.99667 | -0.11484 | 4.0688
28 | -2.127 | -0.91958 | 2.1271 | 0.9163 | 7.3774e-05 | -0.0032777 | 0.06707 | 0.067032 | 0.06707 | 0.99737 | -0.10605 | 0.9974 | -0.10583 | 10.5126
29 | 0.3409 | 0.15449 | -0.34083 | -0.16497 | 7.0058e-05 | -0.010474 | 0.010833 | 0.010962 | 0.010962 | 0.99737 | -0.10605 | 0.99717 | -0.10439 | 4.9827
30 | 0.24867 | 0.11949 | -0.24867 | -0.12044 | 3.4223e-06 | -0.00094549 | 0.0079998 | 0.0080117 | 0.0080117 | 0.99556 | -0.10679 | 0.99555 | -0.10667 | 3.6417
31 | 1.2564 | 0.54833 | -1.2542 | -0.57209 | 0.0021953 | -0.023763 | 0.039748 | 0.040037 | 0.040037 | 0.99556 | -0.10679 | 0.99392 | -0.094287 | 18.1986
32 | -2.4091 | -1.0529 | 2.4092 | 1.0463 | 4.7351e-05 | -0.0065967 | 0.076096 | 0.076019 | 0.076096 | 0.9974 | -0.10583 | 0.99742 | -0.10571 | 5.9636
33 | 0.34083 | 0.16497 | -0.34082 | -0.16506 | 1.9365e-05 | -9.5222e-05 | 0.010962 | 0.010963 | 0.010963 | 0.99717 | -0.10439 | 0.99711 | -0.10476 | 5.2206
34 | 0.19273 | 0.087747 | -0.19273 | -0.08844 | 1.7033e-06 | -0.00069381 | 0.0061274 | 0.0061358 | 0.0061358 | 0.99767 | -0.10723 | 0.99765 | -0.10817 | 0.47564
35 | -0.19273 | -0.087747 | 0.19273 | 0.087554 | 4.7103e-07 | -0.00019221 | 0.0061274 | 0.0061251 | 0.0061274 | 0.99767 | -0.10723 | 0.99767 | -0.10697 | 0.47499
36 | 0.19273 | 0.08844 | -0.19273 | -0.093342 | 2.3017e-07 | -0.004902 | 0.0061358 | 0.0061963 | 0.0061963 | 0.99765 | -0.10817 | 0.99765 | -0.10817 | 0.4856
37 | -0.46505 | -0.21944 | 0.46505 | 0.21545 | 1.0895e-06 | -0.0039969 | 0.014879 | 0.01483 | 0.014879 | 0.99767 | -0.10697 | 0.99768 | -0.10696 | 1.1661
38 | -0.88011 | -0.39308 | 0.88011 | 0.39165 | 1.3697e-06 | -0.0014261 | 0.027888 | 0.027871 | 0.027888 | 0.99775 | -0.10313 | 0.99776 | -0.10312 | 2.1856
39 | 0.88011 | 0.39308 | -0.88008 | -0.39361 | 3.0901e-05 | -0.00052931 | 0.027888 | 0.027895 | 0.027895 | 0.99775 | -0.10313 | 0.99769 | -0.10688 | 2.1624
40 | -1.1337 | -0.51448 | 1.1338 | 0.51379 | 7.5222e-05 | -0.00069199 | 0.036021 | 0.03601 | 0.036021 | 0.99776 | -0.10312 | 0.99788 | -0.096067 | 2.7923
41 | 0.46505 | 0.19263 | -0.46505 | -0.21545 | 6.0851e-06 | -0.022813 | 0.014565 | 0.01483 | 0.01483 | 0.99769 | -0.10688 | 0.99768 | -0.10696 | 1.1622
42 | 0.41503 | 0.20097 | -0.41502 | -0.201 | 9.5046e-06 | -2.9653e-05 | 0.013343 | 0.013343 | 0.013343 | 0.99769 | -0.10688 | 0.99767 | -0.10704 | 6.3538
43 | 0.84917 | 0.37765 | -0.84868 | -0.38939 | 0.00049287 | -0.011737 | 0.026992 | 0.027135 | 0.027135 | 0.99392 | -0.094287 | 0.99338 | -0.09 | 12.3339
44 | 0.40499 | 0.19445 | -0.40498 | -0.19614 | 1.6398e-05 | -0.0016939 | 0.013048 | 0.01307 | 0.01307 | 0.99392 | -0.094287 | 0.99388 | -0.093937 | 5.9407
45 | 0.84868 | 0.38939 | -0.84794 | -0.40676 | 0.00074049 | -0.017375 | 0.027135 | 0.027352 | 0.027352 | 0.99338 | -0.09 | 0.99257 | -0.082924 | 12.4327
46 | 0.84794 | 0.40676 | -0.84787 | -0.40822 | 6.2563e-05 | -0.0014538 | 0.027352 | 0.02737 | 0.02737 | 0.99257 | -0.082924 | 0.9925 | -0.082293 | 12.4411
47 | -0.39351 | -0.19059 | 0.39352 | 0.18992 | 6.0998e-06 | -0.00066284 | 0.012718 | 0.01271 | 0.012718 | 0.9924 | -0.082442 | 0.99242 | -0.082576 | 5.7811
48 | -0.39352 | -0.18992 | 0.39354 | 0.18984 | 2.4699e-05 | -8.5442e-05 | 0.01271 | 0.012709 | 0.01271 | 0.99242 | -0.082576 | 0.99248 | -0.082157 | 6.0524
49 | -0.75995 | -0.36599 | 0.75996 | 0.36564 | 1.2021e-05 | -0.00034834 | 0.024534 | 0.024529 | 0.024534 | 0.99248 | -0.082157 | 0.9925 | -0.082293 | 11.1517
50 | 0.36641 | 0.17615 | -0.3664 | -0.17739 | 9.8748e-06 | -0.0012395 | 0.011825 | 0.011841 | 0.011841 | 0.99248 | -0.082157 | 0.99246 | -0.081924 | 5.3822
51 | 0.13704 | 0.066302 | -0.13703 | -0.066368 | 2.012e-06 | -6.6451e-05 | 0.004428 | 0.0044288 | 0.0044288 | 0.99246 | -0.081924 | 0.99244 | -0.082021 | 2.109
52 | -2.4092 | -1.0463 | 2.4095 | 1.0088 | 0.00026723 | -0.037485 | 0.076019 | 0.075592 | 0.076019 | 0.99742 | -0.10571 | 0.99754 | -0.10497 | 5.9576
53 | -1.3039 | -0.59616 | 1.3039 | 0.59599 | 2.7272e-05 | -0.0001712 | 0.041475 | 0.041472 | 0.041475 | 0.99788 | -0.096067 | 0.99792 | -0.093855 | 3.2152
54 | -2.0525 | -0.91681 | 2.0527 | 0.91661 | 0.00020951 | -0.00020043 | 0.065041 | 0.065032 | 0.065041 | 0.99773 | -0.10479 | 0.99792 | -0.093855 | 5.0419
55 | 2.0525 | 0.91681 | -2.0525 | -0.91997 | 1.6609e-05 | -0.0031677 | 0.065041 | 0.065079 | 0.065079 | 0.99773 | -0.10479 | 0.99772 | -0.10483 | 5.1002
56 | -6.2122 | -2.676 | 6.2155 | 2.6073 | 0.0033239 | -0.068777 | 0.19567 | 0.19487 | 0.19567 | 0.99792 | -0.093855 | 0.99848 | -0.090273 | 15.3346
57 | 2.8556 | 1.1634 | -2.855 | -1.2231 | 0.00059397 | -0.059673 | 0.089199 | 0.089868 | 0.089868 | 0.99792 | -0.093855 | 0.9977 | -0.095328 | 7.043
58 | 1.5387 | 0.6724 | -1.5387 | -0.67338 | 2.8639e-06 | -0.00098048 | 0.048585 | 0.048596 | 0.048596 | 0.99772 | -0.10483 | 0.99772 | -0.10484 | 3.8085
59 | 0.16534 | 0.078812 | -0.16534 | -0.080079 | 2.3268e-06 | -0.0012671 | 0.0052997 | 0.0053156 | 0.0053156 | 0.99772 | -0.10483 | 0.99769 | -0.10628 | 0.41206
60 | -0.43987 | -0.21243 | 0.43987 | 0.19627 | 3.9348e-06 | -0.016163 | 0.014136 | 0.013939 | 0.014136 | 0.99753 | -0.11058 | 0.99754 | -0.11053 | 1.1078
61 | 0.43987 | 0.21243 | -0.43987 | -0.21304 | 1.5037e-07 | -0.00060917 | 0.014136 | 0.014144 | 0.014144 | 0.99753 | -0.11058 | 0.99753 | -0.11058 | 1.1084
62 | 0.074075 | 0.02937 | -0.074075 | -0.035191 | 3.9322e-08 | -0.005821 | 0.002306 | 0.0023732 | 0.0023732 | 0.99754 | -0.11053 | 0.99754 | -0.11054 | 0.18599
63 | -0.51395 | -0.22564 | 0.51395 | 0.22551 | 2.1744e-06 | -0.00012118 | 0.016243 | 0.016242 | 0.016243 | 0.99754 | -0.11053 | 0.99755 | -0.11008 | 1.2592
64 | -0.37248 | -0.1804 | 0.37248 | 0.17985 | 4.4392e-06 | -0.00055184 | 0.011966 | 0.011959 | 0.011966 | 0.99847 | -0.09017 | 0.99848 | -0.090273 | 5.4389
65 | 8.6845 | 3.0816 | -8.6804 | -3.1253 | 0.0040298 | -0.043668 | 0.26642 | 0.26687 | 0.26687 | 0.99848 | -0.090273 | 0.99798 | -0.095123 | 20.9144
66 | -15.2725 | -5.8687 | 15.2843 | 5.8998 | 0.011845 | 0.031035 | 0.47303 | 0.47302 | 0.47303 | 0.99848 | -0.090273 | 0.99985 | -0.0011486 | 36.6689
67 | 0.12841 | 0.04477 | -0.12841 | -0.057637 | 2.5398e-07 | -0.012867 | 0.0039336 | 0.0040714 | 0.0040714 | 0.99798 | -0.095123 | 0.99798 | -0.095139 | 0.31907
68 | 0.4106 | 0.19852 | -0.4106 | -0.19887 | 7.3622e-08 | -0.00034226 | 0.013192 | 0.013197 | 0.013197 | 0.99798 | -0.095123 | 0.99798 | -0.095124 | 1.0342
69 | 8.1414 | 2.882 | -8.1401 | -2.8989 | 0.0013636 | -0.016917 | 0.24982 | 0.24999 | 0.24999 | 0.99798 | -0.095123 | 0.9978 | -0.096896 | 19.5916
70 | -19.5127 | -7.8109 | 19.5154 | 7.8063 | 0.0027849 | -0.0045828 | 0.60683 | 0.60676 | 0.60683 | 0.99985 | -0.0011486 | 1 | 0 | 47.557
71 | 4.2283 | 1.9111 | -4.2265 | -1.917 | 0.0018272 | -0.0058928 | 0.13397 | 0.13406 | 0.13406 | 0.99985 | -0.0011486 | 0.99937 | -0.0067784 | 37.0321
72 | 0.077466 | 0.034549 | -0.077465 | -0.034616 | 6.0492e-07 | -6.7203e-05 | 0.0024486 | 0.0024494 | 0.0024494 | 1 | 0 | 0.99999 | -6.7131e-05 | 1.1664
73 | 0.33341 | 0.16137 | -0.33341 | -0.16148 | 7.0298e-07 | -0.00010946 | 0.0107 | 0.010701 | 0.010701 | 0.99937 | -0.0067784 | 0.99937 | -0.00676 | 4.8641
74 | 3.8931 | 1.7556 | -3.8842 | -1.7634 | 0.0088995 | -0.0077733 | 0.12336 | 0.12348 | 0.12348 | 0.99937 | -0.0067784 | 0.99722 | 0.010185 | 56.1293
75 | 0.13285 | 0.063771 | -0.13285 | -0.064341 | 1.3001e-08 | -0.00057051 | 0.0042638 | 0.0042709 | 0.0042709 | 0.9977 | -0.095328 | 0.9977 | -0.095328 | 0.33471
76 | 2.7221 | 1.1594 | -2.7219 | -1.1592 | 0.0002392 | 0.00014017 | 0.085608 | 0.085614 | 0.085614 | 0.9977 | -0.095328 | 0.99754 | -0.10497 | 6.6368
77 | 0.31244 | 0.15037 | -0.31244 | -0.15103 | 8.222e-08 | -0.0006607 | 0.010034 | 0.010043 | 0.010043 | 0.99754 | -0.10497 | 0.99754 | -0.10497 | 0.78704
78 | 8.1401 | 2.8989 | -8.1397 | -2.9039 | 0.00040392 | -0.0050051 | 0.24999 | 0.25004 | 0.25004 | 0.9978 | -0.096896 | 0.99775 | -0.097417 | 19.5956
79 | 8.061 | 2.8658 | -8.0605 | -2.8729 | 0.00055758 | -0.007052 | 0.24753 | 0.2476 | 0.2476 | 0.99775 | -0.097417 | 0.99768 | -0.098146 | 19.4042
80 | 0.12841 | 0.057637 | -0.12841 | -0.062192 | 9.4453e-08 | -0.0045546 | 0.0040714 | 0.0041271 | 0.0041271 | 0.99798 | -0.095139 | 0.99798 | -0.095142 | 0.32344
81 | -0.21667 | -0.10494 | 0.21668 | 0.10466 | 7.9233e-06 | -0.0002836 | 0.0069673 | 0.0069636 | 0.0069673 | 0.99749 | -0.10661 | 0.99754 | -0.10497 | 1.6993
82 | 1.5387 | 0.67338 | -1.5386 | -0.71562 | 0.00012471 | -0.042246 | 0.048596 | 0.0491 | 0.0491 | 0.99772 | -0.10484 | 0.99763 | -0.10528 | 3.848
83 | 0.29217 | 0.10354 | -0.29217 | -0.10532 | 1.7791e-07 | -0.0017861 | 0.008969 | 0.0089864 | 0.0089864 | 0.99768 | -0.098146 | 0.99768 | -0.098152 | 0.70426
84 | 7.7683 | 2.7693 | -7.7667 | -2.7916 | 0.0016309 | -0.022241 | 0.23863 | 0.23885 | 0.23885 | 0.99768 | -0.098146 | 0.99746 | -0.10033 | 18.719
85 | 0.12791 | 0.032837 | -0.12791 | -0.038517 | 1.0358e-07 | -0.0056801 | 0.0038211 | 0.0038652 | 0.0038652 | 0.99766 | -0.099053 | 0.99766 | -0.099065 | 0.30292
86 | -0.22387 | -0.079314 | 0.22387 | 0.078779 | 1.6526e-06 | -0.00053537 | 0.0068723 | 0.0068671 | 0.0068723 | 0.99766 | -0.099053 | 0.99768 | -0.098174 | 0.53274
87 | 0.12791 | 0.038517 | -0.12791 | -0.060165 | 4.2079e-07 | -0.021648 | 0.0038652 | 0.0040901 | 0.0040901 | 0.99766 | -0.099065 | 0.99766 | -0.099094 | 0.32054
88 | -0.29217 | -0.11186 | 0.29217 | 0.10532 | 6.5641e-07 | -0.0065328 | 0.0090523 | 0.0089864 | 0.0090523 | 0.99768 | -0.098174 | 0.99768 | -0.098152 | 0.70942
89 | -0.38853 | -0.13938 | 0.38853 | 0.13924 | 1.3182e-06 | -0.00013877 | 0.011947 | 0.011946 | 0.011947 | 0.99739 | -0.10112 | 0.99739 | -0.10072 | 0.92612
90 | 0.38853 | 0.13938 | -0.38852 | -0.18703 | 8.7617e-06 | -0.047647 | 0.011947 | 0.01248 | 0.01248 | 0.99739 | -0.10112 | 0.99737 | -0.10127 | 0.97808
91 | -0.78799 | -0.33271 | 0.788 | 0.32918 | 2.6682e-06 | -0.0035267 | 0.024756 | 0.024717 | 0.024756 | 0.99739 | -0.10072 | 0.9974 | -0.10069 | 1.9402
92 | 0.38852 | 0.18703 | -0.38852 | -0.18817 | 2.2004e-07 | -0.0011415 | 0.01248 | 0.012495 | 0.012495 | 0.99737 | -0.10127 | 0.99736 | -0.10128 | 0.97921
93 | -0.12791 | -0.061949 | 0.12791 | 0.060165 | 3.7072e-08 | -0.0017844 | 0.0041123 | 0.0040901 | 0.0041123 | 0.99766 | -0.099095 | 0.99766 | -0.099094 | 0.32228
94 | 0.29548 | 0.14174 | -0.29548 | -0.14311 | 2.9834e-07 | -0.0013721 | 0.0094897 | 0.0095069 | 0.0095069 | 0.99692 | -0.12935 | 0.99692 | -0.12937 | 1.1291
95 | 3.3917 | 1.2575 | -3.3908 | -1.3191 | 0.00084836 | -0.061635 | 0.10474 | 0.10538 | 0.10538 | 0.99692 | -0.12935 | 0.99665 | -0.13164 | 8.2589
96 | -3.6872 | -1.3992 | 3.6875 | 1.3786 | 0.00033395 | -0.020553 | 0.1142 | 0.11399 | 0.1142 | 0.99692 | -0.12935 | 0.99701 | -0.1285 | 8.9497
97 | 3.0399 | 1.1538 | -3.0399 | -1.1547 | 1.0549e-05 | -0.00095489 | 0.094177 | 0.094187 | 0.094187 | 0.99665 | -0.13164 | 0.99665 | -0.13167 | 7.3815
98 | 0.35095 | 0.16531 | -0.35095 | -0.16786 | 3.9981e-07 | -0.0025513 | 0.011236 | 0.011268 | 0.011268 | 0.99665 | -0.13164 | 0.99665 | -0.13165 | 0.88308
99 | 1.7757 | 0.39198 | -1.7757 | -0.40462 | 4.3506e-05 | -0.012644 | 0.052652 | 0.052733 | 0.052733 | 0.99701 | -0.1285 | 0.99699 | -0.12895 | 4.1326
100 | -5.4632 | -1.7706 | 5.4635 | 1.7712 | 0.00028124 | 0.00059966 | 0.16628 | 0.16628 | 0.16628 | 0.99701 | -0.1285 | 0.9971 | -0.12219 | 12.8901
101 | 0.35095 | 0.16786 | -0.35095 | -0.16997 | 3.3256e-07 | -0.0021105 | 0.011268 | 0.011295 | 0.011295 | 0.99665 | -0.13165 | 0.99665 | -0.13165 | 0.88515
102 | 2.9487 | 1.1106 | -2.9487 | -1.1158 | 5.4298e-05 | -0.0052329 | 0.091265 | 0.091319 | 0.091319 | 0.99665 | -0.13167 | 0.99663 | -0.13185 | 7.1567
103 | 1.4323 | 0.24083 | -1.4322 | -0.26352 | 4.981e-05 | -0.022682 | 0.042053 | 0.042167 | 0.042167 | 0.99699 | -0.12895 | 0.99695 | -0.1297 | 3.3046
104 | 0.34343 | 0.16379 | -0.34343 | -0.16625 | 3.7057e-07 | -0.002461 | 0.011017 | 0.011048 | 0.011048 | 0.99699 | -0.12895 | 0.99699 | -0.12896 | 0.86582
105 | -5.8338 | -1.9506 | 5.8349 | 1.9528 | 0.0010221 | 0.0022522 | 0.17809 | 0.17808 | 0.17809 | 0.9971 | -0.12219 | 0.9974 | -0.10093 | 13.8053
106 | 2.9487 | 1.1158 | -2.9485 | -1.1317 | 0.00016534 | -0.015895 | 0.091319 | 0.091484 | 0.091484 | 0.99663 | -0.13185 | 0.99657 | -0.13236 | 7.1696
107 | 0.074075 | 0.035191 | -0.074075 | -0.035876 | 4.743e-09 | -0.00068455 | 0.0023732 | 0.0023818 | 0.0023818 | 0.99754 | -0.11054 | 0.99754 | -0.11054 | 0.18666
108 | -0.83135 | -0.37924 | 0.83139 | 0.37851 | 3.7672e-05 | -0.00072944 | 0.026443 | 0.026433 | 0.026443 | 0.99755 | -0.11008 | 0.99763 | -0.10528 | 2.0498
109 | 0.35704 | 0.17287 | -0.35704 | -0.17292 | 3.8731e-07 | -5.2167e-05 | 0.011481 | 0.011481 | 0.011481 | 0.99744 | -0.10652 | 0.99743 | -0.10651 | 5.2189
110 | -0.35704 | -0.17287 | 0.35711 | 0.17257 | 6.7263e-05 | -0.00029824 | 0.011481 | 0.011477 | 0.011481 | 0.99744 | -0.10652 | 0.99763 | -0.10528 | 5.4671
111 | 0.35008 | 0.16454 | -0.35008 | -0.16955 | 7.793e-07 | -0.0050073 | 0.011193 | 0.011255 | 0.011255 | 0.99763 | -0.10528 | 0.99763 | -0.10528 | 0.88208
112 | 0.13036 | 0.063092 | -0.13036 | -0.063134 | 4.1775e-08 | -4.2179e-05 | 0.0041957 | 0.0041962 | 0.0041962 | 0.99641 | 0.0059061 | 0.99641 | 0.0059089 | 1.9074
113 | -0.13036 | -0.063092 | 0.13036 | 0.060053 | 2.9856e-06 | -0.0030382 | 0.0041957 | 0.0041581 | 0.0041957 | 0.99641 | 0.0059061 | 0.99644 | 0.0057176 | 1.9071
114 | -0.54931 | -0.25909 | 0.54932 | 0.25839 | 1.2223e-05 | -0.00069781 | 0.017595 | 0.017587 | 0.017595 | 0.99644 | 0.0057176 | 0.99646 | 0.0055356 | 7.9978
115 | 0.41895 | 0.19904 | -0.41893 | -0.20126 | 2.276e-05 | -0.0022268 | 0.013437 | 0.013465 | 0.013465 | 0.99644 | 0.0057176 | 0.99639 | 0.0061766 | 6.1206
116 | 0.41893 | 0.20126 | -0.41892 | -0.20222 | 9.7897e-06 | -0.0009549 | 0.013465 | 0.013477 | 0.013477 | 0.99639 | 0.0061766 | 0.99636 | 0.0063777 | 6.1261
117 | 0.2216 | 0.10666 | -0.2216 | -0.10733 | 1.9192e-06 | -0.0006698 | 0.0071254 | 0.0071338 | 0.0071338 | 0.99636 | 0.0063777 | 0.99636 | 0.0064526 | 3.2426
118 | -0.73105 | -0.34641 | 0.73156 | 0.34611 | 0.00050494 | -0.000296 | 0.023436 | 0.023428 | 0.023436 | 0.99646 | 0.0055356 | 0.99719 | 0.010476 | 11.16
119 | -0.32186 | -0.15588 | 0.32186 | 0.15544 | 5.8871e-08 | -0.0004412 | 0.010361 | 0.010356 | 0.010361 | 0.99635 | -0.14276 | 0.99635 | -0.14275 | 0.81203
120 | 0.39819 | 0.127 | -0.39818 | -0.19226 | 1.2488e-05 | -0.06526 | 0.012109 | 0.012811 | 0.012811 | 0.99635 | -0.14275 | 0.99632 | -0.14301 | 1.004
121 | 0.40189 | 0.149 | -0.40188 | -0.19413 | 8.961e-06 | -0.045134 | 0.012418 | 0.012931 | 0.012931 | 0.99635 | -0.14275 | 0.99633 | -0.1429 | 1.0134
122 | -1.1219 | -0.43144 | 1.122 | 0.43115 | 2.8475e-05 | -0.00028444 | 0.034827 | 0.034823 | 0.034827 | 0.99635 | -0.14275 | 0.9964 | -0.13983 | 2.6997
123 | 0.39818 | 0.19226 | -0.39818 | -0.19285 | 1.1914e-07 | -0.00058534 | 0.012811 | 0.012819 | 0.012819 | 0.99632 | -0.14301 | 0.99632 | -0.14301 | 1.0046
124 | 0.40188 | 0.19413 | -0.40188 | -0.19464 | 1.0543e-07 | -0.00050839 | 0.012931 | 0.012938 | 0.012938 | 0.99633 | -0.1429 | 0.99633 | -0.1429 | 1.0139
125 | -1.5372 | -0.63228 | 1.5372 | 0.62983 | 7.0567e-06 | -0.0024546 | 0.048157 | 0.04813 | 0.048157 | 0.9964 | -0.13983 | 0.9964 | -0.1398 | 3.774
126 | 0.11042 | 0.051821 | -0.11042 | -0.053433 | 2.514e-08 | -0.0016118 | 0.0035338 | 0.0035538 | 0.0035538 | 0.99641 | -0.13978 | 0.99641 | -0.13978 | 0.27851
127 | 0.078236 | 0.03774 | -0.078236 | -0.037891 | 5.4021e-08 | -0.00015129 | 0.0025165 | 0.0025184 | 0.0025184 | 0.99641 | -0.13978 | 0.99641 | -0.13978 | 1.1447
128 | -0.18865 | -0.089561 | 0.18865 | 0.089522 | 9.3169e-08 | -3.8887e-05 | 0.0060502 | 0.0060497 | 0.0060502 | 0.99641 | -0.13978 | 0.99642 | -0.13973 | 0.46901
129 | 0.11042 | 0.053433 | -0.11042 | -0.053478 | 1.279e-09 | -4.5412e-05 | 0.0035538 | 0.0035544 | 0.0035544 | 0.99641 | -0.13978 | 0.99641 | -0.13978 | 0.27856
130 | -0.18865 | -0.089522 | 0.18866 | 0.046244 | 1.8082e-06 | -0.043278 | 0.0060497 | 0.0056274 | 0.0060497 | 0.99642 | -0.13973 | 0.99643 | -0.13963 | 0.47412
131 | -1.5372 | -0.62983 | 1.5373 | 0.61808 | 3.3657e-05 | -0.011745 | 0.04813 | 0.048002 | 0.04813 | 0.9964 | -0.1398 | 0.99643 | -0.13963 | 3.7719
132 | -1.7259 | -0.66432 | 1.726 | 0.6581 | 2.2129e-05 | -0.0062205 | 0.053578 | 0.053514 | 0.053578 | 0.99643 | -0.13963 | 0.99644 | -0.13952 | 4.1989
133 | -0.18849 | -0.091289 | 0.18849 | 0.091192 | 2.0357e-07 | -9.673e-05 | 0.0060897 | 0.0060885 | 0.0060897 | 0.99278 | -0.025232 | 0.99278 | -0.025241 | 2.768
134 | 2.4601 | 1.0916 | -2.4546 | -1.1059 | 0.005541 | -0.014232 | 0.078261 | 0.078449 | 0.078449 | 0.99278 | -0.025241 | 0.99067 | -0.0090363 | 35.6588
135 | 0.21586 | 0.094356 | -0.21584 | -0.10426 | 2.6858e-05 | -0.0099083 | 0.0068502 | 0.0069707 | 0.0069707 | 0.99278 | -0.025241 | 0.99267 | -0.024279 | 3.1685
136 | -2.8645 | -1.2772 | 2.8764 | 1.2837 | 0.0119 | 0.0065046 | 0.091196 | 0.091185 | 0.091196 | 0.99278 | -0.025241 | 0.99719 | 0.010476 | 43.4268
137 | 0.33045 | 0.15999 | -0.33044 | -0.16004 | 9.9574e-06 | -5.0969e-05 | 0.010698 | 0.010699 | 0.010699 | 0.99067 | -0.0090363 | 0.99064 | -0.0092351 | 5.0947
138 | 0.21584 | 0.10426 | -0.21584 | -0.10453 | 7.4695e-07 | -0.00027055 | 0.0069707 | 0.0069741 | 0.0069741 | 0.99267 | -0.024279 | 0.99266 | -0.024249 | 3.1701
139 | -3.884 | -1.7635 | 3.8842 | 1.7634 | 0.00015152 | -0.00013177 | 0.12349 | 0.12348 | 0.12349 | 0.99719 | 0.010476 | 0.99722 | 0.010185 | 56.1302
140 | -1.1333 | -0.49229 | 1.1333 | 0.49148 | 1.2741e-06 | -0.00080561 | 0.035763 | 0.035753 | 0.035763 | 0.9974 | -0.10066 | 0.9974 | -0.10066 | 2.8027
141 | 0.788 | 0.32504 | -0.788 | -0.32591 | 6.5532e-07 | -0.00087046 | 0.024671 | 0.02468 | 0.02468 | 0.9974 | -0.10066 | 0.9974 | -0.10067 | 1.9342
142 | -1.1333 | -0.49148 | 1.1334 | 0.47334 | 2.8518e-05 | -0.018141 | 0.035753 | 0.035548 | 0.035753 | 0.9974 | -0.10066 | 0.99743 | -0.10049 | 2.802
143 | 0.788 | 0.32591 | -0.788 | -0.32918 | 2.472e-06 | -0.0032775 | 0.02468 | 0.024717 | 0.024717 | 0.9974 | -0.10067 | 0.9974 | -0.10069 | 1.9371
144 | -1.531 | -0.66484 | 1.5311 | 0.65203 | 3.6895e-05 | -0.012811 | 0.048309 | 0.048162 | 0.048309 | 0.99743 | -0.10049 | 0.99746 | -0.10033 | 3.786
145 | 0.39768 | 0.1915 | -0.39768 | -0.1926 | 2.2275e-07 | -0.0011034 | 0.012775 | 0.012788 | 0.012788 | 0.99743 | -0.10049 | 0.99743 | -0.10049 | 1.0022
146 | 6.2356 | 2.1395 | -6.2354 | -2.1434 | 0.00017981 | -0.0038951 | 0.19079 | 0.19083 | 0.19083 | 0.99746 | -0.10033 | 0.99742 | -0.10066 | 14.9553
147 | 6.1479 | 2.101 | -6.1477 | -2.1043 | 0.00014818 | -0.003307 | 0.18804 | 0.18807 | 0.18807 | 0.99742 | -0.10066 | 0.9974 | -0.10093 | 14.7388
148 | -1.8962 | -0.74057 | 1.8963 | 0.74044 | 7.5051e-05 | -0.00013005 | 0.058976 | 0.058972 | 0.058976 | 0.99644 | -0.13952 | 0.99651 | -0.13499 | 4.5718
149 | -2.1984 | -0.8838 | 2.1984 | 0.88377 | 4.8471e-05 | -2.7904e-05 | 0.068638 | 0.068637 | 0.068638 | 0.99651 | -0.13499 | 0.99655 | -0.13251 | 5.3208
150 | 0.20352 | 0.09562 | -0.20352 | -0.098571 | 1.5589e-07 | -0.0029509 | 0.0065141 | 0.0065509 | 0.0065509 | 0.99651 | -0.13499 | 0.99651 | -0.135 | 0.51339
151 | -2.7585 | -1.155 | 2.7586 | 1.1488 | 5.8373e-05 | -0.0062553 | 0.086629 | 0.086559 | 0.086629 | 0.99655 | -0.13251 | 0.99657 | -0.13236 | 6.7891
152 | -0.18993 | -0.029014 | 0.18993 | -0.0073517 | 1.3671e-06 | -0.036366 | 0.0055654 | 0.0055057 | 0.0055654 | 0.99656 | -0.13263 | 0.99657 | -0.13242 | 0.43616
153 | 0.18993 | 0.029014 | -0.18992 | -0.09155 | 2.5794e-06 | -0.062536 | 0.0055654 | 0.0061074 | 0.0061074 | 0.99656 | -0.13263 | 0.99655 | -0.13281 | 0.47864
154 | -0.18993 | 0.0073517 | 0.18993 | -0.017061 | 3.6534e-07 | -0.0097098 | 0.0055057 | 0.0055237 | 0.0055237 | 0.99657 | -0.13242 | 0.99657 | -0.13236 | 0.4329
155 | 0.18992 | 0.09155 | -0.18992 | -0.091984 | 2.0105e-08 | -0.00043391 | 0.0061074 | 0.0061129 | 0.0061129 | 0.99655 | -0.13281 | 0.99655 | -0.13281 | 0.47907
156 | -0.16887 | -0.081789 | 0.16887 | 0.08088 | 3.3108e-08 | -0.00090852 | 0.0054338 | 0.0054224 | 0.0054338 | 0.99683 | -0.13276 | 0.99683 | -0.13276 | 0.42585
157 | -0.16887 | -0.08088 | 0.16888 | -0.035586 | 3.5085e-06 | -0.11647 | 0.0054224 | 0.0049979 | 0.0054224 | 0.99683 | -0.13276 | 0.99685 | -0.13226 | 0.42496
158 | -0.42613 | -0.088107 | 0.42616 | -0.04747 | 2.5603e-05 | -0.13558 | 0.012601 | 0.012417 | 0.012601 | 0.99685 | -0.13226 | 0.99691 | -0.13049 | 0.98756
159 | 0.25725 | 0.12369 | -0.25725 | -0.12459 | 7.6382e-08 | -0.00090142 | 0.0082662 | 0.0082775 | 0.0082775 | 0.99685 | -0.13226 | 0.99685 | -0.13226 | 0.64871
160 | -1.3025 | -0.25019 | 1.3025 | 0.22346 | 4.8642e-05 | -0.026731 | 0.038405 | 0.038266 | 0.038405 | 0.99691 | -0.13049 | 0.99695 | -0.1297 | 3.0098
161 | 0.8763 | 0.29766 | -0.87625 | -0.34779 | 4.5368e-05 | -0.050124 | 0.026799 | 0.027301 | 0.027301 | 0.99691 | -0.13049 | 0.99686 | -0.131 | 2.1396
162 | 0.080619 | -0.01042 | -0.080618 | -0.028608 | 2.6653e-07 | -0.039027 | 0.002354 | 0.0024772 | 0.0024772 | 0.99686 | -0.131 | 0.99685 | -0.13108 | 0.19414
163 | 0.79563 | 0.35821 | -0.79563 | -0.36062 | 1.9109e-06 | -0.0024152 | 0.025268 | 0.025297 | 0.025297 | 0.99686 | -0.131 | 0.99685 | -0.13101 | 1.9825
164 | 0.080618 | 0.028608 | -0.080618 | -0.039045 | 8.276e-08 | -0.010438 | 0.0024772 | 0.002594 | 0.002594 | 0.99685 | -0.13108 | 0.99685 | -0.13109 | 0.20329
165 | 0.27054 | 0.10635 | -0.27054 | -0.10814 | 1.5699e-07 | -0.001787 | 0.008418 | 0.0084371 | 0.0084371 | 0.99685 | -0.13101 | 0.99685 | -0.13102 | 0.66121
166 | 0.16338 | 0.079083 | -0.16338 | -0.079126 | 1.6571e-07 | -4.3046e-05 | 0.0052563 | 0.0052568 | 0.0052568 | 0.99685 | -0.13101 | 0.99685 | -0.13106 | 0.64108
167 | 0.1297 | 0.040052 | -0.1297 | -0.056249 | 3.2154e-07 | -0.016197 | 0.0039306 | 0.0040936 | 0.0040936 | 0.99695 | -0.1297 | 0.99695 | -0.12972 | 0.32081
168 | 0.26638 | 0.12893 | -0.26637 | -0.12901 | 4.6687e-06 | -8.1161e-05 | 0.0085689 | 0.00857 | 0.00857 | 0.99699 | -0.12896 | 0.99696 | -0.12949 | 2.4486
169 | 0.1297 | 0.056249 | -0.1297 | -0.062816 | 1.3874e-07 | -0.0065672 | 0.0040936 | 0.0041729 | 0.0041729 | 0.99695 | -0.12972 | 0.99695 | -0.12973 | 0.32703
170 | 0.27054 | 0.10814 | -0.27054 | -0.13096 | 2.0717e-06 | -0.022823 | 0.0084371 | 0.0087041 | 0.0087041 | 0.99685 | -0.13102 | 0.99684 | -0.13106 | 0.68214
171 | 0.077465 | 0.034616 | -0.077465 | -0.036638 | 6.8496e-07 | -0.0020217 | 0.0024494 | 0.0024738 | 0.0024738 | 0.99999 | -6.7131e-05 | 0.99998 | 1.1478e-06 | 1.1244
172 | 0.27054 | 0.13096 | -0.27053 | -0.13102 | 7.5108e-06 | -6.1295e-05 | 0.0087041 | 0.0087049 | 0.0087049 | 0.99684 | -0.13106 | 0.99682 | -0.13124 | 4.1452
173 | -0.077464 | -0.037518 | 0.077465 | 0.036638 | 3.0242e-07 | -0.00087985 | 0.0024847 | 0.0024738 | 0.0024847 | 0.99998 | 3.4272e-05 | 0.99998 | 1.1478e-06 | 1.1294

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 19.9249 | 8.0053

## res_load
| p_mw | q_mvar
0 | 0.21418 | 0.10373
1 | 0.21343 | 0.10337
2 | 0.08264 | 0.040024
3 | 0.25385 | 0.12294
4 | 0.2597 | 0.12578
5 | 0.24256 | 0.11748
6 | 0.21984 | 0.10647
7 | 0.25763 | 0.12478
8 | 0.069149 | 0.033491
9 | 0.22438 | 0.10867
10 | 0.078113 | 0.037832
11 | 0.27815 | 0.13471
12 | 0.28209 | 0.13662
13 | 0.27231 | 0.13189
14 | 0.2536 | 0.12283
15 | 0.24867 | 0.12044
16 | 0.40498 | 0.19614
17 | 0.39351 | 0.19059
18 | 0.08791 | 0.042577
19 | 0.22937 | 0.11109
20 | 0.13703 | 0.066368
21 | 0.34082 | 0.16506
22 | 0.17008 | 0.082374
23 | 0.34846 | 0.16877
24 | 0.41502 | 0.201
25 | 0.43987 | 0.21304
26 | 0.19273 | 0.093342
27 | 0.37248 | 0.1804
28 | 0.31794 | 0.15399
29 | 0.13285 | 0.064341
30 | 0.078629 | 0.038082
31 | 0.4106 | 0.19887
32 | 0.21667 | 0.10494
33 | 0.095759 | 0.046378
34 | 0.16534 | 0.080079
35 | 0.095963 | 0.046477
36 | 0.068296 | 0.033077
37 | 0.12841 | 0.062192
38 | 0.39946 | 0.19347
39 | 0.12791 | 0.061949
40 | 0.29548 | 0.14311
41 | 0.35095 | 0.16997
42 | 0.091168 | 0.044155
43 | 0.37031 | 0.17935
44 | 0.3174 | 0.15372
45 | 0.074075 | 0.035876
46 | 0.35704 | 0.17292
47 | 0.13036 | 0.063134
48 | 0.19731 | 0.095564
49 | 0.18173 | 0.088016
50 | 0.35008 | 0.16955
51 | 0.32186 | 0.15588
52 | 0.41527 | 0.20113
53 | 0.39818 | 0.19285
54 | 0.40188 | 0.19464
55 | 0.078236 | 0.037891
56 | 0.11042 | 0.053478
57 | 0.18849 | 0.091289
58 | 0.27609 | 0.13372
59 | 0.33044 | 0.16004
60 | 0.21584 | 0.10453
61 | 0.2216 | 0.10733
62 | 0.34534 | 0.16725
63 | 0.39768 | 0.1926
64 | 0.087549 | 0.042402
65 | 0.17026 | 0.082463
66 | 0.09858 | 0.047745
67 | 0.56006 | 0.27125
68 | 0.20352 | 0.098571
69 | 0.18992 | 0.091984
70 | 0.16887 | 0.081789
71 | 0.25725 | 0.12459
72 | 0.36172 | 0.17519
73 | 0.077055 | 0.037319
74 | 0.1297 | 0.062816
75 | 0.080618 | 0.039045
76 | 0.16338 | 0.079126
77 | 0.26637 | 0.12901
78 | 0.31285 | 0.15152
79 | 0.38852 | 0.18817
80 | 0.33341 | 0.16148
81 | 0.27053 | 0.13102
82 | 0.077464 | 0.037518

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1