## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_35_1_node_67 | 20 | n |  | TRUE
1 | bus_MV_35_1_node_52 | 20 | n |  | TRUE
2 | bus_MV_35_1_node_54 | 20 | n |  | TRUE
3 | bus_MV_35_1_node_152 | 20 | n |  | TRUE
4 | bus_MV_35_1_node_9 | 20 | n |  | TRUE
5 | bus_MV_35_1_node_10 | 20 | n |  | TRUE
6 | bus_MV_35_1_node_11 | 20 | n |  | TRUE
7 | bus_MV_35_1_node_124 | 20 | n |  | TRUE
8 | bus_MV_35_1_node_125 | 20 | n |  | TRUE
9 | bus_MV_35_1_node_12 | 20 | n |  | TRUE
10 | bus_MV_35_1_node_127 | 20 | n |  | TRUE
11 | bus_MV_35_1_node_132 | 20 | n |  | TRUE
12 | bus_MV_35_1_node_126 | 20 | n |  | TRUE
13 | bus_MV_35_1_node_48 | 20 | n |  | TRUE
14 | bus_MV_35_1_node_49 | 20 | n |  | TRUE
15 | bus_MV_35_1_node_51 | 20 | n |  | TRUE
16 | bus_MV_35_1_node_53 | 20 | n |  | TRUE
17 | bus_MV_35_1_node_68 | 20 | n |  | TRUE
18 | bus_MV_35_1_node_150 | 20 | n |  | TRUE
19 | bus_MV_35_1_node_69 | 20 | n |  | TRUE
20 | bus_MV_35_1_node_55 | 20 | n |  | TRUE
21 | bus_MV_35_1_node_57 | 20 | n |  | TRUE
22 | bus_MV_35_1_node_66 | 20 | n |  | TRUE
23 | bus_MV_35_1_node_59 | 20 | n |  | TRUE
24 | bus_MV_35_1_node_60 | 20 | n |  | TRUE
25 | bus_MV_35_1_node_58 | 20 | n |  | TRUE
26 | bus_MV_35_1_node_63 | 20 | n |  | TRUE
27 | bus_MV_35_1_node_62 | 20 | n |  | TRUE
28 | bus_MV_35_1_node_64 | 20 | n |  | TRUE
29 | bus_MV_35_1_node_70 | 20 | n |  | TRUE
30 | bus_MV_35_1_node_90 | 20 | n |  | TRUE
31 | bus_MV_35_1_node_182 | 20 | n |  | TRUE
32 | bus_MV_35_1_node_154 | 20 | n |  | TRUE
33 | bus_MV_35_1_node_61 | 20 | n |  | TRUE
34 | bus_MV_35_1_node_65 | 20 | n |  | TRUE
35 | bus_MV_35_1_node_91 | 20 | n |  | TRUE
36 | bus_MV_35_1_node_72 | 20 | n |  | TRUE
37 | bus_MV_35_1_node_153 | 20 | n |  | TRUE
38 | bus_MV_35_1_node_71 | 20 | n |  | TRUE
39 | bus_MV_35_1_node_83 | 20 | n |  | TRUE
40 | bus_MV_35_1_node_85 | 20 | n |  | TRUE
41 | bus_MV_35_1_node_89 | 20 | n |  | TRUE
42 | bus_MV_35_1_node_87 | 20 | n |  | TRUE
43 | bus_MV_35_1_node_88 | 20 | n |  | TRUE
44 | bus_MV_35_1_node_97 | 20 | n |  | TRUE
45 | bus_MV_35_1_node_93 | 20 | n |  | TRUE
46 | bus_MV_35_1_node_94 | 20 | n |  | TRUE
47 | bus_MV_35_1_node_96 | 20 | n |  | TRUE
48 | bus_MV_35_1_node_98 | 20 | n |  | TRUE
49 | bus_MV_35_1_node_177 | 20 | n |  | TRUE
50 | bus_MV_35_1_node_160 | 20 | n |  | TRUE
51 | bus_MV_35_1_node_190 | 20 | n |  | TRUE
52 | bus_MV_35_1_node_92 | 20 | n |  | TRUE
53 | bus_MV_35_1_node_95 | 20 | n |  | TRUE
54 | bus_MV_35_1_node_155 | 20 | n |  | TRUE
55 | bus_MV_35_1_node_114 | 20 | n |  | TRUE
56 | bus_MV_35_1_node_189 | 20 | n |  | TRUE
57 | bus_MV_35_1_node_123 | 20 | n |  | TRUE
58 | bus_MV_35_1_node_102 | 20 | n |  | TRUE
59 | bus_MV_35_1_node_122 | 20 | n |  | TRUE
60 | bus_MV_35_1_node_101 | 20 | n |  | TRUE
61 | bus_MV_35_1_node_104 | 20 | n |  | TRUE
62 | bus_MV_35_1_node_172 | 20 | n |  | TRUE
63 | bus_MV_35_1_node_171 | 20 | n |  | TRUE
64 | bus_MV_35_1_node_103 | 20 | n |  | TRUE
65 | bus_MV_35_1_node_111 | 20 | n |  | TRUE
66 | bus_MV_35_1_node_113 | 20 | n |  | TRUE
67 | bus_MV_35_1_node_121 | 20 | n |  | TRUE
68 | bus_MV_35_1_node_112 | 20 | n |  | TRUE
69 | bus_MV_35_1_node_108 | 20 | n |  | TRUE
70 | bus_MV_35_1_node_176 | 20 | n |  | TRUE
71 | bus_MV_35_1_node_175 | 20 | n |  | TRUE
72 | bus_MV_35_1_node_116 | 20 | n |  | TRUE
73 | bus_MV_35_1_node_115 | 20 | n |  | TRUE
74 | bus_MV_35_1_node_117 | 20 | n |  | TRUE
75 | bus_MV_35_1_node_118 | 20 | n |  | TRUE
76 | bus_MV_35_1_node_119 | 20 | n |  | TRUE
77 | bus_MV_35_1_node_120 | 20 | n |  | TRUE
78 | bus_MV_35_1_node_167 | 20 | n |  | TRUE
79 | bus_MV_35_1_node_174 | 20 | n |  | TRUE
80 | bus_MV_35_1_node_168 | 20 | n |  | TRUE
81 | bus_MV_35_1_node_169 | 20 | n |  | TRUE
82 | bus_MV_35_1_node_170 | 20 | n |  | TRUE
83 | bus_MV_35_1_node_173 | 20 | n |  | TRUE
84 | bus_MV_35_1_node_99 | 20 | n |  | TRUE
85 | bus_MV_35_1_node_100 | 20 | n |  | TRUE
86 | bus_MV_35_1_node_105 | 20 | n |  | TRUE
87 | bus_MV_35_1_node_193 | 20 | n |  | TRUE
88 | bus_MV_35_1_node_131 | 20 | n |  | TRUE
89 | bus_MV_35_1_node_106 | 20 | n |  | TRUE
90 | bus_MV_35_1_node_107 | 20 | n |  | TRUE
91 | bus_MV_35_1_node_109 | 20 | n |  | TRUE
92 | bus_MV_35_1_node_110 | 20 | n |  | TRUE
93 | bus_MV_35_1_node_166 | 20 | n |  | TRUE
94 | bus_MV_35_1_node_157 | 20 | n |  | TRUE
95 | bus_MV_35_1_node_161 | 20 | n |  | TRUE
96 | bus_MV_35_1_node_165 | 20 | n |  | TRUE
97 | bus_MV_35_1_node_158 | 20 | n |  | TRUE
98 | bus_MV_35_1_node_156 | 20 | n |  | TRUE
99 | bus_MV_35_1_node_181 | 20 | n |  | TRUE
100 | bus_MV_35_1_node_180 | 20 | n |  | TRUE
101 | bus_MV_35_1_node_128 | 20 | n |  | TRUE
102 | bus_MV_35_1_node_129 | 20 | n |  | TRUE
103 | bus_MV_35_1_node_130 | 20 | n |  | TRUE
104 | bus_MV_35_1_node_179 | 20 | n |  | TRUE
105 | bus_MV_35_1_node_178 | 20 | n |  | TRUE
106 | bus_MV_35_1_node_151 | 20 | n |  | TRUE
107 | bus_MV_35_1_node_159 | 20 | n |  | TRUE
108 | bus_MV_35_1_node_162 | 20 | n |  | TRUE
109 | bus_MV_35_1_node_163 | 20 | n |  | TRUE
110 | bus_MV_35_1_node_164 | 20 | n |  | TRUE
111 | bus_HV_35_1_node_87 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_35_1_load_67 | 0 | 0.2321 | 0.11241 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_35_1_load_54 | 2 | 0.10053 | 0.048688 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_35_1_load_9 | 4 | 0.16224 | 0.078577 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_35_1_load_124 | 7 | 0.091285 | 0.044211 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_35_1_load_127 | 10 | 0.35027 | 0.16965 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_35_1_load_132 | 11 | 0.091396 | 0.044265 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_35_1_load_48 | 13 | 0.27344 | 0.13243 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_35_1_load_68 | 17 | 0.17981 | 0.087085 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_35_1_load_150 | 18 | 0.12582 | 0.060937 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_35_1_load_55 | 20 | 0.31026 | 0.15027 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_35_1_load_66 | 22 | 0.256 | 0.12399 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_35_1_load_70 | 29 | 0.20599 | 0.099764 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_35_1_load_90 | 30 | 0.11586 | 0.056113 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_35_1_load_182 | 31 | 0.15037 | 0.072827 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_35_1_load_154 | 32 | 0.13969 | 0.067656 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_35_1_load_61 | 33 | 0.27133 | 0.13141 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_35_1_load_65 | 34 | 0.31084 | 0.15055 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_35_1_load_71 | 38 | 0.22656 | 0.10973 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_35_1_load_83 | 39 | 0.35058 | 0.1698 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_35_1_load_97 | 44 | 0.075556 | 0.036593 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_35_1_load_94 | 46 | 0.29625 | 0.14348 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_35_1_load_96 | 47 | 0.21962 | 0.10637 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_35_1_load_98 | 48 | 0.075044 | 0.036346 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_35_1_load_177 | 49 | 0.07158 | 0.034668 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_35_1_load_190 | 51 | 0.32775 | 0.15873 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_35_1_load_155 | 54 | 0.089859 | 0.043521 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_35_1_load_114 | 55 | 0.073732 | 0.03571 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_35_1_load_189 | 56 | 0.27104 | 0.13127 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_35_1_load_102 | 58 | 0.31043 | 0.15035 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_35_1_load_122 | 59 | 0.053497 | 0.02591 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_35_1_load_172 | 62 | 0.10636 | 0.051511 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_35_1_load_171 | 63 | 0.16508 | 0.079954 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_35_1_load_121 | 67 | 0.27157 | 0.13153 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_35_1_load_176 | 70 | 0.27431 | 0.13285 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_35_1_load_175 | 71 | 0.1214 | 0.058794 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_35_1_load_117 | 74 | 0.15289 | 0.074049 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_35_1_load_118 | 75 | 0.097208 | 0.04708 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_35_1_load_119 | 76 | 0.09384 | 0.045449 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_35_1_load_120 | 77 | 0.30955 | 0.14992 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_35_1_load_167 | 78 | 0.10586 | 0.051272 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_35_1_load_174 | 79 | 0.096513 | 0.046743 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_35_1_load_168 | 80 | 0.20637 | 0.099952 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_35_1_load_169 | 81 | 0.16085 | 0.077905 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_35_1_load_173 | 83 | 0.182 | 0.088145 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_35_1_load_99 | 84 | 0.25154 | 0.12183 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_35_1_load_193 | 87 | 0.25704 | 0.12449 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_35_1_load_106 | 89 | 0.21968 | 0.1064 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_35_1_load_166 | 93 | 0.53969 | 0.26139 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_35_1_load_161 | 95 | 0.1128 | 0.054631 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_35_1_load_156 | 98 | 0.098321 | 0.047619 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_35_1_load_181 | 99 | 0.23987 | 0.11617 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_35_1_load_180 | 100 | 0.20087 | 0.097288 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_35_1_load_128 | 101 | 0.14208 | 0.068812 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_35_1_load_179 | 104 | 0.082236 | 0.039829 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_35_1_load_178 | 105 | 0.11638 | 0.056367 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_35_1_load_151 | 106 | 0.25811 | 0.12501 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_35_1_load_159 | 107 | 0.45125 | 0.21855 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_35_1_load_162 | 108 | 0.31991 | 0.15494 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_35_1_load_163 | 109 | 1.3027 | 0.63093 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_35_1_line_0 |  | 0 | 1 | 0.1221 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_35_1_line_1 |  | 1 | 16 | 0.17893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_35_1_line_2 |  | 2 | 3 | 1.4608 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_35_1_line_3 |  | 3 | 37 | 0.068177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_35_1_line_4 |  | 3 | 106 | 0.14001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_35_1_line_5 |  | 4 | 5 | 0.022383 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_35_1_line_6 |  | 5 | 6 | 0.60164 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_35_1_line_7 |  | 6 | 9 | 0.50172 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_35_1_line_8 |  | 6 | 10 | 0.040863 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_35_1_line_9 |  | 7 | 8 | 0.008475 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_35_1_line_10 |  | 7 | 9 | 0.55026 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_35_1_line_11 |  | 8 | 12 | 0.35391 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_35_1_line_12 |  | 9 | 11 | 0.13866 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_35_1_line_13 |  | 12 | 99 | 0.011875 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_35_1_line_14 |  | 13 | 14 | 0.08153 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_35_1_line_15 |  | 14 | 15 | 0.54603 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_35_1_line_16 |  | 14 | 16 | 0.34856 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_35_1_line_17 |  | 15 | 17 | 0.09348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_35_1_line_18 |  | 16 | 18 | 0.0077314 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_35_1_line_19 |  | 17 | 19 | 0.14774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_35_1_line_20 |  | 19 | 26 | 0.18156 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_35_1_line_21 |  | 20 | 21 | 0.068669 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_35_1_line_22 |  | 20 | 22 | 0.31246 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_35_1_line_23 |  | 21 | 23 | 0.82312 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_35_1_line_24 |  | 21 | 24 | 1.3308 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_35_1_line_25 |  | 22 | 28 | 0.059113 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_35_1_line_26 |  | 23 | 30 | 0.11384 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_35_1_line_27 |  | 24 | 31 | 0.18481 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_35_1_line_28 |  | 25 | 26 | 0.24548 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_35_1_line_29 |  | 25 | 27 | 0.30273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_35_1_line_30 |  | 25 | 28 | 0.22029 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_35_1_line_31 |  | 25 | 29 | 0.050114 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_35_1_line_32 |  | 26 | 32 | 0.046252 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_35_1_line_33 |  | 27 | 33 | 0.031233 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_35_1_line_34 |  | 28 | 34 | 0.03652 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_35_1_line_35 |  | 30 | 35 | 0.016052 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_35_1_line_36 |  | 31 | 36 | 1.7229 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_35_1_line_37 |  | 32 | 37 | 0.055822 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_35_1_line_38 |  | 35 | 43 | 0.86427 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_35_1_line_39 |  | 36 | 38 | 0.037536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_35_1_line_40 |  | 39 | 40 | 0.066541 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_35_1_line_41 |  | 40 | 41 | 0.77049 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_35_1_line_42 |  | 41 | 47 | 0.030044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_35_1_line_43 |  | 41 | 43 | 1.0242 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_35_1_line_44 |  | 42 | 43 | 0.91894 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
45 | MV_35_1_line_45 |  | 42 | 44 | 0.016913 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_35_1_line_46 |  | 43 | 45 | 0.77511 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
47 | MV_35_1_line_47 |  | 43 | 46 | 0.087107 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_35_1_line_48 |  | 45 | 51 | 0.049302 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_35_1_line_49 |  | 45 | 52 | 0.37293 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
50 | MV_35_1_line_50 |  | 48 | 49 | 0.96655 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_35_1_line_51 |  | 49 | 50 | 0.057012 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_35_1_line_52 |  | 50 | 97 | 0.15876 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_35_1_line_53 |  | 51 | 60 | 0.12623 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_35_1_line_54 |  | 52 | 53 | 0.41249 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
55 | MV_35_1_line_55 |  | 52 | 54 | 0.022516 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_35_1_line_56 |  | 53 | 55 | 0.20968 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
57 | MV_35_1_line_57 |  | 53 | 56 | 0.09302 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_35_1_line_58 |  | 55 | 72 | 0.070099 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
59 | MV_35_1_line_59 |  | 56 | 68 | 0.022423 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_35_1_line_60 |  | 57 | 58 | 0.5315 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_35_1_line_61 |  | 57 | 59 | 0.14248 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_35_1_line_62 |  | 58 | 64 | 0.029498 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_35_1_line_63 |  | 60 | 85 | 0.12131 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_35_1_line_64 |  | 61 | 62 | 0.010153 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_35_1_line_65 |  | 61 | 63 | 0.01523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_35_1_line_66 |  | 61 | 64 | 0.28277 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_35_1_line_67 |  | 62 | 83 | 0.012874 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_35_1_line_68 |  | 63 | 82 | 0.03732 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_35_1_line_69 |  | 64 | 86 | 1.2328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_35_1_line_70 |  | 65 | 66 | 0.15833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_35_1_line_71 |  | 65 | 67 | 0.010127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_35_1_line_72 |  | 66 | 70 | 0.015812 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_35_1_line_73 |  | 66 | 71 | 0.030834 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_35_1_line_74 |  | 68 | 69 | 0.19062 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_35_1_line_75 |  | 69 | 89 | 0.012973 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_35_1_line_76 |  | 71 | 83 | 0.028633 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_35_1_line_77 |  | 72 | 75 | 0.040293 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_35_1_line_78 |  | 72 | 76 | 0.06919 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_35_1_line_79 |  | 72 | 73 | 0.026237 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_35_1_line_80 |  | 73 | 74 | 0.048367 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_35_1_line_81 |  | 74 | 77 | 0.018905 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_35_1_line_82 |  | 76 | 78 | 0.021771 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_35_1_line_83 |  | 77 | 79 | 0.012434 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_35_1_line_84 |  | 78 | 80 | 0.020897 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_35_1_line_85 |  | 80 | 81 | 0.031028 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_35_1_line_86 |  | 81 | 82 | 0.012703 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_35_1_line_87 |  | 84 | 85 | 0.047078 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_35_1_line_88 |  | 86 | 87 | 0.044182 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
89 | MV_35_1_line_89 |  | 87 | 88 | 0.048899 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_35_1_line_90 |  | 88 | 102 | 1.3118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_35_1_line_91 |  | 89 | 90 | 0.11158 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
92 | MV_35_1_line_92 |  | 90 | 91 | 0.15358 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_35_1_line_93 |  | 90 | 92 | 0.12319 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_35_1_line_94 |  | 91 | 93 | 0.062554 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_35_1_line_95 |  | 92 | 94 | 0.13414 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_35_1_line_96 |  | 92 | 95 | 0.049422 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_35_1_line_97 |  | 93 | 96 | 0.0016143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_35_1_line_98 |  | 94 | 97 | 0.072488 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_35_1_line_99 |  | 94 | 98 | 0.096004 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_35_1_line_100 |  | 96 | 110 | 0.031186 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_35_1_line_101 |  | 97 | 107 | 0.062533 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_35_1_line_102 |  | 99 | 100 | 0.074959 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_35_1_line_103 |  | 100 | 105 | 0.058287 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_35_1_line_104 |  | 101 | 102 | 0.068797 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_35_1_line_105 |  | 102 | 103 | 0.40737 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_35_1_line_106 |  | 103 | 104 | 0.041872 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_35_1_line_107 |  | 104 | 105 | 0.022928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_35_1_line_108 |  | 107 | 108 | 0.03842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_35_1_line_109 |  | 109 | 110 | 0.060881 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_35_1_trafo_87 | 25 MVA 110/20 kV | 111 | 42 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2711824.1295 | 1256201.3496
1 | 2711872.4533 | 1256313.4788
2 | 2713457.2141 | 1255264.4142
3 | 2712890.8456 | 1256610.9034
4 | 2716323.4145 | 1256211.216
5 | 2716334.1247 | 1256230.8876
6 | 2716693.092 | 1256579.1495
7 | 2716520.8416 | 1257293.948
8 | 2716529.2941 | 1257294.8485
9 | 2716289.7376 | 1256794.5758
10 | 2716713.1636 | 1256614.7757
11 | 2716257.4632 | 1256659.7265
12 | 2716703.8914 | 1257425.7447
13 | 2712174.7562 | 1256417.4302
14 | 2712210.2663 | 1256490.8204
15 | 2712549.096 | 1256578.4031
16 | 2711862.6028 | 1256465.8097
17 | 2712630.447 | 1256624.867
18 | 2711854.9038 | 1256465.1021
19 | 2712759.1555 | 1256698.0675
20 | 2713367.9238 | 1257094.8289
21 | 2713327.1819 | 1257150.1847
22 | 2713180.1463 | 1256845.0825
23 | 2713979.3781 | 1257643.1468
24 | 2712974.7245 | 1258177.064
25 | 2713016.8053 | 1256950.627
26 | 2712923.0312 | 1256776.1346
27 | 2712762.9809 | 1256935.4299
28 | 2713130.978 | 1256812.2683
29 | 2713055.8494 | 1256982.0435
30 | 2714062.5555 | 1257716.7782
31 | 2712977.0659 | 1258340.303
32 | 2712922.9211 | 1256730.537
33 | 2712741.0481 | 1256913.1934
34 | 2713160.2494 | 1256790.3202
35 | 2714078.4769 | 1257714.3941
36 | 2713642.2937 | 1259929.5519
37 | 2712911.3816 | 1256675.9277
38 | 2713607.7572 | 1259944.4904
39 | 2714370.6009 | 1257254.9281
40 | 2714435.3757 | 1257238.9107
41 | 2714581.5101 | 1257639.1563
42 | 2714935.0026 | 1257595.1825
43 | 2714382.0494 | 1257914.8564
44 | 2714935.3537 | 1257578.2749
45 | 2714945.6093 | 1258080.5035
46 | 2714302.4219 | 1257950.1707
47 | 2714553.5523 | 1257628.4289
48 | 2715188.7322 | 1256514.8031
49 | 2715168.9997 | 1257481.1537
50 | 2715225.9753 | 1257483.1766
51 | 2714929.2904 | 1258127.0376
52 | 2715007.4667 | 1258210.2606
53 | 2715194.7886 | 1258310.6337
54 | 2714985.2496 | 1258206.6044
55 | 2715400.897 | 1258349.1482
56 | 2715175.6424 | 1258219.6053
57 | 2715502.9786 | 1258877.7825
58 | 2715840.2759 | 1258467.0211
59 | 2715404.2996 | 1258978.1327
60 | 2714809.836 | 1258086.2512
61 | 2715605.4286 | 1258355.556
62 | 2715595.6392 | 1258352.8639
63 | 2715602.8216 | 1258370.5615
64 | 2715840.635 | 1258437.5249
65 | 2715551.051 | 1258203.8194
66 | 2715588.6742 | 1258292.1854
67 | 2715544.7309 | 1258195.907
68 | 2715183.0679 | 1258198.4427
69 | 2715228.9813 | 1258050.0759
70 | 2715603.5795 | 1258297.4632
71 | 2715579.4708 | 1258321.6142
72 | 2715470.9075 | 1258352.661
73 | 2715470.4544 | 1258326.4296
74 | 2715518.4664 | 1258331.1787
75 | 2715510.9548 | 1258357.0997
76 | 2715510.411 | 1258392.1312
77 | 2715537.1236 | 1258334.2262
78 | 2715532.063 | 1258394.4031
79 | 2715535.9642 | 1258346.6057
80 | 2715552.6362 | 1258397.918
81 | 2715582.9708 | 1258404.4391
82 | 2715595.3864 | 1258407.1264
83 | 2715583.2264 | 1258349.4505
84 | 2714644.983 | 1258055.0739
85 | 2714691.9837 | 1258059.5993
86 | 2716528.3458 | 1258044.6634
87 | 2716551.824 | 1258082.0912
88 | 2716595.5437 | 1258067.84
89 | 2715227.0367 | 1258037.2492
90 | 2715233.7843 | 1257925.8741
91 | 2715081.666 | 1257916.4178
92 | 2715221.08 | 1257806.8582
93 | 2715019.1121 | 1257916.2634
94 | 2715229.134 | 1257700.0458
95 | 2715270.4686 | 1257806.6314
96 | 2715017.4977 | 1257916.2594
97 | 2715235.6312 | 1257627.8549
98 | 2715310.5982 | 1257649.2792
99 | 2716707.7502 | 1257436.9749
100 | 2716756.9596 | 1257493.5168
101 | 2717018.8339 | 1257593.5618
102 | 2717075.4585 | 1257632.8819
103 | 2716846.3202 | 1257537.2279
104 | 2716809.2672 | 1257554.7117
105 | 2716793.3433 | 1257539.028
106 | 2712987.9838 | 1256690.8331
107 | 2715173.1792 | 1257626.4264
108 | 2715135.0945 | 1257622.0542
109 | 2714925.3422 | 1257915.2973
110 | 2714986.2184 | 1257916.096
111 | 2714935.0026 | 1257595.1825

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98636 | 0.011488 | 0.2321 | 0.11241
1 | 0.98641 | 0.011841 | 0 | 0
2 | 0.98719 | 0.0046606 | 0.10053 | 0.048688
3 | 0.98748 | 0.0065892 | 0 | 0
4 | 0.98327 | -0.07621 | 0.16224 | 0.078577
5 | 0.98328 | -0.076255 | 0 | 0
6 | 0.9834 | -0.077167 | 0 | 0
7 | 0.98437 | -0.074172 | 0.091285 | 0.044211
8 | 0.98438 | -0.07423 | 0 | 0
9 | 0.98373 | -0.079648 | 0 | 0
10 | 0.98338 | -0.076991 | 0.35027 | 0.16965
11 | 0.98371 | -0.079807 | 0.091396 | 0.044265
12 | 0.98469 | -0.076524 | 0 | 0
13 | 0.98666 | 0.012771 | 0.27344 | 0.13243
14 | 0.98671 | 0.013048 | 0 | 0
15 | 0.98715 | 0.0092167 | 0 | 0
16 | 0.98647 | 0.011356 | 0 | 0
17 | 0.98723 | 0.0086067 | 0.17981 | 0.087085
18 | 0.98646 | 0.011368 | 0.12582 | 0.060937
19 | 0.98738 | 0.0073439 | 0 | 0
20 | 0.99007 | 0.007794 | 0.31026 | 0.15027
21 | 0.9903 | 0.0058152 | 0 | 0
22 | 0.98864 | -0.0028531 | 0.256 | 0.12399
23 | 0.99349 | -0.018996 | 0 | 0
24 | 0.98967 | 0.0099723 | 0 | 0
25 | 0.98798 | 0.002526 | 0 | 0
26 | 0.98757 | 0.0058381 | 0 | 0
27 | 0.98787 | 0.0034625 | 0 | 0
28 | 0.98848 | -0.0015508 | 0 | 0
29 | 0.98796 | 0.0023981 | 0.20599 | 0.099764
30 | 0.99394 | -0.022334 | 0.11586 | 0.056113
31 | 0.98958 | 0.010763 | 0.15037 | 0.072827
32 | 0.98754 | 0.0060955 | 0.13969 | 0.067656
33 | 0.98786 | 0.0033575 | 0.27133 | 0.13141
34 | 0.98847 | -0.0014128 | 0.31084 | 0.15055
35 | 0.994 | -0.022825 | 0 | 0
36 | 0.98882 | 0.0056609 | 0 | 0
37 | 0.98751 | 0.0063149 | 0 | 0
38 | 0.9888 | 0.0057639 | 0.22656 | 0.10973
39 | 0.99637 | -0.040727 | 0.35058 | 0.1698
40 | 0.9964 | -0.041005 | 0 | 0
41 | 0.99674 | -0.043729 | 0 | 0
42 | 1 | 0 | -12.8729 | -5.7085
43 | 0.99748 | -0.048609 | 0 | 0
44 | 1 | 1.5071e-05 | 0.075556 | 0.036593
45 | 0.99601 | -0.076055 | 0 | 0
46 | 0.99743 | -0.048923 | 0.29625 | 0.14348
47 | 0.99673 | -0.043651 | 0.21962 | 0.10637
48 | 0.99147 | -0.090295 | 0.075044 | 0.036346
49 | 0.99161 | -0.089356 | 0.07158 | 0.034668
50 | 0.99162 | -0.089451 | 0 | 0
51 | 0.99598 | -0.075725 | 0.32775 | 0.15873
52 | 0.99536 | -0.088302 | 0 | 0
53 | 0.99428 | -0.093309 | 0 | 0
54 | 0.99535 | -0.088278 | 0.089859 | 0.043521
55 | 0.99317 | -0.12244 | 0.073732 | 0.03571
56 | 0.99365 | -0.097521 | 0.27104 | 0.13127
57 | 0.99104 | -0.12058 | 0 | 0
58 | 0.9911 | -0.12007 | 0.31043 | 0.15035
59 | 0.99103 | -0.12051 | 0.053497 | 0.02591
60 | 0.99592 | -0.076156 | 0 | 0
61 | 0.99187 | -0.12495 | 0 | 0
62 | 0.99186 | -0.12483 | 0.10636 | 0.051511
63 | 0.99193 | -0.12539 | 0.16508 | 0.079954
64 | 0.99112 | -0.11992 | 0 | 0
65 | 0.99174 | -0.12379 | 0 | 0
66 | 0.9918 | -0.12429 | 0 | 0
67 | 0.99174 | -0.12375 | 0.27157 | 0.13153
68 | 0.99356 | -0.0967 | 0 | 0
69 | 0.99278 | -0.089681 | 0 | 0
70 | 0.99179 | -0.12424 | 0.27431 | 0.13285
71 | 0.99182 | -0.12448 | 0.1214 | 0.058794
72 | 0.9928 | -0.13204 | 0 | 0
73 | 0.99278 | -0.13186 | 0 | 0
74 | 0.99275 | -0.13154 | 0.15289 | 0.074049
75 | 0.9928 | -0.13199 | 0.097208 | 0.04708
76 | 0.99247 | -0.12945 | 0.09384 | 0.045449
77 | 0.99274 | -0.13145 | 0.30955 | 0.14992
78 | 0.99236 | -0.12866 | 0.10586 | 0.051272
79 | 0.99274 | -0.13143 | 0.096513 | 0.046743
80 | 0.99227 | -0.12793 | 0.20637 | 0.099952
81 | 0.99213 | -0.12692 | 0.16085 | 0.077905
82 | 0.99208 | -0.12653 | 0 | 0
83 | 0.99184 | -0.12471 | 0.182 | 0.088145
84 | 0.99586 | -0.075667 | 0.25154 | 0.12183
85 | 0.99588 | -0.075808 | 0 | 0
86 | 0.9884 | -0.10167 | 0 | 0
87 | 0.98825 | -0.10295 | 0.25704 | 0.12449
88 | 0.98816 | -0.10233 | 0 | 0
89 | 0.99273 | -0.0892 | 0.21968 | 0.1064
90 | 0.99209 | -0.093535 | 0 | 0
91 | 0.99172 | -0.090149 | 0 | 0
92 | 0.99191 | -0.09199 | 0 | 0
93 | 0.99157 | -0.088758 | 0.53969 | 0.26139
94 | 0.99173 | -0.090455 | 0 | 0
95 | 0.9919 | -0.091924 | 0.1128 | 0.054631
96 | 0.99157 | -0.088733 | 0 | 0
97 | 0.99165 | -0.08969 | 0 | 0
98 | 0.99172 | -0.090347 | 0.098321 | 0.047619
99 | 0.9847 | -0.076597 | 0.23987 | 0.11617
100 | 0.98479 | -0.077279 | 0.20087 | 0.097288
101 | 0.98567 | -0.084184 | 0.14208 | 0.068812
102 | 0.98568 | -0.084301 | 0 | 0
103 | 0.98499 | -0.07882 | 0 | 0
104 | 0.98491 | -0.078242 | 0.082236 | 0.039829
105 | 0.98488 | -0.077948 | 0.11638 | 0.056367
106 | 0.98744 | 0.0070177 | 0.25811 | 0.12501
107 | 0.99159 | -0.08911 | 0.45125 | 0.21855
108 | 0.99157 | -0.088961 | 0.31991 | 0.15494
109 | 0.99142 | -0.08728 | 1.3027 | 0.63093
110 | 0.99152 | -0.088242 | 0 | 0
111 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.2321 | -0.11241 | 0.23211 | 0.11227 | 1.2389e-05 | -0.00013406 | 0.0075474 | 0.0075456 | 0.0075474 | 0.98636 | 0.011488 | 0.98641 | 0.011841 | 3.594
1 | -0.23211 | -0.11227 | 0.23212 | 0.10812 | 1.3506e-05 | -0.0041531 | 0.0075456 | 0.0074934 | 0.0075456 | 0.98641 | 0.011841 | 0.98647 | 0.011356 | 3.4298
2 | -0.10053 | -0.048688 | 0.10056 | 0.047006 | 2.7584e-05 | -0.0016827 | 0.0032663 | 0.0032449 | 0.0032663 | 0.98719 | 0.0046606 | 0.98748 | 0.0065892 | 1.5554
3 | -0.35868 | -0.16876 | 0.35869 | 0.16717 | 1.2201e-05 | -0.0015837 | 0.011588 | 0.011568 | 0.011588 | 0.98748 | 0.0065892 | 0.98751 | 0.0063149 | 5.2673
4 | 0.25812 | 0.12175 | -0.25811 | -0.12501 | 1.3074e-05 | -0.0032557 | 0.0083431 | 0.0083842 | 0.0083842 | 0.98748 | 0.0065892 | 0.98744 | 0.0070177 | 3.811
5 | -0.16224 | -0.078577 | 0.16224 | 0.07806 | 8.3592e-07 | -0.00051644 | 0.0052924 | 0.0052858 | 0.0052924 | 0.98327 | -0.07621 | 0.98328 | -0.076255 | 2.4056
6 | -0.16224 | -0.07806 | 0.16226 | 0.064177 | 2.1724e-05 | -0.013884 | 0.0052858 | 0.0051222 | 0.0052858 | 0.98328 | -0.076255 | 0.9834 | -0.077167 | 2.4026
7 | -0.51254 | -0.23288 | 0.51273 | 0.22135 | 0.00018139 | -0.011535 | 0.016526 | 0.016388 | 0.016526 | 0.9834 | -0.077167 | 0.98373 | -0.079648 | 7.5118
8 | 0.35028 | 0.1687 | -0.35027 | -0.16965 | 7.1131e-06 | -0.0009414 | 0.011413 | 0.011425 | 0.011425 | 0.9834 | -0.077167 | 0.98338 | -0.076991 | 5.1931
9 | -0.69578 | -0.30926 | 0.69578 | 0.30906 | 5.6405e-06 | -0.0001944 | 0.022329 | 0.022327 | 0.022329 | 0.98437 | -0.074172 | 0.98438 | -0.07423 | 10.1495
10 | 0.60449 | 0.26505 | -0.60412 | -0.26545 | 0.00036747 | -0.00040594 | 0.019356 | 0.019364 | 0.019364 | 0.98437 | -0.074172 | 0.98373 | -0.079648 | 9.2209
11 | -0.69578 | -0.30906 | 0.69602 | 0.30094 | 0.0002345 | -0.0081212 | 0.022327 | 0.02223 | 0.022327 | 0.98438 | -0.07423 | 0.98469 | -0.076524 | 10.1485
12 | 0.091398 | 0.044106 | -0.091396 | -0.044265 | 2.1925e-06 | -0.00015881 | 0.002978 | 0.0029801 | 0.0029801 | 0.98373 | -0.079648 | 0.98371 | -0.079807 | 1.4191
13 | -0.69602 | -0.30094 | 0.69602 | 0.30067 | 7.833e-06 | -0.00027259 | 0.02223 | 0.022227 | 0.02223 | 0.98469 | -0.076524 | 0.9847 | -0.076597 | 10.1047
14 | -0.27344 | -0.13243 | 0.27345 | 0.13234 | 1.1476e-05 | -8.7568e-05 | 0.0088891 | 0.0088879 | 0.0088891 | 0.98666 | 0.012771 | 0.98671 | 0.013048 | 4.2329
15 | -0.63147 | -0.30087 | 0.63178 | 0.28826 | 0.00030292 | -0.012609 | 0.020464 | 0.020307 | 0.020464 | 0.98671 | 0.013048 | 0.98715 | 0.0092167 | 9.302
16 | 0.35802 | 0.16853 | -0.35794 | -0.16888 | 8.327e-05 | -0.00035287 | 0.011577 | 0.011582 | 0.011582 | 0.98671 | 0.013048 | 0.98647 | 0.011356 | 5.5152
17 | -0.63178 | -0.28826 | 0.63183 | 0.2861 | 5.1398e-05 | -0.0021599 | 0.020307 | 0.020281 | 0.020307 | 0.98715 | 0.0092167 | 0.98723 | 0.0086067 | 9.2307
18 | 0.12582 | 0.060757 | -0.12582 | -0.060937 | 1.7266e-07 | -0.00017958 | 0.0040887 | 0.004091 | 0.004091 | 0.98647 | 0.011356 | 0.98646 | 0.011368 | 1.8596
19 | -0.81164 | -0.37319 | 0.81177 | 0.36979 | 0.00013436 | -0.0033985 | 0.026122 | 0.02608 | 0.026122 | 0.98723 | 0.0086067 | 0.98738 | 0.0073439 | 11.8735
20 | -0.81177 | -0.36979 | 0.81193 | 0.36561 | 0.00016453 | -0.0041782 | 0.02608 | 0.026029 | 0.02608 | 0.98738 | 0.0073439 | 0.98757 | 0.0058381 | 11.8544
21 | -2.6699 | -1.236 | 2.6706 | 1.2346 | 0.00067446 | -0.0014075 | 0.085784 | 0.085765 | 0.085784 | 0.99007 | 0.007794 | 0.9903 | 0.0058152 | 38.9929
22 | 2.3596 | 1.0858 | -2.3565 | -1.0841 | 0.0031934 | 0.0016351 | 0.075735 | 0.075739 | 0.075739 | 0.99007 | 0.007794 | 0.98864 | -0.0028531 | 36.0662
23 | -3.048 | -1.379 | 3.0584 | 1.3628 | 0.010426 | -0.016243 | 0.09752 | 0.097289 | 0.09752 | 0.9903 | 0.0058152 | 0.99349 | -0.018996 | 44.3271
24 | 0.37738 | 0.14439 | -0.37713 | -0.17546 | 0.00025364 | -0.031066 | 0.011779 | 0.012133 | 0.012133 | 0.9903 | 0.0058152 | 0.98967 | 0.0099723 | 5.5149
25 | 2.1005 | 0.96014 | -2.1001 | -0.96141 | 0.00035896 | -0.0012728 | 0.067435 | 0.067452 | 0.067452 | 0.98864 | -0.0028531 | 0.98848 | -0.0015508 | 30.6601
26 | -3.0584 | -1.3628 | 3.0598 | 1.3605 | 0.001438 | -0.0022574 | 0.097289 | 0.097257 | 0.097289 | 0.99349 | -0.018996 | 0.99394 | -0.022334 | 44.2223
27 | 0.37713 | 0.17546 | -0.37709 | -0.17977 | 3.6479e-05 | -0.0043106 | 0.012133 | 0.012187 | 0.012187 | 0.98967 | 0.0099723 | 0.98958 | 0.010763 | 5.5393
28 | 1.3109 | 0.59252 | -1.3103 | -0.59807 | 0.00057998 | -0.0055466 | 0.042034 | 0.042103 | 0.042103 | 0.98798 | 0.002526 | 0.98757 | 0.0058381 | 19.138
29 | 0.27137 | 0.12433 | -0.27134 | -0.13138 | 3.1049e-05 | -0.0070454 | 0.0087217 | 0.0088095 | 0.0088095 | 0.98798 | 0.002526 | 0.98787 | 0.0034625 | 4.0043
30 | -1.7883 | -0.81657 | 1.7893 | 0.81172 | 0.00096927 | -0.0048491 | 0.057441 | 0.057379 | 0.057441 | 0.98798 | 0.002526 | 0.98848 | -0.0015508 | 26.1095
31 | 0.20599 | 0.099708 | -0.20599 | -0.099764 | 3.9929e-06 | -5.5895e-05 | 0.0066868 | 0.0066876 | 0.0066876 | 0.98798 | 0.002526 | 0.98796 | 0.0023981 | 3.1846
32 | 0.49841 | 0.23246 | -0.49839 | -0.23353 | 1.597e-05 | -0.0010723 | 0.016076 | 0.016089 | 0.016089 | 0.98757 | 0.0058381 | 0.98754 | 0.0060955 | 7.3132
33 | 0.27134 | 0.13138 | -0.27133 | -0.13141 | 4.319e-06 | -3.3682e-05 | 0.0088095 | 0.00881 | 0.00881 | 0.98787 | 0.0034625 | 0.98786 | 0.0033575 | 4.1952
34 | 0.31085 | 0.1497 | -0.31084 | -0.15055 | 4.9548e-06 | -0.0008505 | 0.010076 | 0.010087 | 0.010087 | 0.98848 | -0.0015508 | 0.98847 | -0.0014128 | 4.5848
35 | -3.1757 | -1.4166 | 3.1759 | 1.4163 | 0.00021857 | -0.00031382 | 0.10099 | 0.10099 | 0.10099 | 0.99394 | -0.022334 | 0.994 | -0.022825 | 45.9065
36 | 0.22673 | 0.10694 | -0.22656 | -0.10885 | 0.00016472 | -0.0019094 | 0.0073128 | 0.007338 | 0.007338 | 0.98958 | 0.010763 | 0.98882 | 0.0056609 | 3.4943
37 | 0.3587 | 0.16588 | -0.35869 | -0.16717 | 9.9591e-06 | -0.0012968 | 0.011552 | 0.011568 | 0.011568 | 0.98754 | 0.0060955 | 0.98751 | 0.0063149 | 5.2583
38 | -3.1759 | -1.4163 | 3.1876 | 1.3993 | 0.01174 | -0.016978 | 0.10099 | 0.10075 | 0.10099 | 0.994 | -0.022825 | 0.99748 | -0.048609 | 45.9045
39 | 0.22656 | 0.10885 | -0.22656 | -0.10973 | 2.7024e-06 | -0.00087547 | 0.007338 | 0.0073491 | 0.0073491 | 0.98882 | 0.0056609 | 0.9888 | 0.0057639 | 3.3405
40 | -0.35058 | -0.1698 | 0.3506 | 0.16822 | 1.1295e-05 | -0.0015739 | 0.011286 | 0.011266 | 0.011286 | 0.99637 | -0.040727 | 0.9964 | -0.041005 | 5.13
41 | -0.3506 | -0.16822 | 0.35072 | 0.14999 | 0.00012798 | -0.018232 | 0.011266 | 0.011048 | 0.011266 | 0.9964 | -0.041005 | 0.99674 | -0.043729 | 5.121
42 | 0.21963 | 0.10566 | -0.21962 | -0.10637 | 2.0009e-06 | -0.00071207 | 0.0070586 | 0.0070676 | 0.0070676 | 0.99674 | -0.043729 | 0.99673 | -0.043651 | 3.2125
43 | -0.57035 | -0.25565 | 0.57079 | 0.23147 | 0.00044106 | -0.024181 | 0.018102 | 0.017826 | 0.018102 | 0.99674 | -0.043729 | 0.99748 | -0.048609 | 8.2281
44 | 12.7834 | 5.6618 | -12.7559 | -5.7066 | 0.027449 | -0.044834 | 0.4036 | 0.40442 | 0.40442 | 1 | 0 | 0.99748 | -0.048609 | 48.0311
45 | 0.075556 | 0.03619 | -0.075556 | -0.036593 | 1.3233e-07 | -0.00040378 | 0.0024184 | 0.0024235 | 0.0024235 | 1 | 0 | 1 | 1.5071e-05 | 1.1016
46 | 8.7012 | 3.9324 | -8.6904 | -3.9813 | 0.01086 | -0.048867 | 0.27634 | 0.27705 | 0.27705 | 0.99748 | -0.048609 | 0.99601 | -0.076055 | 32.9034
47 | 0.29626 | 0.14338 | -0.29625 | -0.14348 | 1.4083e-05 | -9.4638e-05 | 0.0095253 | 0.0095266 | 0.0095266 | 0.99748 | -0.048609 | 0.99743 | -0.048923 | 4.5365
48 | 0.57934 | 0.27528 | -0.57932 | -0.27644 | 2.2764e-05 | -0.001161 | 0.01859 | 0.018605 | 0.018605 | 0.99601 | -0.076055 | 0.99598 | -0.075725 | 8.4567
49 | 8.111 | 3.706 | -8.1065 | -3.7301 | 0.0045649 | -0.024057 | 0.25846 | 0.2588 | 0.2588 | 0.99601 | -0.076055 | 0.99536 | -0.088302 | 30.7363
50 | -0.075044 | -0.036346 | 0.075054 | 0.035217 | 1.009e-05 | -0.0011281 | 0.0024278 | 0.0024135 | 0.0024278 | 0.99147 | -0.090295 | 0.99161 | -0.089356 | 1.1561
51 | -0.14663 | -0.069885 | 0.14664 | 0.068547 | 1.6959e-06 | -0.001338 | 0.0047288 | 0.0047122 | 0.0047288 | 0.99161 | -0.089356 | 0.99162 | -0.089451 | 2.1495
52 | -0.14664 | -0.068547 | 0.14664 | 0.064821 | 4.6609e-06 | -0.003726 | 0.0047122 | 0.0046673 | 0.0047122 | 0.99162 | -0.089451 | 0.99165 | -0.08969 | 2.1419
53 | 0.25157 | 0.1177 | -0.25156 | -0.11784 | 1.4578e-05 | -0.00014034 | 0.0080502 | 0.008052 | 0.008052 | 0.99598 | -0.075725 | 0.99592 | -0.076156 | 3.8343
54 | 8.0166 | 3.6871 | -8.0082 | -3.708 | 0.0083575 | -0.020943 | 0.25591 | 0.25622 | 0.25622 | 0.99536 | -0.088302 | 0.99428 | -0.093309 | 40.1604
55 | 0.08986 | 0.042988 | -0.089859 | -0.043521 | 2.5147e-07 | -0.00053254 | 0.002889 | 0.0028957 | 0.0028957 | 0.99536 | -0.088302 | 0.99535 | -0.088278 | 1.3162
56 | 4.5373 | 2.0599 | -4.5333 | -2.0556 | 0.0040289 | 0.0043481 | 0.14468 | 0.14468 | 0.14468 | 0.99428 | -0.093309 | 0.99317 | -0.12244 | 41.3367
57 | 3.4709 | 1.6481 | -3.4689 | -1.6469 | 0.0020626 | 0.0011822 | 0.11156 | 0.11156 | 0.11156 | 0.99428 | -0.093309 | 0.99365 | -0.097521 | 53.123
58 | 4.4595 | 2.0199 | -4.4582 | -2.0185 | 0.001303 | 0.0014035 | 0.1423 | 0.1423 | 0.1423 | 0.99317 | -0.12244 | 0.9928 | -0.13204 | 40.6569
59 | 3.1978 | 1.5156 | -3.1975 | -1.5161 | 0.00031642 | -0.00043469 | 0.10281 | 0.10282 | 0.10282 | 0.99365 | -0.097521 | 0.99356 | -0.0967 | 46.7346
60 | -0.053497 | -0.022569 | 0.0535 | 0.021947 | 2.6976e-06 | -0.00062154 | 0.0016913 | 0.0016843 | 0.0016913 | 0.99104 | -0.12058 | 0.9911 | -0.12007 | 0.80537
61 | 0.053497 | 0.022569 | -0.053497 | -0.02591 | 5.5672e-07 | -0.0033411 | 0.0016913 | 0.0017314 | 0.0017314 | 0.99104 | -0.12058 | 0.99103 | -0.12051 | 0.78702
62 | -0.36393 | -0.1723 | 0.36394 | 0.17227 | 7.229e-06 | -3.0064e-05 | 0.011728 | 0.011728 | 0.011728 | 0.9911 | -0.12007 | 0.99112 | -0.11992 | 5.5849
63 | 0.25156 | 0.11784 | -0.25154 | -0.12071 | 1.0546e-05 | -0.0028696 | 0.008052 | 0.0080877 | 0.0080877 | 0.99592 | -0.076156 | 0.99588 | -0.075808 | 3.6762
64 | 0.9557 | 0.45659 | -0.95569 | -0.45682 | 1.2881e-05 | -0.00023466 | 0.030826 | 0.030829 | 0.030829 | 0.99187 | -0.12495 | 0.99186 | -0.12483 | 14.0133
65 | -3.0665 | -1.3534 | 3.0667 | 1.3531 | 0.00019349 | -0.00030038 | 0.097555 | 0.09755 | 0.097555 | 0.99187 | -0.12495 | 0.99193 | -0.12539 | 44.343
66 | 2.1108 | 0.89685 | -2.1091 | -0.90299 | 0.0016838 | -0.0061375 | 0.066749 | 0.066825 | 0.066825 | 0.99187 | -0.12495 | 0.99112 | -0.11992 | 30.3748
67 | 0.84933 | 0.40531 | -0.84932 | -0.40561 | 1.2895e-05 | -0.00029856 | 0.02739 | 0.027394 | 0.027394 | 0.99186 | -0.12483 | 0.99184 | -0.12471 | 12.4516
68 | -3.2318 | -1.4331 | 3.2323 | 1.4324 | 0.00052734 | -0.00072045 | 0.10289 | 0.10287 | 0.10289 | 0.99193 | -0.12539 | 0.99208 | -0.12653 | 46.7661
69 | 1.7452 | 0.73072 | -1.7402 | -0.75807 | 0.0050275 | -0.027342 | 0.055107 | 0.055437 | 0.055437 | 0.99112 | -0.11992 | 0.9884 | -0.10167 | 25.1987
70 | -0.27157 | -0.13129 | 0.27159 | 0.12758 | 1.6208e-05 | -0.0037135 | 0.0087801 | 0.0087336 | 0.0087801 | 0.99174 | -0.12379 | 0.9918 | -0.12429 | 3.991
71 | 0.27157 | 0.13129 | -0.27157 | -0.13153 | 1.0426e-06 | -0.0002375 | 0.0087801 | 0.0087832 | 0.0087832 | 0.99174 | -0.12379 | 0.99174 | -0.12375 | 3.9923
72 | 0.27431 | 0.13248 | -0.27431 | -0.13285 | 1.6604e-06 | -0.00037087 | 0.0088665 | 0.0088712 | 0.0088712 | 0.9918 | -0.12429 | 0.99179 | -0.12424 | 4.0324
73 | -0.5459 | -0.26006 | 0.54591 | 0.25934 | 1.2744e-05 | -0.00072041 | 0.0176 | 0.017591 | 0.0176 | 0.9918 | -0.12429 | 0.99182 | -0.12448 | 7.9999
74 | 3.1975 | 1.5161 | -3.1948 | -1.5198 | 0.0026916 | -0.003691 | 0.10282 | 0.10287 | 0.10287 | 0.99356 | -0.0967 | 0.99278 | -0.089681 | 46.7601
75 | 3.1948 | 1.5198 | -3.1946 | -1.52 | 0.00018329 | -0.0002509 | 0.10287 | 0.10288 | 0.10288 | 0.99278 | -0.089681 | 0.99273 | -0.0892 | 46.7618
76 | -0.6673 | -0.31813 | 0.66732 | 0.31747 | 1.769e-05 | -0.00066728 | 0.021517 | 0.021508 | 0.021517 | 0.99182 | -0.12448 | 0.99184 | -0.12471 | 9.7803
77 | 0.097209 | 0.046132 | -0.097208 | -0.04708 | 5.2853e-07 | -0.00094807 | 0.0031287 | 0.0031406 | 0.0031406 | 0.9928 | -0.13204 | 0.9928 | -0.13199 | 1.4275
78 | 3.802 | 1.7041 | -3.8007 | -1.7053 | 0.0013559 | -0.0012255 | 0.12115 | 0.12117 | 0.12117 | 0.9928 | -0.13204 | 0.99247 | -0.12945 | 55.0762
79 | 0.55899 | 0.26823 | -0.55898 | -0.26885 | 1.1389e-05 | -0.00061406 | 0.018028 | 0.018036 | 0.018036 | 0.9928 | -0.13204 | 0.99278 | -0.13186 | 8.1981
80 | 0.55898 | 0.26885 | -0.55896 | -0.26998 | 2.1021e-05 | -0.0011319 | 0.018036 | 0.01805 | 0.01805 | 0.99278 | -0.13186 | 0.99275 | -0.13154 | 8.2046
81 | 0.40607 | 0.19593 | -0.40606 | -0.19637 | 4.3398e-06 | -0.00044355 | 0.01311 | 0.013116 | 0.013116 | 0.99275 | -0.13154 | 0.99274 | -0.13145 | 5.9618
82 | 3.7069 | 1.6599 | -3.7064 | -1.6603 | 0.00040564 | -0.00039162 | 0.11814 | 0.11814 | 0.11814 | 0.99247 | -0.12945 | 0.99236 | -0.12866 | 53.701
83 | 0.096513 | 0.046451 | -0.096513 | -0.046743 | 1.6122e-07 | -0.00029252 | 0.0031146 | 0.0031183 | 0.0031183 | 0.99274 | -0.13145 | 0.99274 | -0.13143 | 1.4174
84 | 3.6006 | 1.609 | -3.6002 | -1.6094 | 0.00036718 | -0.00038238 | 0.11472 | 0.11473 | 0.11473 | 0.99236 | -0.12866 | 0.99227 | -0.12793 | 52.1491
85 | 3.3938 | 1.5094 | -3.3934 | -1.51 | 0.00048372 | -0.00058583 | 0.10806 | 0.10807 | 0.10807 | 0.99227 | -0.12793 | 0.99213 | -0.12692 | 49.1222
86 | 3.2325 | 1.4321 | -3.2323 | -1.4324 | 0.00017947 | -0.0002453 | 0.10287 | 0.10287 | 0.10287 | 0.99213 | -0.12692 | 0.99208 | -0.12653 | 46.7614
87 | -0.25154 | -0.12183 | 0.25154 | 0.12071 | 4.1181e-06 | -0.0011136 | 0.0081017 | 0.0080877 | 0.0081017 | 0.99586 | -0.075667 | 0.99588 | -0.075808 | 3.6826
88 | 1.7402 | 0.75807 | -1.7399 | -0.75797 | 0.00024193 | 0.00010002 | 0.055437 | 0.055438 | 0.055438 | 0.9884 | -0.10167 | 0.98825 | -0.10295 | 26.3989
89 | 1.4829 | 0.63347 | -1.4827 | -0.63457 | 0.00014488 | -0.0010972 | 0.047103 | 0.047116 | 0.047116 | 0.98825 | -0.10295 | 0.98816 | -0.10233 | 21.4164
90 | 1.4827 | 0.63457 | -1.4788 | -0.66392 | 0.0039169 | -0.029344 | 0.047116 | 0.047474 | 0.047474 | 0.98816 | -0.10233 | 0.98568 | -0.084301 | 21.5793
91 | 2.975 | 1.4136 | -2.9731 | -1.4126 | 0.0018237 | 0.0010111 | 0.095778 | 0.09578 | 0.09578 | 0.99273 | -0.0892 | 0.99209 | -0.093535 | 45.6095
92 | 1.8436 | 0.88541 | -1.8429 | -0.8888 | 0.00072668 | -0.0033921 | 0.059512 | 0.059557 | 0.059557 | 0.99209 | -0.093535 | 0.99172 | -0.090149 | 27.0716
93 | 1.1295 | 0.5272 | -1.1293 | -0.53003 | 0.00021655 | -0.0028301 | 0.036269 | 0.036305 | 0.036305 | 0.99209 | -0.093535 | 0.99191 | -0.09199 | 16.5023
94 | 1.8429 | 0.8888 | -1.8426 | -0.89018 | 0.00029631 | -0.0013808 | 0.059557 | 0.059576 | 0.059576 | 0.99172 | -0.090149 | 0.99157 | -0.088758 | 27.08
95 | 1.0165 | 0.47656 | -1.0163 | -0.47965 | 0.00019138 | -0.0030937 | 0.032672 | 0.032711 | 0.032711 | 0.99191 | -0.09199 | 0.99173 | -0.090455 | 14.8687
96 | 0.1128 | 0.053471 | -0.1128 | -0.054631 | 8.7431e-07 | -0.0011607 | 0.003633 | 0.0036476 | 0.0036476 | 0.99191 | -0.09199 | 0.9919 | -0.091924 | 1.658
97 | 1.3029 | 0.6288 | -1.3029 | -0.62884 | 3.8232e-06 | -3.6763e-05 | 0.042118 | 0.042119 | 0.042119 | 0.99157 | -0.088758 | 0.99157 | -0.088733 | 19.1449
98 | 0.91795 | 0.43428 | -0.91787 | -0.43596 | 8.4615e-05 | -0.001677 | 0.029559 | 0.02958 | 0.02958 | 0.99173 | -0.090455 | 0.99165 | -0.08969 | 13.4457
99 | 0.098323 | 0.045365 | -0.098321 | -0.047619 | 1.2845e-06 | -0.0022541 | 0.0031519 | 0.00318 | 0.00318 | 0.99173 | -0.090455 | 0.99172 | -0.090347 | 1.4454
100 | 1.3029 | 0.62884 | -1.3029 | -0.62955 | 7.3873e-05 | -0.00071015 | 0.042119 | 0.042128 | 0.042128 | 0.99157 | -0.088733 | 0.99152 | -0.088242 | 19.1491
101 | 0.77122 | 0.37114 | -0.77117 | -0.37259 | 5.1861e-05 | -0.0014527 | 0.024915 | 0.024934 | 0.024934 | 0.99165 | -0.08969 | 0.99159 | -0.08911 | 11.3336
102 | -0.93589 | -0.41684 | 0.93598 | 0.41513 | 9.0211e-05 | -0.0017088 | 0.030035 | 0.030014 | 0.030035 | 0.9847 | -0.076597 | 0.98479 | -0.077279 | 13.6523
103 | -1.1369 | -0.51242 | 1.137 | 0.5111 | 0.00010393 | -0.001319 | 0.036554 | 0.036538 | 0.036554 | 0.98479 | -0.077279 | 0.98488 | -0.077948 | 16.6154
104 | -0.14208 | -0.068812 | 0.14208 | 0.067217 | 1.9547e-06 | -0.0015953 | 0.0046235 | 0.0046033 | 0.0046235 | 0.98567 | -0.084184 | 0.98568 | -0.084301 | 2.1016
105 | 1.3367 | 0.5967 | -1.3357 | -0.60584 | 0.0010022 | -0.009146 | 0.042872 | 0.042986 | 0.042986 | 0.98568 | -0.084301 | 0.98499 | -0.07882 | 19.5389
106 | 1.3357 | 0.60584 | -1.3356 | -0.60678 | 0.00010332 | -0.00093923 | 0.042986 | 0.042997 | 0.042997 | 0.98499 | -0.07882 | 0.98491 | -0.078242 | 19.5443
107 | 1.2534 | 0.56695 | -1.2533 | -0.56747 | 4.9769e-05 | -0.00051626 | 0.04032 | 0.040327 | 0.040327 | 0.98491 | -0.078242 | 0.98488 | -0.077948 | 18.3303
108 | 0.31992 | 0.15404 | -0.31991 | -0.15494 | 5.4866e-06 | -0.0009003 | 0.010337 | 0.010348 | 0.010348 | 0.99159 | -0.08911 | 0.99157 | -0.088961 | 4.7038
109 | -1.3027 | -0.63093 | 1.3029 | 0.62955 | 0.00014431 | -0.0013861 | 0.042146 | 0.042128 | 0.042146 | 0.99142 | -0.08728 | 0.99152 | -0.088242 | 19.1574

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 12.8729 | 5.7085

## res_load
| p_mw | q_mvar
0 | 0.2321 | 0.11241
1 | 0.10053 | 0.048688
2 | 0.16224 | 0.078577
3 | 0.091285 | 0.044211
4 | 0.35027 | 0.16965
5 | 0.091396 | 0.044265
6 | 0.27344 | 0.13243
7 | 0.17981 | 0.087085
8 | 0.12582 | 0.060937
9 | 0.31026 | 0.15027
10 | 0.256 | 0.12399
11 | 0.20599 | 0.099764
12 | 0.11586 | 0.056113
13 | 0.15037 | 0.072827
14 | 0.13969 | 0.067656
15 | 0.27133 | 0.13141
16 | 0.31084 | 0.15055
17 | 0.22656 | 0.10973
18 | 0.35058 | 0.1698
19 | 0.075556 | 0.036593
20 | 0.29625 | 0.14348
21 | 0.21962 | 0.10637
22 | 0.075044 | 0.036346
23 | 0.07158 | 0.034668
24 | 0.32775 | 0.15873
25 | 0.089859 | 0.043521
26 | 0.073732 | 0.03571
27 | 0.27104 | 0.13127
28 | 0.31043 | 0.15035
29 | 0.053497 | 0.02591
30 | 0.10636 | 0.051511
31 | 0.16508 | 0.079954
32 | 0.27157 | 0.13153
33 | 0.27431 | 0.13285
34 | 0.1214 | 0.058794
35 | 0.15289 | 0.074049
36 | 0.097208 | 0.04708
37 | 0.09384 | 0.045449
38 | 0.30955 | 0.14992
39 | 0.10586 | 0.051272
40 | 0.096513 | 0.046743
41 | 0.20637 | 0.099952
42 | 0.16085 | 0.077905
43 | 0.182 | 0.088145
44 | 0.25154 | 0.12183
45 | 0.25704 | 0.12449
46 | 0.21968 | 0.1064
47 | 0.53969 | 0.26139
48 | 0.1128 | 0.054631
49 | 0.098321 | 0.047619
50 | 0.23987 | 0.11617
51 | 0.20087 | 0.097288
52 | 0.14208 | 0.068812
53 | 0.082236 | 0.039829
54 | 0.11638 | 0.056367
55 | 0.25811 | 0.12501
56 | 0.45125 | 0.21855
57 | 0.31991 | 0.15494
58 | 1.3027 | 0.63093

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1