## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_360_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_360_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_360_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_360_0_node_5 | 20 | n |  | TRUE
4 | bus_MV_360_0_node_7 | 20 | n |  | TRUE
5 | bus_MV_360_0_node_6 | 20 | n |  | TRUE
6 | bus_MV_360_0_node_118 | 20 | n |  | TRUE
7 | bus_MV_360_0_node_3 | 20 | n |  | TRUE
8 | bus_MV_360_0_node_4 | 20 | n |  | TRUE
9 | bus_MV_360_0_node_32 | 20 | n |  | TRUE
10 | bus_MV_360_0_node_33 | 20 | n |  | TRUE
11 | bus_MV_360_0_node_168 | 20 | n |  | TRUE
12 | bus_MV_360_0_node_58 | 20 | n |  | TRUE
13 | bus_MV_360_0_node_167 | 20 | n |  | TRUE
14 | bus_MV_360_0_node_54 | 20 | n |  | TRUE
15 | bus_MV_360_0_node_55 | 20 | n |  | TRUE
16 | bus_MV_360_0_node_182 | 20 | n |  | TRUE
17 | bus_MV_360_0_node_28 | 20 | n |  | TRUE
18 | bus_MV_360_0_node_120 | 20 | n |  | TRUE
19 | bus_MV_360_0_node_25 | 20 | n |  | TRUE
20 | bus_MV_360_0_node_27 | 20 | n |  | TRUE
21 | bus_MV_360_0_node_8 | 20 | n |  | TRUE
22 | bus_MV_360_0_node_9 | 20 | n |  | TRUE
23 | bus_MV_360_0_node_11 | 20 | n |  | TRUE
24 | bus_MV_360_0_node_12 | 20 | n |  | TRUE
25 | bus_MV_360_0_node_165 | 20 | n |  | TRUE
26 | bus_MV_360_0_node_164 | 20 | n |  | TRUE
27 | bus_MV_360_0_node_35 | 20 | n |  | TRUE
28 | bus_MV_360_0_node_36 | 20 | n |  | TRUE
29 | bus_MV_360_0_node_37 | 20 | n |  | TRUE
30 | bus_MV_360_0_node_134 | 20 | n |  | TRUE
31 | bus_MV_360_0_node_103 | 20 | n |  | TRUE
32 | bus_MV_360_0_node_13 | 20 | n |  | TRUE
33 | bus_MV_360_0_node_14 | 20 | n |  | TRUE
34 | bus_MV_360_0_node_15 | 20 | n |  | TRUE
35 | bus_MV_360_0_node_147 | 20 | n |  | TRUE
36 | bus_MV_360_0_node_156 | 20 | n |  | TRUE
37 | bus_MV_360_0_node_17 | 20 | n |  | TRUE
38 | bus_MV_360_0_node_148 | 20 | n |  | TRUE
39 | bus_MV_360_0_node_16 | 20 | n |  | TRUE
40 | bus_MV_360_0_node_34 | 20 | n |  | TRUE
41 | bus_MV_360_0_node_169 | 20 | n |  | TRUE
42 | bus_MV_360_0_node_149 | 20 | n |  | TRUE
43 | bus_MV_360_0_node_166 | 20 | n |  | TRUE
44 | bus_MV_360_0_node_177 | 20 | n |  | TRUE
45 | bus_MV_360_0_node_18 | 20 | n |  | TRUE
46 | bus_MV_360_0_node_19 | 20 | n |  | TRUE
47 | bus_MV_360_0_node_20 | 20 | n |  | TRUE
48 | bus_MV_360_0_node_21 | 20 | n |  | TRUE
49 | bus_MV_360_0_node_22 | 20 | n |  | TRUE
50 | bus_MV_360_0_node_125 | 20 | n |  | TRUE
51 | bus_MV_360_0_node_153 | 20 | n |  | TRUE
52 | bus_MV_360_0_node_171 | 20 | n |  | TRUE
53 | bus_MV_360_0_node_38 | 20 | n |  | TRUE
54 | bus_MV_360_0_node_155 | 20 | n |  | TRUE
55 | bus_MV_360_0_node_126 | 20 | n |  | TRUE
56 | bus_MV_360_0_node_129 | 20 | n |  | TRUE
57 | bus_MV_360_0_node_172 | 20 | n |  | TRUE
58 | bus_MV_360_0_node_130 | 20 | n |  | TRUE
59 | bus_MV_360_0_node_128 | 20 | n |  | TRUE
60 | bus_MV_360_0_node_43 | 20 | n |  | TRUE
61 | bus_MV_360_0_node_179 | 20 | n |  | TRUE
62 | bus_MV_360_0_node_41 | 20 | n |  | TRUE
63 | bus_MV_360_0_node_91 | 20 | n |  | TRUE
64 | bus_MV_360_0_node_85 | 20 | n |  | TRUE
65 | bus_MV_360_0_node_23 | 20 | n |  | TRUE
66 | bus_MV_360_0_node_24 | 20 | n |  | TRUE
67 | bus_MV_360_0_node_26 | 20 | n |  | TRUE
68 | bus_MV_360_0_node_161 | 20 | n |  | TRUE
69 | bus_MV_360_0_node_49 | 20 | n |  | TRUE
70 | bus_MV_360_0_node_160 | 20 | n |  | TRUE
71 | bus_MV_360_0_node_57 | 20 | n |  | TRUE
72 | bus_MV_360_0_node_170 | 20 | n |  | TRUE
73 | bus_MV_360_0_node_56 | 20 | n |  | TRUE
74 | bus_MV_360_0_node_47 | 20 | n |  | TRUE
75 | bus_MV_360_0_node_29 | 20 | n |  | TRUE
76 | bus_MV_360_0_node_30 | 20 | n |  | TRUE
77 | bus_MV_360_0_node_31 | 20 | n |  | TRUE
78 | bus_MV_360_0_node_39 | 20 | n |  | TRUE
79 | bus_MV_360_0_node_42 | 20 | n |  | TRUE
80 | bus_MV_360_0_node_163 | 20 | n |  | TRUE
81 | bus_MV_360_0_node_123 | 20 | n |  | TRUE
82 | bus_MV_360_0_node_44 | 20 | n |  | TRUE
83 | bus_MV_360_0_node_45 | 20 | n |  | TRUE
84 | bus_MV_360_0_node_50 | 20 | n |  | TRUE
85 | bus_MV_360_0_node_112 | 20 | n |  | TRUE
86 | bus_MV_360_0_node_184 | 20 | n |  | TRUE
87 | bus_MV_360_0_node_48 | 20 | n |  | TRUE
88 | bus_MV_360_0_node_108 | 20 | n |  | TRUE
89 | bus_MV_360_0_node_110 | 20 | n |  | TRUE
90 | bus_MV_360_0_node_51 | 20 | n |  | TRUE
91 | bus_MV_360_0_node_52 | 20 | n |  | TRUE
92 | bus_MV_360_0_node_119 | 20 | n |  | TRUE
93 | bus_MV_360_0_node_53 | 20 | n |  | TRUE
94 | bus_MV_360_0_node_136 | 20 | n |  | TRUE
95 | bus_MV_360_0_node_111 | 20 | n |  | TRUE
96 | bus_MV_360_0_node_113 | 20 | n |  | TRUE
97 | bus_MV_360_0_node_114 | 20 | n |  | TRUE
98 | bus_MV_360_0_node_117 | 20 | n |  | TRUE
99 | bus_MV_360_0_node_115 | 20 | n |  | TRUE
100 | bus_MV_360_0_node_116 | 20 | n |  | TRUE
101 | bus_MV_360_0_node_162 | 20 | n |  | TRUE
102 | bus_MV_360_0_node_59 | 20 | n |  | TRUE
103 | bus_MV_360_0_node_61 | 20 | n |  | TRUE
104 | bus_MV_360_0_node_60 | 20 | n |  | TRUE
105 | bus_MV_360_0_node_63 | 20 | n |  | TRUE
106 | bus_MV_360_0_node_62 | 20 | n |  | TRUE
107 | bus_MV_360_0_node_137 | 20 | n |  | TRUE
108 | bus_MV_360_0_node_158 | 20 | n |  | TRUE
109 | bus_MV_360_0_node_124 | 20 | n |  | TRUE
110 | bus_MV_360_0_node_74 | 20 | n |  | TRUE
111 | bus_MV_360_0_node_87 | 20 | n |  | TRUE
112 | bus_MV_360_0_node_174 | 20 | n |  | TRUE
113 | bus_MV_360_0_node_67 | 20 | n |  | TRUE
114 | bus_MV_360_0_node_72 | 20 | n |  | TRUE
115 | bus_MV_360_0_node_64 | 20 | n |  | TRUE
116 | bus_MV_360_0_node_65 | 20 | n |  | TRUE
117 | bus_MV_360_0_node_66 | 20 | n |  | TRUE
118 | bus_MV_360_0_node_75 | 20 | n |  | TRUE
119 | bus_MV_360_0_node_154 | 20 | n |  | TRUE
120 | bus_MV_360_0_node_77 | 20 | n |  | TRUE
121 | bus_MV_360_0_node_70 | 20 | n |  | TRUE
122 | bus_MV_360_0_node_78 | 20 | n |  | TRUE
123 | bus_MV_360_0_node_173 | 20 | n |  | TRUE
124 | bus_MV_360_0_node_73 | 20 | n |  | TRUE
125 | bus_MV_360_0_node_69 | 20 | n |  | TRUE
126 | bus_MV_360_0_node_68 | 20 | n |  | TRUE
127 | bus_MV_360_0_node_71 | 20 | n |  | TRUE
128 | bus_MV_360_0_node_79 | 20 | n |  | TRUE
129 | bus_MV_360_0_node_80 | 20 | n |  | TRUE
130 | bus_MV_360_0_node_76 | 20 | n |  | TRUE
131 | bus_MV_360_0_node_81 | 20 | n |  | TRUE
132 | bus_MV_360_0_node_82 | 20 | n |  | TRUE
133 | bus_MV_360_0_node_83 | 20 | n |  | TRUE
134 | bus_MV_360_0_node_90 | 20 | n |  | TRUE
135 | bus_MV_360_0_node_86 | 20 | n |  | TRUE
136 | bus_MV_360_0_node_89 | 20 | n |  | TRUE
137 | bus_MV_360_0_node_157 | 20 | n |  | TRUE
138 | bus_MV_360_0_node_159 | 20 | n |  | TRUE
139 | bus_MV_360_0_node_178 | 20 | n |  | TRUE
140 | bus_MV_360_0_node_146 | 20 | n |  | TRUE
141 | bus_MV_360_0_node_98 | 20 | n |  | TRUE
142 | bus_MV_360_0_node_99 | 20 | n |  | TRUE
143 | bus_MV_360_0_node_95 | 20 | n |  | TRUE
144 | bus_MV_360_0_node_101 | 20 | n |  | TRUE
145 | bus_MV_360_0_node_92 | 20 | n |  | TRUE
146 | bus_MV_360_0_node_93 | 20 | n |  | TRUE
147 | bus_MV_360_0_node_96 | 20 | n |  | TRUE
148 | bus_MV_360_0_node_97 | 20 | n |  | TRUE
149 | bus_MV_360_0_node_105 | 20 | n |  | TRUE
150 | bus_MV_360_0_node_106 | 20 | n |  | TRUE
151 | bus_MV_360_0_node_138 | 20 | n |  | TRUE
152 | bus_MV_360_0_node_107 | 20 | n |  | TRUE
153 | bus_MV_360_0_node_181 | 20 | n |  | TRUE
154 | bus_MV_360_0_node_183 | 20 | n |  | TRUE
155 | bus_MV_360_0_node_144 | 20 | n |  | TRUE
156 | bus_MV_360_0_node_100 | 20 | n |  | TRUE
157 | bus_MV_360_0_node_142 | 20 | n |  | TRUE
158 | bus_MV_360_0_node_176 | 20 | n |  | TRUE
159 | bus_MV_360_0_node_175 | 20 | n |  | TRUE
160 | bus_MV_360_0_node_143 | 20 | n |  | TRUE
161 | bus_MV_360_0_node_102 | 20 | n |  | TRUE
162 | bus_MV_360_0_node_152 | 20 | n |  | TRUE
163 | bus_MV_360_0_node_180 | 20 | n |  | TRUE
164 | bus_MV_360_0_node_151 | 20 | n |  | TRUE
165 | bus_MV_360_0_node_121 | 20 | n |  | TRUE
166 | bus_MV_360_0_node_122 | 20 | n |  | TRUE
167 | bus_MV_360_0_node_131 | 20 | n |  | TRUE
168 | bus_MV_360_0_node_132 | 20 | n |  | TRUE
169 | bus_MV_360_0_node_133 | 20 | n |  | TRUE
170 | bus_MV_360_0_node_135 | 20 | n |  | TRUE
171 | bus_MV_360_0_node_150 | 20 | n |  | TRUE
172 | bus_MV_360_0_node_139 | 20 | n |  | TRUE
173 | bus_MV_360_0_node_140 | 20 | n |  | TRUE
174 | bus_MV_360_0_node_141 | 20 | n |  | TRUE
175 | bus_MV_360_0_node_145 | 20 | n |  | TRUE
176 | bus_HV_360_0_node_155 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_360_0_load_0 | 0 | 0.17133 | 0.082981 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_360_0_load_6 | 5 | 0.15884 | 0.07693 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_360_0_load_118 | 6 | 0.1113 | 0.053906 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_360_0_load_32 | 9 | 0.31936 | 0.15467 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_360_0_load_168 | 11 | 0.30319 | 0.14684 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_360_0_load_58 | 12 | 0.26558 | 0.12863 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_360_0_load_167 | 13 | 0.2739 | 0.13265 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_360_0_load_54 | 14 | 0.064225 | 0.031105 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_360_0_load_182 | 16 | 0.090913 | 0.044031 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_360_0_load_120 | 18 | 0.19651 | 0.095176 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_360_0_load_8 | 21 | 0.32533 | 0.15756 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_360_0_load_165 | 25 | 0.4029 | 0.19513 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_360_0_load_164 | 26 | 0.19622 | 0.095034 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_360_0_load_35 | 27 | 0.15483 | 0.074988 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_360_0_load_13 | 32 | 0.38396 | 0.18596 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_360_0_load_147 | 35 | 0.0829 | 0.04015 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_360_0_load_156 | 36 | 0.19105 | 0.092532 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_360_0_load_34 | 40 | 0.36927 | 0.17885 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_360_0_load_169 | 41 | 0.15043 | 0.072857 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_360_0_load_166 | 43 | 0.36987 | 0.17913 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_360_0_load_177 | 44 | 0.29886 | 0.14474 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_360_0_load_18 | 45 | 0.3986 | 0.19305 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_360_0_load_125 | 50 | 0.10147 | 0.049146 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_360_0_load_153 | 51 | 0.40581 | 0.19654 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_360_0_load_171 | 52 | 0.41407 | 0.20054 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_360_0_load_38 | 53 | 0.40041 | 0.19393 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_360_0_load_155 | 54 | 0.36542 | 0.17698 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_360_0_load_172 | 57 | 0.21565 | 0.10445 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_360_0_load_179 | 61 | 0.2798 | 0.13551 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_360_0_load_23 | 65 | 0.20993 | 0.10167 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_360_0_load_161 | 68 | 0.28608 | 0.13855 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_360_0_load_160 | 70 | 0.25162 | 0.12187 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_360_0_load_170 | 72 | 0.23388 | 0.11327 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_360_0_load_56 | 73 | 0.28259 | 0.13687 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_360_0_load_29 | 75 | 0.17182 | 0.083214 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_360_0_load_39 | 78 | 0.12908 | 0.062517 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_360_0_load_163 | 80 | 0.17225 | 0.083426 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_360_0_load_44 | 82 | 0.34319 | 0.16622 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_360_0_load_184 | 86 | 0.52457 | 0.25406 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_360_0_load_108 | 88 | 0.13318 | 0.0645 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_360_0_load_110 | 89 | 0.26011 | 0.12598 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_360_0_load_119 | 92 | 0.083534 | 0.040458 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_360_0_load_136 | 94 | 0.60449 | 0.29277 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_360_0_load_111 | 95 | 0.069206 | 0.033518 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_360_0_load_117 | 98 | 0.069908 | 0.033858 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_360_0_load_115 | 99 | 0.15709 | 0.076084 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_360_0_load_116 | 100 | 0.15096 | 0.073113 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_360_0_load_162 | 101 | 0.28742 | 0.1392 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_360_0_load_59 | 102 | 0.36003 | 0.17437 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_360_0_load_137 | 107 | 0.089251 | 0.043226 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_360_0_load_158 | 108 | 0.53268 | 0.25799 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_360_0_load_87 | 111 | 0.34804 | 0.16856 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_360_0_load_72 | 114 | 0.24038 | 0.11642 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_360_0_load_75 | 118 | 0.34477 | 0.16698 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_360_0_load_154 | 119 | 0.2621 | 0.12694 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_360_0_load_77 | 120 | 0.35293 | 0.17093 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_360_0_load_78 | 122 | 0.41089 | 0.199 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_360_0_load_173 | 123 | 0.18618 | 0.090173 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_360_0_load_68 | 126 | 0.28963 | 0.14027 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_360_0_load_71 | 127 | 0.16873 | 0.081719 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_360_0_load_80 | 129 | 0.092197 | 0.044653 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_360_0_load_76 | 130 | 0.2245 | 0.10873 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_360_0_load_83 | 133 | 0.13759 | 0.066637 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_360_0_load_89 | 136 | 0.28734 | 0.13917 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_360_0_load_157 | 137 | 0.18201 | 0.088151 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_360_0_load_159 | 138 | 0.18849 | 0.091291 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_360_0_load_98 | 141 | 0.26261 | 0.12719 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_360_0_load_92 | 145 | 0.32227 | 0.15608 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_360_0_load_105 | 149 | 0.37789 | 0.18302 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_360_0_load_138 | 151 | 0.082628 | 0.040018 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_360_0_load_181 | 153 | 0.3512 | 0.17009 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_360_0_load_183 | 154 | 0.081333 | 0.039391 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_360_0_load_144 | 155 | 0.13388 | 0.064841 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_360_0_load_142 | 157 | 0.47251 | 0.22885 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_360_0_load_176 | 158 | 1.4498 | 0.70218 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_360_0_load_175 | 159 | 0.41407 | 0.20054 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_360_0_load_143 | 160 | 0.1706 | 0.082625 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_360_0_load_102 | 161 | 0.058621 | 0.028391 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_360_0_load_151 | 164 | 0.050797 | 0.024602 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_360_0_load_121 | 165 | 0.24237 | 0.11739 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_360_0_load_131 | 167 | 0.081372 | 0.03941 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_360_0_load_132 | 168 | 0.24249 | 0.11745 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_360_0_load_150 | 171 | 0.13864 | 0.067145 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_360_0_load_139 | 172 | 0.085041 | 0.041187 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 54 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_360_0_line_0 |  | 0 | 1 | 0.054046 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_360_0_line_1 |  | 1 | 2 | 0.29495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_360_0_line_2 |  | 1 | 3 | 0.26783 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_360_0_line_3 |  | 2 | 4 | 0.4101 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_360_0_line_4 |  | 2 | 5 | 0.053759 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_360_0_line_5 |  | 2 | 6 | 0.18491 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_360_0_line_6 |  | 3 | 12 | 0.07463 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_360_0_line_7 |  | 3 | 7 | 0.99657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_360_0_line_8 |  | 4 | 13 | 0.007738 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_360_0_line_9 |  | 6 | 15 | 0.071203 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_360_0_line_10 |  | 6 | 14 | 0.06883 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_360_0_line_11 |  | 7 | 8 | 0.33316 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_360_0_line_12 |  | 7 | 9 | 0.004926 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_360_0_line_13 |  | 8 | 10 | 0.379 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_360_0_line_14 |  | 8 | 11 | 0.041833 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_360_0_line_15 |  | 10 | 16 | 0.022506 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_360_0_line_16 |  | 15 | 18 | 0.17774 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_360_0_line_17 |  | 15 | 93 | 0.088431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_360_0_line_18 |  | 17 | 18 | 0.10317 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_360_0_line_19 |  | 17 | 19 | 0.085099 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_360_0_line_20 |  | 17 | 20 | 0.12268 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
21 | MV_360_0_line_21 |  | 19 | 65 | 0.050673 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_360_0_line_22 |  | 20 | 70 | 0.031457 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
23 | MV_360_0_line_23 |  | 21 | 22 | 0.038755 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_360_0_line_24 |  | 22 | 23 | 1.022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_360_0_line_25 |  | 22 | 24 | 0.48937 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_360_0_line_26 |  | 23 | 25 | 0.03827 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_360_0_line_27 |  | 24 | 26 | 0.09697 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_360_0_line_28 |  | 25 | 30 | 0.075329 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_360_0_line_29 |  | 26 | 31 | 0.51659 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_360_0_line_30 |  | 27 | 28 | 0.024799 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_360_0_line_31 |  | 28 | 29 | 0.083443 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_360_0_line_32 |  | 29 | 53 | 0.040246 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_360_0_line_33 |  | 30 | 170 | 0.50775 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_360_0_line_34 |  | 30 | 169 | 0.36932 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_360_0_line_35 |  | 31 | 161 | 0.010231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_360_0_line_36 |  | 32 | 33 | 0.049578 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_360_0_line_37 |  | 33 | 34 | 0.48833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_360_0_line_38 |  | 33 | 35 | 1.4687 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_360_0_line_39 |  | 34 | 36 | 0.009885 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_360_0_line_40 |  | 34 | 37 | 1.1438 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_360_0_line_41 |  | 34 | 38 | 0.4087 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_360_0_line_42 |  | 37 | 41 | 0.047097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_360_0_line_43 |  | 37 | 39 | 0.39946 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_360_0_line_44 |  | 38 | 44 | 0.025014 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_360_0_line_45 |  | 38 | 42 | 0.41783 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_360_0_line_46 |  | 39 | 40 | 0.00529 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_360_0_line_47 |  | 42 | 43 | 0.044962 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_360_0_line_48 |  | 43 | 77 | 0.049635 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_360_0_line_49 |  | 44 | 59 | 0.029778 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_360_0_line_50 |  | 45 | 46 | 0.004769 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_360_0_line_51 |  | 46 | 47 | 0.1364 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
52 | MV_360_0_line_52 |  | 46 | 48 | 0.45564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_360_0_line_53 |  | 46 | 49 | 0.34643 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
54 | MV_360_0_line_54 |  | 47 | 50 | 0.16089 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
55 | MV_360_0_line_55 |  | 47 | 51 | 0.025421 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_360_0_line_56 |  | 48 | 52 | 0.039479 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_360_0_line_57 |  | 49 | 53 | 0.051614 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_360_0_line_58 |  | 49 | 54 | 0.34604 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
59 | MV_360_0_line_59 |  | 50 | 55 | 0.021525 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
60 | MV_360_0_line_60 |  | 54 | 63 | 0.010625 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
61 | MV_360_0_line_61 |  | 55 | 56 | 0.10076 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
62 | MV_360_0_line_62 |  | 56 | 57 | 0.015589 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_360_0_line_63 |  | 56 | 58 | 0.34731 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
64 | MV_360_0_line_64 |  | 56 | 59 | 0.27196 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_360_0_line_65 |  | 58 | 70 | 0.037095 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
66 | MV_360_0_line_66 |  | 60 | 61 | 0.08425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_360_0_line_67 |  | 60 | 62 | 0.18359 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_360_0_line_68 |  | 61 | 81 | 0.01358 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_360_0_line_69 |  | 62 | 78 | 0.071633 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_360_0_line_70 |  | 63 | 64 | 0.47912 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
71 | MV_360_0_line_71 |  | 64 | 134 | 0.38254 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_360_0_line_72 |  | 64 | 135 | 0.17431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_360_0_line_73 |  | 64 | 136 | 0.005171 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_360_0_line_74 |  | 64 | 132 | 0.31262 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
75 | MV_360_0_line_75 |  | 65 | 66 | 0.038058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_360_0_line_76 |  | 66 | 67 | 0.1991 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_360_0_line_77 |  | 67 | 68 | 0.038022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_360_0_line_78 |  | 67 | 69 | 0.43845 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_360_0_line_79 |  | 69 | 73 | 0.009077 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_360_0_line_80 |  | 69 | 74 | 0.37877 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_360_0_line_81 |  | 69 | 71 | 0.50984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_360_0_line_82 |  | 71 | 72 | 0.028312 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_360_0_line_83 |  | 74 | 86 | 0.014593 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_360_0_line_84 |  | 74 | 87 | 0.253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_360_0_line_85 |  | 75 | 76 | 0.12527 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_360_0_line_86 |  | 76 | 77 | 0.20901 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_360_0_line_87 |  | 78 | 79 | 0.29841 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
88 | MV_360_0_line_88 |  | 79 | 80 | 0.024885 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_360_0_line_89 |  | 81 | 139 | 0.13789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_360_0_line_90 |  | 81 | 166 | 0.15478 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_360_0_line_91 |  | 82 | 83 | 0.042534 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
92 | MV_360_0_line_92 |  | 83 | 84 | 0.37263 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_360_0_line_93 |  | 83 | 85 | 0.075834 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
94 | MV_360_0_line_94 |  | 84 | 89 | 0.01753 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_360_0_line_95 |  | 85 | 96 | 0.10238 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_360_0_line_96 |  | 85 | 95 | 0.028633 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_360_0_line_97 |  | 87 | 88 | 0.013869 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_360_0_line_98 |  | 88 | 101 | 0.08067 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_360_0_line_99 |  | 90 | 91 | 0.049993 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_360_0_line_100 |  | 90 | 92 | 0.069046 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_360_0_line_101 |  | 91 | 93 | 0.099681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_360_0_line_102 |  | 91 | 94 | 0.024901 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_360_0_line_103 |  | 94 | 96 | 0.060433 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_360_0_line_104 |  | 96 | 97 | 0.029814 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_360_0_line_105 |  | 97 | 98 | 0.05024 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_360_0_line_106 |  | 97 | 99 | 0.05527 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_360_0_line_107 |  | 99 | 100 | 0.014559 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_360_0_line_108 |  | 102 | 103 | 0.096277 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
109 | MV_360_0_line_109 |  | 102 | 104 | 0.098256 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
110 | MV_360_0_line_110 |  | 103 | 105 | 0.48373 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
111 | MV_360_0_line_111 |  | 104 | 106 | 0.43551 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_360_0_line_112 |  | 105 | 113 | 0.53853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_360_0_line_113 |  | 105 | 114 | 0.041855 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
114 | MV_360_0_line_114 |  | 106 | 111 | 0.12617 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
115 | MV_360_0_line_115 |  | 106 | 112 | 0.20591 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
116 | MV_360_0_line_116 |  | 107 | 108 | 0.091127 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
117 | MV_360_0_line_117 |  | 107 | 109 | 0.066031 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_360_0_line_118 |  | 107 | 110 | 0.39091 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
119 | MV_360_0_line_119 |  | 109 | 118 | 0.48093 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
120 | MV_360_0_line_120 |  | 110 | 130 | 0.013888 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
121 | MV_360_0_line_121 |  | 110 | 124 | 0.27541 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
122 | MV_360_0_line_122 |  | 112 | 123 | 0.013497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_360_0_line_123 |  | 113 | 121 | 0.24507 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_360_0_line_124 |  | 113 | 122 | 0.08241 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
125 | MV_360_0_line_125 |  | 114 | 124 | 0.06581 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
126 | MV_360_0_line_126 |  | 115 | 116 | 0.33309 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_360_0_line_127 |  | 115 | 117 | 0.58748 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_360_0_line_128 |  | 115 | 118 | 0.029527 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_360_0_line_129 |  | 116 | 119 | 0.052342 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
130 | MV_360_0_line_130 |  | 117 | 120 | 0.019108 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_360_0_line_131 |  | 121 | 127 | 0.013473 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_360_0_line_132 |  | 121 | 125 | 0.18251 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_360_0_line_133 |  | 122 | 128 | 0.040887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_360_0_line_134 |  | 123 | 158 | 0.056468 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
135 | MV_360_0_line_135 |  | 125 | 126 | 0.12778 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
136 | MV_360_0_line_136 |  | 128 | 129 | 0.024676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_360_0_line_137 |  | 130 | 131 | 0.13425 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
138 | MV_360_0_line_138 |  | 131 | 132 | 0.06502 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
139 | MV_360_0_line_139 |  | 132 | 133 | 0.059043 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_360_0_line_140 |  | 134 | 138 | 0.023808 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_360_0_line_141 |  | 135 | 137 | 0.036135 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_360_0_line_142 |  | 137 | 140 | 0.074093 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
143 | MV_360_0_line_143 |  | 138 | 139 | 0.072875 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
144 | MV_360_0_line_144 |  | 140 | 175 | 0.28324 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_360_0_line_145 |  | 141 | 142 | 0.09738 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
146 | MV_360_0_line_146 |  | 141 | 143 | 0.067794 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_360_0_line_147 |  | 142 | 144 | 0.33212 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_360_0_line_148 |  | 143 | 146 | 0.74835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_360_0_line_149 |  | 144 | 158 | 0.054074 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_360_0_line_150 |  | 144 | 159 | 0.020756 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_360_0_line_151 |  | 144 | 156 | 0.13595 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_360_0_line_152 |  | 145 | 146 | 0.052519 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
153 | MV_360_0_line_153 |  | 147 | 148 | 0.57458 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_360_0_line_154 |  | 147 | 149 | 0.075996 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_360_0_line_155 |  | 148 | 150 | 0.22916 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_360_0_line_156 |  | 148 | 151 | 0.010468 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_360_0_line_157 |  | 150 | 152 | 0.075874 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_360_0_line_158 |  | 150 | 153 | 0.040546 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_360_0_line_159 |  | 151 | 155 | 0.31663 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
160 | MV_360_0_line_160 |  | 152 | 154 | 0.012305 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_360_0_line_161 |  | 153 | 163 | 0.006676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_360_0_line_162 |  | 155 | 175 | 0.021773 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_360_0_line_163 |  | 156 | 157 | 0.01862 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_360_0_line_164 |  | 157 | 160 | 0.032403 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_360_0_line_165 |  | 160 | 174 | 0.04796 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_360_0_line_166 |  | 161 | 162 | 0.24923 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
167 | MV_360_0_line_167 |  | 162 | 163 | 0.061267 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_360_0_line_168 |  | 162 | 164 | 0.12089 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
169 | MV_360_0_line_169 |  | 165 | 166 | 0.035561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_360_0_line_170 |  | 167 | 168 | 0.033309 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
171 | MV_360_0_line_171 |  | 167 | 169 | 0.14211 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_360_0_line_172 |  | 170 | 171 | 0.06345 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_360_0_line_173 |  | 172 | 173 | 0.15915 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
174 | MV_360_0_line_174 |  | 173 | 174 | 0.055982 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_360_0_trafo_155 | 25 MVA 110/20 kV | 176 | 54 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2681512.6763 | 1241067.9142
1 | 2681528.6781 | 1241119.5375
2 | 2681684.5265 | 1240979.1905
3 | 2681486.7904 | 1241279.488
4 | 2681803.7991 | 1240706.0039
5 | 2681675.6461 | 1240927.22
6 | 2681802.6994 | 1241121.4097
7 | 2681529.0868 | 1241725.2658
8 | 2681279.292 | 1241671.2573
9 | 2681529.072 | 1241730.1913
10 | 2681276.5374 | 1241864.0243
11 | 2681305.581 | 1241638.7162
12 | 2681459.2446 | 1241348.8485
13 | 2681797.2831 | 1240710.2061
14 | 2681756.2517 | 1241172.2047
15 | 2681866.2651 | 1241100.3693
16 | 2681279.3987 | 1241841.703
17 | 2682042.6657 | 1240903.2854
18 | 2682014.5843 | 1241002.434
19 | 2682047.3627 | 1240951.874
20 | 2682128.1049 | 1240828.0795
21 | 2682622.3685 | 1240294.9886
22 | 2682654.5339 | 1240316.6073
23 | 2682433.6597 | 1239901.2176
24 | 2682894.8269 | 1240379.0463
25 | 2682403.7422 | 1239924.4634
26 | 2682991.2299 | 1240368.5743
27 | 2682672.2744 | 1240693.9245
28 | 2682686.6478 | 1240714.1614
29 | 2682675.9275 | 1240767.139
30 | 2682340.9204 | 1239888.6664
31 | 2683501.8199 | 1240290.0431
32 | 2681873.0413 | 1239674.778
33 | 2681824.8407 | 1239663.172
34 | 2681955.3888 | 1240028.7663
35 | 2680422.6346 | 1239226.1628
36 | 2681948.1262 | 1240035.4931
37 | 2682252.8801 | 1239531.6138
38 | 2682154.6049 | 1240328.1441
39 | 2682091.8026 | 1239351.3566
40 | 2682087.5732 | 1239348.1625
41 | 2682287.485 | 1239503.7067
42 | 2681885.943 | 1240329.256
43 | 2681840.9877 | 1240332.7831
44 | 2682167.1999 | 1240349.756
45 | 2682351.4722 | 1240723.3652
46 | 2682353.0772 | 1240718.8731
47 | 2682304.4563 | 1240649.3825
48 | 2682496.3515 | 1240985.7312
49 | 2682648.0007 | 1240854.5462
50 | 2682146.5351 | 1240618.6219
51 | 2682296.0775 | 1240625.3825
52 | 2682492.0425 | 1240946.4876
53 | 2682664.9081 | 1240805.7799
54 | 2682977.1225 | 1240961.4247
55 | 2682125.2805 | 1240620.2028
56 | 2682132.2117 | 1240567.4609
57 | 2682132.9943 | 1240551.894
58 | 2682195.6676 | 1240817.9628
59 | 2682170.7154 | 1240379.3258
60 | 2682629.0089 | 1241421.6111
61 | 2682709.5782 | 1241445.1611
62 | 2682575.0768 | 1241596.3641
63 | 2682986.7532 | 1240965.9737
64 | 2683160.5117 | 1241248.9862
65 | 2682085.4186 | 1240985.3329
66 | 2682114.0032 | 1241010.4595
67 | 2682165.0041 | 1241154.2793
68 | 2682158.2704 | 1241191.6907
69 | 2682061.4728 | 1241364.0755
70 | 2682159.1351 | 1240822.9162
71 | 2682356.896 | 1241204.7854
72 | 2682332.0274 | 1241218.3169
73 | 2682067.1512 | 1241356.9822
74 | 2682021.3169 | 1241631.3456
75 | 2681697.5896 | 1240072.7007
76 | 2681820.2109 | 1240080.1165
77 | 2681833.3452 | 1240283.7428
78 | 2682552.8071 | 1241664.4589
79 | 2682310.2009 | 1241838.215
80 | 2682291.9185 | 1241855.1514
81 | 2682722.4773 | 1241449.5218
82 | 2681832.4047 | 1241440.7463
83 | 2681869.6628 | 1241461.2636
84 | 2681906.6911 | 1241662.6966
85 | 2681797.8975 | 1241436.7568
86 | 2682023.5521 | 1241617.878
87 | 2681949.8289 | 1241715.0295
88 | 2681946.4369 | 1241728.3138
89 | 2681917.3137 | 1241654.02
90 | 2681850.4979 | 1241252.8166
91 | 2681815.3847 | 1241264.73
92 | 2681866.9447 | 1241185.7577
93 | 2681840.6284 | 1241184.9875
94 | 2681810.8199 | 1241289.2086
95 | 2681769.2755 | 1241435.9551
96 | 2681806.1014 | 1241346.2828
97 | 2681788.5514 | 1241359.4615
98 | 2681738.3151 | 1241355.5557
99 | 2681771.6722 | 1241402.5666
100 | 2681757.1184 | 1241402.192
101 | 2681887.238 | 1241783.1147
102 | 2683915.5988 | 1241587.5668
103 | 2683850.4084 | 1241590.1586
104 | 2683932.461 | 1241490.7686
105 | 2683639.7213 | 1241741.7847
106 | 2683982.5332 | 1241188.8478
107 | 2682948.4129 | 1241666.8297
108 | 2683005.7798 | 1241596.026
109 | 2682927.0806 | 1241727.7432
110 | 2683328.951 | 1241577.3623
111 | 2683861.603 | 1241152.8568
112 | 2684129.7651 | 1241332.7918
113 | 2683880.9747 | 1242088.1614
114 | 2683604.0966 | 1241719.6447
115 | 2683410.9575 | 1241890.362
116 | 2683344.3882 | 1242179.1465
117 | 2683637.224 | 1242255.0981
118 | 2683383.5172 | 1241879.2574
119 | 2683296.7781 | 1242200.894
120 | 2683655.4831 | 1242260.9041
121 | 2683884.6517 | 1241904.0691
122 | 2683963.2708 | 1242083.8329
123 | 2684141.5266 | 1241339.4744
124 | 2683546.3332 | 1241687.8418
125 | 2683968.9102 | 1241842.4714
126 | 2683975.5178 | 1241714.8616
127 | 2683889.0194 | 1241891.3995
128 | 2683977.6635 | 1242045.5532
129 | 2684000.9193 | 1242053.8048
130 | 2683335.4671 | 1241565.0894
131 | 2683378.5051 | 1241438.6471
132 | 2683389.2059 | 1241374.5178
133 | 2683447.5695 | 1241374.9114
134 | 2682853.4596 | 1241282.8063
135 | 2683283.4682 | 1241195.1711
136 | 2683160.4934 | 1241243.8156
137 | 2683315.0836 | 1241180.5931
138 | 2682829.6203 | 1241283.2184
139 | 2682772.9063 | 1241328.9825
140 | 2683346.5145 | 1241113.4971
141 | 2684319.9659 | 1240935.2922
142 | 2684362.2753 | 1241023.001
143 | 2684291.1609 | 1240874.7284
144 | 2684210.5198 | 1241253.5017
145 | 2684373.9197 | 1240629.5716
146 | 2684359.4912 | 1240680.0697
147 | 2684034.4701 | 1240720.3784
148 | 2683756.8627 | 1240700.5526
149 | 2684096.1133 | 1240757.9783
150 | 2683667.5092 | 1240513.8363
151 | 2683756.799 | 1240711.0202
152 | 2683619.4339 | 1240541.2677
153 | 2683689.3853 | 1240479.6645
154 | 2683611.2537 | 1240533.5914
155 | 2683491.5858 | 1240883.9926
156 | 2684312.2424 | 1241314.3228
157 | 2684300.0027 | 1241328.3541
158 | 2684180.1972 | 1241298.3263
159 | 2684189.9688 | 1241250.219
160 | 2684278.796 | 1241352.8537
161 | 2683511.2154 | 1240294.156
162 | 2683725.1837 | 1240421.9499
163 | 2683692.4411 | 1240473.7255
164 | 2683796.598 | 1240324.4095
165 | 2682675.4276 | 1241566.784
166 | 2682707.7446 | 1241580.4773
167 | 2682181.1103 | 1239897.9986
168 | 2682191.3431 | 1239866.3005
169 | 2682137.4513 | 1240033.2406
170 | 2682489.3232 | 1239617.855
171 | 2682438.0271 | 1239580.3048
172 | 2684324.4503 | 1241377.2541
173 | 2684262.7982 | 1241421.3203
174 | 2684247.4818 | 1241389.1797
175 | 2683472.8206 | 1240895.0256
176 | 2682977.1225 | 1240961.4247

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99086 | -0.21164 | 0.17133 | 0.082981
1 | 0.99087 | -0.21153 | 0 | 0
2 | 0.99131 | -0.21469 | 0 | 0
3 | 0.99054 | -0.2091 | 0 | 0
4 | 0.99116 | -0.21346 | 0 | 0
5 | 0.9913 | -0.21459 | 0.15884 | 0.07693
6 | 0.99187 | -0.21005 | 0.1113 | 0.053906
7 | 0.98964 | -0.2023 | 0 | 0
8 | 0.98947 | -0.20098 | 0 | 0
9 | 0.98964 | -0.20228 | 0.31936 | 0.15467
10 | 0.98943 | -0.20068 | 0 | 0
11 | 0.98945 | -0.20114 | 0.30319 | 0.14684
12 | 0.9905 | -0.20934 | 0.26558 | 0.12863
13 | 0.99116 | -0.21343 | 0.2739 | 0.13265
14 | 0.99186 | -0.2101 | 0.064225 | 0.031105
15 | 0.99203 | -0.21126 | 0 | 0
16 | 0.98942 | -0.20066 | 0.090913 | 0.044031
17 | 0.99371 | -0.20622 | 0 | 0
18 | 0.99322 | -0.20221 | 0.19651 | 0.095176
19 | 0.9935 | -0.20445 | 0 | 0
20 | 0.99409 | -0.20187 | 0 | 0
21 | 0.99083 | -0.018678 | 0.32533 | 0.15756
22 | 0.99085 | -0.018523 | 0 | 0
23 | 0.98973 | -0.010437 | 0 | 0
24 | 0.99159 | -0.023763 | 0 | 0
25 | 0.98969 | -0.010103 | 0.4029 | 0.19513
26 | 0.99181 | -0.021799 | 0.19622 | 0.095034
27 | 0.99761 | -0.13296 | 0.15483 | 0.074988
28 | 0.99761 | -0.133 | 0 | 0
29 | 0.99763 | -0.13315 | 0 | 0
30 | 0.98964 | -0.0098094 | 0 | 0
31 | 0.99318 | -0.010096 | 0 | 0
32 | 0.99321 | -0.18269 | 0.38396 | 0.18596
33 | 0.99324 | -0.18246 | 0 | 0
34 | 0.99353 | -0.18499 | 0 | 0
35 | 0.99301 | -0.18406 | 0.0829 | 0.04015
36 | 0.99353 | -0.18496 | 0.19105 | 0.092532
37 | 0.99278 | -0.17956 | 0 | 0
38 | 0.99414 | -0.18934 | 0 | 0
39 | 0.99259 | -0.17789 | 0 | 0
40 | 0.99259 | -0.17787 | 0.36927 | 0.17885
41 | 0.99277 | -0.17947 | 0.15043 | 0.072857
42 | 0.99386 | -0.18701 | 0 | 0
43 | 0.99383 | -0.18674 | 0.36987 | 0.17913
44 | 0.99423 | -0.18864 | 0.29886 | 0.14474
45 | 0.99662 | -0.13815 | 0.3986 | 0.19305
46 | 0.99663 | -0.13817 | 0 | 0
47 | 0.99624 | -0.14009 | 0 | 0
48 | 0.99639 | -0.13606 | 0 | 0
49 | 0.99769 | -0.13285 | 0 | 0
50 | 0.99536 | -0.19122 | 0.10147 | 0.049146
51 | 0.99622 | -0.14021 | 0.40581 | 0.19654
52 | 0.99635 | -0.13626 | 0.41407 | 0.20054
53 | 0.99764 | -0.13322 | 0.40041 | 0.19393
54 | 1 | 0 | -21.3758 | -9.7302
55 | 0.9953 | -0.19151 | 0 | 0
56 | 0.99504 | -0.19287 | 0 | 0
57 | 0.99503 | -0.19283 | 0.21565 | 0.10445
58 | 0.99437 | -0.19611 | 0 | 0
59 | 0.99434 | -0.1877 | 0 | 0
60 | 0.99739 | -0.0037729 | 0 | 0
61 | 0.99742 | -0.0040351 | 0.2798 | 0.13551
62 | 0.99732 | -0.0031643 | 0 | 0
63 | 0.99996 | -0.00019473 | 0 | 0
64 | 0.99821 | -0.0088823 | 0 | 0
65 | 0.99337 | -0.2034 | 0.20993 | 0.10167
66 | 0.99329 | -0.2027 | 0 | 0
67 | 0.99284 | -0.19901 | 0 | 0
68 | 0.99283 | -0.19888 | 0.28608 | 0.13855
69 | 0.99203 | -0.19216 | 0 | 0
70 | 0.99429 | -0.19645 | 0.25162 | 0.12187
71 | 0.99187 | -0.19091 | 0 | 0
72 | 0.99186 | -0.19099 | 0.23388 | 0.11327
73 | 0.99202 | -0.19213 | 0.28259 | 0.13687
74 | 0.99157 | -0.18808 | 0 | 0
75 | 0.99374 | -0.18605 | 0.17182 | 0.083214
76 | 0.99377 | -0.1863 | 0 | 0
77 | 0.99381 | -0.18666 | 0 | 0
78 | 0.99729 | -0.0029128 | 0.12908 | 0.062517
79 | 0.99719 | -0.003557 | 0 | 0
80 | 0.99719 | -0.0035059 | 0.17225 | 0.083426
81 | 0.99743 | -0.004122 | 0 | 0
82 | 0.99127 | -0.20642 | 0.34319 | 0.16622
83 | 0.9913 | -0.20624 | 0 | 0
84 | 0.99117 | -0.20518 | 0 | 0
85 | 0.99139 | -0.20562 | 0 | 0
86 | 0.99156 | -0.18799 | 0.52457 | 0.25406
87 | 0.99143 | -0.18684 | 0 | 0
88 | 0.99142 | -0.18677 | 0.13318 | 0.0645
89 | 0.99117 | -0.20512 | 0.26011 | 0.12598
90 | 0.9916 | -0.20752 | 0 | 0
91 | 0.99161 | -0.20757 | 0 | 0
92 | 0.9916 | -0.20745 | 0.083534 | 0.040458
93 | 0.99183 | -0.20953 | 0 | 0
94 | 0.99156 | -0.20709 | 0.60449 | 0.29277
95 | 0.99138 | -0.2056 | 0.069206 | 0.033518
96 | 0.99147 | -0.20638 | 0 | 0
97 | 0.99146 | -0.20625 | 0 | 0
98 | 0.99146 | -0.20621 | 0.069908 | 0.033858
99 | 0.99144 | -0.20605 | 0.15709 | 0.076084
100 | 0.99143 | -0.20602 | 0.15096 | 0.073113
101 | 0.99138 | -0.18706 | 0.28742 | 0.1392
102 | 0.99547 | -0.022866 | 0.36003 | 0.17437
103 | 0.99568 | -0.020528 | 0 | 0
104 | 0.99476 | -0.027767 | 0 | 0
105 | 0.99633 | -0.017712 | 0 | 0
106 | 0.99269 | -0.0094074 | 0 | 0
107 | 0.99579 | -0.023041 | 0.089251 | 0.043226
108 | 0.9957 | -0.023633 | 0.53268 | 0.25799
109 | 0.99571 | -0.022379 | 0 | 0
110 | 0.99698 | -0.014661 | 0 | 0
111 | 0.9926 | -0.0099468 | 0.34804 | 0.16856
112 | 0.99135 | -0.018625 | 0 | 0
113 | 0.99567 | -0.012111 | 0 | 0
114 | 0.9964 | -0.017396 | 0.24038 | 0.11642
115 | 0.9948 | -0.028795 | 0 | 0
116 | 0.99469 | -0.027825 | 0 | 0
117 | 0.99454 | -0.026567 | 0 | 0
118 | 0.99482 | -0.028972 | 0.34477 | 0.16698
119 | 0.99466 | -0.027993 | 0.2621 | 0.12694
120 | 0.99453 | -0.026486 | 0.35293 | 0.17093
121 | 0.99552 | -0.010876 | 0 | 0
122 | 0.99559 | -0.012628 | 0.41089 | 0.199
123 | 0.99129 | -0.018107 | 0.18618 | 0.090173
124 | 0.99651 | -0.016876 | 0 | 0
125 | 0.99546 | -0.010265 | 0 | 0
126 | 0.99539 | -0.010717 | 0.28963 | 0.14027
127 | 0.99552 | -0.010849 | 0.16873 | 0.081719
128 | 0.99558 | -0.012585 | 0 | 0
129 | 0.99558 | -0.012558 | 0.092197 | 0.044653
130 | 0.99701 | -0.014517 | 0.2245 | 0.10873
131 | 0.99732 | -0.013076 | 0 | 0
132 | 0.99748 | -0.012373 | 0 | 0
133 | 0.99746 | -0.012278 | 0.13759 | 0.066637
134 | 0.99772 | -0.0047775 | 0 | 0
135 | 0.99761 | -0.0043276 | 0 | 0
136 | 0.99821 | -0.0088645 | 0.28734 | 0.13917
137 | 0.99749 | -0.003377 | 0.18201 | 0.088151
138 | 0.99769 | -0.0045146 | 0.18849 | 0.091291
139 | 0.99757 | -0.0053506 | 0 | 0
140 | 0.99713 | -0.0062888 | 0 | 0
141 | 0.99046 | -0.018501 | 0.26261 | 0.12719
142 | 0.99057 | -0.017637 | 0 | 0
143 | 0.99044 | -0.018315 | 0 | 0
144 | 0.99082 | -0.019505 | 0 | 0
145 | 0.99009 | -0.016011 | 0.32227 | 0.15608
146 | 0.99013 | -0.015802 | 0 | 0
147 | 0.9944 | -0.0080503 | 0 | 0
148 | 0.99467 | -0.010359 | 0 | 0
149 | 0.99436 | -0.0077072 | 0.37789 | 0.18302
150 | 0.99411 | -0.0060738 | 0 | 0
151 | 0.9947 | -0.01059 | 0.082628 | 0.040018
152 | 0.9941 | -0.0060049 | 0 | 0
153 | 0.99402 | -0.0053413 | 0.3512 | 0.17009
154 | 0.9941 | -0.0059929 | 0.081333 | 0.039391
155 | 0.99615 | 0.0011573 | 0.13388 | 0.064841
156 | 0.99069 | -0.018378 | 0 | 0
157 | 0.99068 | -0.018221 | 0.47251 | 0.22885
158 | 0.99094 | -0.020507 | 1.4498 | 0.70218
159 | 0.99081 | -0.019401 | 0.41407 | 0.20054
160 | 0.99067 | -0.018134 | 0.1706 | 0.082625
161 | 0.9932 | -0.010225 | 0.058621 | 0.028391
162 | 0.99389 | -0.0043969 | 0 | 0
163 | 0.994 | -0.0052488 | 0 | 0
164 | 0.99388 | -0.0044727 | 0.050797 | 0.024602
165 | 0.99737 | -0.0035948 | 0.24237 | 0.11739
166 | 0.99738 | -0.0036974 | 0 | 0
167 | 0.98943 | -0.0080105 | 0.081372 | 0.03941
168 | 0.98942 | -0.0079127 | 0.24249 | 0.11745
169 | 0.98949 | -0.0085504 | 0 | 0
170 | 0.98955 | -0.0091946 | 0 | 0
171 | 0.98954 | -0.0090902 | 0.13864 | 0.067145
172 | 0.99064 | -0.017914 | 0.085041 | 0.041187
173 | 0.99065 | -0.01806 | 0 | 0
174 | 0.99066 | -0.018102 | 0 | 0
175 | 0.99622 | 0.00062057 | 0 | 0
176 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.17133 | -0.082981 | 0.17134 | 0.082919 | 2.9617e-06 | -6.1493e-05 | 0.0055463 | 0.0055454 | 0.0055463 | 0.99086 | -0.21164 | 0.99087 | -0.21153 | 2.6411
1 | -1.1515 | -0.51041 | 1.152 | 0.50365 | 0.00052904 | -0.0067604 | 0.036695 | 0.036614 | 0.036695 | 0.99087 | -0.21153 | 0.99131 | -0.21469 | 16.6797
2 | 0.98018 | 0.42749 | -0.97983 | -0.43366 | 0.00034784 | -0.0061732 | 0.031154 | 0.031227 | 0.031227 | 0.99087 | -0.21153 | 0.99054 | -0.2091 | 14.1942
3 | 0.27394 | 0.12287 | -0.2739 | -0.13247 | 4.2409e-05 | -0.0096081 | 0.008743 | 0.0088613 | 0.0088613 | 0.99131 | -0.21469 | 0.99116 | -0.21346 | 4.0279
4 | 0.15884 | 0.075669 | -0.15884 | -0.07693 | 1.8899e-06 | -0.0012608 | 0.0051236 | 0.0051395 | 0.0051395 | 0.99131 | -0.21469 | 0.9913 | -0.21459 | 2.3361
5 | -1.5848 | -0.70218 | 1.5857 | 0.70249 | 0.00083942 | 0.00030874 | 0.050478 | 0.050476 | 0.050478 | 0.99131 | -0.21469 | 0.99187 | -0.21005 | 24.0373
6 | 0.26559 | 0.12855 | -0.26558 | -0.12863 | 9.8336e-06 | -8.1254e-05 | 0.0085991 | 0.0086002 | 0.0086002 | 0.99054 | -0.2091 | 0.9905 | -0.20934 | 4.0954
7 | 0.71424 | 0.30512 | -0.71355 | -0.32824 | 0.00068983 | -0.02312 | 0.022635 | 0.022911 | 0.022911 | 0.99054 | -0.2091 | 0.98964 | -0.2023 | 10.414
8 | 0.2739 | 0.13247 | -0.2739 | -0.13265 | 8.1137e-07 | -0.00018126 | 0.0088613 | 0.0088636 | 0.0088636 | 0.99116 | -0.21346 | 0.99116 | -0.21343 | 4.0289
9 | -1.7612 | -0.78742 | 1.7615 | 0.78584 | 0.00029957 | -0.0015839 | 0.056148 | 0.056128 | 0.056148 | 0.99187 | -0.21005 | 0.99203 | -0.21126 | 25.5219
10 | 0.064225 | 0.031025 | -0.064225 | -0.031105 | 5.2873e-07 | -8.0506e-05 | 0.0020759 | 0.0020769 | 0.0020769 | 0.99187 | -0.21005 | 0.99186 | -0.2101 | 0.98901
11 | 0.39419 | 0.17368 | -0.39412 | -0.18145 | 7.0738e-05 | -0.0077683 | 0.012565 | 0.012658 | 0.012658 | 0.98964 | -0.2023 | 0.98947 | -0.20098 | 5.7538
12 | 0.31936 | 0.15456 | -0.31936 | -0.15467 | 7.0448e-07 | -0.00011498 | 0.010349 | 0.010351 | 0.010351 | 0.98964 | -0.2023 | 0.98964 | -0.20228 | 4.7049
13 | 0.090917 | 0.034647 | -0.090913 | -0.043505 | 4.2175e-06 | -0.0088579 | 0.0028386 | 0.0029405 | 0.0029405 | 0.98947 | -0.20098 | 0.98943 | -0.20068 | 1.3366
14 | 0.3032 | 0.1468 | -0.30319 | -0.14684 | 7.1997e-06 | -4.4384e-05 | 0.009828 | 0.0098286 | 0.0098286 | 0.98947 | -0.20098 | 0.98945 | -0.20114 | 4.6803
15 | 0.090913 | 0.043505 | -0.090913 | -0.044031 | 2.6038e-07 | -0.00052597 | 0.0029405 | 0.0029472 | 0.0029472 | 0.98943 | -0.20068 | 0.98942 | -0.20066 | 1.3396
16 | -3.5011 | -1.6031 | 3.5051 | 1.6054 | 0.003976 | 0.0022814 | 0.11205 | 0.11205 | 0.11205 | 0.99203 | -0.21126 | 0.99322 | -0.20221 | 53.3588
17 | 1.7396 | 0.81725 | -1.7393 | -0.81922 | 0.00036947 | -0.0019679 | 0.05593 | 0.055956 | 0.055956 | 0.99203 | -0.21126 | 0.99183 | -0.20953 | 25.4346
18 | 3.7036 | 1.6987 | -3.7016 | -1.7005 | 0.0019301 | -0.0018586 | 0.11837 | 0.1184 | 0.1184 | 0.99371 | -0.20622 | 0.99322 | -0.20221 | 53.8162
19 | 1.9612 | 0.90139 | -1.9608 | -0.90326 | 0.00044685 | -0.0018734 | 0.062704 | 0.062728 | 0.062728 | 0.99371 | -0.20622 | 0.9935 | -0.20445 | 28.5127
20 | -5.6648 | -2.6001 | 5.6667 | 2.5973 | 0.0019422 | -0.0027461 | 0.18107 | 0.18102 | 0.18107 | 0.99371 | -0.20622 | 0.99409 | -0.20187 | 50.0193
21 | 1.9608 | 0.90326 | -1.9605 | -0.90438 | 0.00026624 | -0.0011151 | 0.062728 | 0.062742 | 0.062742 | 0.9935 | -0.20445 | 0.99337 | -0.2034 | 28.5193
22 | -5.6667 | -2.5973 | 5.6677 | 2.5984 | 0.00094625 | 0.0010432 | 0.18102 | 0.18102 | 0.18102 | 0.99409 | -0.20187 | 0.99429 | -0.19645 | 51.7198
23 | -0.32533 | -0.15756 | 0.32533 | 0.15752 | 7.658e-06 | -4.0626e-05 | 0.010531 | 0.010531 | 0.010531 | 0.99083 | -0.018678 | 0.99085 | -0.018523 | 5.015
24 | 0.86659 | 0.36681 | -0.86555 | -0.39043 | 0.0010359 | -0.023623 | 0.027416 | 0.027695 | 0.027695 | 0.99085 | -0.018523 | 0.98973 | -0.010437 | 12.5887
25 | -1.1919 | -0.52433 | 1.1929 | 0.51313 | 0.00093694 | -0.011202 | 0.037937 | 0.037804 | 0.037937 | 0.99085 | -0.018523 | 0.99159 | -0.023763 | 17.2441
26 | 0.86555 | 0.39043 | -0.86551 | -0.39131 | 3.9203e-05 | -0.0008834 | 0.027695 | 0.027706 | 0.027706 | 0.98973 | -0.010437 | 0.98969 | -0.010103 | 12.5936
27 | -1.1929 | -0.51313 | 1.1931 | 0.51317 | 0.0002469 | 4.0801e-05 | 0.037804 | 0.037802 | 0.037804 | 0.99159 | -0.023763 | 0.99181 | -0.021799 | 18.0017
28 | 0.46262 | 0.19618 | -0.4626 | -0.19794 | 2.1633e-05 | -0.0017552 | 0.014657 | 0.014677 | 0.014677 | 0.98969 | -0.010103 | 0.98964 | -0.0098094 | 6.6714
29 | -1.3893 | -0.6082 | 1.3911 | 0.60872 | 0.0017932 | 0.00051571 | 0.044143 | 0.044135 | 0.044143 | 0.99181 | -0.021799 | 0.99318 | -0.010096 | 21.0203
30 | -0.15483 | -0.074988 | 0.15483 | 0.074399 | 8.1922e-07 | -0.00058903 | 0.0049781 | 0.0049707 | 0.0049781 | 0.99761 | -0.13296 | 0.99761 | -0.133 | 2.2628
31 | -0.15483 | -0.074399 | 0.15483 | 0.072417 | 2.7387e-06 | -0.001982 | 0.0049707 | 0.0049461 | 0.0049707 | 0.99761 | -0.133 | 0.99763 | -0.13315 | 2.2594
32 | -0.15483 | -0.072417 | 0.15484 | 0.071461 | 1.3113e-06 | -0.00095598 | 0.0049461 | 0.0049345 | 0.0049461 | 0.99763 | -0.13315 | 0.99764 | -0.13322 | 2.2482
33 | 0.13865 | 0.053794 | -0.13864 | -0.065662 | 1.3146e-05 | -0.011868 | 0.0043382 | 0.0044751 | 0.0044751 | 0.98964 | -0.0098094 | 0.98955 | -0.0091946 | 2.0341
34 | 0.32394 | 0.14414 | -0.32389 | -0.15276 | 5.3269e-05 | -0.008619 | 0.010343 | 0.010447 | 0.010447 | 0.98964 | -0.0098094 | 0.98949 | -0.0085504 | 4.7488
35 | -1.3911 | -0.60872 | 1.3911 | 0.60848 | 2.6604e-05 | -0.00023307 | 0.044135 | 0.044133 | 0.044135 | 0.99318 | -0.010096 | 0.9932 | -0.010225 | 20.0616
36 | -0.38396 | -0.18596 | 0.38397 | 0.18591 | 1.3581e-05 | -4.9881e-05 | 0.0124 | 0.012399 | 0.0124 | 0.99321 | -0.18269 | 0.99324 | -0.18246 | 5.9046
37 | -0.46689 | -0.22434 | 0.46704 | 0.21288 | 0.00014635 | -0.011462 | 0.015055 | 0.014913 | 0.015055 | 0.99324 | -0.18246 | 0.99353 | -0.18499 | 6.8431
38 | 0.082918 | 0.038432 | -0.0829 | -0.04015 | 1.8611e-05 | -0.0017177 | 0.0026562 | 0.0026777 | 0.0026777 | 0.99324 | -0.18246 | 0.99301 | -0.18406 | 1.2751
39 | 0.19105 | 0.092299 | -0.19105 | -0.092532 | 5.0181e-07 | -0.00023282 | 0.006165 | 0.006168 | 0.006168 | 0.99353 | -0.18499 | 0.99353 | -0.18496 | 2.8036
40 | 0.5202 | 0.21428 | -0.51978 | -0.2411 | 0.0004157 | -0.026814 | 0.016347 | 0.016661 | 0.016661 | 0.99353 | -0.18499 | 0.99278 | -0.17956 | 7.573
41 | -1.1783 | -0.51946 | 1.1791 | 0.51005 | 0.0007615 | -0.0094124 | 0.037415 | 0.037303 | 0.037415 | 0.99353 | -0.18499 | 0.99414 | -0.18934 | 17.0068
42 | 0.15043 | 0.071749 | -0.15043 | -0.072857 | 1.4809e-06 | -0.0011079 | 0.0048462 | 0.0048602 | 0.0048602 | 0.99278 | -0.17956 | 0.99277 | -0.17947 | 2.2092
43 | 0.36935 | 0.16935 | -0.36927 | -0.17872 | 7.5168e-05 | -0.0093763 | 0.011815 | 0.011931 | 0.011931 | 0.99278 | -0.17956 | 0.99259 | -0.17789 | 5.4233
44 | -1.7209 | -0.75249 | 1.7211 | 0.75254 | 0.00013257 | 5.3522e-05 | 0.05454 | 0.05454 | 0.05454 | 0.99414 | -0.18934 | 0.99423 | -0.18864 | 25.9714
45 | 0.54188 | 0.24244 | -0.54171 | -0.25224 | 0.00016688 | -0.0098073 | 0.017238 | 0.017357 | 0.017357 | 0.99414 | -0.18934 | 0.99386 | -0.18701 | 7.8895
46 | 0.36927 | 0.17872 | -0.36927 | -0.17885 | 1.0055e-06 | -0.00012414 | 0.011931 | 0.011933 | 0.011933 | 0.99259 | -0.17789 | 0.99259 | -0.17787 | 5.424
47 | 0.54171 | 0.25224 | -0.5417 | -0.2533 | 1.8096e-05 | -0.001055 | 0.017357 | 0.01737 | 0.01737 | 0.99386 | -0.18701 | 0.99383 | -0.18674 | 7.8954
48 | 0.17183 | 0.074166 | -0.17183 | -0.075336 | 1.9631e-06 | -0.0011699 | 0.0054362 | 0.0054498 | 0.0054498 | 0.99383 | -0.18674 | 0.99381 | -0.18666 | 2.4772
49 | -2.0199 | -0.89728 | 2.0201 | 0.89738 | 0.0002185 | 0.00010172 | 0.064175 | 0.064174 | 0.064175 | 0.99423 | -0.18864 | 0.99434 | -0.1877 | 30.5595
50 | -0.3986 | -0.19305 | 0.3986 | 0.19294 | 1.0476e-06 | -0.00011279 | 0.012828 | 0.012827 | 0.012828 | 0.99662 | -0.13815 | 0.99663 | -0.13817 | 5.8311
51 | 8.6779 | 3.9375 | -8.6746 | -3.9442 | 0.0032124 | -0.0067006 | 0.27602 | 0.27612 | 0.27612 | 0.99663 | -0.13817 | 0.99624 | -0.14009 | 43.2794
52 | 0.41419 | 0.18973 | -0.41408 | -0.2005 | 0.00010698 | -0.010771 | 0.013196 | 0.013329 | 0.013329 | 0.99663 | -0.13817 | 0.99639 | -0.13606 | 6.0588
53 | -9.4906 | -4.3201 | 9.5004 | 4.304 | 0.0097574 | -0.016149 | 0.30204 | 0.30178 | 0.30204 | 0.99663 | -0.13817 | 0.99769 | -0.13285 | 47.3416
54 | 8.2688 | 3.7476 | -8.2648 | -3.7372 | 0.0039748 | 0.010468 | 0.26306 | 0.26306 | 0.26306 | 0.99624 | -0.14009 | 0.99536 | -0.19122 | 40.7851
55 | 0.40582 | 0.19652 | -0.40581 | -0.19654 | 7.7318e-06 | -2.5276e-05 | 0.013065 | 0.013066 | 0.013066 | 0.99624 | -0.14009 | 0.99622 | -0.14021 | 6.2218
56 | 0.41408 | 0.2005 | -0.41407 | -0.20054 | 1.2498e-05 | -3.8961e-05 | 0.013329 | 0.01333 | 0.01333 | 0.99639 | -0.13606 | 0.99635 | -0.13626 | 6.3476
57 | 0.55528 | 0.26535 | -0.55525 | -0.26539 | 2.916e-05 | -4.3065e-05 | 0.017807 | 0.017808 | 0.017808 | 0.99769 | -0.13285 | 0.99764 | -0.13322 | 8.4798
58 | -10.0557 | -4.5693 | 10.0683 | 4.6028 | 0.012617 | 0.033451 | 0.31958 | 0.31958 | 0.31958 | 0.99769 | -0.13285 | 1 | 0 | 49.5479
59 | 8.1634 | 3.688 | -8.1629 | -3.6891 | 0.00044894 | -0.001087 | 0.2598 | 0.25981 | 0.25981 | 0.99536 | -0.19122 | 0.9953 | -0.19151 | 40.7227
60 | 11.2935 | 5.117 | -11.2931 | -5.1174 | 0.00042059 | -0.00043072 | 0.35792 | 0.35793 | 0.35793 | 1 | 0 | 0.99996 | -0.00019473 | 56.1012
61 | 8.1629 | 3.6891 | -8.1608 | -3.6942 | 0.0021023 | -0.0050862 | 0.25981 | 0.25989 | 0.25989 | 0.9953 | -0.19151 | 0.99504 | -0.19287 | 40.7345
62 | 0.21565 | 0.10408 | -0.21565 | -0.10445 | 1.005e-06 | -0.00036822 | 0.006947 | 0.0069516 | 0.0069516 | 0.99504 | -0.19287 | 0.99503 | -0.19283 | 3.1598
63 | 5.9235 | 2.6987 | -5.9197 | -2.7182 | 0.0038325 | -0.019433 | 0.18885 | 0.18911 | 0.18911 | 0.99504 | -0.19287 | 0.99437 | -0.19611 | 29.6405
64 | 2.0216 | 0.8914 | -2.0201 | -0.89738 | 0.0014935 | -0.0059815 | 0.064099 | 0.064174 | 0.064174 | 0.99504 | -0.19287 | 0.99434 | -0.1877 | 29.1702
65 | 5.9197 | 2.7182 | -5.9193 | -2.7202 | 0.00040997 | -0.0020735 | 0.18911 | 0.18913 | 0.18913 | 0.99437 | -0.19611 | 0.99429 | -0.19645 | 29.6449
66 | -0.30138 | -0.13896 | 0.30139 | 0.13696 | 1.0351e-05 | -0.0019981 | 0.0096055 | 0.0095814 | 0.0096055 | 0.99739 | -0.0037729 | 0.99742 | -0.0040351 | 4.3661
67 | 0.30138 | 0.13896 | -0.30136 | -0.14331 | 2.2739e-05 | -0.0043536 | 0.0096055 | 0.009659 | 0.009659 | 0.99739 | -0.0037729 | 0.99732 | -0.0031643 | 4.3905
68 | -0.5812 | -0.27247 | 0.5812 | 0.27215 | 6.2557e-06 | -0.00032071 | 0.018578 | 0.018574 | 0.018578 | 0.99742 | -0.0040351 | 0.99743 | -0.004122 | 8.4445
69 | 0.30136 | 0.14331 | -0.30135 | -0.14501 | 8.9416e-06 | -0.0016985 | 0.009659 | 0.0096803 | 0.0096803 | 0.99732 | -0.0031643 | 0.99729 | -0.0029128 | 4.4001
70 | 11.2931 | 5.1174 | -11.2741 | -5.1367 | 0.018985 | -0.019358 | 0.35793 | 0.35828 | 0.35828 | 0.99996 | -0.00019473 | 0.99821 | -0.0088823 | 56.1575
71 | 1.0129 | 0.46355 | -1.0123 | -0.47249 | 0.00053175 | -0.0089388 | 0.032213 | 0.032323 | 0.032323 | 0.99821 | -0.0088823 | 0.99772 | -0.0047775 | 14.6925
72 | 2.721 | 1.2133 | -2.7193 | -1.2169 | 0.0017284 | -0.0036318 | 0.086159 | 0.086208 | 0.086208 | 0.99821 | -0.0088823 | 0.99761 | -0.0043276 | 39.1852
73 | 0.28734 | 0.13904 | -0.28734 | -0.13917 | 5.884e-07 | -0.00012285 | 0.0092315 | 0.009233 | 0.009233 | 0.99821 | -0.0088823 | 0.99821 | -0.0088645 | 4.1968
74 | 7.2528 | 3.3209 | -7.2477 | -3.3375 | 0.0051459 | -0.01666 | 0.23069 | 0.23092 | 0.23092 | 0.99821 | -0.0088823 | 0.99748 | -0.012373 | 36.1949
75 | 1.7506 | 0.8027 | -1.7504 | -0.80355 | 0.00015917 | -0.00084939 | 0.055965 | 0.055976 | 0.055976 | 0.99337 | -0.2034 | 0.99329 | -0.2027 | 25.4437
76 | 1.7504 | 0.80355 | -1.7496 | -0.80799 | 0.00083369 | -0.0044408 | 0.055976 | 0.056033 | 0.056033 | 0.99329 | -0.2027 | 0.99284 | -0.19901 | 25.4696
77 | 0.28608 | 0.13766 | -0.28608 | -0.13855 | 4.3304e-06 | -0.00089357 | 0.0092308 | 0.0092421 | 0.0092421 | 0.99284 | -0.19901 | 0.99283 | -0.19888 | 4.201
78 | 1.4635 | 0.67033 | -1.4622 | -0.68026 | 0.0012857 | -0.0099294 | 0.046804 | 0.046929 | 0.046929 | 0.99284 | -0.19901 | 0.99203 | -0.19216 | 21.3316
79 | 0.2826 | 0.13665 | -0.28259 | -0.13687 | 1.0114e-06 | -0.00021298 | 0.0091344 | 0.0091371 | 0.0091371 | 0.99203 | -0.19216 | 0.99202 | -0.19213 | 4.1532
80 | 0.94571 | 0.44233 | -0.94525 | -0.45109 | 0.00046843 | -0.0087568 | 0.030381 | 0.030492 | 0.030492 | 0.99203 | -0.19216 | 0.99157 | -0.18808 | 13.86
81 | 0.23392 | 0.10127 | -0.23388 | -0.11324 | 3.8168e-05 | -0.011966 | 0.0074175 | 0.0075628 | 0.0075628 | 0.99203 | -0.19216 | 0.99187 | -0.19091 | 3.4376
82 | 0.23388 | 0.11324 | -0.23388 | -0.11327 | 2.8853e-06 | -3.1444e-05 | 0.0075628 | 0.0075632 | 0.0075632 | 0.99187 | -0.19091 | 0.99186 | -0.19099 | 3.6015
83 | 0.52457 | 0.25372 | -0.52457 | -0.25406 | 5.6081e-06 | -0.00034091 | 0.016964 | 0.016969 | 0.016969 | 0.99157 | -0.18808 | 0.99156 | -0.18799 | 7.7131
84 | 0.42067 | 0.19737 | -0.42061 | -0.20329 | 6.215e-05 | -0.00592 | 0.013528 | 0.013602 | 0.013602 | 0.99157 | -0.18808 | 0.99143 | -0.18684 | 6.1829
85 | -0.17182 | -0.083214 | 0.17182 | 0.080262 | 5.1091e-06 | -0.0029523 | 0.0055457 | 0.0055088 | 0.0055457 | 0.99374 | -0.18605 | 0.99377 | -0.1863 | 2.5208
86 | -0.17182 | -0.080262 | 0.17183 | 0.075336 | 8.3761e-06 | -0.0049261 | 0.0055088 | 0.0054498 | 0.0055088 | 0.99377 | -0.1863 | 0.99381 | -0.18666 | 2.504
87 | 0.17227 | 0.082491 | -0.17225 | -0.082835 | 1.6265e-05 | -0.00034409 | 0.0055287 | 0.0055332 | 0.0055332 | 0.99729 | -0.0029128 | 0.99719 | -0.003557 | 2.6348
88 | 0.17225 | 0.082835 | -0.17225 | -0.083426 | 1.0185e-06 | -0.00059052 | 0.0055332 | 0.0055406 | 0.0055406 | 0.99719 | -0.003557 | 0.99719 | -0.0035059 | 2.5185
89 | -0.82359 | -0.38502 | 0.82372 | 0.38178 | 0.00012725 | -0.0032381 | 0.026312 | 0.026272 | 0.026312 | 0.99743 | -0.004122 | 0.99757 | -0.0053506 | 11.9601
90 | 0.24239 | 0.11287 | -0.24237 | -0.11654 | 1.2446e-05 | -0.0036727 | 0.0077384 | 0.0077839 | 0.0077839 | 0.99743 | -0.004122 | 0.99738 | -0.0036974 | 3.5381
91 | -0.34319 | -0.16622 | 0.3432 | 0.16617 | 9.3449e-06 | -4.4042e-05 | 0.011105 | 0.011104 | 0.011105 | 0.99127 | -0.20642 | 0.9913 | -0.20624 | 5.288
92 | 0.26014 | 0.11683 | -0.26011 | -0.12556 | 3.4746e-05 | -0.0087313 | 0.0083045 | 0.008412 | 0.008412 | 0.9913 | -0.20624 | 0.99117 | -0.20518 | 3.8237
93 | -0.60335 | -0.28301 | 0.6034 | 0.28295 | 5.0884e-05 | -5.7098e-05 | 0.019407 | 0.019406 | 0.019407 | 0.9913 | -0.20624 | 0.99139 | -0.20562 | 9.2413
94 | 0.26011 | 0.12556 | -0.26011 | -0.12598 | 1.657e-06 | -0.00041069 | 0.008412 | 0.0084173 | 0.0084173 | 0.99117 | -0.20518 | 0.99117 | -0.20512 | 3.826
95 | -0.6726 | -0.31579 | 0.67267 | 0.31341 | 6.3896e-05 | -0.0023838 | 0.021636 | 0.021607 | 0.021636 | 0.99139 | -0.20562 | 0.99147 | -0.20638 | 9.8347
96 | 0.069207 | 0.032846 | -0.069206 | -0.033518 | 1.9091e-07 | -0.00067186 | 0.0022306 | 0.0022391 | 0.0022391 | 0.99139 | -0.20562 | 0.99138 | -0.2056 | 1.0178
97 | 0.42061 | 0.20329 | -0.42061 | -0.20362 | 3.4268e-06 | -0.00032447 | 0.013602 | 0.013606 | 0.013606 | 0.99143 | -0.18684 | 0.99142 | -0.18677 | 6.1848
98 | 0.28743 | 0.13912 | -0.28742 | -0.1392 | 1.2427e-05 | -8.6871e-05 | 0.0092979 | 0.0092991 | 0.0092991 | 0.99142 | -0.18677 | 0.99138 | -0.18706 | 4.4281
99 | -0.083535 | -0.038837 | 0.083536 | 0.037663 | 4.7746e-07 | -0.0011735 | 0.0026818 | 0.0026676 | 0.0026818 | 0.9916 | -0.20752 | 0.99161 | -0.20757 | 1.219
100 | 0.083535 | 0.038837 | -0.083534 | -0.040458 | 6.6793e-07 | -0.0016208 | 0.0026818 | 0.0027021 | 0.0027021 | 0.9916 | -0.20752 | 0.9916 | -0.20745 | 1.2282
101 | -1.7389 | -0.82143 | 1.7393 | 0.81922 | 0.00041689 | -0.0022171 | 0.055985 | 0.055956 | 0.055985 | 0.99161 | -0.20757 | 0.99183 | -0.20953 | 25.4478
102 | 1.6553 | 0.78377 | -1.6552 | -0.78433 | 9.4515e-05 | -0.00055652 | 0.053318 | 0.053325 | 0.053325 | 0.99161 | -0.20757 | 0.99156 | -0.20709 | 24.2388
103 | 1.0507 | 0.49156 | -1.0506 | -0.49295 | 9.2067e-05 | -0.0013912 | 0.033772 | 0.03379 | 0.03379 | 0.99156 | -0.20709 | 0.99147 | -0.20638 | 15.3591
104 | 0.37798 | 0.17954 | -0.37797 | -0.18024 | 5.9124e-06 | -0.000698 | 0.012184 | 0.012192 | 0.012192 | 0.99147 | -0.20638 | 0.99146 | -0.20625 | 5.5419
105 | 0.069908 | 0.032679 | -0.069908 | -0.033858 | 3.4081e-07 | -0.001179 | 0.0022469 | 0.0022616 | 0.0022616 | 0.99146 | -0.20625 | 0.99146 | -0.20621 | 1.028
106 | 0.30806 | 0.14756 | -0.30806 | -0.14886 | 7.3103e-06 | -0.001295 | 0.0099455 | 0.0099619 | 0.0099619 | 0.99146 | -0.20625 | 0.99144 | -0.20605 | 4.5281
107 | 0.15096 | 0.072772 | -0.15096 | -0.073113 | 4.6318e-07 | -0.00034154 | 0.0048795 | 0.0048839 | 0.0048839 | 0.99144 | -0.20605 | 0.99143 | -0.20602 | 2.2199
108 | -4.0883 | -1.9289 | 4.0891 | 1.9262 | 0.00079886 | -0.0026932 | 0.13109 | 0.13105 | 0.13109 | 0.99547 | -0.022866 | 0.99568 | -0.020528 | 36.2126
109 | 3.7283 | 1.7546 | -3.7258 | -1.7531 | 0.0024995 | 0.0014495 | 0.11949 | 0.11949 | 0.11949 | 0.99547 | -0.022866 | 0.99476 | -0.027767 | 56.9007
110 | -4.0891 | -1.9262 | 4.0916 | 1.8975 | 0.0025597 | -0.02871 | 0.13105 | 0.13068 | 0.13105 | 0.99568 | -0.020528 | 0.99633 | -0.017712 | 20.5406
111 | 3.7258 | 1.7531 | -3.7174 | -1.7609 | 0.0083103 | -0.0078031 | 0.11949 | 0.11962 | 0.11962 | 0.99476 | -0.027767 | 0.99269 | -0.0094074 | 54.3722
112 | 0.96227 | 0.44092 | -0.96159 | -0.45347 | 0.00067962 | -0.012554 | 0.030668 | 0.030824 | 0.030824 | 0.99633 | -0.017712 | 0.99567 | -0.012111 | 14.011
113 | -5.0539 | -2.3385 | 5.0543 | 2.336 | 0.00033662 | -0.0024212 | 0.16135 | 0.16132 | 0.16135 | 0.99633 | -0.017712 | 0.9964 | -0.017396 | 25.2895
114 | 0.34806 | 0.16843 | -0.34804 | -0.16856 | 2.8429e-05 | -0.00013061 | 0.011245 | 0.011246 | 0.011246 | 0.99269 | -0.0094074 | 0.9926 | -0.0099468 | 5.3554
115 | 3.3694 | 1.5925 | -3.3651 | -1.59 | 0.0043089 | 0.0024571 | 0.10837 | 0.10838 | 0.10838 | 0.99269 | -0.0094074 | 0.99135 | -0.018625 | 51.6084
116 | 0.53272 | 0.25791 | -0.53268 | -0.25799 | 4.7803e-05 | -7.7921e-05 | 0.017158 | 0.017159 | 0.017159 | 0.99579 | -0.023041 | 0.9957 | -0.023633 | 8.1712
117 | 0.96084 | 0.44034 | -0.96076 | -0.44188 | 8.2809e-05 | -0.0015386 | 0.03064 | 0.030659 | 0.030659 | 0.99579 | -0.023041 | 0.99571 | -0.022379 | 13.9359
118 | -1.5828 | -0.74147 | 1.5846 | 0.74213 | 0.001788 | 0.00065665 | 0.05067 | 0.050665 | 0.05067 | 0.99579 | -0.023041 | 0.99698 | -0.014661 | 24.1287
119 | 0.96076 | 0.44188 | -0.95995 | -0.44194 | 0.00080562 | -6.4099e-05 | 0.030659 | 0.030666 | 0.030666 | 0.99571 | -0.022379 | 0.99482 | -0.028972 | 14.6028
120 | -6.8822 | -3.175 | 6.8824 | 3.1742 | 0.00020667 | -0.000751 | 0.21946 | 0.21945 | 0.21946 | 0.99698 | -0.014661 | 0.99701 | -0.014517 | 34.3977
121 | 5.2976 | 2.4328 | -5.2952 | -2.4487 | 0.0024276 | -0.015825 | 0.16879 | 0.169 | 0.169 | 0.99698 | -0.014661 | 0.99651 | -0.016876 | 26.4894
122 | 3.3651 | 1.59 | -3.3649 | -1.5903 | 0.00021165 | -0.0002539 | 0.10838 | 0.10838 | 0.10838 | 0.99135 | -0.018625 | 0.99129 | -0.018107 | 49.2643
123 | 0.45847 | 0.21144 | -0.4584 | -0.21722 | 7.0442e-05 | -0.005779 | 0.014638 | 0.014709 | 0.014709 | 0.99567 | -0.012111 | 0.99552 | -0.010876 | 6.686
124 | 0.50312 | 0.24203 | -0.50308 | -0.2421 | 3.8476e-05 | -7.3423e-05 | 0.016187 | 0.016188 | 0.016188 | 0.99567 | -0.012111 | 0.99559 | -0.012628 | 7.7088
125 | -5.2946 | -2.4525 | 5.2952 | 2.4487 | 0.00058098 | -0.0037785 | 0.16905 | 0.169 | 0.16905 | 0.9964 | -0.017396 | 0.99651 | -0.016876 | 26.4972
126 | 0.26214 | 0.11902 | -0.2621 | -0.12688 | 3.1391e-05 | -0.0078601 | 0.0083542 | 0.0084511 | 0.0084511 | 0.9948 | -0.028795 | 0.99469 | -0.027825 | 3.8414
127 | 0.35304 | 0.15663 | -0.35294 | -0.17048 | 9.9982e-05 | -0.013848 | 0.011208 | 0.011377 | 0.011377 | 0.9948 | -0.028795 | 0.99454 | -0.026567 | 5.1713
128 | -0.61517 | -0.27566 | 0.61519 | 0.27496 | 1.5077e-05 | -0.00069322 | 0.019562 | 0.019553 | 0.019562 | 0.9948 | -0.028795 | 0.99482 | -0.028972 | 8.8916
129 | 0.2621 | 0.12688 | -0.2621 | -0.12694 | 6.6612e-06 | -5.765e-05 | 0.0084511 | 0.0084519 | 0.0084519 | 0.99469 | -0.027825 | 0.99466 | -0.027993 | 4.0247
130 | 0.35294 | 0.17048 | -0.35293 | -0.17093 | 3.3034e-06 | -0.00045027 | 0.011377 | 0.011383 | 0.011383 | 0.99454 | -0.026567 | 0.99453 | -0.026486 | 5.1739
131 | 0.16873 | 0.0814 | -0.16873 | -0.081719 | 5.3116e-07 | -0.00031865 | 0.0054323 | 0.0054363 | 0.0054363 | 0.99552 | -0.010876 | 0.99552 | -0.010849 | 2.471
132 | 0.28967 | 0.13582 | -0.28965 | -0.14014 | 2.1092e-05 | -0.0043123 | 0.0092772 | 0.009331 | 0.009331 | 0.99552 | -0.010876 | 0.99546 | -0.010265 | 4.2414
133 | 0.092198 | 0.043102 | -0.092198 | -0.044069 | 4.7727e-07 | -0.00096748 | 0.002951 | 0.002963 | 0.002963 | 0.99559 | -0.012628 | 0.99558 | -0.012585 | 1.3468
134 | 3.1787 | 1.5001 | -3.1776 | -1.4995 | 0.0010541 | 0.00059403 | 0.10236 | 0.10236 | 0.10236 | 0.99129 | -0.018107 | 0.99094 | -0.020507 | 48.7421
135 | 0.28965 | 0.14014 | -0.28963 | -0.14027 | 1.9827e-05 | -0.00013873 | 0.009331 | 0.0093329 | 0.0093329 | 0.99546 | -0.010265 | 0.99539 | -0.010717 | 4.4443
136 | 0.092198 | 0.044069 | -0.092197 | -0.044653 | 2.8993e-07 | -0.00058389 | 0.002963 | 0.0029704 | 0.0029704 | 0.99558 | -0.012585 | 0.99558 | -0.012558 | 1.3502
137 | -7.1069 | -3.283 | 7.1091 | 3.2758 | 0.0021304 | -0.0071879 | 0.22667 | 0.22657 | 0.22667 | 0.99701 | -0.014517 | 0.99732 | -0.013076 | 35.5279
138 | -7.1091 | -3.2758 | 7.1101 | 3.2723 | 0.0010311 | -0.0034835 | 0.22657 | 0.22652 | 0.22657 | 0.99732 | -0.013076 | 0.99748 | -0.012373 | 35.512
139 | 0.13759 | 0.065235 | -0.13759 | -0.066637 | 1.5368e-06 | -0.0014021 | 0.0044068 | 0.0044243 | 0.0044243 | 0.99748 | -0.012373 | 0.99746 | -0.012278 | 2.0111
140 | 1.0123 | 0.47249 | -1.0123 | -0.47304 | 3.3215e-05 | -0.00055598 | 0.032323 | 0.03233 | 0.03233 | 0.99772 | -0.0047775 | 0.99769 | -0.0045146 | 14.6956
141 | 2.7193 | 1.2169 | -2.719 | -1.2177 | 0.00035855 | -0.00075219 | 0.086208 | 0.086218 | 0.086218 | 0.99761 | -0.0043276 | 0.99749 | -0.003377 | 39.1899
142 | 2.5369 | 1.1295 | -2.5361 | -1.1291 | 0.00085267 | 0.00044611 | 0.080368 | 0.080369 | 0.080369 | 0.99749 | -0.003377 | 0.99713 | -0.0062888 | 38.2709
143 | 0.82381 | 0.38175 | -0.82372 | -0.38178 | 8.9618e-05 | -3.0454e-05 | 0.026271 | 0.026272 | 0.026272 | 0.99769 | -0.0045146 | 0.99757 | -0.0053506 | 12.5106
144 | 2.5361 | 1.1291 | -2.5336 | -1.1351 | 0.0024448 | -0.0059927 | 0.080369 | 0.080448 | 0.080448 | 0.99713 | -0.0062888 | 0.99622 | 0.00062057 | 36.5674
145 | -0.58501 | -0.26414 | 0.58507 | 0.26407 | 6.0719e-05 | -7.6027e-05 | 0.018708 | 0.018707 | 0.018708 | 0.99046 | -0.018501 | 0.99057 | -0.017637 | 8.9085
146 | 0.3224 | 0.13695 | -0.32239 | -0.13854 | 9.4498e-06 | -0.0015851 | 0.010209 | 0.010227 | 0.010227 | 0.99046 | -0.018501 | 0.99044 | -0.018315 | 4.6488
147 | -0.58507 | -0.26407 | 0.58523 | 0.25633 | 0.00015438 | -0.007737 | 0.018707 | 0.018614 | 0.018707 | 0.99057 | -0.017637 | 0.99082 | -0.019505 | 8.503
148 | 0.32239 | 0.13854 | -0.32228 | -0.15603 | 0.00010663 | -0.01749 | 0.010227 | 0.01044 | 0.01044 | 0.99044 | -0.018315 | 0.99013 | -0.015802 | 4.7453
149 | -1.7276 | -0.79854 | 1.7278 | 0.79734 | 0.0002219 | -0.0012018 | 0.05545 | 0.055434 | 0.05545 | 0.99082 | -0.019505 | 0.99094 | -0.020507 | 25.2045
150 | 0.41408 | 0.20006 | -0.41407 | -0.20054 | 4.9766e-06 | -0.00048503 | 0.013398 | 0.013405 | 0.013405 | 0.99082 | -0.019505 | 0.99081 | -0.019401 | 6.093
151 | 0.72827 | 0.34215 | -0.72817 | -0.34531 | 9.9912e-05 | -0.0031565 | 0.023443 | 0.023483 | 0.023483 | 0.99082 | -0.019505 | 0.99069 | -0.018378 | 10.674
152 | -0.32227 | -0.15608 | 0.32228 | 0.15603 | 1.0199e-05 | -5.5075e-05 | 0.01044 | 0.01044 | 0.01044 | 0.99009 | -0.016011 | 0.99013 | -0.015802 | 4.9716
153 | -0.3779 | -0.18123 | 0.37801 | 0.16769 | 0.00011199 | -0.013536 | 0.012167 | 0.012002 | 0.012167 | 0.9944 | -0.0080503 | 0.99467 | -0.010359 | 5.5304
154 | 0.3779 | 0.18123 | -0.37789 | -0.18302 | 1.5046e-05 | -0.0017897 | 0.012167 | 0.012189 | 0.012189 | 0.9944 | -0.0080503 | 0.99436 | -0.0077072 | 5.5407
155 | 1.9356 | 0.86153 | -1.9344 | -0.86659 | 0.0011579 | -0.0050669 | 0.061488 | 0.061552 | 0.061552 | 0.99467 | -0.010359 | 0.99411 | -0.0060738 | 27.9782
156 | -2.3136 | -1.0292 | 2.3137 | 1.029 | 7.547e-05 | -0.0002249 | 0.07349 | 0.073487 | 0.07349 | 0.99467 | -0.010359 | 0.9947 | -0.01059 | 33.4045
157 | 0.081334 | 0.037311 | -0.081333 | -0.039101 | 6.897e-07 | -0.0017901 | 0.0025985 | 0.0026206 | 0.0026206 | 0.99411 | -0.0060738 | 0.9941 | -0.0060049 | 1.1912
158 | 1.8531 | 0.82928 | -1.8529 | -0.83018 | 0.00018816 | -0.00090081 | 0.058954 | 0.058965 | 0.058965 | 0.99411 | -0.0060738 | 0.99402 | -0.0053413 | 26.8023
159 | -2.3963 | -1.069 | 2.3996 | 1.0707 | 0.0032712 | 0.0016744 | 0.07615 | 0.076146 | 0.07615 | 0.9947 | -0.01059 | 0.99615 | 0.0011573 | 36.2619
160 | 0.081333 | 0.039101 | -0.081333 | -0.039391 | 1.1295e-07 | -0.00029031 | 0.0026206 | 0.0026242 | 0.0026242 | 0.9941 | -0.0060049 | 0.9941 | -0.0059929 | 1.1928
161 | 1.5017 | 0.66009 | -1.5017 | -0.66024 | 2.0227e-05 | -0.00015149 | 0.047639 | 0.047641 | 0.047641 | 0.99402 | -0.0053413 | 0.994 | -0.0052488 | 21.6549
162 | -2.5335 | -1.1355 | 2.5336 | 1.1351 | 0.00018814 | -0.0004601 | 0.080454 | 0.080448 | 0.080454 | 0.99615 | 0.0011573 | 0.99622 | 0.00062057 | 36.5702
163 | 0.72817 | 0.34531 | -0.72816 | -0.34574 | 1.3711e-05 | -0.00043225 | 0.023483 | 0.023488 | 0.023488 | 0.99069 | -0.018378 | 0.99068 | -0.018221 | 10.6765
164 | 0.25565 | 0.11689 | -0.25564 | -0.11765 | 2.9057e-06 | -0.00075844 | 0.0081911 | 0.0082003 | 0.0082003 | 0.99068 | -0.018221 | 0.99067 | -0.018134 | 3.7274
165 | 0.085044 | 0.035023 | -0.085043 | -0.036147 | 4.6204e-07 | -0.0011237 | 0.0026801 | 0.0026927 | 0.0026927 | 0.99067 | -0.018134 | 0.99066 | -0.018102 | 1.224
166 | -1.4498 | -0.63688 | 1.4507 | 0.63717 | 0.00094053 | 0.00029542 | 0.046024 | 0.046021 | 0.046024 | 0.9932 | -0.010225 | 0.99389 | -0.0043969 | 21.9164
167 | -1.5015 | -0.66163 | 1.5017 | 0.66024 | 0.0001857 | -0.0013901 | 0.047658 | 0.047641 | 0.047658 | 0.99389 | -0.0043969 | 0.994 | -0.0052488 | 21.6625
168 | 0.050798 | 0.02446 | -0.050797 | -0.024602 | 5.7822e-07 | -0.0001422 | 0.0016376 | 0.0016394 | 0.0016394 | 0.99389 | -0.0043969 | 0.99388 | -0.0044727 | 0.78065
169 | -0.24237 | -0.11739 | 0.24237 | 0.11654 | 2.8804e-06 | -0.00084376 | 0.0077946 | 0.0077839 | 0.0077946 | 0.99737 | -0.0035948 | 0.99738 | -0.0036974 | 3.543
170 | 0.2425 | 0.11667 | -0.24249 | -0.11745 | 2.7445e-06 | -0.00077774 | 0.0078513 | 0.0078612 | 0.0078612 | 0.98943 | -0.0080105 | 0.98942 | -0.0079127 | 3.5733
171 | -0.32387 | -0.15608 | 0.32389 | 0.15276 | 2.0791e-05 | -0.0033158 | 0.010489 | 0.010447 | 0.010489 | 0.98943 | -0.0080105 | 0.98949 | -0.0085504 | 4.7678
172 | 0.13864 | 0.065662 | -0.13864 | -0.067145 | 1.7034e-06 | -0.0014829 | 0.0044751 | 0.0044938 | 0.0044938 | 0.98955 | -0.0091946 | 0.98954 | -0.0090902 | 2.0426
173 | -0.085041 | -0.041187 | 0.085043 | 0.037459 | 1.5838e-06 | -0.0037287 | 0.0027535 | 0.0027079 | 0.0027535 | 0.99064 | -0.017914 | 0.99065 | -0.01806 | 1.2516
174 | -0.085043 | -0.037459 | 0.085043 | 0.036147 | 5.4491e-07 | -0.0013116 | 0.0027079 | 0.0026927 | 0.0027079 | 0.99065 | -0.01806 | 0.99066 | -0.018102 | 1.2309

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 21.7412 | 9.9072

## res_load
| p_mw | q_mvar
0 | 0.17133 | 0.082981
1 | 0.15884 | 0.07693
2 | 0.1113 | 0.053906
3 | 0.31936 | 0.15467
4 | 0.30319 | 0.14684
5 | 0.26558 | 0.12863
6 | 0.2739 | 0.13265
7 | 0.064225 | 0.031105
8 | 0.090913 | 0.044031
9 | 0.19651 | 0.095176
10 | 0.32533 | 0.15756
11 | 0.4029 | 0.19513
12 | 0.19622 | 0.095034
13 | 0.15483 | 0.074988
14 | 0.38396 | 0.18596
15 | 0.0829 | 0.04015
16 | 0.19105 | 0.092532
17 | 0.36927 | 0.17885
18 | 0.15043 | 0.072857
19 | 0.36987 | 0.17913
20 | 0.29886 | 0.14474
21 | 0.3986 | 0.19305
22 | 0.10147 | 0.049146
23 | 0.40581 | 0.19654
24 | 0.41407 | 0.20054
25 | 0.40041 | 0.19393
26 | 0.36542 | 0.17698
27 | 0.21565 | 0.10445
28 | 0.2798 | 0.13551
29 | 0.20993 | 0.10167
30 | 0.28608 | 0.13855
31 | 0.25162 | 0.12187
32 | 0.23388 | 0.11327
33 | 0.28259 | 0.13687
34 | 0.17182 | 0.083214
35 | 0.12908 | 0.062517
36 | 0.17225 | 0.083426
37 | 0.34319 | 0.16622
38 | 0.52457 | 0.25406
39 | 0.13318 | 0.0645
40 | 0.26011 | 0.12598
41 | 0.083534 | 0.040458
42 | 0.60449 | 0.29277
43 | 0.069206 | 0.033518
44 | 0.069908 | 0.033858
45 | 0.15709 | 0.076084
46 | 0.15096 | 0.073113
47 | 0.28742 | 0.1392
48 | 0.36003 | 0.17437
49 | 0.089251 | 0.043226
50 | 0.53268 | 0.25799
51 | 0.34804 | 0.16856
52 | 0.24038 | 0.11642
53 | 0.34477 | 0.16698
54 | 0.2621 | 0.12694
55 | 0.35293 | 0.17093
56 | 0.41089 | 0.199
57 | 0.18618 | 0.090173
58 | 0.28963 | 0.14027
59 | 0.16873 | 0.081719
60 | 0.092197 | 0.044653
61 | 0.2245 | 0.10873
62 | 0.13759 | 0.066637
63 | 0.28734 | 0.13917
64 | 0.18201 | 0.088151
65 | 0.18849 | 0.091291
66 | 0.26261 | 0.12719
67 | 0.32227 | 0.15608
68 | 0.37789 | 0.18302
69 | 0.082628 | 0.040018
70 | 0.3512 | 0.17009
71 | 0.081333 | 0.039391
72 | 0.13388 | 0.064841
73 | 0.47251 | 0.22885
74 | 1.4498 | 0.70218
75 | 0.41407 | 0.20054
76 | 0.1706 | 0.082625
77 | 0.058621 | 0.028391
78 | 0.050797 | 0.024602
79 | 0.24237 | 0.11739
80 | 0.081372 | 0.03941
81 | 0.24249 | 0.11745
82 | 0.13864 | 0.067145
83 | 0.085041 | 0.041187

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1