## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_367_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_367_0_node_72 | 20 | n |  | TRUE
2 | bus_MV_367_0_node_25 | 20 | n |  | TRUE
3 | bus_MV_367_0_node_26 | 20 | n |  | TRUE
4 | bus_MV_367_0_node_221 | 20 | n |  | TRUE
5 | bus_MV_367_0_node_29 | 20 | n |  | TRUE
6 | bus_MV_367_0_node_30 | 20 | n |  | TRUE
7 | bus_MV_367_0_node_240 | 20 | n |  | TRUE
8 | bus_MV_367_0_node_226 | 20 | n |  | TRUE
9 | bus_MV_367_0_node_49 | 20 | n |  | TRUE
10 | bus_MV_367_0_node_51 | 20 | n |  | TRUE
11 | bus_MV_367_0_node_241 | 20 | n |  | TRUE
12 | bus_MV_367_0_node_66 | 20 | n |  | TRUE
13 | bus_MV_367_0_node_68 | 20 | n |  | TRUE
14 | bus_MV_367_0_node_67 | 20 | n |  | TRUE
15 | bus_MV_367_0_node_69 | 20 | n |  | TRUE
16 | bus_MV_367_0_node_246 | 20 | n |  | TRUE
17 | bus_MV_367_0_node_73 | 20 | n |  | TRUE
18 | bus_MV_367_0_node_70 | 20 | n |  | TRUE
19 | bus_MV_367_0_node_71 | 20 | n |  | TRUE
20 | bus_MV_367_0_node_254 | 20 | n |  | TRUE
21 | bus_MV_367_0_node_74 | 20 | n |  | TRUE
22 | bus_MV_367_0_node_75 | 20 | n |  | TRUE
23 | bus_MV_367_0_node_80 | 20 | n |  | TRUE
24 | bus_MV_367_0_node_76 | 20 | n |  | TRUE
25 | bus_MV_367_0_node_77 | 20 | n |  | TRUE
26 | bus_MV_367_0_node_79 | 20 | n |  | TRUE
27 | bus_MV_367_0_node_84 | 20 | n |  | TRUE
28 | bus_MV_367_0_node_86 | 20 | n |  | TRUE
29 | bus_MV_367_0_node_78 | 20 | n |  | TRUE
30 | bus_MV_367_0_node_88 | 20 | n |  | TRUE
31 | bus_MV_367_0_node_249 | 20 | n |  | TRUE
32 | bus_MV_367_0_node_87 | 20 | n |  | TRUE
33 | bus_MV_367_0_node_82 | 20 | n |  | TRUE
34 | bus_MV_367_0_node_81 | 20 | n |  | TRUE
35 | bus_MV_367_0_node_145 | 20 | n |  | TRUE
36 | bus_MV_367_0_node_146 | 20 | n |  | TRUE
37 | bus_MV_367_0_node_225 | 20 | n |  | TRUE
38 | bus_MV_367_0_node_204 | 20 | n |  | TRUE
39 | bus_MV_367_0_node_147 | 20 | n |  | TRUE
40 | bus_MV_367_0_node_148 | 20 | n |  | TRUE
41 | bus_MV_367_0_node_149 | 20 | n |  | TRUE
42 | bus_MV_367_0_node_197 | 20 | n |  | TRUE
43 | bus_MV_367_0_node_151 | 20 | n |  | TRUE
44 | bus_MV_367_0_node_150 | 20 | n |  | TRUE
45 | bus_MV_367_0_node_210 | 20 | n |  | TRUE
46 | bus_MV_367_0_node_152 | 20 | n |  | TRUE
47 | bus_MV_367_0_node_153 | 20 | n |  | TRUE
48 | bus_MV_367_0_node_154 | 20 | n |  | TRUE
49 | bus_MV_367_0_node_155 | 20 | n |  | TRUE
50 | bus_MV_367_0_node_156 | 20 | n |  | TRUE
51 | bus_MV_367_0_node_158 | 20 | n |  | TRUE
52 | bus_MV_367_0_node_168 | 20 | n |  | TRUE
53 | bus_MV_367_0_node_159 | 20 | n |  | TRUE
54 | bus_MV_367_0_node_160 | 20 | n |  | TRUE
55 | bus_MV_367_0_node_166 | 20 | n |  | TRUE
56 | bus_MV_367_0_node_165 | 20 | n |  | TRUE
57 | bus_MV_367_0_node_161 | 20 | n |  | TRUE
58 | bus_MV_367_0_node_162 | 20 | n |  | TRUE
59 | bus_MV_367_0_node_164 | 20 | n |  | TRUE
60 | bus_MV_367_0_node_231 | 20 | n |  | TRUE
61 | bus_MV_367_0_node_167 | 20 | n |  | TRUE
62 | bus_MV_367_0_node_176 | 20 | n |  | TRUE
63 | bus_MV_367_0_node_170 | 20 | n |  | TRUE
64 | bus_MV_367_0_node_169 | 20 | n |  | TRUE
65 | bus_MV_367_0_node_171 | 20 | n |  | TRUE
66 | bus_MV_367_0_node_172 | 20 | n |  | TRUE
67 | bus_MV_367_0_node_173 | 20 | n |  | TRUE
68 | bus_MV_367_0_node_175 | 20 | n |  | TRUE
69 | bus_MV_367_0_node_174 | 20 | n |  | TRUE
70 | bus_MV_367_0_node_232 | 20 | n |  | TRUE
71 | bus_MV_367_0_node_178 | 20 | n |  | TRUE
72 | bus_MV_367_0_node_179 | 20 | n |  | TRUE
73 | bus_MV_367_0_node_224 | 20 | n |  | TRUE
74 | bus_MV_367_0_node_180 | 20 | n |  | TRUE
75 | bus_MV_367_0_node_222 | 20 | n |  | TRUE
76 | bus_MV_367_0_node_181 | 20 | n |  | TRUE
77 | bus_MV_367_0_node_247 | 20 | n |  | TRUE
78 | bus_MV_367_0_node_183 | 20 | n |  | TRUE
79 | bus_MV_367_0_node_184 | 20 | n |  | TRUE
80 | bus_MV_367_0_node_198 | 20 | n |  | TRUE
81 | bus_MV_367_0_node_187 | 20 | n |  | TRUE
82 | bus_MV_367_0_node_189 | 20 | n |  | TRUE
83 | bus_MV_367_0_node_188 | 20 | n |  | TRUE
84 | bus_MV_367_0_node_190 | 20 | n |  | TRUE
85 | bus_MV_367_0_node_191 | 20 | n |  | TRUE
86 | bus_MV_367_0_node_192 | 20 | n |  | TRUE
87 | bus_MV_367_0_node_207 | 20 | n |  | TRUE
88 | bus_MV_367_0_node_255 | 20 | n |  | TRUE
89 | bus_MV_367_0_node_193 | 20 | n |  | TRUE
90 | bus_MV_367_0_node_194 | 20 | n |  | TRUE
91 | bus_MV_367_0_node_218 | 20 | n |  | TRUE
92 | bus_MV_367_0_node_195 | 20 | n |  | TRUE
93 | bus_MV_367_0_node_196 | 20 | n |  | TRUE
94 | bus_MV_367_0_node_209 | 20 | n |  | TRUE
95 | bus_MV_367_0_node_199 | 20 | n |  | TRUE
96 | bus_MV_367_0_node_201 | 20 | n |  | TRUE
97 | bus_MV_367_0_node_200 | 20 | n |  | TRUE
98 | bus_MV_367_0_node_203 | 20 | n |  | TRUE
99 | bus_MV_367_0_node_202 | 20 | n |  | TRUE
100 | bus_MV_367_0_node_206 | 20 | n |  | TRUE
101 | bus_MV_367_0_node_205 | 20 | n |  | TRUE
102 | bus_MV_367_0_node_237 | 20 | n |  | TRUE
103 | bus_MV_367_0_node_227 | 20 | n |  | TRUE
104 | bus_MV_367_0_node_208 | 20 | n |  | TRUE
105 | bus_MV_367_0_node_211 | 20 | n |  | TRUE
106 | bus_MV_367_0_node_212 | 20 | n |  | TRUE
107 | bus_MV_367_0_node_219 | 20 | n |  | TRUE
108 | bus_MV_367_0_node_220 | 20 | n |  | TRUE
109 | bus_MV_367_0_node_233 | 20 | n |  | TRUE
110 | bus_MV_367_0_node_245 | 20 | n |  | TRUE
111 | bus_MV_367_0_node_248 | 20 | n |  | TRUE
112 | bus_HV_367_0_node_237 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_367_0_load_0 | 0 | 0.25094 | 0.12153 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_367_0_load_25 | 2 | 0.096719 | 0.046843 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_367_0_load_221 | 4 | 0.1993 | 0.096526 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_367_0_load_29 | 5 | 0.05241 | 0.025383 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_367_0_load_49 | 9 | 0.17495 | 0.084735 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_367_0_load_51 | 10 | 0.33708 | 0.16326 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_367_0_load_241 | 11 | 0.19474 | 0.094318 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_367_0_load_66 | 12 | 0.14113 | 0.06835 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_367_0_load_246 | 16 | 0.12928 | 0.062615 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_367_0_load_73 | 17 | 0.12767 | 0.061832 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_367_0_load_71 | 19 | 0.14669 | 0.071046 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_367_0_load_254 | 20 | 0.15789 | 0.076468 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_367_0_load_74 | 21 | 0.098651 | 0.047779 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_367_0_load_80 | 23 | 0.056601 | 0.027413 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_367_0_load_84 | 27 | 0.099565 | 0.048221 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_367_0_load_88 | 30 | 0.087314 | 0.042288 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_367_0_load_249 | 31 | 0.11348 | 0.054961 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_367_0_load_87 | 32 | 0.16345 | 0.079164 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_367_0_load_82 | 33 | 0.092319 | 0.044712 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_367_0_load_145 | 35 | 0.12692 | 0.061469 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_367_0_load_146 | 36 | 0.10576 | 0.051221 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_367_0_load_225 | 37 | 0.15115 | 0.073207 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_367_0_load_204 | 38 | 0.11603 | 0.056195 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_367_0_load_147 | 39 | 0.15213 | 0.073681 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_367_0_load_148 | 40 | 0.15672 | 0.075901 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_367_0_load_149 | 41 | 0.14264 | 0.069086 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_367_0_load_150 | 44 | 0.15645 | 0.075774 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_367_0_load_152 | 46 | 0.15092 | 0.073095 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_367_0_load_153 | 47 | 0.13204 | 0.063951 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_367_0_load_155 | 49 | 0.12125 | 0.058726 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_367_0_load_158 | 51 | 0.15054 | 0.07291 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_367_0_load_168 | 52 | 0.14258 | 0.069057 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_367_0_load_165 | 56 | 0.12297 | 0.059557 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_367_0_load_161 | 57 | 0.084093 | 0.040728 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_367_0_load_231 | 60 | 0.060334 | 0.029221 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_367_0_load_167 | 61 | 0.13796 | 0.066818 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_367_0_load_176 | 62 | 0.054474 | 0.026383 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_367_0_load_170 | 63 | 0.097547 | 0.047244 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_367_0_load_169 | 64 | 0.15963 | 0.077313 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_367_0_load_174 | 69 | 0.11884 | 0.057556 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_367_0_load_232 | 70 | 0.11317 | 0.054811 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_367_0_load_224 | 73 | 0.16151 | 0.078223 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_367_0_load_222 | 75 | 0.1196 | 0.057926 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_367_0_load_181 | 76 | 0.096273 | 0.046627 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_367_0_load_183 | 78 | 0.091191 | 0.044166 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_367_0_load_198 | 80 | 0.14861 | 0.071973 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_367_0_load_187 | 81 | 0.099872 | 0.04837 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_367_0_load_207 | 87 | 0.16302 | 0.078955 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_367_0_load_255 | 88 | 0.11991 | 0.058075 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_367_0_load_194 | 90 | 0.1553 | 0.075217 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_367_0_load_218 | 91 | 1.1241 | 0.54442 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_367_0_load_205 | 101 | 0.14178 | 0.068667 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_367_0_load_237 | 102 | 0.16062 | 0.077794 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_367_0_load_227 | 103 | 0.13652 | 0.06612 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_367_0_load_208 | 104 | 0.11937 | 0.057813 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_367_0_load_219 | 107 | 0.12174 | 0.058964 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_367_0_load_220 | 108 | 0.13894 | 0.067292 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_367_0_load_245 | 110 | 0.10013 | 0.048496 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_367_0_load_248 | 111 | 0.10954 | 0.053051 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 102 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_367_0_line_0 |  | 0 | 1 | 1.0533 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
1 | MV_367_0_line_1 |  | 0 | 2 | 1.5284 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
2 | MV_367_0_line_2 |  | 1 | 19 | 0.011768 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
3 | MV_367_0_line_3 |  | 2 | 3 | 0.006532 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
4 | MV_367_0_line_4 |  | 3 | 4 | 1.0388 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
5 | MV_367_0_line_5 |  | 4 | 72 | 0.11663 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
6 | MV_367_0_line_6 |  | 5 | 6 | 0.057372 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_367_0_line_7 |  | 5 | 7 | 1.4766 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_367_0_line_8 |  | 6 | 8 | 1.2496 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_367_0_line_9 |  | 7 | 11 | 0.18006 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_367_0_line_10 |  | 7 | 9 | 2.063 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_367_0_line_11 |  | 8 | 103 | 0.24899 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_367_0_line_12 |  | 10 | 11 | 2.5366 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_367_0_line_13 |  | 12 | 13 | 0.056375 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_367_0_line_14 |  | 13 | 16 | 0.088583 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
15 | MV_367_0_line_15 |  | 13 | 14 | 0.076664 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
16 | MV_367_0_line_16 |  | 14 | 15 | 0.12812 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
17 | MV_367_0_line_17 |  | 15 | 17 | 0.087563 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
18 | MV_367_0_line_18 |  | 16 | 28 | 0.076035 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
19 | MV_367_0_line_19 |  | 18 | 19 | 0.010387 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
20 | MV_367_0_line_20 |  | 18 | 20 | 1.0643 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
21 | MV_367_0_line_21 |  | 20 | 29 | 0.61669 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
22 | MV_367_0_line_22 |  | 21 | 22 | 0.20916 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
23 | MV_367_0_line_23 |  | 22 | 23 | 0.19137 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
24 | MV_367_0_line_24 |  | 23 | 34 | 0.14184 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
25 | MV_367_0_line_25 |  | 24 | 25 | 0.14523 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
26 | MV_367_0_line_26 |  | 24 | 26 | 0.21889 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
27 | MV_367_0_line_27 |  | 24 | 27 | 0.11273 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
28 | MV_367_0_line_28 |  | 24 | 28 | 0.21046 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
29 | MV_367_0_line_29 |  | 25 | 29 | 0.3557 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
30 | MV_367_0_line_30 |  | 25 | 30 | 0.059151 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_367_0_line_31 |  | 26 | 32 | 0.010581 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
32 | MV_367_0_line_32 |  | 26 | 33 | 0.2906 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
33 | MV_367_0_line_33 |  | 29 | 31 | 0.050749 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
34 | MV_367_0_line_34 |  | 33 | 34 | 0.028174 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
35 | MV_367_0_line_35 |  | 35 | 36 | 0.17541 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
36 | MV_367_0_line_36 |  | 35 | 37 | 0.30701 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
37 | MV_367_0_line_37 |  | 36 | 38 | 0.29362 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
38 | MV_367_0_line_38 |  | 37 | 42 | 0.070558 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
39 | MV_367_0_line_39 |  | 37 | 93 | 0.056046 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
40 | MV_367_0_line_40 |  | 38 | 96 | 0.056206 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
41 | MV_367_0_line_41 |  | 39 | 40 | 0.034174 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_367_0_line_42 |  | 40 | 41 | 0.060544 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_367_0_line_43 |  | 41 | 42 | 0.059274 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
44 | MV_367_0_line_44 |  | 41 | 43 | 0.035525 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
45 | MV_367_0_line_45 |  | 42 | 92 | 0.011682 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
46 | MV_367_0_line_46 |  | 43 | 44 | 0.029603 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
47 | MV_367_0_line_47 |  | 44 | 45 | 0.090765 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
48 | MV_367_0_line_48 |  | 44 | 46 | 0.053248 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
49 | MV_367_0_line_49 |  | 45 | 105 | 0.098975 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
50 | MV_367_0_line_50 |  | 46 | 47 | 0.016511 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
51 | MV_367_0_line_51 |  | 46 | 48 | 0.049411 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
52 | MV_367_0_line_52 |  | 47 | 49 | 0.0078598 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
53 | MV_367_0_line_53 |  | 48 | 50 | 0.28525 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
54 | MV_367_0_line_54 |  | 49 | 51 | 0.021711 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
55 | MV_367_0_line_55 |  | 50 | 52 | 0.067679 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
56 | MV_367_0_line_56 |  | 51 | 53 | 0.039278 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
57 | MV_367_0_line_57 |  | 52 | 63 | 0.054912 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
58 | MV_367_0_line_58 |  | 53 | 54 | 0.1445 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
59 | MV_367_0_line_59 |  | 54 | 55 | 0.18035 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
60 | MV_367_0_line_60 |  | 54 | 56 | 0.036953 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
61 | MV_367_0_line_61 |  | 55 | 61 | 0.047361 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
62 | MV_367_0_line_62 |  | 55 | 62 | 0.37072 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
63 | MV_367_0_line_63 |  | 57 | 58 | 0.044517 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
64 | MV_367_0_line_64 |  | 58 | 59 | 0.16 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
65 | MV_367_0_line_65 |  | 59 | 60 | 0.037915 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
66 | MV_367_0_line_66 |  | 60 | 67 | 0.024434 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
67 | MV_367_0_line_67 |  | 63 | 64 | 0.079191 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
68 | MV_367_0_line_68 |  | 64 | 65 | 0.011687 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
69 | MV_367_0_line_69 |  | 65 | 66 | 0.054368 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
70 | MV_367_0_line_70 |  | 65 | 67 | 0.14213 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
71 | MV_367_0_line_71 |  | 66 | 68 | 0.28398 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
72 | MV_367_0_line_72 |  | 66 | 69 | 0.041926 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
73 | MV_367_0_line_73 |  | 68 | 70 | 0.029088 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
74 | MV_367_0_line_74 |  | 70 | 109 | 0.034545 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
75 | MV_367_0_line_75 |  | 71 | 72 | 0.44943 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
76 | MV_367_0_line_76 |  | 71 | 73 | 0.047584 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
77 | MV_367_0_line_77 |  | 72 | 74 | 0.051787 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
78 | MV_367_0_line_78 |  | 73 | 105 | 0.053387 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
79 | MV_367_0_line_79 |  | 73 | 106 | 0.07276 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
80 | MV_367_0_line_80 |  | 74 | 75 | 0.06872 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
81 | MV_367_0_line_81 |  | 76 | 77 | 0.46016 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
82 | MV_367_0_line_82 |  | 77 | 111 | 0.093628 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
83 | MV_367_0_line_83 |  | 77 | 109 | 0.30717 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
84 | MV_367_0_line_84 |  | 78 | 79 | 0.089852 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
85 | MV_367_0_line_85 |  | 79 | 80 | 0.38647 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
86 | MV_367_0_line_86 |  | 80 | 95 | 0.10105 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
87 | MV_367_0_line_87 |  | 81 | 82 | 0.016592 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
88 | MV_367_0_line_88 |  | 81 | 83 | 0.15144 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
89 | MV_367_0_line_89 |  | 82 | 85 | 0.069107 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
90 | MV_367_0_line_90 |  | 83 | 84 | 0.009038 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
91 | MV_367_0_line_91 |  | 84 | 86 | 0.16562 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
92 | MV_367_0_line_92 |  | 84 | 87 | 0.030495 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
93 | MV_367_0_line_93 |  | 85 | 88 | 0.18831 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
94 | MV_367_0_line_94 |  | 86 | 89 | 0.12194 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
95 | MV_367_0_line_95 |  | 86 | 90 | 0.088 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
96 | MV_367_0_line_96 |  | 88 | 97 | 0.003921 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
97 | MV_367_0_line_97 |  | 89 | 91 | 0.15275 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
98 | MV_367_0_line_98 |  | 90 | 92 | 0.038284 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
99 | MV_367_0_line_99 |  | 93 | 94 | 0.004051 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
100 | MV_367_0_line_100 |  | 94 | 104 | 0.062586 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
101 | MV_367_0_line_101 |  | 95 | 96 | 0.31451 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
102 | MV_367_0_line_102 |  | 97 | 98 | 0.25111 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
103 | MV_367_0_line_103 |  | 98 | 102 | 0.016797 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
104 | MV_367_0_line_104 |  | 98 | 99 | 0.28381 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_367_0_line_105 |  | 99 | 100 | 0.31302 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_367_0_line_106 |  | 99 | 101 | 0.032541 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_367_0_line_107 |  | 100 | 103 | 0.15586 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
108 | MV_367_0_line_108 |  | 106 | 107 | 0.023084 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
109 | MV_367_0_line_109 |  | 107 | 108 | 0.032201 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
110 | MV_367_0_line_110 |  | 110 | 111 | 1.1327 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_367_0_trafo_237 | 25 MVA 110/20 kV | 112 | 102 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2552358.2886 | 1166094.8716
1 | 2553408.6809 | 1166173.5819
2 | 2551749.0146 | 1167496.5415
3 | 2551754.8332 | 1167499.5407
4 | 2551654.2374 | 1168533.489
5 | 2549460.6546 | 1166310.7405
6 | 2549515.3603 | 1166325.6098
7 | 2548054.9306 | 1165858.6215
8 | 2550230.0786 | 1167350.6696
9 | 2546660.6367 | 1167379.154
10 | 2545576.3663 | 1164880.2407
11 | 2547977.2442 | 1165698.7872
12 | 2553635.8732 | 1165262.2631
13 | 2553601.8481 | 1165217.3137
14 | 2553576.2961 | 1165289.594
15 | 2553513.9896 | 1165382.5478
16 | 2553635.329 | 1165135.4895
17 | 2553474.6415 | 1165460.7719
18 | 2553420.825 | 1166155.0333
19 | 2553415.1274 | 1166163.7266
20 | 2554345.3474 | 1165627.8121
21 | 2554496.4771 | 1164459.5055
22 | 2554419.6419 | 1164654.0465
23 | 2554237.4971 | 1164595.3472
24 | 2553888.7447 | 1165066.4994
25 | 2553923.6748 | 1165124.7727
26 | 2553915.3644 | 1164903.3979
27 | 2553781.0994 | 1165099.9678
28 | 2553678.3772 | 1165072.7461
29 | 2554109.1814 | 1165058.1375
30 | 2553878.5962 | 1165162.7614
31 | 2554155.8373 | 1165037.8589
32 | 2553905.4652 | 1164899.7165
33 | 2554121.6848 | 1164698.753
34 | 2554148.4419 | 1164705.7409
35 | 2550536.6539 | 1168853.9692
36 | 2550444.6574 | 1168704.6245
37 | 2550836.8618 | 1168789.7069
38 | 2550663.2083 | 1168508.5415
39 | 2550859.2508 | 1168871.3891
40 | 2550879.9649 | 1168845.8434
41 | 2550928.4931 | 1168810.6117
42 | 2550900.3351 | 1168758.8925
43 | 2550951.2976 | 1168836.65
44 | 2550980.5006 | 1168831.9308
45 | 2551020.0177 | 1168750.2198
46 | 2551025.1473 | 1168860.948
47 | 2551036.9482 | 1168872.4878
48 | 2550992.3173 | 1168897.5024
49 | 2551042.7714 | 1168877.7665
50 | 2551014.9441 | 1169055.3682
51 | 2551058.9302 | 1168892.2665
52 | 2551082.403 | 1169049.9144
53 | 2551089.1045 | 1168917.4892
54 | 2551195.7453 | 1168946.5799
55 | 2551322.3491 | 1169000.8792
56 | 2551230.499 | 1168959.137
57 | 2550919.2058 | 1169392.9202
58 | 2550927.7551 | 1169349.238
59 | 2550918.5125 | 1169200.9013
60 | 2550923.8985 | 1169163.3706
61 | 2551357.3823 | 1169032.8452
62 | 2551571.5347 | 1168726.3925
63 | 2551121.7209 | 1169088.2474
64 | 2551081.7668 | 1169156.6209
65 | 2551087.7519 | 1169166.1104
66 | 2551132.5301 | 1169196.5947
67 | 2550947.0277 | 1169155.3881
68 | 2551272.1682 | 1169378.7549
69 | 2551104.602 | 1169227.917
70 | 2551249.137 | 1169394.9619
71 | 2551181.8997 | 1168670.2455
72 | 2551627.3388 | 1168615.3162
73 | 2551134.4867 | 1168666.2186
74 | 2551592.3794 | 1168585.0156
75 | 2551537.8864 | 1168543.3278
76 | 2551876.4265 | 1169503.3166
77 | 2551428.0794 | 1169606.933
78 | 2550174.267 | 1168443.171
79 | 2550150.0071 | 1168356.8599
80 | 2550512.2359 | 1168222.1536
81 | 2550924.9805 | 1168350.9401
82 | 2550916.2013 | 1168336.8489
83 | 2550897.3165 | 1168499.8348
84 | 2550890.0287 | 1168505.2085
85 | 2550879.8319 | 1168278.0378
86 | 2550940.0684 | 1168631.6883
87 | 2550860.6537 | 1168513.398
88 | 2550780.9248 | 1168117.7971
89 | 2551001.403 | 1168529.0542
90 | 2550927.9941 | 1168718.8558
91 | 2551076.2814 | 1168407.0999
92 | 2550904.0336 | 1168747.9452
93 | 2550824.8277 | 1168735.1766
94 | 2550824.2514 | 1168731.1681
95 | 2550564.1313 | 1168308.8605
96 | 2550705.5598 | 1168529.1687
97 | 2550777.0174 | 1168118.2405
98 | 2550767.9004 | 1167996.0503
99 | 2550599.4753 | 1167827.057
100 | 2550410.9349 | 1167679.6128
101 | 2550605.8653 | 1167795.343
102 | 2550781.3804 | 1167985.9787
103 | 2550390.971 | 1167525.0401
104 | 2550819.6461 | 1168668.9172
105 | 2551099.3659 | 1168706.4264
106 | 2551149.1724 | 1168737.4813
107 | 2551143.3345 | 1168759.7572
108 | 2551118.1947 | 1168779.8786
109 | 2551226.3061 | 1169412.2569
110 | 2551982.641 | 1170694.9767
111 | 2551442.8071 | 1169699.1739
112 | 2550781.3804 | 1167985.9787

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99276 | -0.31591 | 0.25094 | 0.12153
1 | 0.99178 | -0.37386 | 0 | 0
2 | 0.99445 | -0.2174 | 0.096719 | 0.046843
3 | 0.99445 | -0.21738 | 0 | 0
4 | 0.99567 | -0.14677 | 0.1993 | 0.096526
5 | 0.99683 | -0.0068229 | 0.05241 | 0.025383
6 | 0.99688 | -0.0073052 | 0 | 0
7 | 0.99481 | -0.02088 | 0 | 0
8 | 0.99871 | 0.0056583 | 0 | 0
9 | 0.99411 | -0.025506 | 0.17495 | 0.084735
10 | 0.99302 | -0.030566 | 0.33708 | 0.16326
11 | 0.99469 | -0.01978 | 0.19474 | 0.094318
12 | 0.99014 | -0.45843 | 0.14113 | 0.06835
13 | 0.99016 | -0.45834 | 0 | 0
14 | 0.99015 | -0.4584 | 0 | 0
15 | 0.99014 | -0.4585 | 0 | 0
16 | 0.99017 | -0.45818 | 0.12928 | 0.062615
17 | 0.99013 | -0.45883 | 0.12767 | 0.061832
18 | 0.99177 | -0.37392 | 0 | 0
19 | 0.99178 | -0.37389 | 0.14669 | 0.071046
20 | 0.99089 | -0.42656 | 0.15789 | 0.076468
21 | 0.99009 | -0.46034 | 0.098651 | 0.047779
22 | 0.99011 | -0.45965 | 0 | 0
23 | 0.99013 | -0.45902 | 0.056601 | 0.027413
24 | 0.99027 | -0.45509 | 0 | 0
25 | 0.99033 | -0.45401 | 0 | 0
26 | 0.99023 | -0.45582 | 0 | 0
27 | 0.99026 | -0.45547 | 0.099565 | 0.048221
28 | 0.99019 | -0.45799 | 0 | 0
29 | 0.99044 | -0.45336 | 0 | 0
30 | 0.99032 | -0.45395 | 0.087314 | 0.042288
31 | 0.99044 | -0.45337 | 0.11348 | 0.054961
32 | 0.99023 | -0.45583 | 0.16345 | 0.079164
33 | 0.99016 | -0.45824 | 0.092319 | 0.044712
34 | 0.99016 | -0.45828 | 0 | 0
35 | 0.99647 | -0.1347 | 0.12692 | 0.061469
36 | 0.99642 | -0.13785 | 0.10576 | 0.051221
37 | 0.99658 | -0.1277 | 0.15115 | 0.073207
38 | 0.99635 | -0.14196 | 0.11603 | 0.056195
39 | 0.9965 | -0.12565 | 0.15213 | 0.073681
40 | 0.9965 | -0.12571 | 0.15672 | 0.075901
41 | 0.99653 | -0.12593 | 0.14264 | 0.069086
42 | 0.99662 | -0.12536 | 0 | 0
43 | 0.99647 | -0.12625 | 0 | 0
44 | 0.99643 | -0.12651 | 0.15645 | 0.075774
45 | 0.99628 | -0.1353 | 0 | 0
46 | 0.99636 | -0.13056 | 0.15092 | 0.073095
47 | 0.99636 | -0.13059 | 0.13204 | 0.063951
48 | 0.99635 | -0.1307 | 0 | 0
49 | 0.99636 | -0.13059 | 0.12125 | 0.058726
50 | 0.99625 | -0.13143 | 0 | 0
51 | 0.99635 | -0.13061 | 0.15054 | 0.07291
52 | 0.9962 | -0.1343 | 0.14258 | 0.069057
53 | 0.99635 | -0.13064 | 0 | 0
54 | 0.99634 | -0.13074 | 0 | 0
55 | 0.99633 | -0.1308 | 0 | 0
56 | 0.99633 | -0.13089 | 0.12297 | 0.059557
57 | 0.99611 | -0.13922 | 0.084093 | 0.040728
58 | 0.99611 | -0.13922 | 0 | 0
59 | 0.99612 | -0.13918 | 0 | 0
60 | 0.99612 | -0.13905 | 0.060334 | 0.029221
61 | 0.99632 | -0.13081 | 0.13796 | 0.066818
62 | 0.99631 | -0.13157 | 0.054474 | 0.026383
63 | 0.99617 | -0.13633 | 0.097547 | 0.047244
64 | 0.99613 | -0.13896 | 0.15963 | 0.077313
65 | 0.99613 | -0.13898 | 0 | 0
66 | 0.99612 | -0.13906 | 0 | 0
67 | 0.99612 | -0.13905 | 0 | 0
68 | 0.99608 | -0.13937 | 0 | 0
69 | 0.99612 | -0.13907 | 0.11884 | 0.057556
70 | 0.99608 | -0.13939 | 0.11317 | 0.054811
71 | 0.99605 | -0.14474 | 0 | 0
72 | 0.99575 | -0.1464 | 0 | 0
73 | 0.99611 | -0.14091 | 0.16151 | 0.078223
74 | 0.99574 | -0.14641 | 0 | 0
75 | 0.99574 | -0.14643 | 0.1196 | 0.057926
76 | 0.99601 | -0.14129 | 0.096273 | 0.046627
77 | 0.99604 | -0.13961 | 0 | 0
78 | 0.99628 | -0.14448 | 0.091191 | 0.044166
79 | 0.99628 | -0.14446 | 0 | 0
80 | 0.99631 | -0.14309 | 0.14861 | 0.071973
81 | 0.9982 | -0.058881 | 0.099872 | 0.04837
82 | 0.99824 | -0.058661 | 0 | 0
83 | 0.99747 | -0.10185 | 0 | 0
84 | 0.99745 | -0.10197 | 0 | 0
85 | 0.99841 | -0.057743 | 0 | 0
86 | 0.99707 | -0.10412 | 0 | 0
87 | 0.99745 | -0.10214 | 0.16302 | 0.078955
88 | 0.99933 | -0.0036829 | 0.11991 | 0.058075
89 | 0.99702 | -0.10431 | 0 | 0
90 | 0.99672 | -0.1248 | 0.1553 | 0.075217
91 | 0.99696 | -0.10452 | 1.1241 | 0.54442
92 | 0.99665 | -0.12523 | 0 | 0
93 | 0.99658 | -0.12772 | 0 | 0
94 | 0.99658 | -0.12772 | 0 | 0
95 | 0.99632 | -0.14216 | 0 | 0
96 | 0.99635 | -0.142 | 0 | 0
97 | 0.99934 | -0.0036306 | 0 | 0
98 | 0.99995 | -0.00025667 | 0 | 0
99 | 0.99958 | 0.0027094 | 0 | 0
100 | 0.99922 | 0.0056093 | 0 | 0
101 | 0.99957 | 0.0027639 | 0.14178 | 0.068667
102 | 1 | 0 | -8.6654 | -3.8459
103 | 0.99896 | 0.0036483 | 0.13652 | 0.06612
104 | 0.99658 | -0.12773 | 0.11937 | 0.057813
105 | 0.9962 | -0.13574 | 0 | 0
106 | 0.9961 | -0.14163 | 0 | 0
107 | 0.9961 | -0.14164 | 0.12174 | 0.058964
108 | 0.9961 | -0.14164 | 0.13894 | 0.067292
109 | 0.99607 | -0.13942 | 0 | 0
110 | 0.99596 | -0.14395 | 0.10013 | 0.048496
111 | 0.99604 | -0.13964 | 0.10954 | 0.053051
112 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 1.4159 | 0.62882 | -1.4152 | -0.6282 | 0.00076347 | 0.00061941 | 0.04505 | 0.045067 | 0.045067 | 0.99276 | -0.31591 | 0.99178 | -0.37386 | 6.9871
1 | -1.6669 | -0.75036 | 1.6684 | 0.75241 | 0.0015409 | 0.0020577 | 0.053154 | 0.053129 | 0.053154 | 0.99276 | -0.31591 | 0.99445 | -0.2174 | 8.2409
2 | 1.4152 | 0.6282 | -1.4152 | -0.62893 | 7.3869e-06 | -0.00072314 | 0.045067 | 0.045076 | 0.045076 | 0.99178 | -0.37386 | 0.99178 | -0.37389 | 7.0651
3 | -1.7651 | -0.79926 | 1.7651 | 0.79886 | 6.3852e-06 | -0.00040228 | 0.056247 | 0.056243 | 0.056247 | 0.99445 | -0.2174 | 0.99445 | -0.21738 | 8.8162
4 | -1.7651 | -0.79886 | 1.7663 | 0.80059 | 0.0011728 | 0.0017318 | 0.056243 | 0.056226 | 0.056243 | 0.99445 | -0.21738 | 0.99567 | -0.14677 | 8.7198
5 | -1.9656 | -0.89711 | 1.9658 | 0.88993 | 0.00014123 | -0.0071857 | 0.062644 | 0.062557 | 0.062644 | 0.99567 | -0.14677 | 0.99575 | -0.1464 | 9.8188
6 | -0.76126 | -0.35754 | 0.76131 | 0.35619 | 4.5405e-05 | -0.0013478 | 0.024356 | 0.024339 | 0.024356 | 0.99683 | -0.0068229 | 0.99688 | -0.0073052 | 11.071
7 | 0.70885 | 0.33216 | -0.7075 | -0.33306 | 0.0013534 | -0.0009004 | 0.02267 | 0.022691 | 0.022691 | 0.99683 | -0.0068229 | 0.99481 | -0.02088 | 10.8054
8 | -0.76131 | -0.35619 | 0.76263 | 0.35553 | 0.001318 | -0.00065971 | 0.024339 | 0.024321 | 0.024339 | 0.99688 | -0.0073052 | 0.99871 | 0.0056583 | 11.5902
9 | 0.53243 | 0.25068 | -0.53236 | -0.25492 | 7.0318e-05 | -0.0042333 | 0.017077 | 0.01713 | 0.01713 | 0.99481 | -0.02088 | 0.99469 | -0.01978 | 7.7863
10 | 0.17507 | 0.082372 | -0.17495 | -0.084735 | 0.00011649 | -0.0023627 | 0.0056145 | 0.0056449 | 0.0056449 | 0.99481 | -0.02088 | 0.99411 | -0.025506 | 2.6881
11 | -0.76263 | -0.35553 | 0.76282 | 0.34966 | 0.00019604 | -0.005873 | 0.024321 | 0.024249 | 0.024321 | 0.99871 | 0.0056583 | 0.99896 | 0.0036483 | 11.0551
12 | -0.33708 | -0.16326 | 0.33762 | 0.1606 | 0.0005339 | -0.0026567 | 0.010888 | 0.01085 | 0.010888 | 0.99302 | -0.030566 | 0.99469 | -0.01978 | 5.1847
13 | -0.14113 | -0.06835 | 0.14113 | 0.068286 | 2.0989e-06 | -6.4667e-05 | 0.0045717 | 0.0045708 | 0.0045717 | 0.99014 | -0.45843 | 0.99016 | -0.45834 | 2.177
14 | -0.2688 | -0.12313 | 0.2688 | 0.12015 | 3.1657e-06 | -0.0029772 | 0.0086197 | 0.0085839 | 0.0086197 | 0.99016 | -0.45834 | 0.99017 | -0.45818 | 2.3811
15 | 0.12767 | 0.05484 | -0.12767 | -0.057418 | 6.1217e-07 | -0.0025781 | 0.004051 | 0.0040813 | 0.0040813 | 0.99016 | -0.45834 | 0.99015 | -0.4584 | 1.1274
16 | 0.12767 | 0.057418 | -0.12767 | -0.061726 | 1.044e-06 | -0.0043084 | 0.0040813 | 0.0041344 | 0.0041344 | 0.99015 | -0.4584 | 0.99014 | -0.4585 | 1.1421
17 | 0.12767 | 0.061726 | -0.12767 | -0.061832 | 1.3745e-06 | -0.0001063 | 0.0041344 | 0.0041358 | 0.0041358 | 0.99014 | -0.4585 | 0.99013 | -0.45883 | 1.1817
18 | -0.39809 | -0.18276 | 0.39809 | 0.18021 | 5.9748e-06 | -0.0025531 | 0.01277 | 0.01274 | 0.01277 | 0.99017 | -0.45818 | 0.99019 | -0.45799 | 3.5278
19 | -1.2685 | -0.55852 | 1.2685 | 0.55788 | 5.2225e-06 | -0.000639 | 0.040342 | 0.040334 | 0.040342 | 0.99177 | -0.37392 | 0.99178 | -0.37389 | 6.3232
20 | 1.2685 | 0.55852 | -1.2678 | -0.5583 | 0.00061862 | 0.00021774 | 0.040342 | 0.040359 | 0.040359 | 0.99177 | -0.37392 | 0.99089 | -0.42656 | 6.2572
21 | 1.11 | 0.48183 | -1.1097 | -0.48194 | 0.00027366 | -0.0001007 | 0.035252 | 0.035262 | 0.035262 | 0.99089 | -0.42656 | 0.99044 | -0.45336 | 5.4669
22 | -0.098651 | -0.047779 | 0.098652 | 0.047516 | 1.5212e-06 | -0.00026319 | 0.0031959 | 0.0031925 | 0.0031959 | 0.99009 | -0.46034 | 0.99011 | -0.45965 | 0.77949
23 | -0.098652 | -0.047516 | 0.098654 | 0.047275 | 1.389e-06 | -0.00024082 | 0.0031925 | 0.0031895 | 0.0031925 | 0.99011 | -0.45965 | 0.99013 | -0.45902 | 0.77867
24 | -0.15526 | -0.074688 | 0.15526 | 0.074512 | 2.5497e-06 | -0.00017629 | 0.005023 | 0.0050208 | 0.005023 | 0.99013 | -0.45902 | 0.99016 | -0.45828 | 1.2251
25 | -0.90874 | -0.41646 | 0.90878 | 0.41106 | 4.5032e-05 | -0.0053994 | 0.02914 | 0.029074 | 0.02914 | 0.99027 | -0.45509 | 0.99033 | -0.45401 | 6.9216
26 | 0.41106 | 0.1884 | -0.41104 | -0.19659 | 1.4026e-05 | -0.0081869 | 0.013181 | 0.013283 | 0.013283 | 0.99027 | -0.45509 | 0.99023 | -0.45582 | 3.1551
27 | 0.099566 | 0.04808 | -0.099565 | -0.048221 | 8.3522e-07 | -0.00014187 | 0.0032231 | 0.003225 | 0.003225 | 0.99027 | -0.45509 | 0.99026 | -0.45547 | 0.78657
28 | 0.39812 | 0.17998 | -0.39809 | -0.18021 | 2.4341e-05 | -0.00023187 | 0.012736 | 0.01274 | 0.01274 | 0.99027 | -0.45509 | 0.99019 | -0.45799 | 3.1072
29 | -0.9961 | -0.45196 | 0.99621 | 0.4301 | 0.00011083 | -0.021859 | 0.031885 | 0.031626 | 0.031885 | 0.99033 | -0.45401 | 0.99044 | -0.45336 | 4.9976
30 | 0.087315 | 0.040903 | -0.087314 | -0.042288 | 6.2764e-07 | -0.0013849 | 0.0028106 | 0.002828 | 0.002828 | 0.99033 | -0.45401 | 0.99032 | -0.45395 | 1.2854
31 | 0.16345 | 0.078767 | -0.16345 | -0.079164 | 1.0846e-07 | -0.00039625 | 0.0052894 | 0.0052945 | 0.0052945 | 0.99023 | -0.45582 | 0.99023 | -0.45583 | 1.2576
32 | 0.24759 | 0.11782 | -0.24758 | -0.11817 | 1.3243e-05 | -0.00034962 | 0.0079934 | 0.007998 | 0.007998 | 0.99023 | -0.45582 | 0.99016 | -0.45824 | 1.9507
33 | 0.11348 | 0.051833 | -0.11348 | -0.054961 | 2.0953e-07 | -0.0031279 | 0.0036362 | 0.003675 | 0.003675 | 0.99044 | -0.45336 | 0.99044 | -0.45337 | 0.57602
34 | 0.15526 | 0.073457 | -0.15526 | -0.074512 | 2.5925e-07 | -0.001055 | 0.0050075 | 0.0050208 | 0.0050208 | 0.99016 | -0.45824 | 0.99016 | -0.45828 | 1.1926
35 | 0.46162 | 0.1936 | -0.46161 | -0.1938 | 1.3171e-05 | -0.00020532 | 0.014502 | 0.014504 | 0.014504 | 0.99647 | -0.1347 | 0.99642 | -0.13785 | 2.2487
36 | -0.58854 | -0.25507 | 0.58857 | 0.25475 | 3.7836e-05 | -0.00031969 | 0.018582 | 0.018577 | 0.018582 | 0.99647 | -0.1347 | 0.99658 | -0.1277 | 2.881
37 | 0.35585 | 0.14258 | -0.35583 | -0.14295 | 1.2935e-05 | -0.00036816 | 0.011106 | 0.011111 | 0.011111 | 0.99642 | -0.13785 | 0.99635 | -0.14196 | 1.7226
38 | -0.8591 | -0.37811 | 0.85912 | 0.37807 | 1.862e-05 | -4.6801e-05 | 0.027189 | 0.027188 | 0.027189 | 0.99658 | -0.1277 | 0.99662 | -0.12536 | 4.2153
39 | 0.11937 | 0.050158 | -0.11937 | -0.053655 | 2.462e-07 | -0.0034973 | 0.0037506 | 0.003791 | 0.003791 | 0.99658 | -0.1277 | 0.99658 | -0.12772 | 0.5942
40 | 0.23981 | 0.086756 | -0.23981 | -0.090261 | 9.5262e-07 | -0.0035052 | 0.0073887 | 0.0074239 | 0.0074239 | 0.99635 | -0.14196 | 0.99635 | -0.142 | 1.1636
41 | -0.15213 | -0.073681 | 0.15213 | 0.072871 | 1.0917e-06 | -0.00080992 | 0.0048968 | 0.0048866 | 0.0048968 | 0.9965 | -0.12565 | 0.9965 | -0.12571 | 2.2258
42 | -0.30885 | -0.14877 | 0.30886 | 0.14734 | 7.9569e-06 | -0.0014331 | 0.0099309 | 0.0099129 | 0.0099309 | 0.9965 | -0.12571 | 0.99653 | -0.12593 | 4.5141
43 | -5.0697 | -2.2137 | 5.0702 | 2.2102 | 0.00047023 | -0.003434 | 0.16025 | 0.16021 | 0.16025 | 0.99653 | -0.12593 | 0.99662 | -0.12536 | 25.1177
44 | 4.6182 | 1.9973 | -4.618 | -1.9993 | 0.00023325 | -0.0020852 | 0.14576 | 0.14578 | 0.14578 | 0.99653 | -0.12593 | 0.99647 | -0.12625 | 22.8499
45 | -5.9293 | -2.5883 | 5.9295 | 2.5877 | 0.00012676 | -0.00065769 | 0.1874 | 0.18739 | 0.1874 | 0.99662 | -0.12536 | 0.99665 | -0.12523 | 29.3724
46 | 4.618 | 1.9993 | -4.6178 | -2.0011 | 0.00019443 | -0.0017373 | 0.14578 | 0.1458 | 0.1458 | 0.99647 | -0.12625 | 0.99643 | -0.12651 | 22.8532
47 | 2.5088 | 1.1084 | -2.5085 | -1.1079 | 0.00020458 | 0.00042559 | 0.079458 | 0.07946 | 0.07946 | 0.99643 | -0.12651 | 0.99628 | -0.1353 | 12.3193
48 | 1.9526 | 0.81694 | -1.9525 | -0.81682 | 7.1481e-05 | 0.00011914 | 0.061321 | 0.061321 | 0.061321 | 0.99643 | -0.12651 | 0.99636 | -0.13056 | 9.5072
49 | 2.5085 | 1.1079 | -2.5084 | -1.114 | 0.00019327 | -0.0060633 | 0.07946 | 0.079532 | 0.079532 | 0.99628 | -0.1353 | 0.9962 | -0.13574 | 12.4658
50 | 0.71926 | 0.31926 | -0.71925 | -0.32029 | 2.6534e-06 | -0.0010284 | 0.0228 | 0.022812 | 0.022812 | 0.99636 | -0.13056 | 0.99636 | -0.13059 | 3.5755
51 | 1.0824 | 0.42447 | -1.0823 | -0.42754 | 1.7341e-05 | -0.0030722 | 0.033684 | 0.033717 | 0.033717 | 0.99636 | -0.13056 | 0.99635 | -0.1307 | 5.2848
52 | 0.58721 | 0.25633 | -0.58721 | -0.25682 | 8.372e-07 | -0.00048978 | 0.018564 | 0.018569 | 0.018569 | 0.99636 | -0.13059 | 0.99636 | -0.13059 | 2.9105
53 | 1.0823 | 0.42754 | -1.0822 | -0.44528 | 0.00010077 | -0.017734 | 0.033717 | 0.03391 | 0.03391 | 0.99635 | -0.1307 | 0.99625 | -0.13143 | 5.315
54 | 0.46595 | 0.1981 | -0.46595 | -0.19945 | 1.4452e-06 | -0.0013534 | 0.01467 | 0.014685 | 0.014685 | 0.99636 | -0.13059 | 0.99635 | -0.13061 | 2.3017
55 | 1.0822 | 0.44528 | -1.0822 | -0.44529 | 2.7784e-05 | -1.8136e-05 | 0.03391 | 0.033911 | 0.033911 | 0.99625 | -0.13143 | 0.9962 | -0.1343 | 5.2575
56 | 0.31541 | 0.12654 | -0.31541 | -0.12899 | 1.1799e-06 | -0.0024493 | 0.0098465 | 0.0098732 | 0.0098732 | 0.99635 | -0.13061 | 0.99635 | -0.13064 | 1.5475
57 | 0.93963 | 0.37624 | -0.93962 | -0.37627 | 1.6864e-05 | -2.9978e-05 | 0.02933 | 0.029331 | 0.029331 | 0.9962 | -0.1343 | 0.99617 | -0.13633 | 4.5474
58 | 0.31541 | 0.12899 | -0.31541 | -0.138 | 4.397e-06 | -0.0090107 | 0.0098732 | 0.0099749 | 0.0099749 | 0.99635 | -0.13064 | 0.99634 | -0.13074 | 1.5635
59 | 0.19244 | 0.078491 | -0.19244 | -0.089739 | 2.0635e-06 | -0.011248 | 0.0060216 | 0.0061521 | 0.0061521 | 0.99634 | -0.13074 | 0.99633 | -0.1308 | 0.96428
60 | 0.12297 | 0.05951 | -0.12297 | -0.059557 | 4.1273e-07 | -4.6882e-05 | 0.0039582 | 0.0039588 | 0.0039588 | 0.99634 | -0.13074 | 0.99633 | -0.13089 | 0.96555
61 | 0.13796 | 0.063864 | -0.13796 | -0.066818 | 2.8628e-07 | -0.0029538 | 0.0044048 | 0.0044414 | 0.0044414 | 0.99633 | -0.1308 | 0.99632 | -0.13081 | 0.69615
62 | 0.054474 | 0.025875 | -0.054474 | -0.026383 | 4.0556e-07 | -0.0005076 | 0.0017474 | 0.0017537 | 0.0017537 | 0.99633 | -0.1308 | 0.99631 | -0.13157 | 0.2719
63 | -0.084093 | -0.040728 | 0.084093 | 0.037953 | 9.9566e-08 | -0.0027753 | 0.0027078 | 0.0026737 | 0.0027078 | 0.99611 | -0.13922 | 0.99611 | -0.13922 | 0.42442
64 | -0.084093 | -0.037953 | 0.084093 | 0.027978 | 3.3874e-07 | -0.0099747 | 0.0026737 | 0.0025684 | 0.0026737 | 0.99611 | -0.13922 | 0.99612 | -0.13918 | 0.41908
65 | -0.084093 | -0.027978 | 0.084093 | 0.027926 | 8.9272e-08 | -5.1764e-05 | 0.0025684 | 0.0025679 | 0.0025684 | 0.99612 | -0.13918 | 0.99612 | -0.13905 | 0.39819
66 | -0.14443 | -0.057147 | 0.14443 | 0.055624 | 1.5243e-07 | -0.0015233 | 0.0045012 | 0.0044852 | 0.0045012 | 0.99612 | -0.13905 | 0.99612 | -0.13905 | 0.70552
67 | 0.84207 | 0.32902 | -0.84205 | -0.32908 | 1.9405e-05 | -5.6443e-05 | 0.026198 | 0.0262 | 0.0262 | 0.99617 | -0.13633 | 0.99613 | -0.13896 | 4.062
68 | 0.68242 | 0.25177 | -0.68242 | -0.25249 | 1.6052e-06 | -0.00072774 | 0.021079 | 0.021087 | 0.021087 | 0.99613 | -0.13896 | 0.99613 | -0.13898 | 3.3051
69 | 0.53799 | 0.20573 | -0.53798 | -0.20912 | 4.6906e-06 | -0.003387 | 0.016692 | 0.016727 | 0.016727 | 0.99613 | -0.13898 | 0.99612 | -0.13906 | 2.6218
70 | 0.14443 | 0.046763 | -0.14443 | -0.055624 | 8.6605e-07 | -0.0088609 | 0.0043994 | 0.0044852 | 0.0044852 | 0.99613 | -0.13898 | 0.99612 | -0.13905 | 0.703
71 | 0.41915 | 0.15418 | -0.41913 | -0.17187 | 1.4906e-05 | -0.017696 | 0.012943 | 0.013128 | 0.013128 | 0.99612 | -0.13906 | 0.99608 | -0.13937 | 2.0578
72 | 0.11884 | 0.054942 | -0.11884 | -0.057556 | 1.8809e-07 | -0.0026138 | 0.0037942 | 0.0038266 | 0.0038266 | 0.99612 | -0.13906 | 0.99612 | -0.13907 | 0.59978
73 | 0.41913 | 0.17187 | -0.41913 | -0.17368 | 1.5515e-06 | -0.0018125 | 0.013128 | 0.013149 | 0.013149 | 0.99608 | -0.13937 | 0.99608 | -0.13939 | 2.0609
74 | 0.30596 | 0.11887 | -0.30596 | -0.12103 | 9.6829e-07 | -0.002153 | 0.0095128 | 0.0095356 | 0.0095356 | 0.99608 | -0.13939 | 0.99607 | -0.13942 | 1.4946
75 | 2.086 | 0.91268 | -2.0854 | -0.94035 | 0.00060774 | -0.027665 | 0.065989 | 0.066319 | 0.066319 | 0.99605 | -0.14474 | 0.99575 | -0.1464 | 10.3948
76 | -2.086 | -0.91268 | 2.086 | 0.91282 | 7.3971e-05 | 0.00013365 | 0.065989 | 0.065988 | 0.065989 | 0.99605 | -0.14474 | 0.99611 | -0.14091 | 10.2308
77 | 0.1196 | 0.050419 | -0.1196 | -0.053645 | 2.288e-07 | -0.0032261 | 0.0037629 | 0.0038002 | 0.0038002 | 0.99575 | -0.1464 | 0.99574 | -0.14641 | 0.59564
78 | -2.5082 | -1.1138 | 2.5084 | 1.114 | 0.00012056 | 0.00025096 | 0.079533 | 0.079532 | 0.079533 | 0.99611 | -0.14091 | 0.9962 | -0.13574 | 12.3307
79 | 0.26069 | 0.12271 | -0.26069 | -0.12281 | 1.8113e-06 | -9.4924e-05 | 0.0083499 | 0.0083512 | 0.0083512 | 0.99611 | -0.14091 | 0.9961 | -0.14163 | 1.2948
80 | 0.1196 | 0.053645 | -0.1196 | -0.057926 | 3.1085e-07 | -0.004281 | 0.0038002 | 0.0038527 | 0.0038527 | 0.99574 | -0.14641 | 0.99574 | -0.14643 | 0.60386
81 | -0.096273 | -0.046627 | 0.096274 | 0.046 | 1.575e-06 | -0.00062681 | 0.0031003 | 0.0030924 | 0.0031003 | 0.99601 | -0.14129 | 0.99604 | -0.13961 | 0.48067
82 | 0.20967 | 0.09417 | -0.20967 | -0.10001 | 1.2974e-06 | -0.0058356 | 0.0066616 | 0.0067327 | 0.0067327 | 0.99604 | -0.13961 | 0.99604 | -0.13964 | 1.0553
83 | -0.30595 | -0.14017 | 0.30596 | 0.12103 | 8.8226e-06 | -0.019143 | 0.0097534 | 0.0095356 | 0.0097534 | 0.99604 | -0.13961 | 0.99607 | -0.13942 | 1.5287
84 | -0.091191 | -0.044166 | 0.091191 | 0.038562 | 2.3373e-07 | -0.0056035 | 0.0029359 | 0.0028688 | 0.0029359 | 0.99628 | -0.14448 | 0.99628 | -0.14446 | 0.46017
85 | -0.091191 | -0.038562 | 0.091192 | 0.038035 | 1.1331e-06 | -0.00052721 | 0.0028688 | 0.0028629 | 0.0028688 | 0.99628 | -0.14446 | 0.99631 | -0.14309 | 0.44478
86 | -0.2398 | -0.11001 | 0.2398 | 0.10988 | 2.1076e-06 | -0.00013299 | 0.0076443 | 0.0076426 | 0.0076443 | 0.99631 | -0.14309 | 0.99632 | -0.14216 | 1.1852
87 | -7.4792 | -3.3167 | 7.4795 | 3.3158 | 0.00028701 | -0.00087719 | 0.23661 | 0.2366 | 0.23661 | 0.9982 | -0.058881 | 0.99824 | -0.058661 | 37.086
88 | 7.3793 | 3.2683 | -7.3764 | -3.2606 | 0.0029453 | 0.0077117 | 0.2334 | 0.2334 | 0.2334 | 0.9982 | -0.058881 | 0.99747 | -0.10185 | 36.1866
89 | -7.4795 | -3.3158 | 7.4807 | 3.3122 | 0.0011951 | -0.0036546 | 0.2366 | 0.23655 | 0.2366 | 0.99824 | -0.058661 | 0.99841 | -0.057743 | 37.0841
90 | 7.3764 | 3.2606 | -7.3762 | -3.2611 | 0.00015215 | -0.00047932 | 0.2334 | 0.23341 | 0.23341 | 0.99747 | -0.10185 | 0.99745 | -0.10197 | 36.5847
91 | 7.2132 | 3.1822 | -7.2105 | -3.191 | 0.0026658 | -0.008848 | 0.22817 | 0.22829 | 0.22829 | 0.99745 | -0.10197 | 0.99707 | -0.10412 | 35.7826
92 | 0.16302 | 0.078917 | -0.16302 | -0.078955 | 5.9732e-07 | -3.8405e-05 | 0.0052418 | 0.0052423 | 0.0052423 | 0.99745 | -0.10197 | 0.99745 | -0.10214 | 1.2786
93 | -7.4807 | -3.3122 | 7.4844 | 3.322 | 0.0037615 | 0.0098552 | 0.23655 | 0.23654 | 0.23655 | 0.99841 | -0.057743 | 0.99933 | -0.0036829 | 36.6738
94 | 1.1242 | 0.52732 | -1.1241 | -0.53491 | 4.8829e-05 | -0.0075893 | 0.035951 | 0.036045 | 0.036045 | 0.99707 | -0.10412 | 0.99702 | -0.10431 | 5.6497
95 | 6.0863 | 2.6637 | -6.0852 | -2.6607 | 0.0011624 | 0.0030048 | 0.19235 | 0.19235 | 0.19235 | 0.99707 | -0.10412 | 0.99672 | -0.1248 | 29.8222
96 | -7.6043 | -3.3801 | 7.6044 | 3.3799 | 7.0013e-05 | -0.00020661 | 0.24039 | 0.24039 | 0.24039 | 0.99933 | -0.0036829 | 0.99934 | -0.0036306 | 37.6786
97 | 1.1241 | 0.53491 | -1.1241 | -0.54442 | 6.1525e-05 | -0.009505 | 0.036045 | 0.036165 | 0.036165 | 0.99702 | -0.10431 | 0.99696 | -0.10452 | 5.6685
98 | 5.9299 | 2.5855 | -5.9295 | -2.5877 | 0.00041533 | -0.0021556 | 0.18736 | 0.18739 | 0.18739 | 0.99672 | -0.1248 | 0.99665 | -0.12523 | 29.371
99 | 0.11937 | 0.053655 | -0.11937 | -0.053908 | 1.8122e-08 | -0.00025278 | 0.003791 | 0.003794 | 0.003794 | 0.99658 | -0.12772 | 0.99658 | -0.12772 | 0.59467
100 | 0.11937 | 0.053908 | -0.11937 | -0.057813 | 2.8185e-07 | -0.0039054 | 0.003794 | 0.0038419 | 0.0038419 | 0.99658 | -0.12772 | 0.99658 | -0.12773 | 0.60218
101 | -0.2398 | -0.10988 | 0.23981 | 0.090261 | 5.5085e-06 | -0.019614 | 0.0076426 | 0.0074239 | 0.0076426 | 0.99632 | -0.14216 | 0.99635 | -0.142 | 1.1979
102 | -7.6044 | -3.3799 | 7.6089 | 3.3667 | 0.0044802 | -0.013243 | 0.24039 | 0.2402 | 0.24039 | 0.99934 | -0.0036306 | 0.99995 | -0.00025667 | 37.6781
103 | -8.651 | -3.8363 | 8.6514 | 3.8354 | 0.00038737 | -0.0008372 | 0.2732 | 0.27319 | 0.2732 | 0.99995 | -0.00025667 | 1 | 0 | 42.8212
104 | 1.0421 | 0.46961 | -1.0417 | -0.47626 | 0.00041357 | -0.0066505 | 0.032998 | 0.033079 | 0.033079 | 0.99995 | -0.00025667 | 0.99958 | 0.0027094 | 15.0359
105 | 0.89991 | 0.40837 | -0.89957 | -0.41574 | 0.00034145 | -0.0073636 | 0.02854 | 0.02863 | 0.02863 | 0.99958 | 0.0027094 | 0.99922 | 0.0056093 | 13.0135
106 | 0.14178 | 0.067891 | -0.14178 | -0.068667 | 8.9725e-07 | -0.00077603 | 0.0045398 | 0.0045495 | 0.0045495 | 0.99958 | 0.0027094 | 0.99957 | 0.0027639 | 2.068
107 | 0.89957 | 0.41574 | -0.89934 | -0.41578 | 0.00022763 | -4.3144e-05 | 0.02863 | 0.028632 | 0.028632 | 0.99922 | 0.0056093 | 0.99896 | 0.0036483 | 13.6343
108 | 0.26069 | 0.12281 | -0.26068 | -0.12425 | 4.9852e-07 | -0.0014388 | 0.0083512 | 0.008369 | 0.008369 | 0.9961 | -0.14163 | 0.9961 | -0.14164 | 1.3118
109 | 0.13894 | 0.065284 | -0.13894 | -0.067292 | 1.9805e-07 | -0.0020074 | 0.0044489 | 0.004474 | 0.004474 | 0.9961 | -0.14164 | 0.9961 | -0.14164 | 0.70125
110 | -0.10013 | -0.048496 | 0.10014 | 0.046954 | 4.1799e-06 | -0.001542 | 0.0032248 | 0.0032054 | 0.0032248 | 0.99596 | -0.14395 | 0.99604 | -0.13964 | 0.49997

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 8.826 | 3.9237

## res_load
| p_mw | q_mvar
0 | 0.25094 | 0.12153
1 | 0.096719 | 0.046843
2 | 0.1993 | 0.096526
3 | 0.05241 | 0.025383
4 | 0.17495 | 0.084735
5 | 0.33708 | 0.16326
6 | 0.19474 | 0.094318
7 | 0.14113 | 0.06835
8 | 0.12928 | 0.062615
9 | 0.12767 | 0.061832
10 | 0.14669 | 0.071046
11 | 0.15789 | 0.076468
12 | 0.098651 | 0.047779
13 | 0.056601 | 0.027413
14 | 0.099565 | 0.048221
15 | 0.087314 | 0.042288
16 | 0.11348 | 0.054961
17 | 0.16345 | 0.079164
18 | 0.092319 | 0.044712
19 | 0.12692 | 0.061469
20 | 0.10576 | 0.051221
21 | 0.15115 | 0.073207
22 | 0.11603 | 0.056195
23 | 0.15213 | 0.073681
24 | 0.15672 | 0.075901
25 | 0.14264 | 0.069086
26 | 0.15645 | 0.075774
27 | 0.15092 | 0.073095
28 | 0.13204 | 0.063951
29 | 0.12125 | 0.058726
30 | 0.15054 | 0.07291
31 | 0.14258 | 0.069057
32 | 0.12297 | 0.059557
33 | 0.084093 | 0.040728
34 | 0.060334 | 0.029221
35 | 0.13796 | 0.066818
36 | 0.054474 | 0.026383
37 | 0.097547 | 0.047244
38 | 0.15963 | 0.077313
39 | 0.11884 | 0.057556
40 | 0.11317 | 0.054811
41 | 0.16151 | 0.078223
42 | 0.1196 | 0.057926
43 | 0.096273 | 0.046627
44 | 0.091191 | 0.044166
45 | 0.14861 | 0.071973
46 | 0.099872 | 0.04837
47 | 0.16302 | 0.078955
48 | 0.11991 | 0.058075
49 | 0.1553 | 0.075217
50 | 1.1241 | 0.54442
51 | 0.14178 | 0.068667
52 | 0.16062 | 0.077794
53 | 0.13652 | 0.06612
54 | 0.11937 | 0.057813
55 | 0.12174 | 0.058964
56 | 0.13894 | 0.067292
57 | 0.10013 | 0.048496
58 | 0.10954 | 0.053051

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1