## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_368_2_node_128 | 20 | n |  | TRUE
1 | bus_MV_368_2_node_124 | 20 | n |  | TRUE
2 | bus_MV_368_2_node_129 | 20 | n |  | TRUE
3 | bus_MV_368_2_node_154 | 20 | n |  | TRUE
4 | bus_MV_368_2_node_131 | 20 | n |  | TRUE
5 | bus_MV_368_2_node_101 | 20 | n |  | TRUE
6 | bus_MV_368_2_node_146 | 20 | n |  | TRUE
7 | bus_MV_368_2_node_97 | 20 | n |  | TRUE
8 | bus_MV_368_2_node_147 | 20 | n |  | TRUE
9 | bus_MV_368_2_node_148 | 20 | n |  | TRUE
10 | bus_MV_368_2_node_149 | 20 | n |  | TRUE
11 | bus_MV_368_2_node_150 | 20 | n |  | TRUE
12 | bus_MV_368_2_node_121 | 20 | n |  | TRUE
13 | bus_MV_368_2_node_151 | 20 | n |  | TRUE
14 | bus_MV_368_2_node_126 | 20 | n |  | TRUE
15 | bus_MV_368_2_node_116 | 20 | n |  | TRUE
16 | bus_MV_368_2_node_155 | 20 | n |  | TRUE
17 | bus_MV_368_2_node_94 | 20 | n |  | TRUE
18 | bus_MV_368_2_node_166 | 20 | n |  | TRUE
19 | bus_MV_368_2_node_63 | 20 | n |  | TRUE
20 | bus_MV_368_2_node_59 | 20 | n |  | TRUE
21 | bus_MV_368_2_node_60 | 20 | n |  | TRUE
22 | bus_MV_368_2_node_83 | 20 | n |  | TRUE
23 | bus_MV_368_2_node_62 | 20 | n |  | TRUE
24 | bus_MV_368_2_node_66 | 20 | n |  | TRUE
25 | bus_MV_368_2_node_64 | 20 | n |  | TRUE
26 | bus_MV_368_2_node_65 | 20 | n |  | TRUE
27 | bus_MV_368_2_node_82 | 20 | n |  | TRUE
28 | bus_MV_368_2_node_92 | 20 | n |  | TRUE
29 | bus_MV_368_2_node_93 | 20 | n |  | TRUE
30 | bus_MV_368_2_node_95 | 20 | n |  | TRUE
31 | bus_MV_368_2_node_96 | 20 | n |  | TRUE
32 | bus_MV_368_2_node_115 | 20 | n |  | TRUE
33 | bus_MV_368_2_node_98 | 20 | n |  | TRUE
34 | bus_MV_368_2_node_100 | 20 | n |  | TRUE
35 | bus_MV_368_2_node_99 | 20 | n |  | TRUE
36 | bus_MV_368_2_node_102 | 20 | n |  | TRUE
37 | bus_MV_368_2_node_103 | 20 | n |  | TRUE
38 | bus_MV_368_2_node_105 | 20 | n |  | TRUE
39 | bus_MV_368_2_node_117 | 20 | n |  | TRUE
40 | bus_MV_368_2_node_123 | 20 | n |  | TRUE
41 | bus_MV_368_2_node_106 | 20 | n |  | TRUE
42 | bus_MV_368_2_node_107 | 20 | n |  | TRUE
43 | bus_MV_368_2_node_108 | 20 | n |  | TRUE
44 | bus_MV_368_2_node_109 | 20 | n |  | TRUE
45 | bus_MV_368_2_node_111 | 20 | n |  | TRUE
46 | bus_MV_368_2_node_112 | 20 | n |  | TRUE
47 | bus_MV_368_2_node_119 | 20 | n |  | TRUE
48 | bus_MV_368_2_node_110 | 20 | n |  | TRUE
49 | bus_MV_368_2_node_113 | 20 | n |  | TRUE
50 | bus_MV_368_2_node_114 | 20 | n |  | TRUE
51 | bus_MV_368_2_node_125 | 20 | n |  | TRUE
52 | bus_MV_368_2_node_118 | 20 | n |  | TRUE
53 | bus_MV_368_2_node_120 | 20 | n |  | TRUE
54 | bus_MV_368_2_node_122 | 20 | n |  | TRUE
55 | bus_MV_368_2_node_127 | 20 | n |  | TRUE
56 | bus_HV_368_2_node_154 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_368_2_load_128 | 0 | 0.11897 | 0.057618 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_368_2_load_129 | 2 | 0.12078 | 0.058497 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_368_2_load_154 | 3 | 0.060367 | 0.029237 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_368_2_load_131 | 4 | 0.099809 | 0.04834 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_368_2_load_146 | 6 | 0.11781 | 0.057057 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_368_2_load_147 | 8 | 0.25565 | 0.12382 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_368_2_load_148 | 9 | 0.2633 | 0.12752 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_368_2_load_149 | 10 | 0.099913 | 0.04839 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_368_2_load_150 | 11 | 0.16648 | 0.080628 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_368_2_load_151 | 13 | 0.12745 | 0.061729 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_368_2_load_155 | 16 | 0.15074 | 0.073007 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_368_2_load_166 | 18 | 0.23123 | 0.11199 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_368_2_load_59 | 20 | 0.17065 | 0.082652 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_368_2_load_66 | 24 | 0.27586 | 0.1336 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_368_2_load_65 | 26 | 0.19225 | 0.093111 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_368_2_load_82 | 27 | 0.19997 | 0.096851 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_368_2_load_92 | 28 | 0.10769 | 0.052156 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_368_2_load_95 | 30 | 0.27767 | 0.13448 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_368_2_load_115 | 32 | 0.1079 | 0.052261 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_368_2_load_98 | 33 | 0.16173 | 0.078329 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_368_2_load_105 | 38 | 0.13754 | 0.066616 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_368_2_load_117 | 39 | 0.14207 | 0.06881 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_368_2_load_106 | 41 | 0.14627 | 0.070842 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_368_2_load_112 | 46 | 0.10772 | 0.052173 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_368_2_load_119 | 47 | 0.23801 | 0.11527 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_368_2_load_110 | 48 | 0.10702 | 0.051832 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_368_2_load_113 | 49 | 0.14936 | 0.072339 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_368_2_load_118 | 52 | 0.052647 | 0.025498 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_368_2_load_122 | 54 | 0.12095 | 0.058581 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_368_2_load_127 | 55 | 0.12035 | 0.058289 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_368_2_line_0 |  | 0 | 1 | 0.20343 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_368_2_line_1 |  | 0 | 2 | 0.98816 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_368_2_line_2 |  | 0 | 3 | 1.1117 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_368_2_line_3 |  | 1 | 14 | 0.85859 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_368_2_line_4 |  | 3 | 15 | 0.23888 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_368_2_line_5 |  | 4 | 5 | 0.081963 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_368_2_line_6 |  | 5 | 35 | 0.065821 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_368_2_line_7 |  | 6 | 7 | 0.056685 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_368_2_line_8 |  | 6 | 8 | 0.13677 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_368_2_line_9 |  | 7 | 26 | 2.3972 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_368_2_line_10 |  | 7 | 31 | 0.60817 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_368_2_line_11 |  | 9 | 10 | 0.034686 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_368_2_line_12 |  | 10 | 11 | 0.050835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_368_2_line_13 |  | 11 | 12 | 0.036737 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_368_2_line_14 |  | 12 | 53 | 0.043841 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_368_2_line_15 |  | 13 | 14 | 0.017102 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_368_2_line_16 |  | 14 | 40 | 0.81576 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_368_2_line_17 |  | 14 | 51 | 0.11307 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_368_2_line_18 |  | 15 | 32 | 0.039153 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_368_2_line_19 |  | 16 | 17 | 0.082885 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_368_2_line_20 |  | 17 | 29 | 0.58979 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_368_2_line_21 |  | 18 | 19 | 0.027518 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_368_2_line_22 |  | 19 | 25 | 0.40426 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_368_2_line_23 |  | 19 | 23 | 0.61154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_368_2_line_24 |  | 20 | 21 | 0.076305 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_368_2_line_25 |  | 20 | 22 | 1.7731 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_368_2_line_26 |  | 21 | 23 | 0.4918 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_368_2_line_27 |  | 22 | 27 | 0.012941 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_368_2_line_28 |  | 23 | 24 | 0.035923 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_368_2_line_29 |  | 25 | 26 | 0.065732 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_368_2_line_30 |  | 28 | 29 | 0.062506 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_368_2_line_31 |  | 28 | 30 | 1.2709 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_368_2_line_32 |  | 30 | 31 | 0.024183 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_368_2_line_33 |  | 31 | 32 | 1.7637 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_368_2_line_34 |  | 33 | 34 | 0.027352 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_368_2_line_35 |  | 33 | 35 | 0.067165 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_368_2_line_36 |  | 34 | 36 | 0.17706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_368_2_line_37 |  | 36 | 37 | 0.18257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_368_2_line_38 |  | 36 | 38 | 0.077688 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_368_2_line_39 |  | 37 | 39 | 0.10895 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_368_2_line_40 |  | 38 | 40 | 0.29377 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_368_2_line_41 |  | 40 | 54 | 0.093157 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_368_2_line_42 |  | 41 | 42 | 0.038384 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_368_2_line_43 |  | 42 | 43 | 0.28118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_368_2_line_44 |  | 42 | 44 | 1.0078 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_368_2_line_45 |  | 43 | 45 | 0.038421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_368_2_line_46 |  | 43 | 46 | 0.069148 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_368_2_line_47 |  | 44 | 47 | 0.040412 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_368_2_line_48 |  | 45 | 49 | 0.032934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_368_2_line_49 |  | 46 | 50 | 0.079558 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_368_2_line_50 |  | 46 | 48 | 0.10476 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_368_2_line_51 |  | 47 | 52 | 0.090288 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_368_2_line_52 |  | 50 | 51 | 0.21067 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_368_2_line_53 |  | 51 | 55 | 0.1387 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_368_2_line_54 |  | 52 | 53 | 0.040607 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_368_2_trafo_154 | 25 MVA 110/20 kV | 56 | 3 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2700867.2785 | 1276720.6649
1 | 2701071.2281 | 1276726.8266
2 | 2699881.0314 | 1276782.0984
3 | 2700734.5306 | 1275616.9574
4 | 2702393.7224 | 1276569.6103
5 | 2702323.1494 | 1276610.8446
6 | 2699763.6842 | 1273550.9974
7 | 2699763.2725 | 1273607.6808
8 | 2699771.88 | 1273414.4713
9 | 2700704.2846 | 1278082.1323
10 | 2700738.9693 | 1278082.4909
11 | 2700789.8014 | 1278083.0164
12 | 2700826.537 | 1278083.3961
13 | 2701665.4261 | 1277050.4509
14 | 2701652.4329 | 1277061.6146
15 | 2700617.1476 | 1275408.9076
16 | 2701523.9953 | 1272576.9047
17 | 2701443.0574 | 1272595.185
18 | 2697128.8385 | 1274346.9635
19 | 2697131.1959 | 1274321.6251
20 | 2696634.5585 | 1274447.2154
21 | 2696707.1694 | 1274423.7621
22 | 2696835.33 | 1276208.961
23 | 2696708.8757 | 1274146.7758
24 | 2696705.8978 | 1274110.9965
25 | 2697383.0906 | 1274220.8331
26 | 2697448.3356 | 1274230.2956
27 | 2696829.9948 | 1276220.7281
28 | 2700866.6934 | 1272653.0394
29 | 2700877.3373 | 1272591.4461
30 | 2700116.6457 | 1273679.0612
31 | 2700097.0637 | 1273693.2485
32 | 2700631.661 | 1275373.958
33 | 2702205.5004 | 1276671.8704
34 | 2702186.8783 | 1276691.9545
35 | 2702262.8093 | 1276636.8437
36 | 2702027.6435 | 1276766.7426
37 | 2702141.5512 | 1276852.8888
38 | 2701955.8521 | 1276796.5724
39 | 2702244.4679 | 1276817.1397
40 | 2701663.4976 | 1276767.792
41 | 2701625.5431 | 1277605.4959
42 | 2701587.1268 | 1277605.2229
43 | 2701577.3679 | 1277391.6784
44 | 2700870.2209 | 1277914.8726
45 | 2701612.1921 | 1277408.1369
46 | 2701523.2987 | 1277348.3653
47 | 2700868.6178 | 1277955.2497
48 | 2701592.2434 | 1277269.4938
49 | 2701639.71 | 1277426.3602
50 | 2701460.9499 | 1277298.7048
51 | 2701563.1594 | 1277128.3359
52 | 2700863.2755 | 1278045.3796
53 | 2700870.4676 | 1278085.3488
54 | 2701756.622 | 1276765.3394
55 | 2701452.2286 | 1277045.0768
56 | 2700734.5306 | 1275616.9574

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99473 | -0.044408 | 0.11897 | 0.057618
1 | 0.99415 | -0.040298 | 0 | 0
2 | 0.9945 | -0.045916 | 0.12078 | 0.058497
3 | 1 | 0 | -4.6275 | -2.0548
4 | 0.99057 | -0.01831 | 0.099809 | 0.04834
5 | 0.99058 | -0.018404 | 0 | 0
6 | 0.99108 | -0.052418 | 0.11781 | 0.057057
7 | 0.99111 | -0.052672 | 0 | 0
8 | 0.99101 | -0.052849 | 0.25565 | 0.12382
9 | 0.98924 | -0.0034942 | 0.2633 | 0.12752
10 | 0.98925 | -0.0036049 | 0.099913 | 0.04839
11 | 0.98928 | -0.003826 | 0.16648 | 0.080628
12 | 0.9893 | -0.004058 | 0 | 0
13 | 0.9917 | -0.022176 | 0.12745 | 0.061729
14 | 0.99171 | -0.022202 | 0 | 0
15 | 0.99904 | -0.0076793 | 0 | 0
16 | 0.99145 | -0.066419 | 0.15074 | 0.073007
17 | 0.99146 | -0.066566 | 0 | 0
18 | 0.98563 | -0.089086 | 0.23123 | 0.11199
19 | 0.98564 | -0.089164 | 0 | 0
20 | 0.98484 | -0.083545 | 0.17065 | 0.082652
21 | 0.9849 | -0.083177 | 0 | 0
22 | 0.98415 | -0.088172 | 0 | 0
23 | 0.98513 | -0.085163 | 0 | 0
24 | 0.98512 | -0.085042 | 0.27586 | 0.1336
25 | 0.98609 | -0.092627 | 0 | 0
26 | 0.98616 | -0.093166 | 0.19225 | 0.093111
27 | 0.98414 | -0.08814 | 0.19997 | 0.096851
28 | 0.99159 | -0.067107 | 0.10769 | 0.052156
29 | 0.99157 | -0.067309 | 0 | 0
30 | 0.99221 | -0.061247 | 0.27767 | 0.13448
31 | 0.99223 | -0.061377 | 0 | 0
32 | 0.99894 | -0.0068834 | 0.1079 | 0.052261
33 | 0.99061 | -0.01837 | 0.16173 | 0.078329
34 | 0.99061 | -0.01845 | 0 | 0
35 | 0.99059 | -0.018473 | 0 | 0
36 | 0.99067 | -0.018943 | 0 | 0
37 | 0.99064 | -0.018654 | 0 | 0
38 | 0.99071 | -0.019256 | 0.13754 | 0.066616
39 | 0.99061 | -0.018845 | 0.14207 | 0.06881
40 | 0.99102 | -0.016924 | 0 | 0
41 | 0.99055 | -0.013155 | 0.14627 | 0.070842
42 | 0.99056 | -0.013222 | 0 | 0
43 | 0.99091 | -0.015921 | 0 | 0
44 | 0.9895 | -0.0042871 | 0 | 0
45 | 0.9909 | -0.015854 | 0 | 0
46 | 0.99101 | -0.016684 | 0.10772 | 0.052173
47 | 0.98946 | -0.0038962 | 0.23801 | 0.11527
48 | 0.99098 | -0.016822 | 0.10702 | 0.051832
49 | 0.99089 | -0.015795 | 0.14936 | 0.072339
50 | 0.99114 | -0.01776 | 0 | 0
51 | 0.9915 | -0.020562 | 0 | 0
52 | 0.98936 | -0.0045836 | 0.052647 | 0.025498
53 | 0.98933 | -0.0043323 | 0 | 0
54 | 0.991 | -0.017064 | 0.12095 | 0.058581
55 | 0.99147 | -0.020769 | 0.12035 | 0.058289
56 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 2.2512 | 0.97882 | -2.2498 | -0.98321 | 0.0013793 | -0.004394 | 0.071238 | 0.071294 | 0.071294 | 0.99473 | -0.044408 | 0.99415 | -0.040298 | 32.4062
1 | 0.12081 | 0.057347 | -0.12078 | -0.058497 | 2.6616e-05 | -0.0011503 | 0.0038809 | 0.0038955 | 0.0038955 | 0.99473 | -0.044408 | 0.9945 | -0.045916 | 1.855
2 | -2.4909 | -1.0938 | 2.5033 | 1.1002 | 0.012343 | 0.0064112 | 0.07895 | 0.078935 | 0.07895 | 0.99473 | -0.044408 | 1 | 0 | 37.5952
3 | 2.2498 | 0.98321 | -2.2439 | -1.0017 | 0.0058453 | -0.018477 | 0.071294 | 0.071531 | 0.071531 | 0.99415 | -0.040298 | 0.99171 | -0.022202 | 32.5141
4 | 2.1102 | 0.94412 | -2.1083 | -0.94321 | 0.0018957 | 0.00090247 | 0.066736 | 0.06674 | 0.06674 | 1 | 0 | 0.99904 | -0.0076793 | 31.7808
5 | -0.099809 | -0.04834 | 0.09981 | 0.04642 | 1.1343e-06 | -0.0019199 | 0.0032318 | 0.0032078 | 0.0032318 | 0.99057 | -0.01831 | 0.99058 | -0.018404 | 1.469
6 | -0.09981 | -0.04642 | 0.099811 | 0.044878 | 8.9892e-07 | -0.0015418 | 0.0032078 | 0.0031892 | 0.0032078 | 0.99058 | -0.018404 | 0.99059 | -0.018473 | 1.4581
7 | -0.37348 | -0.18073 | 0.37349 | 0.1794 | 1.1037e-05 | -0.0013261 | 0.012085 | 0.012068 | 0.012085 | 0.99108 | -0.052418 | 0.99111 | -0.052672 | 5.4932
8 | 0.25567 | 0.12367 | -0.25565 | -0.12382 | 1.668e-05 | -0.00014992 | 0.0082724 | 0.0082744 | 0.0082744 | 0.99108 | -0.052418 | 0.99101 | -0.052849 | 3.9402
9 | 1.0761 | 0.47855 | -1.0711 | -0.4782 | 0.0050306 | 0.00035388 | 0.034303 | 0.034336 | 0.034336 | 0.99111 | -0.052672 | 0.98616 | -0.093166 | 16.3505
10 | -1.4496 | -0.65795 | 1.4513 | 0.64419 | 0.0017391 | -0.013764 | 0.046367 | 0.046197 | 0.046367 | 0.99111 | -0.052672 | 0.99223 | -0.061377 | 21.076
11 | -0.2633 | -0.12752 | 0.2633 | 0.12671 | 3.3708e-06 | -0.00080946 | 0.0085371 | 0.0085268 | 0.0085371 | 0.98924 | -0.0034942 | 0.98925 | -0.0036049 | 3.8805
12 | -0.36321 | -0.1751 | 0.36322 | 0.17392 | 9.3836e-06 | -0.001185 | 0.011766 | 0.011751 | 0.011766 | 0.98925 | -0.0036049 | 0.98928 | -0.003826 | 5.3483
13 | -0.5297 | -0.25454 | 0.52971 | 0.25369 | 1.4414e-05 | -0.00085418 | 0.017149 | 0.017138 | 0.017149 | 0.98928 | -0.003826 | 0.9893 | -0.004058 | 7.795
14 | -0.52971 | -0.25369 | 0.52973 | 0.25267 | 1.7177e-05 | -0.0010194 | 0.017138 | 0.017125 | 0.017138 | 0.9893 | -0.004058 | 0.98933 | -0.0043323 | 7.79
15 | -0.12745 | -0.061729 | 0.12745 | 0.061327 | 3.875e-07 | -0.00040147 | 0.0041223 | 0.0041172 | 0.0041223 | 0.9917 | -0.022176 | 0.99171 | -0.022202 | 1.8738
16 | 0.66281 | 0.28678 | -0.66232 | -0.30578 | 0.00048643 | -0.018998 | 0.021022 | 0.02125 | 0.02125 | 0.99171 | -0.022202 | 0.99102 | -0.016924 | 9.6589
17 | 1.4537 | 0.65358 | -1.4533 | -0.65614 | 0.00032514 | -0.0025581 | 0.046395 | 0.046427 | 0.046427 | 0.99171 | -0.022202 | 0.9915 | -0.020562 | 21.103
18 | 2.1083 | 0.94321 | -2.1081 | -0.94408 | 0.00023285 | -0.00086386 | 0.06674 | 0.066751 | 0.066751 | 0.99904 | -0.0076793 | 0.99894 | -0.0068834 | 30.3412
19 | -0.15074 | -0.073007 | 0.15074 | 0.071062 | 2.6183e-06 | -0.0019445 | 0.0048767 | 0.0048523 | 0.0048767 | 0.99145 | -0.066419 | 0.99146 | -0.066566 | 2.2167
20 | -0.15074 | -0.071062 | 0.15076 | 0.057224 | 1.7914e-05 | -0.013839 | 0.0048523 | 0.0046946 | 0.0048523 | 0.99146 | -0.066566 | 0.99157 | -0.067309 | 2.2056
21 | -0.23123 | -0.11199 | 0.23124 | 0.11135 | 2.078e-06 | -0.00063766 | 0.007525 | 0.0075169 | 0.007525 | 0.98563 | -0.089086 | 0.98564 | -0.089164 | 3.4204
22 | -0.87833 | -0.39585 | 0.87876 | 0.3866 | 0.00042798 | -0.0092543 | 0.028216 | 0.028105 | 0.028216 | 0.98564 | -0.089164 | 0.98609 | -0.092627 | 12.8257
23 | 0.64709 | 0.2845 | -0.64674 | -0.29857 | 0.00035278 | -0.014073 | 0.020703 | 0.020874 | 0.020874 | 0.98564 | -0.089164 | 0.98513 | -0.085163 | 9.488
24 | -0.37076 | -0.17724 | 0.37078 | 0.17716 | 1.9724e-05 | -7.6002e-05 | 0.012046 | 0.012044 | 0.012046 | 0.98484 | -0.083545 | 0.9849 | -0.083177 | 5.736
25 | 0.20011 | 0.094584 | -0.19997 | -0.096552 | 0.0001335 | -0.001968 | 0.0064877 | 0.0065137 | 0.0065137 | 0.98484 | -0.083545 | 0.98415 | -0.088172 | 3.1017
26 | -0.37078 | -0.17716 | 0.37088 | 0.16579 | 9.4127e-05 | -0.011365 | 0.012044 | 0.011904 | 0.012044 | 0.9849 | -0.083177 | 0.98513 | -0.085163 | 5.4748
27 | 0.19997 | 0.096552 | -0.19997 | -0.096851 | 7.3342e-07 | -0.00029904 | 0.0065137 | 0.0065175 | 0.0065175 | 0.98415 | -0.088172 | 0.98414 | -0.08814 | 2.9625
28 | 0.27586 | 0.13277 | -0.27586 | -0.1336 | 3.8643e-06 | -0.00083123 | 0.0089713 | 0.0089819 | 0.0089819 | 0.98513 | -0.085163 | 0.98512 | -0.085042 | 4.0827
29 | -0.87876 | -0.3866 | 0.87882 | 0.38509 | 6.9269e-05 | -0.0015056 | 0.028105 | 0.028087 | 0.028105 | 0.98609 | -0.092627 | 0.98616 | -0.093166 | 12.7749
30 | 0.15076 | 0.057152 | -0.15076 | -0.057224 | 2.4541e-06 | -7.1832e-05 | 0.0046939 | 0.0046946 | 0.0046946 | 0.99159 | -0.067107 | 0.99157 | -0.067309 | 2.2355
31 | -0.25845 | -0.10931 | 0.2586 | 0.10791 | 0.00015082 | -0.0013983 | 0.0081694 | 0.0081526 | 0.0081694 | 0.99159 | -0.067107 | 0.99221 | -0.061247 | 3.8902
32 | -0.53627 | -0.24239 | 0.53628 | 0.24183 | 9.4609e-06 | -0.00056563 | 0.017122 | 0.017115 | 0.017122 | 0.99221 | -0.061247 | 0.99223 | -0.061377 | 7.7828
33 | -1.9876 | -0.88602 | 2.0002 | 0.89182 | 0.012591 | 0.0057997 | 0.063312 | 0.063288 | 0.063312 | 0.99223 | -0.061377 | 0.99894 | -0.0068834 | 30.1487
34 | -0.26154 | -0.12313 | 0.26154 | 0.12249 | 2.5888e-06 | -0.00064008 | 0.008424 | 0.0084161 | 0.008424 | 0.99061 | -0.01837 | 0.99061 | -0.01845 | 3.8291
35 | 0.099813 | 0.0448 | -0.099811 | -0.044878 | 1.2168e-06 | -7.792e-05 | 0.0031882 | 0.0031892 | 0.0031892 | 0.99061 | -0.01837 | 0.99059 | -0.018473 | 1.5186
36 | -0.26154 | -0.12249 | 0.26156 | 0.11835 | 1.6642e-05 | -0.0041439 | 0.0084161 | 0.0083655 | 0.0084161 | 0.99061 | -0.01845 | 0.99067 | -0.018943 | 3.8255
37 | 0.14208 | 0.064408 | -0.14208 | -0.068685 | 5.0943e-06 | -0.0042764 | 0.0045458 | 0.0045986 | 0.0045986 | 0.99067 | -0.018943 | 0.99064 | -0.018654 | 2.0903
38 | -0.40365 | -0.18275 | 0.40366 | 0.18094 | 1.726e-05 | -0.0018154 | 0.012911 | 0.01289 | 0.012911 | 0.99067 | -0.018943 | 0.99071 | -0.019256 | 5.8688
39 | 0.14208 | 0.068685 | -0.14207 | -0.06881 | 4.1064e-06 | -0.00012506 | 0.0045986 | 0.0046002 | 0.0046002 | 0.99064 | -0.018654 | 0.99061 | -0.018845 | 2.1906
40 | -0.54121 | -0.24755 | 0.54136 | 0.24731 | 0.00015736 | -0.00024576 | 0.017341 | 0.017337 | 0.017341 | 0.99071 | -0.019256 | 0.99102 | -0.016924 | 8.2577
41 | 0.12096 | 0.058474 | -0.12095 | -0.058581 | 2.5429e-06 | -0.00010763 | 0.0039135 | 0.0039149 | 0.0039149 | 0.99102 | -0.016924 | 0.991 | -0.017064 | 1.8642
42 | -0.14627 | -0.070842 | 0.14627 | 0.069943 | 1.1468e-06 | -0.0008989 | 0.0047364 | 0.004725 | 0.0047364 | 0.99055 | -0.013155 | 0.99056 | -0.013222 | 2.1529
43 | -0.9677 | -0.43813 | 0.96806 | 0.43165 | 0.00035882 | -0.0064832 | 0.030957 | 0.030878 | 0.030957 | 0.99056 | -0.013222 | 0.99091 | -0.015921 | 14.0714
44 | 0.82143 | 0.36819 | -0.8205 | -0.39149 | 0.000936 | -0.023308 | 0.026233 | 0.026522 | 0.026522 | 0.99056 | -0.013222 | 0.9895 | -0.0042871 | 12.0555
45 | 0.14936 | 0.070667 | -0.14936 | -0.071567 | 1.1913e-06 | -0.00090038 | 0.0048137 | 0.004825 | 0.004825 | 0.99091 | -0.015921 | 0.9909 | -0.015854 | 2.1932
46 | -1.1174 | -0.50231 | 1.1175 | 0.50073 | 0.00011753 | -0.0015864 | 0.035691 | 0.035672 | 0.035691 | 0.99091 | -0.015921 | 0.99101 | -0.016684 | 16.2232
47 | 0.8205 | 0.39149 | -0.82046 | -0.39243 | 3.7967e-05 | -0.00093344 | 0.026522 | 0.026534 | 0.026534 | 0.9895 | -0.0042871 | 0.98946 | -0.0038962 | 12.0609
48 | 0.14936 | 0.071567 | -0.14936 | -0.072339 | 1.0257e-06 | -0.00077178 | 0.004825 | 0.0048348 | 0.0048348 | 0.9909 | -0.015854 | 0.99089 | -0.015795 | 2.1976
49 | -1.3323 | -0.60461 | 1.3325 | 0.6028 | 0.00019281 | -0.0018086 | 0.042618 | 0.042596 | 0.042618 | 0.99101 | -0.016684 | 0.99114 | -0.01776 | 19.3719
50 | 0.10702 | 0.05171 | -0.10702 | -0.051832 | 2.2384e-06 | -0.00012142 | 0.0034623 | 0.0034639 | 0.0034639 | 0.99101 | -0.016684 | 0.99098 | -0.016822 | 1.6495
51 | 0.58245 | 0.27715 | -0.58239 | -0.27722 | 5.6974e-05 | -6.9829e-05 | 0.018819 | 0.01882 | 0.01882 | 0.98946 | -0.0038962 | 0.98936 | -0.0045836 | 8.9619
52 | -1.3325 | -0.6028 | 1.333 | 0.59801 | 0.00050958 | -0.0047918 | 0.042596 | 0.042537 | 0.042596 | 0.99114 | -0.01776 | 0.9915 | -0.020562 | 19.3617
53 | 0.12035 | 0.058128 | -0.12035 | -0.058289 | 3.7442e-06 | -0.00016043 | 0.0038914 | 0.0038935 | 0.0038935 | 0.9915 | -0.020562 | 0.99147 | -0.020769 | 1.854
54 | 0.52975 | 0.25173 | -0.52973 | -0.25267 | 1.5887e-05 | -0.00094427 | 0.017113 | 0.017125 | 0.017125 | 0.98936 | -0.0045836 | 0.98933 | -0.0043323 | 7.7842

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 4.6879 | 2.084

## res_load
| p_mw | q_mvar
0 | 0.11897 | 0.057618
1 | 0.12078 | 0.058497
2 | 0.060367 | 0.029237
3 | 0.099809 | 0.04834
4 | 0.11781 | 0.057057
5 | 0.25565 | 0.12382
6 | 0.2633 | 0.12752
7 | 0.099913 | 0.04839
8 | 0.16648 | 0.080628
9 | 0.12745 | 0.061729
10 | 0.15074 | 0.073007
11 | 0.23123 | 0.11199
12 | 0.17065 | 0.082652
13 | 0.27586 | 0.1336
14 | 0.19225 | 0.093111
15 | 0.19997 | 0.096851
16 | 0.10769 | 0.052156
17 | 0.27767 | 0.13448
18 | 0.1079 | 0.052261
19 | 0.16173 | 0.078329
20 | 0.13754 | 0.066616
21 | 0.14207 | 0.06881
22 | 0.14627 | 0.070842
23 | 0.10772 | 0.052173
24 | 0.23801 | 0.11527
25 | 0.10702 | 0.051832
26 | 0.14936 | 0.072339
27 | 0.052647 | 0.025498
28 | 0.12095 | 0.058581
29 | 0.12035 | 0.058289

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1