## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_36_2_node_70 | 20 | n |  | TRUE
1 | bus_MV_36_2_node_71 | 20 | n |  | TRUE
2 | bus_MV_36_2_node_72 | 20 | n |  | TRUE
3 | bus_MV_36_2_node_73 | 20 | n |  | TRUE
4 | bus_MV_36_2_node_110 | 20 | n |  | TRUE
5 | bus_MV_36_2_node_74 | 20 | n |  | TRUE
6 | bus_MV_36_2_node_235 | 20 | n |  | TRUE
7 | bus_MV_36_2_node_75 | 20 | n |  | TRUE
8 | bus_MV_36_2_node_108 | 20 | n |  | TRUE
9 | bus_MV_36_2_node_111 | 20 | n |  | TRUE
10 | bus_MV_36_2_node_76 | 20 | n |  | TRUE
11 | bus_MV_36_2_node_80 | 20 | n |  | TRUE
12 | bus_MV_36_2_node_88 | 20 | n |  | TRUE
13 | bus_MV_36_2_node_220 | 20 | n |  | TRUE
14 | bus_MV_36_2_node_77 | 20 | n |  | TRUE
15 | bus_MV_36_2_node_79 | 20 | n |  | TRUE
16 | bus_MV_36_2_node_224 | 20 | n |  | TRUE
17 | bus_MV_36_2_node_81 | 20 | n |  | TRUE
18 | bus_MV_36_2_node_82 | 20 | n |  | TRUE
19 | bus_MV_36_2_node_83 | 20 | n |  | TRUE
20 | bus_MV_36_2_node_85 | 20 | n |  | TRUE
21 | bus_MV_36_2_node_86 | 20 | n |  | TRUE
22 | bus_MV_36_2_node_223 | 20 | n |  | TRUE
23 | bus_MV_36_2_node_87 | 20 | n |  | TRUE
24 | bus_MV_36_2_node_84 | 20 | n |  | TRUE
25 | bus_MV_36_2_node_179 | 20 | n |  | TRUE
26 | bus_MV_36_2_node_191 | 20 | n |  | TRUE
27 | bus_MV_36_2_node_91 | 20 | n |  | TRUE
28 | bus_MV_36_2_node_230 | 20 | n |  | TRUE
29 | bus_MV_36_2_node_89 | 20 | n |  | TRUE
30 | bus_MV_36_2_node_90 | 20 | n |  | TRUE
31 | bus_MV_36_2_node_214 | 20 | n |  | TRUE
32 | bus_MV_36_2_node_92 | 20 | n |  | TRUE
33 | bus_MV_36_2_node_93 | 20 | n |  | TRUE
34 | bus_MV_36_2_node_109 | 20 | n |  | TRUE
35 | bus_MV_36_2_node_94 | 20 | n |  | TRUE
36 | bus_MV_36_2_node_95 | 20 | n |  | TRUE
37 | bus_MV_36_2_node_105 | 20 | n |  | TRUE
38 | bus_MV_36_2_node_229 | 20 | n |  | TRUE
39 | bus_MV_36_2_node_96 | 20 | n |  | TRUE
40 | bus_MV_36_2_node_97 | 20 | n |  | TRUE
41 | bus_MV_36_2_node_98 | 20 | n |  | TRUE
42 | bus_MV_36_2_node_99 | 20 | n |  | TRUE
43 | bus_MV_36_2_node_103 | 20 | n |  | TRUE
44 | bus_MV_36_2_node_217 | 20 | n |  | TRUE
45 | bus_MV_36_2_node_100 | 20 | n |  | TRUE
46 | bus_MV_36_2_node_101 | 20 | n |  | TRUE
47 | bus_MV_36_2_node_104 | 20 | n |  | TRUE
48 | bus_MV_36_2_node_227 | 20 | n |  | TRUE
49 | bus_MV_36_2_node_216 | 20 | n |  | TRUE
50 | bus_MV_36_2_node_102 | 20 | n |  | TRUE
51 | bus_MV_36_2_node_106 | 20 | n |  | TRUE
52 | bus_MV_36_2_node_226 | 20 | n |  | TRUE
53 | bus_MV_36_2_node_107 | 20 | n |  | TRUE
54 | bus_MV_36_2_node_208 | 20 | n |  | TRUE
55 | bus_MV_36_2_node_164 | 20 | n |  | TRUE
56 | bus_MV_36_2_node_166 | 20 | n |  | TRUE
57 | bus_MV_36_2_node_168 | 20 | n |  | TRUE
58 | bus_MV_36_2_node_173 | 20 | n |  | TRUE
59 | bus_MV_36_2_node_167 | 20 | n |  | TRUE
60 | bus_MV_36_2_node_174 | 20 | n |  | TRUE
61 | bus_MV_36_2_node_169 | 20 | n |  | TRUE
62 | bus_MV_36_2_node_212 | 20 | n |  | TRUE
63 | bus_MV_36_2_node_175 | 20 | n |  | TRUE
64 | bus_MV_36_2_node_233 | 20 | n |  | TRUE
65 | bus_MV_36_2_node_170 | 20 | n |  | TRUE
66 | bus_MV_36_2_node_171 | 20 | n |  | TRUE
67 | bus_MV_36_2_node_172 | 20 | n |  | TRUE
68 | bus_MV_36_2_node_210 | 20 | n |  | TRUE
69 | bus_MV_36_2_node_211 | 20 | n |  | TRUE
70 | bus_MV_36_2_node_221 | 20 | n |  | TRUE
71 | bus_MV_36_2_node_180 | 20 | n |  | TRUE
72 | bus_MV_36_2_node_181 | 20 | n |  | TRUE
73 | bus_MV_36_2_node_182 | 20 | n |  | TRUE
74 | bus_MV_36_2_node_183 | 20 | n |  | TRUE
75 | bus_MV_36_2_node_189 | 20 | n |  | TRUE
76 | bus_MV_36_2_node_188 | 20 | n |  | TRUE
77 | bus_MV_36_2_node_184 | 20 | n |  | TRUE
78 | bus_MV_36_2_node_185 | 20 | n |  | TRUE
79 | bus_MV_36_2_node_186 | 20 | n |  | TRUE
80 | bus_MV_36_2_node_187 | 20 | n |  | TRUE
81 | bus_MV_36_2_node_190 | 20 | n |  | TRUE
82 | bus_MV_36_2_node_215 | 20 | n |  | TRUE
83 | bus_MV_36_2_node_231 | 20 | n |  | TRUE
84 | bus_MV_36_2_node_234 | 20 | n |  | TRUE
85 | bus_HV_36_2_node_77 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_36_2_load_70 | 0 | 0.25739 | 0.12466 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_36_2_load_110 | 4 | 0.16827 | 0.081496 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_36_2_load_235 | 6 | 0.16054 | 0.077751 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_36_2_load_111 | 9 | 0.38383 | 0.1859 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_36_2_load_88 | 12 | 0.34767 | 0.16838 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_36_2_load_220 | 13 | 0.090685 | 0.043921 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_36_2_load_77 | 14 | 0.32918 | 0.15943 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_36_2_load_224 | 16 | 0.18548 | 0.089832 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_36_2_load_81 | 17 | 0.20586 | 0.099703 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_36_2_load_223 | 22 | 0.29361 | 0.1422 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_36_2_load_179 | 25 | 0.15524 | 0.075187 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_36_2_load_191 | 26 | 0.1168 | 0.05657 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_36_2_load_91 | 27 | 0.26296 | 0.12736 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_36_2_load_230 | 28 | 0.1367 | 0.066207 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_36_2_load_214 | 31 | 0.17775 | 0.086086 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_36_2_load_92 | 32 | 0.26292 | 0.12734 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_36_2_load_105 | 37 | 0.30335 | 0.14692 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_36_2_load_229 | 38 | 0.1922 | 0.093087 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_36_2_load_96 | 39 | 0.29921 | 0.14492 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_36_2_load_217 | 44 | 0.1951 | 0.094491 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_36_2_load_104 | 47 | 0.27138 | 0.13144 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_36_2_load_227 | 48 | 0.22265 | 0.10784 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_36_2_load_106 | 51 | 0.2927 | 0.14176 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_36_2_load_226 | 52 | 0.25946 | 0.12566 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_36_2_load_107 | 53 | 0.32873 | 0.15921 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_36_2_load_208 | 54 | 0.0854 | 0.041361 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_36_2_load_164 | 55 | 0.14904 | 0.072184 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_36_2_load_173 | 58 | 0.14854 | 0.071941 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_36_2_load_212 | 62 | 0.11796 | 0.05713 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_36_2_load_175 | 63 | 0.13641 | 0.066067 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_36_2_load_170 | 65 | 0.058405 | 0.028287 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_36_2_load_210 | 68 | 0.084881 | 0.04111 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_36_2_load_221 | 70 | 0.05316 | 0.025747 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_36_2_load_183 | 74 | 0.17023 | 0.082445 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_36_2_load_188 | 76 | 0.11017 | 0.053359 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_36_2_load_184 | 77 | 0.13951 | 0.067568 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_36_2_load_186 | 79 | 0.2615 | 0.12665 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_36_2_load_190 | 81 | 0.13481 | 0.065292 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_36_2_load_231 | 83 | 0.077143 | 0.037362 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_36_2_load_234 | 84 | 0.064368 | 0.031175 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_36_2_line_0 |  | 0 | 1 | 0.035743 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_36_2_line_1 |  | 1 | 2 | 1.1194 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_36_2_line_2 |  | 1 | 3 | 0.43066 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_36_2_line_3 |  | 2 | 4 | 0.033002 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_36_2_line_4 |  | 3 | 5 | 0.36934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_36_2_line_5 |  | 3 | 6 | 0.03414 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_36_2_line_6 |  | 5 | 7 | 0.41684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_36_2_line_7 |  | 5 | 8 | 0.63515 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_36_2_line_8 |  | 5 | 9 | 0.013516 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_36_2_line_9 |  | 7 | 10 | 0.34795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_36_2_line_10 |  | 7 | 11 | 1.1202 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
11 | MV_36_2_line_11 |  | 7 | 12 | 0.012335 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
12 | MV_36_2_line_12 |  | 8 | 53 | 0.25767 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_36_2_line_13 |  | 10 | 13 | 0.042023 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_36_2_line_14 |  | 11 | 16 | 0.044691 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_36_2_line_15 |  | 11 | 15 | 0.15299 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
16 | MV_36_2_line_16 |  | 12 | 29 | 0.02883 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
17 | MV_36_2_line_17 |  | 14 | 15 | 0.039106 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
18 | MV_36_2_line_18 |  | 16 | 70 | 1.0707 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_36_2_line_19 |  | 17 | 18 | 0.03429 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_36_2_line_20 |  | 18 | 19 | 0.6297 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_36_2_line_21 |  | 18 | 20 | 0.29921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_36_2_line_22 |  | 18 | 21 | 0.30219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_36_2_line_23 |  | 19 | 22 | 0.012939 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_36_2_line_24 |  | 19 | 23 | 0.13177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_36_2_line_25 |  | 19 | 24 | 0.40654 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_36_2_line_26 |  | 20 | 26 | 0.056336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_36_2_line_27 |  | 21 | 27 | 0.1061 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_36_2_line_28 |  | 23 | 28 | 0.040794 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_36_2_line_29 |  | 24 | 25 | 0.043737 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_36_2_line_30 |  | 25 | 71 | 0.0044883 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_36_2_line_31 |  | 26 | 41 | 0.019558 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_36_2_line_32 |  | 28 | 83 | 0.044101 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_36_2_line_33 |  | 29 | 30 | 0.29672 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
34 | MV_36_2_line_34 |  | 30 | 31 | 0.04448 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
35 | MV_36_2_line_35 |  | 31 | 82 | 0.0347 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
36 | MV_36_2_line_36 |  | 32 | 33 | 0.065039 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_36_2_line_37 |  | 33 | 34 | 0.14615 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_36_2_line_38 |  | 34 | 38 | 0.012152 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_36_2_line_39 |  | 35 | 36 | 0.29928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_36_2_line_40 |  | 35 | 37 | 0.029659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_36_2_line_41 |  | 36 | 38 | 0.05331 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_36_2_line_42 |  | 37 | 45 | 0.26604 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_36_2_line_43 |  | 39 | 40 | 0.027215 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_36_2_line_44 |  | 40 | 41 | 0.19407 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_36_2_line_45 |  | 40 | 42 | 0.20634 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_36_2_line_46 |  | 41 | 43 | 0.74183 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_36_2_line_47 |  | 42 | 44 | 0.10236 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_36_2_line_48 |  | 43 | 52 | 0.042834 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_36_2_line_49 |  | 43 | 50 | 0.48412 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_36_2_line_50 |  | 44 | 49 | 0.051825 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_36_2_line_51 |  | 45 | 46 | 0.40443 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_36_2_line_52 |  | 45 | 47 | 0.047021 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_36_2_line_53 |  | 46 | 48 | 0.035557 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_36_2_line_54 |  | 46 | 49 | 0.10374 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_36_2_line_55 |  | 49 | 82 | 0.25605 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
56 | MV_36_2_line_56 |  | 50 | 51 | 0.054864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_36_2_line_57 |  | 53 | 54 | 1.6709 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_36_2_line_58 |  | 55 | 56 | 0.058778 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_36_2_line_59 |  | 56 | 57 | 0.33644 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_36_2_line_60 |  | 56 | 58 | 0.26737 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_36_2_line_61 |  | 57 | 61 | 0.3524 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_36_2_line_62 |  | 57 | 62 | 0.051713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_36_2_line_63 |  | 58 | 59 | 0.031195 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_36_2_line_64 |  | 59 | 60 | 0.69684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_36_2_line_65 |  | 60 | 70 | 0.27206 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_36_2_line_66 |  | 61 | 63 | 0.089973 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_36_2_line_67 |  | 61 | 64 | 1.0283 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
68 | MV_36_2_line_68 |  | 62 | 69 | 0.021653 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_36_2_line_69 |  | 64 | 84 | 0.028168 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_36_2_line_70 |  | 65 | 66 | 0.55255 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_36_2_line_71 |  | 66 | 67 | 0.803 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_36_2_line_72 |  | 67 | 68 | 0.025905 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_36_2_line_73 |  | 67 | 69 | 0.18198 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_36_2_line_74 |  | 71 | 72 | 0.092544 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_36_2_line_75 |  | 72 | 73 | 0.094187 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_36_2_line_76 |  | 72 | 74 | 0.044854 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_36_2_line_77 |  | 73 | 75 | 0.037738 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_36_2_line_78 |  | 73 | 76 | 0.058182 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_36_2_line_79 |  | 75 | 81 | 0.054212 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_36_2_line_80 |  | 76 | 80 | 0.050566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_36_2_line_81 |  | 77 | 78 | 0.0077793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_36_2_line_82 |  | 77 | 79 | 0.054277 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_36_2_line_83 |  | 78 | 80 | 0.077456 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_36_2_trafo_77 | 25 MVA 110/20 kV | 85 | 14 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2579112.9566 | 1180240.795
1 | 2579101.1677 | 1180207.0522
2 | 2579042.4266 | 1179946.6792
3 | 2578828.265 | 1180368.7416
4 | 2579012.062 | 1179959.4755
5 | 2578965.8132 | 1180574.684
6 | 2578860.8455 | 1180378.9425
7 | 2578683.9507 | 1180561.3879
8 | 2579296.2876 | 1180409.9105
9 | 2578973.5907 | 1180566.7192
10 | 2578842.6032 | 1180645.0891
11 | 2578413.9065 | 1180183.9964
12 | 2578677.8485 | 1180572.1152
13 | 2578834.9033 | 1180603.7839
14 | 2578286.4051 | 1180255.1621
15 | 2578279.3785 | 1180217.457
16 | 2578415.2115 | 1180139.3241
17 | 2577569.699 | 1180930.5828
18 | 2577536.2388 | 1180938.0792
19 | 2577871.3308 | 1180718.3809
20 | 2577752.1771 | 1180989.7197
21 | 2577319.1897 | 1180769.9458
22 | 2577866.1397 | 1180706.6274
23 | 2577917.3818 | 1180691.0296
24 | 2577985.6893 | 1180645.2537
25 | 2577971.9045 | 1180603.7457
26 | 2577807.5609 | 1181000.0349
27 | 2577219.453 | 1180733.3843
28 | 2577904.5223 | 1180652.3127
29 | 2578661.3062 | 1180595.7421
30 | 2578530.3088 | 1180676.4312
31 | 2578496.8328 | 1180705.6668
32 | 2579030.3853 | 1180845.5636
33 | 2578969.3599 | 1180868.0565
34 | 2578852.9784 | 1180956.4578
35 | 2578780.1041 | 1181269.356
36 | 2578810.4927 | 1181005.5894
37 | 2578750.8172 | 1181264.9135
38 | 2578844.7139 | 1180964.7135
39 | 2577987.9412 | 1180949.3472
40 | 2577998.1685 | 1180974.567
41 | 2577826.7883 | 1181003.616
42 | 2578136.6829 | 1180898.1854
43 | 2578005.7623 | 1181263.3108
44 | 2578236.9746 | 1180877.7306
45 | 2578571.6058 | 1181068.2967
46 | 2578333.1113 | 1180960.0569
47 | 2578561.6503 | 1181022.342
48 | 2578364.4614 | 1180943.279
49 | 2578280.9908 | 1180870.3554
50 | 2578304.2326 | 1181349.8414
51 | 2578358.3755 | 1181345.6872
52 | 2577977.9822 | 1181230.7075
53 | 2579505.8162 | 1180259.9323
54 | 2580746.4417 | 1181379.213
55 | 2577755.4899 | 1178205.4807
56 | 2577727.7113 | 1178257.3109
57 | 2577574.0507 | 1178091.5337
58 | 2577945.783 | 1178412.0037
59 | 2577940.0515 | 1178442.6629
60 | 2578097.5679 | 1178925.3875
61 | 2577768.4342 | 1177861.0774
62 | 2577523.4424 | 1178080.2292
63 | 2577851.9213 | 1177894.6179
64 | 2577453.485 | 1176882.1765
65 | 2576271.6116 | 1177559.3566
66 | 2576768.1337 | 1177801.7971
67 | 2577376.7676 | 1177966.0907
68 | 2577402.5509 | 1177962.9026
69 | 2577504.5906 | 1178069.4835
70 | 2577969.8803 | 1179165.6254
71 | 2577970.4899 | 1180599.4861
72 | 2577951.8068 | 1180543.1481
73 | 2578040.7232 | 1180514.1833
74 | 2577909.135 | 1180556.9693
75 | 2578076.6602 | 1180502.3451
76 | 2578059.3301 | 1180569.3098
77 | 2578152.025 | 1180601.1154
78 | 2578149.5288 | 1180593.7475
79 | 2578169.4407 | 1180652.5228
80 | 2578075.5012 | 1180617.2199
81 | 2578093.0774 | 1180554.0112
82 | 2578469.2924 | 1180726.777
83 | 2577865.1833 | 1180632.3799
84 | 2577425.3135 | 1176883.5836
85 | 2578286.4051 | 1180255.1621

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99506 | -0.063292 | 0.25739 | 0.12466
1 | 0.99508 | -0.063179 | 0 | 0
2 | 0.99484 | -0.061912 | 0 | 0
3 | 0.99531 | -0.064496 | 0 | 0
4 | 0.99483 | -0.061846 | 0.16827 | 0.081496
5 | 0.99558 | -0.066116 | 0 | 0
6 | 0.9953 | -0.064563 | 0.16054 | 0.077751
7 | 0.99631 | -0.071233 | 0 | 0
8 | 0.99524 | -0.063338 | 0 | 0
9 | 0.99557 | -0.066053 | 0.38383 | 0.1859
10 | 0.99627 | -0.070967 | 0 | 0
11 | 0.99939 | -0.011898 | 0 | 0
12 | 0.99628 | -0.071726 | 0.34767 | 0.16838
13 | 0.99626 | -0.070922 | 0.090685 | 0.043921
14 | 1 | 0 | -7.4196 | -3.2632
15 | 0.99988 | -0.002423 | 0 | 0
16 | 0.99931 | -0.012687 | 0.18548 | 0.089832
17 | 0.99163 | -0.081867 | 0.20586 | 0.099703
18 | 0.99164 | -0.08178 | 0 | 0
19 | 0.99045 | -0.071939 | 0 | 0
20 | 0.99239 | -0.087755 | 0 | 0
21 | 0.99154 | -0.080931 | 0 | 0
22 | 0.99045 | -0.071893 | 0.29361 | 0.1422
23 | 0.99042 | -0.071626 | 0 | 0
24 | 0.98995 | -0.067629 | 0 | 0
25 | 0.98989 | -0.06715 | 0.15524 | 0.075187
26 | 0.99253 | -0.088863 | 0.1168 | 0.05657
27 | 0.99151 | -0.0806 | 0.26296 | 0.12736
28 | 0.99041 | -0.071523 | 0.1367 | 0.066207
29 | 0.99622 | -0.072803 | 0 | 0
30 | 0.99564 | -0.083861 | 0 | 0
31 | 0.99555 | -0.085514 | 0.17775 | 0.086086
32 | 0.99324 | -0.096188 | 0.26292 | 0.12734
33 | 0.99328 | -0.095978 | 0 | 0
34 | 0.99335 | -0.095505 | 0 | 0
35 | 0.99358 | -0.096816 | 0 | 0
36 | 0.9934 | -0.095244 | 0 | 0
37 | 0.99359 | -0.096964 | 0.30335 | 0.14692
38 | 0.99335 | -0.095544 | 0.1922 | 0.093087
39 | 0.99321 | -0.094345 | 0.29921 | 0.14492
40 | 0.99322 | -0.094245 | 0 | 0
41 | 0.99258 | -0.089275 | 0 | 0
42 | 0.99399 | -0.10021 | 0 | 0
43 | 0.99206 | -0.085327 | 0 | 0
44 | 0.99456 | -0.095631 | 0.1951 | 0.094491
45 | 0.99398 | -0.0943 | 0 | 0
46 | 0.99452 | -0.098991 | 0 | 0
47 | 0.99396 | -0.094456 | 0.27138 | 0.13144
48 | 0.9945 | -0.099088 | 0.22265 | 0.10784
49 | 0.99477 | -0.097238 | 0 | 0
50 | 0.99188 | -0.083823 | 0 | 0
51 | 0.99186 | -0.08363 | 0.2927 | 0.14176
52 | 0.99204 | -0.085463 | 0.25946 | 0.12566
53 | 0.99504 | -0.064687 | 0.32873 | 0.15921
54 | 0.99476 | -0.066571 | 0.0854 | 0.041361
55 | 0.99629 | -0.032008 | 0.14904 | 0.072184
56 | 0.9963 | -0.032111 | 0 | 0
57 | 0.9961 | -0.031116 | 0 | 0
58 | 0.9966 | -0.029063 | 0.14854 | 0.071941
59 | 0.99663 | -0.029255 | 0 | 0
60 | 0.9973 | -0.033156 | 0 | 0
61 | 0.99601 | -0.030402 | 0 | 0
62 | 0.99609 | -0.031038 | 0.11796 | 0.05713
63 | 0.99599 | -0.030552 | 0.13641 | 0.066067
64 | 0.99589 | -0.031321 | 0 | 0
65 | 0.99593 | -0.031351 | 0.058405 | 0.028287
66 | 0.99599 | -0.030942 | 0 | 0
67 | 0.99605 | -0.030983 | 0 | 0
68 | 0.99605 | -0.030957 | 0.084881 | 0.04111
69 | 0.99608 | -0.031035 | 0 | 0
70 | 0.99768 | -0.029157 | 0.05316 | 0.025747
71 | 0.98989 | -0.067109 | 0 | 0
72 | 0.98979 | -0.066261 | 0 | 0
73 | 0.98971 | -0.065573 | 0 | 0
74 | 0.98978 | -0.066169 | 0.17023 | 0.082445
75 | 0.98971 | -0.065515 | 0 | 0
76 | 0.98968 | -0.065229 | 0.11017 | 0.053359
77 | 0.98961 | -0.064589 | 0.13951 | 0.067568
78 | 0.98961 | -0.064627 | 0 | 0
79 | 0.98959 | -0.064418 | 0.2615 | 0.12665
80 | 0.98965 | -0.064994 | 0 | 0
81 | 0.9897 | -0.065428 | 0.13481 | 0.065292
82 | 0.99537 | -0.090149 | 0 | 0
83 | 0.9904 | -0.071483 | 0.077143 | 0.037362
84 | 0.99588 | -0.0313 | 0.064368 | 0.031175
85 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.25739 | -0.12466 | 0.2574 | 0.12462 | 4.3836e-06 | -3.9504e-05 | 0.0082969 | 0.0082964 | 0.0082969 | 0.99506 | -0.063292 | 0.99508 | -0.063179 | 3.9509
1 | 0.16831 | 0.05427 | -0.16827 | -0.080717 | 4.1361e-05 | -0.026447 | 0.0051303 | 0.0054154 | 0.0054154 | 0.99508 | -0.063179 | 0.99484 | -0.061912 | 2.4616
2 | -0.42571 | -0.17889 | 0.42581 | 0.16874 | 0.00010231 | -0.010154 | 0.013396 | 0.013284 | 0.013396 | 0.99508 | -0.063179 | 0.99531 | -0.064496 | 6.0891
3 | 0.16827 | 0.080717 | -0.16827 | -0.081496 | 1.2944e-06 | -0.00077946 | 0.0054154 | 0.0054253 | 0.0054253 | 0.99484 | -0.061912 | 0.99483 | -0.061846 | 2.466
4 | -0.58635 | -0.24645 | 0.58652 | 0.23776 | 0.00016691 | -0.0086887 | 0.018447 | 0.018351 | 0.018447 | 0.99531 | -0.064496 | 0.99558 | -0.066116 | 8.3852
5 | 0.16054 | 0.077712 | -0.16054 | -0.077751 | 1.6279e-06 | -3.9355e-05 | 0.005173 | 0.0051735 | 0.0051735 | 0.99531 | -0.064496 | 0.9953 | -0.064563 | 2.4636
6 | -1.3847 | -0.60672 | 1.3858 | 0.59716 | 0.0010666 | -0.0095555 | 0.043836 | 0.043722 | 0.043836 | 0.99558 | -0.066116 | 0.99631 | -0.071233 | 19.9256
7 | 0.41438 | 0.18338 | -0.41424 | -0.19836 | 0.00014839 | -0.014982 | 0.013139 | 0.013322 | 0.013322 | 0.99558 | -0.066116 | 0.99524 | -0.063338 | 6.0553
8 | 0.38383 | 0.18558 | -0.38383 | -0.1859 | 2.7584e-06 | -0.00031904 | 0.012362 | 0.012366 | 0.012366 | 0.99558 | -0.066116 | 0.99557 | -0.066053 | 5.6209
9 | 0.090689 | 0.03468 | -0.090685 | -0.042925 | 3.7945e-06 | -0.008245 | 0.0028133 | 0.0029072 | 0.0029072 | 0.99631 | -0.071233 | 0.99627 | -0.070967 | 1.3214
10 | -6.3843 | -2.8642 | 6.4011 | 2.837 | 0.016811 | -0.027176 | 0.20274 | 0.20224 | 0.20274 | 0.99631 | -0.071233 | 0.99939 | -0.011898 | 48.1577
11 | 4.9078 | 2.2323 | -4.9077 | -2.2327 | 0.00011018 | -0.00036658 | 0.15622 | 0.15623 | 0.15623 | 0.99631 | -0.071233 | 0.99628 | -0.071726 | 37.1082
12 | 0.41424 | 0.19836 | -0.41415 | -0.19861 | 8.1497e-05 | -0.00025358 | 0.013322 | 0.013325 | 0.013325 | 0.99524 | -0.063338 | 0.99504 | -0.064687 | 6.3454
13 | 0.090685 | 0.042925 | -0.090685 | -0.043921 | 4.7617e-07 | -0.00099572 | 0.0029072 | 0.0029196 | 0.0029196 | 0.99627 | -0.070967 | 0.99626 | -0.070922 | 1.3271
14 | 1.0007 | 0.4195 | -1.0006 | -0.4195 | 7.8221e-05 | -4.2881e-06 | 0.031342 | 0.031343 | 0.031343 | 0.99939 | -0.011898 | 0.99931 | -0.012687 | 14.9251
15 | -7.4018 | -3.2565 | 7.4048 | 3.2534 | 0.0030541 | -0.0030364 | 0.23358 | 0.23351 | 0.23358 | 0.99939 | -0.011898 | 0.99988 | -0.002423 | 55.4818
16 | 4.56 | 2.0643 | -4.5598 | -2.0652 | 0.00022198 | -0.00088933 | 0.14504 | 0.14505 | 0.14505 | 0.99628 | -0.071726 | 0.99622 | -0.072803 | 34.4535
17 | 7.4056 | 3.2527 | -7.4048 | -3.2534 | 0.00078038 | -0.00077732 | 0.23349 | 0.23351 | 0.23351 | 1 | 0 | 0.99988 | -0.002423 | 55.4657
18 | 0.81514 | 0.32967 | -0.8139 | -0.33017 | 0.0012314 | -0.00050303 | 0.0254 | 0.025414 | 0.025414 | 0.99931 | -0.012687 | 0.99768 | -0.029157 | 12.1019
19 | -0.20586 | -0.099703 | 0.20586 | 0.099665 | 2.7086e-06 | -3.8557e-05 | 0.0066588 | 0.0066583 | 0.0066588 | 0.99163 | -0.081867 | 0.99164 | -0.08178 | 3.1708
20 | 1.4816 | 0.67291 | -1.4797 | -0.68711 | 0.0018935 | -0.014205 | 0.047371 | 0.04755 | 0.04755 | 0.99164 | -0.08178 | 0.99045 | -0.071939 | 21.6138
21 | -1.9505 | -0.89036 | 1.952 | 0.88379 | 0.001554 | -0.0065693 | 0.062416 | 0.062331 | 0.062416 | 0.99164 | -0.08178 | 0.99239 | -0.087755 | 28.371
22 | 0.263 | 0.11779 | -0.26297 | -0.12487 | 2.8681e-05 | -0.0070859 | 0.008389 | 0.0084755 | 0.0084755 | 0.99164 | -0.08178 | 0.99154 | -0.080931 | 3.8525
23 | 0.29361 | 0.1419 | -0.29361 | -0.1422 | 1.561e-06 | -0.0003026 | 0.0095045 | 0.0095083 | 0.0095083 | 0.99045 | -0.071939 | 0.99045 | -0.071893 | 4.322
24 | 0.21386 | 0.098498 | -0.21385 | -0.10158 | 8.3301e-06 | -0.0030839 | 0.0068623 | 0.0069004 | 0.0069004 | 0.99045 | -0.071939 | 0.99042 | -0.071626 | 3.1366
25 | 0.97225 | 0.44672 | -0.97172 | -0.45608 | 0.00052978 | -0.0093602 | 0.031185 | 0.031302 | 0.031302 | 0.99045 | -0.071939 | 0.98995 | -0.067629 | 14.2281
26 | -1.952 | -0.88379 | 1.9523 | 0.88255 | 0.00029213 | -0.0012382 | 0.062331 | 0.062316 | 0.062331 | 0.99239 | -0.087755 | 0.99253 | -0.088863 | 28.3325
27 | 0.26297 | 0.12487 | -0.26296 | -0.12736 | 1.0213e-05 | -0.0024875 | 0.0084755 | 0.0085068 | 0.0085068 | 0.99154 | -0.080931 | 0.99151 | -0.0806 | 3.8667
28 | 0.21385 | 0.10158 | -0.21384 | -0.10254 | 2.5977e-06 | -0.00095464 | 0.0069004 | 0.0069124 | 0.0069124 | 0.99042 | -0.071626 | 0.99041 | -0.071523 | 3.142
29 | 0.97172 | 0.45608 | -0.97167 | -0.45708 | 5.7233e-05 | -0.0010064 | 0.031302 | 0.031315 | 0.031315 | 0.98995 | -0.067629 | 0.98989 | -0.06715 | 14.2339
30 | 0.81643 | 0.3819 | -0.81642 | -0.382 | 4.14e-06 | -0.00010378 | 0.026285 | 0.026286 | 0.026286 | 0.98989 | -0.06715 | 0.98989 | -0.067109 | 11.9482
31 | -2.0691 | -0.93912 | 2.0692 | 0.9387 | 0.00011403 | -0.00042621 | 0.066089 | 0.066083 | 0.066089 | 0.99253 | -0.088863 | 0.99258 | -0.089275 | 30.0404
32 | 0.077143 | 0.036329 | -0.077143 | -0.037362 | 3.6556e-07 | -0.0010327 | 0.0024854 | 0.0024983 | 0.0024983 | 0.99041 | -0.071523 | 0.9904 | -0.071483 | 1.1356
33 | 4.5598 | 2.0652 | -4.5575 | -2.0743 | 0.0022869 | -0.0091435 | 0.14505 | 0.14518 | 0.14518 | 0.99622 | -0.072803 | 0.99564 | -0.083861 | 34.4855
34 | 4.5575 | 2.0743 | -4.5572 | -2.0757 | 0.0003432 | -0.0013692 | 0.14518 | 0.1452 | 0.1452 | 0.99564 | -0.083861 | 0.99555 | -0.085514 | 34.4903
35 | 4.3794 | 1.9896 | -4.3788 | -1.989 | 0.00061972 | 0.00066562 | 0.13948 | 0.13948 | 0.13948 | 0.99555 | -0.085514 | 0.99537 | -0.090149 | 39.8513
36 | -0.26292 | -0.12734 | 0.26292 | 0.12726 | 8.3524e-06 | -7.1369e-05 | 0.0084904 | 0.0084894 | 0.0084904 | 0.99324 | -0.096188 | 0.99328 | -0.095978 | 4.043
37 | -0.26292 | -0.12726 | 0.26294 | 0.1271 | 1.8762e-05 | -0.0001604 | 0.0084894 | 0.0084872 | 0.0084894 | 0.99328 | -0.095978 | 0.99335 | -0.095505 | 4.0426
38 | -0.26294 | -0.1271 | 0.26294 | 0.12682 | 1.1681e-06 | -0.00028595 | 0.0084872 | 0.0084836 | 0.0084872 | 0.99335 | -0.095505 | 0.99335 | -0.095544 | 3.8578
39 | 0.45525 | 0.21283 | -0.45516 | -0.21985 | 8.5688e-05 | -0.0070276 | 0.014601 | 0.014689 | 0.014689 | 0.99358 | -0.096816 | 0.9934 | -0.095244 | 6.6768
40 | -0.45525 | -0.21283 | 0.45526 | 0.21213 | 8.4361e-06 | -0.00069658 | 0.014601 | 0.014592 | 0.014601 | 0.99358 | -0.096816 | 0.99359 | -0.096964 | 6.6368
41 | 0.45516 | 0.21985 | -0.45514 | -0.2199 | 2.0495e-05 | -4.9964e-05 | 0.014689 | 0.01469 | 0.01469 | 0.9934 | -0.095244 | 0.99335 | -0.095544 | 6.9951
42 | -0.75861 | -0.35905 | 0.75889 | 0.35891 | 0.00028179 | -0.00013715 | 0.024385 | 0.024381 | 0.024385 | 0.99359 | -0.096964 | 0.99398 | -0.0943 | 11.6117
43 | -0.29921 | -0.14492 | 0.29922 | 0.14489 | 4.5272e-06 | -2.9214e-05 | 0.0096629 | 0.0096625 | 0.0096629 | 0.99321 | -0.094345 | 0.99322 | -0.094245 | 4.6014
44 | 2.6236 | 1.172 | -2.6218 | -1.1761 | 0.0018083 | -0.0040318 | 0.083516 | 0.08357 | 0.08357 | 0.99322 | -0.094245 | 0.99258 | -0.089275 | 37.9865
45 | -2.9228 | -1.3169 | 2.9252 | 1.3128 | 0.0023899 | -0.0041549 | 0.093174 | 0.093117 | 0.093174 | 0.99322 | -0.094245 | 0.99399 | -0.10021 | 42.352
46 | 0.55253 | 0.23738 | -0.55222 | -0.25473 | 0.00030647 | -0.01735 | 0.01749 | 0.017696 | 0.017696 | 0.99258 | -0.089275 | 0.99206 | -0.085327 | 8.0437
47 | -2.9252 | -1.3128 | 2.9268 | 1.3136 | 0.0015812 | 0.00086964 | 0.093117 | 0.093115 | 0.093117 | 0.99399 | -0.10021 | 0.99456 | -0.095631 | 44.3412
48 | 0.25946 | 0.12561 | -0.25946 | -0.12566 | 5.3703e-06 | -4.6961e-05 | 0.0083883 | 0.0083889 | 0.0083889 | 0.99206 | -0.085327 | 0.99204 | -0.085463 | 3.9947
49 | 0.29276 | 0.12912 | -0.29271 | -0.14047 | 5.6848e-05 | -0.011357 | 0.0093107 | 0.0094491 | 0.0094491 | 0.99206 | -0.085327 | 0.99188 | -0.083823 | 4.2951
50 | -3.1219 | -1.4081 | 3.1226 | 1.4071 | 0.00068355 | -0.0010214 | 0.099405 | 0.09939 | 0.099405 | 0.99456 | -0.095631 | 0.99477 | -0.097238 | 45.1839
51 | -1.0303 | -0.4903 | 1.0309 | 0.48093 | 0.00059075 | -0.0093703 | 0.033137 | 0.033019 | 0.033137 | 0.99398 | -0.0943 | 0.99452 | -0.098991 | 15.0623
52 | 0.27139 | 0.13138 | -0.27138 | -0.13144 | 6.4246e-06 | -5.1435e-05 | 0.0087568 | 0.0087575 | 0.0087575 | 0.99398 | -0.0943 | 0.99396 | -0.094456 | 4.1702
53 | 0.22266 | 0.1078 | -0.22265 | -0.10784 | 3.2667e-06 | -3.9937e-05 | 0.0071806 | 0.0071811 | 0.0071811 | 0.99452 | -0.098991 | 0.9945 | -0.099088 | 3.4196
54 | -1.2535 | -0.58873 | 1.2538 | 0.58879 | 0.00029868 | 6.456e-05 | 0.040199 | 0.040197 | 0.040199 | 0.99452 | -0.098991 | 0.99477 | -0.097238 | 19.1424
55 | -4.3764 | -1.9959 | 4.3788 | 1.989 | 0.0024078 | -0.0069479 | 0.13958 | 0.13948 | 0.13958 | 0.99477 | -0.097238 | 0.99537 | -0.090149 | 38.5591
56 | 0.29271 | 0.14047 | -0.2927 | -0.14176 | 6.5509e-06 | -0.0012868 | 0.0094491 | 0.0094654 | 0.0094654 | 0.99188 | -0.083823 | 0.99186 | -0.08363 | 4.3025
57 | 0.085423 | 0.039401 | -0.0854 | -0.041361 | 2.2372e-05 | -0.0019604 | 0.0027292 | 0.0027536 | 0.0027536 | 0.99504 | -0.064687 | 0.99476 | -0.066571 | 1.3113
58 | -0.14904 | -0.072184 | 0.14904 | 0.070791 | 1.8001e-06 | -0.0013925 | 0.0047983 | 0.0047809 | 0.0047983 | 0.99629 | -0.032008 | 0.9963 | -0.032111 | 2.1811
59 | 0.46216 | 0.17917 | -0.46207 | -0.18711 | 9.3192e-05 | -0.0079444 | 0.014362 | 0.014447 | 0.014447 | 0.9963 | -0.032111 | 0.9961 | -0.031116 | 6.5669
60 | -0.61121 | -0.24996 | 0.61138 | 0.24975 | 0.00017436 | -0.00020771 | 0.019133 | 0.01913 | 0.019133 | 0.9963 | -0.032111 | 0.9966 | -0.029063 | 9.1111
61 | 0.20081 | 0.086916 | -0.20079 | -0.095258 | 1.9211e-05 | -0.008342 | 0.0063413 | 0.0064412 | 0.0064412 | 0.9961 | -0.031116 | 0.99601 | -0.030402 | 2.9278
62 | 0.26126 | 0.1002 | -0.26126 | -0.10142 | 4.5469e-06 | -0.0012237 | 0.0081091 | 0.0081219 | 0.0081219 | 0.9961 | -0.031116 | 0.99609 | -0.031038 | 3.6918
63 | -0.75992 | -0.32169 | 0.75994 | 0.32096 | 2.3786e-05 | -0.00073273 | 0.023903 | 0.023894 | 0.023903 | 0.9966 | -0.029063 | 0.99663 | -0.029255 | 10.8649
64 | -0.75994 | -0.32096 | 0.76047 | 0.30458 | 0.00052705 | -0.016381 | 0.023894 | 0.023712 | 0.023894 | 0.99663 | -0.029255 | 0.9973 | -0.033156 | 10.8611
65 | -0.76047 | -0.30458 | 0.76074 | 0.30443 | 0.00027251 | -0.00015247 | 0.023712 | 0.023709 | 0.023712 | 0.9973 | -0.033156 | 0.99768 | -0.029157 | 11.2916
66 | 0.13642 | 0.065963 | -0.13641 | -0.066067 | 3.0927e-06 | -0.00010462 | 0.0043917 | 0.004393 | 0.004393 | 0.99601 | -0.030402 | 0.99599 | -0.030552 | 2.0919
67 | 0.064376 | 0.029295 | -0.064368 | -0.030508 | 7.7544e-06 | -0.0012128 | 0.0020499 | 0.0020648 | 0.0020648 | 0.99601 | -0.030402 | 0.99589 | -0.031321 | 0.98323
68 | 0.1433 | 0.044289 | -0.1433 | -0.044802 | 5.4672e-07 | -0.00051279 | 0.0043467 | 0.0043511 | 0.0043511 | 0.99609 | -0.031038 | 0.99608 | -0.031035 | 1.9778
69 | 0.064368 | 0.030508 | -0.064368 | -0.031175 | 1.6097e-07 | -0.00066697 | 0.0020648 | 0.0020731 | 0.0020731 | 0.99589 | -0.031321 | 0.99588 | -0.0313 | 0.94233
70 | -0.058405 | -0.028287 | 0.058408 | 0.027635 | 3.468e-06 | -0.00065215 | 0.001881 | 0.0018728 | 0.001881 | 0.99593 | -0.031351 | 0.99599 | -0.030942 | 0.89571
71 | -0.058408 | -0.027635 | 0.058412 | 0.0086154 | 3.368e-06 | -0.019019 | 0.0018728 | 0.0017112 | 0.0018728 | 0.99599 | -0.030942 | 0.99605 | -0.030983 | 0.85127
72 | 0.084881 | 0.040496 | -0.084881 | -0.04111 | 2.5765e-07 | -0.00061356 | 0.0027256 | 0.0027334 | 0.0027334 | 0.99605 | -0.030983 | 0.99605 | -0.030957 | 1.2424
73 | -0.14329 | -0.049111 | 0.1433 | 0.044802 | 4.6398e-06 | -0.0043094 | 0.00439 | 0.0043511 | 0.00439 | 0.99605 | -0.030983 | 0.99608 | -0.031035 | 1.9955
74 | 0.81642 | 0.382 | -0.81634 | -0.38414 | 8.5452e-05 | -0.0021396 | 0.026286 | 0.026313 | 0.026313 | 0.98989 | -0.067109 | 0.98979 | -0.066261 | 11.9604
75 | 0.64611 | 0.30274 | -0.64605 | -0.30493 | 5.4523e-05 | -0.0021868 | 0.02081 | 0.020837 | 0.020837 | 0.98979 | -0.066261 | 0.98971 | -0.065573 | 9.4715
76 | 0.17023 | 0.081397 | -0.17023 | -0.082445 | 1.8178e-06 | -0.0010486 | 0.0055032 | 0.0055164 | 0.0055164 | 0.98979 | -0.066261 | 0.98978 | -0.066169 | 2.5075
77 | 0.13481 | 0.063143 | -0.13481 | -0.064025 | 9.5227e-07 | -0.00088231 | 0.0043421 | 0.0043531 | 0.0043531 | 0.98971 | -0.065573 | 0.98971 | -0.065515 | 1.9787
78 | 0.51124 | 0.24179 | -0.51122 | -0.24314 | 2.1156e-05 | -0.0013544 | 0.016495 | 0.016512 | 0.016512 | 0.98971 | -0.065573 | 0.98968 | -0.065229 | 7.5055
79 | 0.13481 | 0.064025 | -0.13481 | -0.065292 | 1.3765e-06 | -0.0012674 | 0.0043531 | 0.0043691 | 0.0043691 | 0.98971 | -0.065515 | 0.9897 | -0.065428 | 1.986
80 | 0.40104 | 0.18978 | -0.40103 | -0.19096 | 1.1319e-05 | -0.0011791 | 0.012942 | 0.012956 | 0.012956 | 0.98968 | -0.065229 | 0.98965 | -0.064994 | 5.8892
81 | -0.40101 | -0.19295 | 0.40101 | 0.19277 | 1.7498e-06 | -0.00018138 | 0.012981 | 0.012979 | 0.012981 | 0.98961 | -0.064589 | 0.98961 | -0.064627 | 5.9007
82 | 0.2615 | 0.12538 | -0.2615 | -0.12665 | 5.1955e-06 | -0.0012676 | 0.0084597 | 0.0084757 | 0.0084757 | 0.98961 | -0.064589 | 0.98959 | -0.064418 | 3.8526
83 | -0.40101 | -0.19277 | 0.40103 | 0.19096 | 1.7389e-05 | -0.001806 | 0.012979 | 0.012956 | 0.012979 | 0.98961 | -0.064627 | 0.98965 | -0.064994 | 5.8996

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 7.7488 | 3.4226

## res_load
| p_mw | q_mvar
0 | 0.25739 | 0.12466
1 | 0.16827 | 0.081496
2 | 0.16054 | 0.077751
3 | 0.38383 | 0.1859
4 | 0.34767 | 0.16838
5 | 0.090685 | 0.043921
6 | 0.32918 | 0.15943
7 | 0.18548 | 0.089832
8 | 0.20586 | 0.099703
9 | 0.29361 | 0.1422
10 | 0.15524 | 0.075187
11 | 0.1168 | 0.05657
12 | 0.26296 | 0.12736
13 | 0.1367 | 0.066207
14 | 0.17775 | 0.086086
15 | 0.26292 | 0.12734
16 | 0.30335 | 0.14692
17 | 0.1922 | 0.093087
18 | 0.29921 | 0.14492
19 | 0.1951 | 0.094491
20 | 0.27138 | 0.13144
21 | 0.22265 | 0.10784
22 | 0.2927 | 0.14176
23 | 0.25946 | 0.12566
24 | 0.32873 | 0.15921
25 | 0.0854 | 0.041361
26 | 0.14904 | 0.072184
27 | 0.14854 | 0.071941
28 | 0.11796 | 0.05713
29 | 0.13641 | 0.066067
30 | 0.058405 | 0.028287
31 | 0.084881 | 0.04111
32 | 0.05316 | 0.025747
33 | 0.17023 | 0.082445
34 | 0.11017 | 0.053359
35 | 0.13951 | 0.067568
36 | 0.2615 | 0.12665
37 | 0.13481 | 0.065292
38 | 0.077143 | 0.037362
39 | 0.064368 | 0.031175

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1