## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_370_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_370_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_370_0_node_54 | 20 | n |  | TRUE
3 | bus_MV_370_0_node_2 | 20 | n |  | TRUE
4 | bus_MV_370_0_node_53 | 20 | n |  | TRUE
5 | bus_MV_370_0_node_173 | 20 | n |  | TRUE
6 | bus_MV_370_0_node_176 | 20 | n |  | TRUE
7 | bus_MV_370_0_node_51 | 20 | n |  | TRUE
8 | bus_MV_370_0_node_30 | 20 | n |  | TRUE
9 | bus_MV_370_0_node_3 | 20 | n |  | TRUE
10 | bus_MV_370_0_node_4 | 20 | n |  | TRUE
11 | bus_MV_370_0_node_5 | 20 | n |  | TRUE
12 | bus_MV_370_0_node_6 | 20 | n |  | TRUE
13 | bus_MV_370_0_node_190 | 20 | n |  | TRUE
14 | bus_MV_370_0_node_8 | 20 | n |  | TRUE
15 | bus_MV_370_0_node_42 | 20 | n |  | TRUE
16 | bus_MV_370_0_node_166 | 20 | n |  | TRUE
17 | bus_MV_370_0_node_7 | 20 | n |  | TRUE
18 | bus_MV_370_0_node_151 | 20 | n |  | TRUE
19 | bus_MV_370_0_node_17 | 20 | n |  | TRUE
20 | bus_MV_370_0_node_14 | 20 | n |  | TRUE
21 | bus_MV_370_0_node_16 | 20 | n |  | TRUE
22 | bus_MV_370_0_node_9 | 20 | n |  | TRUE
23 | bus_MV_370_0_node_15 | 20 | n |  | TRUE
24 | bus_MV_370_0_node_131 | 20 | n |  | TRUE
25 | bus_MV_370_0_node_117 | 20 | n |  | TRUE
26 | bus_MV_370_0_node_10 | 20 | n |  | TRUE
27 | bus_MV_370_0_node_11 | 20 | n |  | TRUE
28 | bus_MV_370_0_node_12 | 20 | n |  | TRUE
29 | bus_MV_370_0_node_13 | 20 | n |  | TRUE
30 | bus_MV_370_0_node_124 | 20 | n |  | TRUE
31 | bus_MV_370_0_node_154 | 20 | n |  | TRUE
32 | bus_MV_370_0_node_21 | 20 | n |  | TRUE
33 | bus_MV_370_0_node_121 | 20 | n |  | TRUE
34 | bus_MV_370_0_node_122 | 20 | n |  | TRUE
35 | bus_MV_370_0_node_19 | 20 | n |  | TRUE
36 | bus_MV_370_0_node_161 | 20 | n |  | TRUE
37 | bus_MV_370_0_node_34 | 20 | n |  | TRUE
38 | bus_MV_370_0_node_40 | 20 | n |  | TRUE
39 | bus_MV_370_0_node_41 | 20 | n |  | TRUE
40 | bus_MV_370_0_node_171 | 20 | n |  | TRUE
41 | bus_MV_370_0_node_39 | 20 | n |  | TRUE
42 | bus_MV_370_0_node_36 | 20 | n |  | TRUE
43 | bus_MV_370_0_node_35 | 20 | n |  | TRUE
44 | bus_MV_370_0_node_37 | 20 | n |  | TRUE
45 | bus_MV_370_0_node_38 | 20 | n |  | TRUE
46 | bus_MV_370_0_node_148 | 20 | n |  | TRUE
47 | bus_MV_370_0_node_150 | 20 | n |  | TRUE
48 | bus_MV_370_0_node_50 | 20 | n |  | TRUE
49 | bus_MV_370_0_node_163 | 20 | n |  | TRUE
50 | bus_MV_370_0_node_130 | 20 | n |  | TRUE
51 | bus_MV_370_0_node_18 | 20 | n |  | TRUE
52 | bus_MV_370_0_node_115 | 20 | n |  | TRUE
53 | bus_MV_370_0_node_158 | 20 | n |  | TRUE
54 | bus_MV_370_0_node_118 | 20 | n |  | TRUE
55 | bus_MV_370_0_node_120 | 20 | n |  | TRUE
56 | bus_MV_370_0_node_20 | 20 | n |  | TRUE
57 | bus_MV_370_0_node_169 | 20 | n |  | TRUE
58 | bus_MV_370_0_node_23 | 20 | n |  | TRUE
59 | bus_MV_370_0_node_25 | 20 | n |  | TRUE
60 | bus_MV_370_0_node_123 | 20 | n |  | TRUE
61 | bus_MV_370_0_node_119 | 20 | n |  | TRUE
62 | bus_MV_370_0_node_116 | 20 | n |  | TRUE
63 | bus_MV_370_0_node_134 | 20 | n |  | TRUE
64 | bus_MV_370_0_node_24 | 20 | n |  | TRUE
65 | bus_MV_370_0_node_33 | 20 | n |  | TRUE
66 | bus_MV_370_0_node_29 | 20 | n |  | TRUE
67 | bus_MV_370_0_node_137 | 20 | n |  | TRUE
68 | bus_MV_370_0_node_22 | 20 | n |  | TRUE
69 | bus_MV_370_0_node_177 | 20 | n |  | TRUE
70 | bus_MV_370_0_node_170 | 20 | n |  | TRUE
71 | bus_MV_370_0_node_31 | 20 | n |  | TRUE
72 | bus_MV_370_0_node_27 | 20 | n |  | TRUE
73 | bus_MV_370_0_node_32 | 20 | n |  | TRUE
74 | bus_MV_370_0_node_26 | 20 | n |  | TRUE
75 | bus_MV_370_0_node_28 | 20 | n |  | TRUE
76 | bus_MV_370_0_node_167 | 20 | n |  | TRUE
77 | bus_MV_370_0_node_52 | 20 | n |  | TRUE
78 | bus_MV_370_0_node_188 | 20 | n |  | TRUE
79 | bus_MV_370_0_node_55 | 20 | n |  | TRUE
80 | bus_MV_370_0_node_56 | 20 | n |  | TRUE
81 | bus_MV_370_0_node_57 | 20 | n |  | TRUE
82 | bus_MV_370_0_node_178 | 20 | n |  | TRUE
83 | bus_MV_370_0_node_58 | 20 | n |  | TRUE
84 | bus_MV_370_0_node_59 | 20 | n |  | TRUE
85 | bus_MV_370_0_node_172 | 20 | n |  | TRUE
86 | bus_MV_370_0_node_185 | 20 | n |  | TRUE
87 | bus_MV_370_0_node_183 | 20 | n |  | TRUE
88 | bus_MV_370_0_node_60 | 20 | n |  | TRUE
89 | bus_MV_370_0_node_61 | 20 | n |  | TRUE
90 | bus_MV_370_0_node_62 | 20 | n |  | TRUE
91 | bus_MV_370_0_node_63 | 20 | n |  | TRUE
92 | bus_MV_370_0_node_64 | 20 | n |  | TRUE
93 | bus_MV_370_0_node_69 | 20 | n |  | TRUE
94 | bus_MV_370_0_node_94 | 20 | n |  | TRUE
95 | bus_MV_370_0_node_160 | 20 | n |  | TRUE
96 | bus_MV_370_0_node_65 | 20 | n |  | TRUE
97 | bus_MV_370_0_node_83 | 20 | n |  | TRUE
98 | bus_MV_370_0_node_66 | 20 | n |  | TRUE
99 | bus_MV_370_0_node_114 | 20 | n |  | TRUE
100 | bus_MV_370_0_node_155 | 20 | n |  | TRUE
101 | bus_MV_370_0_node_67 | 20 | n |  | TRUE
102 | bus_MV_370_0_node_68 | 20 | n |  | TRUE
103 | bus_MV_370_0_node_89 | 20 | n |  | TRUE
104 | bus_MV_370_0_node_87 | 20 | n |  | TRUE
105 | bus_MV_370_0_node_186 | 20 | n |  | TRUE
106 | bus_MV_370_0_node_95 | 20 | n |  | TRUE
107 | bus_MV_370_0_node_70 | 20 | n |  | TRUE
108 | bus_MV_370_0_node_72 | 20 | n |  | TRUE
109 | bus_MV_370_0_node_77 | 20 | n |  | TRUE
110 | bus_MV_370_0_node_73 | 20 | n |  | TRUE
111 | bus_MV_370_0_node_74 | 20 | n |  | TRUE
112 | bus_MV_370_0_node_75 | 20 | n |  | TRUE
113 | bus_MV_370_0_node_76 | 20 | n |  | TRUE
114 | bus_MV_370_0_node_88 | 20 | n |  | TRUE
115 | bus_MV_370_0_node_153 | 20 | n |  | TRUE
116 | bus_MV_370_0_node_157 | 20 | n |  | TRUE
117 | bus_MV_370_0_node_159 | 20 | n |  | TRUE
118 | bus_MV_370_0_node_101 | 20 | n |  | TRUE
119 | bus_MV_370_0_node_79 | 20 | n |  | TRUE
120 | bus_MV_370_0_node_149 | 20 | n |  | TRUE
121 | bus_MV_370_0_node_105 | 20 | n |  | TRUE
122 | bus_MV_370_0_node_109 | 20 | n |  | TRUE
123 | bus_MV_370_0_node_111 | 20 | n |  | TRUE
124 | bus_MV_370_0_node_78 | 20 | n |  | TRUE
125 | bus_MV_370_0_node_80 | 20 | n |  | TRUE
126 | bus_MV_370_0_node_108 | 20 | n |  | TRUE
127 | bus_MV_370_0_node_81 | 20 | n |  | TRUE
128 | bus_MV_370_0_node_82 | 20 | n |  | TRUE
129 | bus_MV_370_0_node_152 | 20 | n |  | TRUE
130 | bus_MV_370_0_node_84 | 20 | n |  | TRUE
131 | bus_MV_370_0_node_85 | 20 | n |  | TRUE
132 | bus_MV_370_0_node_97 | 20 | n |  | TRUE
133 | bus_MV_370_0_node_86 | 20 | n |  | TRUE
134 | bus_MV_370_0_node_93 | 20 | n |  | TRUE
135 | bus_MV_370_0_node_91 | 20 | n |  | TRUE
136 | bus_MV_370_0_node_92 | 20 | n |  | TRUE
137 | bus_MV_370_0_node_98 | 20 | n |  | TRUE
138 | bus_MV_370_0_node_99 | 20 | n |  | TRUE
139 | bus_MV_370_0_node_107 | 20 | n |  | TRUE
140 | bus_MV_370_0_node_100 | 20 | n |  | TRUE
141 | bus_MV_370_0_node_102 | 20 | n |  | TRUE
142 | bus_MV_370_0_node_103 | 20 | n |  | TRUE
143 | bus_MV_370_0_node_104 | 20 | n |  | TRUE
144 | bus_MV_370_0_node_110 | 20 | n |  | TRUE
145 | bus_MV_370_0_node_189 | 20 | n |  | TRUE
146 | bus_MV_370_0_node_168 | 20 | n |  | TRUE
147 | bus_MV_370_0_node_113 | 20 | n |  | TRUE
148 | bus_MV_370_0_node_187 | 20 | n |  | TRUE
149 | bus_MV_370_0_node_179 | 20 | n |  | TRUE
150 | bus_MV_370_0_node_180 | 20 | n |  | TRUE
151 | bus_MV_370_0_node_181 | 20 | n |  | TRUE
152 | bus_MV_370_0_node_184 | 20 | n |  | TRUE
153 | bus_MV_370_0_node_145 | 20 | n |  | TRUE
154 | bus_MV_370_0_node_162 | 20 | n |  | TRUE
155 | bus_MV_370_0_node_43 | 20 | n |  | TRUE
156 | bus_MV_370_0_node_44 | 20 | n |  | TRUE
157 | bus_MV_370_0_node_49 | 20 | n |  | TRUE
158 | bus_MV_370_0_node_45 | 20 | n |  | TRUE
159 | bus_MV_370_0_node_46 | 20 | n |  | TRUE
160 | bus_MV_370_0_node_139 | 20 | n |  | TRUE
161 | bus_MV_370_0_node_48 | 20 | n |  | TRUE
162 | bus_MV_370_0_node_147 | 20 | n |  | TRUE
163 | bus_MV_370_0_node_47 | 20 | n |  | TRUE
164 | bus_MV_370_0_node_156 | 20 | n |  | TRUE
165 | bus_MV_370_0_node_125 | 20 | n |  | TRUE
166 | bus_MV_370_0_node_141 | 20 | n |  | TRUE
167 | bus_MV_370_0_node_140 | 20 | n |  | TRUE
168 | bus_MV_370_0_node_138 | 20 | n |  | TRUE
169 | bus_MV_370_0_node_126 | 20 | n |  | TRUE
170 | bus_MV_370_0_node_127 | 20 | n |  | TRUE
171 | bus_MV_370_0_node_142 | 20 | n |  | TRUE
172 | bus_MV_370_0_node_174 | 20 | n |  | TRUE
173 | bus_MV_370_0_node_175 | 20 | n |  | TRUE
174 | bus_MV_370_0_node_146 | 20 | n |  | TRUE
175 | bus_MV_370_0_node_128 | 20 | n |  | TRUE
176 | bus_MV_370_0_node_129 | 20 | n |  | TRUE
177 | bus_MV_370_0_node_132 | 20 | n |  | TRUE
178 | bus_MV_370_0_node_133 | 20 | n |  | TRUE
179 | bus_MV_370_0_node_135 | 20 | n |  | TRUE
180 | bus_MV_370_0_node_136 | 20 | n |  | TRUE
181 | bus_MV_370_0_node_143 | 20 | n |  | TRUE
182 | bus_MV_370_0_node_144 | 20 | n |  | TRUE
183 | bus_MV_370_0_node_164 | 20 | n |  | TRUE
184 | bus_MV_370_0_node_165 | 20 | n |  | TRUE
185 | bus_HV_370_0_node_34 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_370_0_load_0 | 0 | 0.37428 | 0.18127 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_370_0_load_53 | 4 | 0.27281 | 0.13213 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_370_0_load_173 | 5 | 0.19267 | 0.093316 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_370_0_load_51 | 7 | 0.40065 | 0.19405 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_370_0_load_3 | 9 | 0.31641 | 0.15324 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_370_0_load_190 | 13 | 0.12472 | 0.060403 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_370_0_load_166 | 16 | 0.29745 | 0.14406 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_370_0_load_151 | 18 | 0.26127 | 0.12654 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_370_0_load_16 | 21 | 0.17821 | 0.086312 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_370_0_load_131 | 24 | 0.16061 | 0.077787 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_370_0_load_117 | 25 | 0.23025 | 0.11151 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_370_0_load_124 | 30 | 0.1606 | 0.077783 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_370_0_load_154 | 31 | 0.36066 | 0.17468 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_370_0_load_121 | 33 | 0.25603 | 0.124 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_370_0_load_19 | 35 | 0.3681 | 0.17828 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_370_0_load_161 | 36 | 0.29786 | 0.14426 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_370_0_load_34 | 37 | 0.21338 | 0.10335 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_370_0_load_171 | 40 | 0.20686 | 0.10019 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_370_0_load_35 | 43 | 0.39626 | 0.19192 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_370_0_load_148 | 46 | 0.12158 | 0.058882 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_370_0_load_150 | 47 | 0.10266 | 0.049722 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_370_0_load_50 | 48 | 0.34649 | 0.16781 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_370_0_load_163 | 49 | 0.25448 | 0.12325 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_370_0_load_130 | 50 | 0.085948 | 0.041627 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_370_0_load_115 | 52 | 0.2789 | 0.13508 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_370_0_load_158 | 53 | 0.33465 | 0.16208 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_370_0_load_169 | 57 | 0.26792 | 0.12976 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_370_0_load_25 | 59 | 0.3273 | 0.15852 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_370_0_load_116 | 62 | 0.29353 | 0.14216 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_370_0_load_137 | 67 | 0.11794 | 0.057121 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_370_0_load_22 | 68 | 0.15509 | 0.075116 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_370_0_load_177 | 69 | 0.32247 | 0.15618 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_370_0_load_170 | 70 | 0.35455 | 0.17172 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_370_0_load_26 | 74 | 0.24581 | 0.11905 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_370_0_load_167 | 76 | 0.17206 | 0.083333 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_370_0_load_188 | 78 | 0.073891 | 0.035787 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_370_0_load_55 | 79 | 0.2223 | 0.10766 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_370_0_load_56 | 80 | 0.30596 | 0.14818 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_370_0_load_178 | 82 | 0.10095 | 0.048892 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_370_0_load_172 | 85 | 0.0962 | 0.046592 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_370_0_load_185 | 86 | 0.47365 | 0.2294 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_370_0_load_183 | 87 | 0.16872 | 0.081717 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_370_0_load_60 | 88 | 0.40623 | 0.19675 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_370_0_load_94 | 94 | 0.18884 | 0.091461 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_370_0_load_160 | 95 | 0.30664 | 0.14851 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_370_0_load_83 | 97 | 0.2095 | 0.10146 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_370_0_load_114 | 99 | 0.14882 | 0.072075 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_370_0_load_155 | 100 | 0.26926 | 0.13041 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_370_0_load_89 | 103 | 0.16406 | 0.079459 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_370_0_load_186 | 105 | 0.31887 | 0.15443 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_370_0_load_95 | 106 | 0.15588 | 0.075497 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_370_0_load_70 | 107 | 0.39481 | 0.19122 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_370_0_load_88 | 114 | 0.29408 | 0.14243 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_370_0_load_153 | 115 | 0.21055 | 0.10197 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_370_0_load_157 | 116 | 0.41201 | 0.19955 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_370_0_load_159 | 117 | 0.2985 | 0.14457 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_370_0_load_101 | 118 | 0.22786 | 0.11036 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_370_0_load_149 | 120 | 0.19626 | 0.095054 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_370_0_load_109 | 122 | 0.30134 | 0.14594 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_370_0_load_111 | 123 | 0.34494 | 0.16706 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_370_0_load_80 | 125 | 0.2407 | 0.11658 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_370_0_load_152 | 129 | 0.2128 | 0.10306 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_370_0_load_84 | 130 | 0.13276 | 0.064299 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_370_0_load_97 | 132 | 0.07548 | 0.036557 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_370_0_load_86 | 133 | 0.35106 | 0.17002 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_370_0_load_93 | 134 | 0.17443 | 0.084479 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_370_0_load_98 | 137 | 0.32964 | 0.15965 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_370_0_load_102 | 141 | 0.096165 | 0.046575 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_370_0_load_110 | 144 | 0.221 | 0.10703 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_370_0_load_189 | 145 | 0.19914 | 0.096449 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_370_0_load_168 | 146 | 0.30494 | 0.14769 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_370_0_load_187 | 148 | 0.21324 | 0.10328 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_370_0_load_181 | 151 | 0.235 | 0.11381 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_370_0_load_184 | 152 | 0.10477 | 0.050743 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_370_0_load_43 | 155 | 0.15831 | 0.076674 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_370_0_load_139 | 160 | 0.26344 | 0.12759 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_370_0_load_147 | 162 | 0.20944 | 0.10144 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_370_0_load_156 | 164 | 0.35046 | 0.16973 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_370_0_load_125 | 165 | 0.79734 | 0.38617 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_370_0_load_140 | 167 | 0.082474 | 0.039944 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_370_0_load_138 | 168 | 0.07865 | 0.038092 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_370_0_load_127 | 170 | 0.52463 | 0.25409 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_370_0_load_142 | 171 | 0.082506 | 0.03996 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_370_0_load_174 | 172 | 0.41481 | 0.2009 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_370_0_load_146 | 174 | 0.1118 | 0.054148 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_370_0_load_129 | 176 | 0.24443 | 0.11838 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_370_0_load_132 | 177 | 0.24442 | 0.11838 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_370_0_load_136 | 180 | 0.095476 | 0.046241 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_370_0_load_143 | 181 | 0.12644 | 0.06124 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_370_0_load_165 | 184 | 0.16231 | 0.078612 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 37 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_370_0_line_0 |  | 0 | 1 | 0.103 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
1 | MV_370_0_line_1 |  | 0 | 2 | 1.5712 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
2 | MV_370_0_line_2 |  | 1 | 3 | 0.16579 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
3 | MV_370_0_line_3 |  | 2 | 4 | 0.042225 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
4 | MV_370_0_line_4 |  | 3 | 5 | 0.002455 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
5 | MV_370_0_line_5 |  | 4 | 71 | 0.022868 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
6 | MV_370_0_line_6 |  | 5 | 6 | 0.059494 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
7 | MV_370_0_line_7 |  | 6 | 173 | 0.12517 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
8 | MV_370_0_line_8 |  | 7 | 8 | 0.086474 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
9 | MV_370_0_line_9 |  | 8 | 77 | 0.60668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_370_0_line_10 |  | 8 | 71 | 0.88479 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
11 | MV_370_0_line_11 |  | 9 | 10 | 0.026959 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_370_0_line_12 |  | 10 | 11 | 0.29514 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
13 | MV_370_0_line_13 |  | 10 | 12 | 0.21645 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
14 | MV_370_0_line_14 |  | 11 | 13 | 0.01623 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
15 | MV_370_0_line_15 |  | 11 | 14 | 0.43735 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
16 | MV_370_0_line_16 |  | 12 | 15 | 0.27079 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
17 | MV_370_0_line_17 |  | 12 | 16 | 0.099855 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
18 | MV_370_0_line_18 |  | 14 | 19 | 0.20794 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
19 | MV_370_0_line_19 |  | 14 | 20 | 0.65128 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
20 | MV_370_0_line_20 |  | 14 | 21 | 0.002357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_370_0_line_21 |  | 14 | 17 | 0.24402 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
22 | MV_370_0_line_22 |  | 15 | 50 | 0.012167 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_370_0_line_23 |  | 15 | 38 | 0.46223 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
24 | MV_370_0_line_24 |  | 15 | 42 | 0.34569 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_370_0_line_25 |  | 17 | 18 | 0.062765 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
26 | MV_370_0_line_26 |  | 19 | 51 | 0.13188 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
27 | MV_370_0_line_27 |  | 19 | 52 | 0.010811 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_370_0_line_28 |  | 20 | 36 | 0.021401 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
29 | MV_370_0_line_29 |  | 20 | 29 | 0.73914 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
30 | MV_370_0_line_30 |  | 22 | 23 | 0.57003 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
31 | MV_370_0_line_31 |  | 22 | 24 | 0.037268 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_370_0_line_32 |  | 22 | 25 | 0.041489 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
33 | MV_370_0_line_33 |  | 23 | 37 | 0.061863 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
34 | MV_370_0_line_34 |  | 25 | 54 | 0.077821 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
35 | MV_370_0_line_35 |  | 25 | 55 | 0.1349 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_370_0_line_36 |  | 26 | 27 | 0.37415 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
37 | MV_370_0_line_37 |  | 26 | 28 | 0.21759 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
38 | MV_370_0_line_38 |  | 26 | 29 | 0.44806 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
39 | MV_370_0_line_39 |  | 26 | 30 | 0.018857 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_370_0_line_40 |  | 27 | 31 | 0.022174 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_370_0_line_41 |  | 27 | 32 | 0.68948 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
42 | MV_370_0_line_42 |  | 28 | 33 | 0.033228 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_370_0_line_43 |  | 28 | 34 | 0.072914 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
44 | MV_370_0_line_44 |  | 29 | 35 | 0.055324 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_370_0_line_45 |  | 32 | 58 | 0.27331 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
46 | MV_370_0_line_46 |  | 32 | 59 | 0.043212 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_370_0_line_47 |  | 32 | 56 | 0.11669 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
48 | MV_370_0_line_48 |  | 34 | 60 | 0.22406 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
49 | MV_370_0_line_49 |  | 36 | 61 | 0.067596 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
50 | MV_370_0_line_50 |  | 37 | 62 | 2.4168 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
51 | MV_370_0_line_51 |  | 38 | 39 | 0.63074 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
52 | MV_370_0_line_52 |  | 38 | 40 | 0.06328 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
53 | MV_370_0_line_53 |  | 38 | 41 | 0.31776 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
54 | MV_370_0_line_54 |  | 39 | 49 | 0.039165 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
55 | MV_370_0_line_55 |  | 41 | 48 | 0.006006 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_370_0_line_56 |  | 41 | 44 | 0.23224 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
57 | MV_370_0_line_57 |  | 42 | 43 | 0.013022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_370_0_line_58 |  | 44 | 45 | 0.14904 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_370_0_line_59 |  | 44 | 46 | 0.017245 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_370_0_line_60 |  | 45 | 47 | 0.004894 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_370_0_line_61 |  | 49 | 153 | 0.024498 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_370_0_line_62 |  | 49 | 154 | 0.017988 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
63 | MV_370_0_line_63 |  | 51 | 53 | 0.01865 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
64 | MV_370_0_line_64 |  | 54 | 61 | 0.11205 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
65 | MV_370_0_line_65 |  | 55 | 174 | 0.003339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_370_0_line_66 |  | 56 | 57 | 0.041446 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
67 | MV_370_0_line_67 |  | 57 | 63 | 0.034765 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
68 | MV_370_0_line_68 |  | 58 | 68 | 0.015799 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_370_0_line_69 |  | 58 | 64 | 0.048256 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
70 | MV_370_0_line_70 |  | 60 | 168 | 0.021477 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
71 | MV_370_0_line_71 |  | 62 | 140 | 0.004403 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
72 | MV_370_0_line_72 |  | 63 | 178 | 0.068954 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
73 | MV_370_0_line_73 |  | 64 | 65 | 0.41161 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
74 | MV_370_0_line_74 |  | 64 | 66 | 0.42675 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
75 | MV_370_0_line_75 |  | 64 | 67 | 0.13487 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
76 | MV_370_0_line_76 |  | 65 | 69 | 0.010882 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
77 | MV_370_0_line_77 |  | 66 | 70 | 0.055416 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
78 | MV_370_0_line_78 |  | 66 | 71 | 0.81477 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
79 | MV_370_0_line_79 |  | 71 | 72 | 0.63229 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
80 | MV_370_0_line_80 |  | 72 | 73 | 0.25236 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
81 | MV_370_0_line_81 |  | 72 | 74 | 0.077892 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
82 | MV_370_0_line_82 |  | 73 | 78 | 0.069942 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
83 | MV_370_0_line_83 |  | 73 | 75 | 0.61339 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
84 | MV_370_0_line_84 |  | 75 | 76 | 0.052311 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
85 | MV_370_0_line_85 |  | 77 | 79 | 0.034222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_370_0_line_86 |  | 80 | 81 | 0.055749 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
87 | MV_370_0_line_87 |  | 80 | 82 | 1.0586 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
88 | MV_370_0_line_88 |  | 81 | 83 | 0.36914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_370_0_line_89 |  | 81 | 84 | 0.32823 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
90 | MV_370_0_line_90 |  | 82 | 148 | 0.70959 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
91 | MV_370_0_line_91 |  | 82 | 130 | 0.66564 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
92 | MV_370_0_line_92 |  | 83 | 85 | 0.029058 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
93 | MV_370_0_line_93 |  | 84 | 86 | 0.074334 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_370_0_line_94 |  | 84 | 87 | 0.066755 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
95 | MV_370_0_line_95 |  | 87 | 152 | 0.17404 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
96 | MV_370_0_line_96 |  | 88 | 89 | 0.05355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_370_0_line_97 |  | 89 | 90 | 0.34405 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_370_0_line_98 |  | 89 | 91 | 0.36283 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_370_0_line_99 |  | 89 | 92 | 1.0266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_370_0_line_100 |  | 90 | 93 | 0.51479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_370_0_line_101 |  | 90 | 94 | 0.007842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_370_0_line_102 |  | 91 | 95 | 0.014792 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_370_0_line_103 |  | 92 | 96 | 0.5885 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_370_0_line_104 |  | 92 | 97 | 0.041417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_370_0_line_105 |  | 93 | 106 | 0.057622 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
106 | MV_370_0_line_106 |  | 95 | 119 | 0.006835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_370_0_line_107 |  | 96 | 98 | 0.14162 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_370_0_line_108 |  | 96 | 99 | 0.028683 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
109 | MV_370_0_line_109 |  | 98 | 100 | 0.015295 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_370_0_line_110 |  | 101 | 102 | 0.38062 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
111 | MV_370_0_line_111 |  | 101 | 103 | 0.018773 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
112 | MV_370_0_line_112 |  | 102 | 104 | 0.7538 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
113 | MV_370_0_line_113 |  | 102 | 105 | 0.0259 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
114 | MV_370_0_line_114 |  | 103 | 134 | 0.17635 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
115 | MV_370_0_line_115 |  | 104 | 130 | 0.72805 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
116 | MV_370_0_line_116 |  | 104 | 133 | 0.005807 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_370_0_line_117 |  | 107 | 108 | 0.004104 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_370_0_line_118 |  | 108 | 109 | 0.33707 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_370_0_line_119 |  | 109 | 119 | 0.29453 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_370_0_line_120 |  | 109 | 120 | 0.081191 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_370_0_line_121 |  | 109 | 121 | 0.264 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
122 | MV_370_0_line_122 |  | 109 | 122 | 0.42112 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
123 | MV_370_0_line_123 |  | 109 | 123 | 0.17306 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
124 | MV_370_0_line_124 |  | 110 | 111 | 0.081424 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_370_0_line_125 |  | 110 | 112 | 0.59459 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_370_0_line_126 |  | 110 | 113 | 0.96443 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_370_0_line_127 |  | 110 | 114 | 0.00607 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_370_0_line_128 |  | 111 | 115 | 0.015464 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
129 | MV_370_0_line_129 |  | 112 | 116 | 0.030582 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
130 | MV_370_0_line_130 |  | 113 | 117 | 0.062515 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
131 | MV_370_0_line_131 |  | 113 | 118 | 0.37433 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
132 | MV_370_0_line_132 |  | 117 | 147 | 0.47946 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
133 | MV_370_0_line_133 |  | 118 | 136 | 0.1204 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
134 | MV_370_0_line_134 |  | 121 | 139 | 0.17039 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
135 | MV_370_0_line_135 |  | 121 | 144 | 0.037946 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_370_0_line_136 |  | 122 | 146 | 0.30172 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
137 | MV_370_0_line_137 |  | 122 | 143 | 0.035674 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_370_0_line_138 |  | 124 | 125 | 0.093905 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
139 | MV_370_0_line_139 |  | 124 | 126 | 0.29133 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
140 | MV_370_0_line_140 |  | 125 | 127 | 0.008425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_370_0_line_141 |  | 126 | 138 | 0.41755 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
142 | MV_370_0_line_142 |  | 127 | 128 | 0.25281 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_370_0_line_143 |  | 128 | 129 | 0.02253 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
144 | MV_370_0_line_144 |  | 130 | 131 | 0.004391 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_370_0_line_145 |  | 131 | 132 | 1.0631 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
146 | MV_370_0_line_146 |  | 134 | 135 | 0.004421 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
147 | MV_370_0_line_147 |  | 135 | 136 | 0.26355 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
148 | MV_370_0_line_148 |  | 137 | 138 | 0.082978 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
149 | MV_370_0_line_149 |  | 137 | 139 | 0.4227 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
150 | MV_370_0_line_150 |  | 138 | 140 | 0.31751 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
151 | MV_370_0_line_151 |  | 139 | 145 | 0.032126 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
152 | MV_370_0_line_152 |  | 141 | 142 | 0.044406 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_370_0_line_153 |  | 142 | 143 | 0.10934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_370_0_line_154 |  | 146 | 147 | 0.03071 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
155 | MV_370_0_line_155 |  | 148 | 150 | 0.011133 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_370_0_line_156 |  | 149 | 150 | 0.28594 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_370_0_line_157 |  | 149 | 151 | 0.064157 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
158 | MV_370_0_line_158 |  | 153 | 182 | 0.2511 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_370_0_line_159 |  | 154 | 183 | 0.12992 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
160 | MV_370_0_line_160 |  | 155 | 156 | 0.003517 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_370_0_line_161 |  | 156 | 157 | 0.12523 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
162 | MV_370_0_line_162 |  | 157 | 166 | 0.00294 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
163 | MV_370_0_line_163 |  | 157 | 167 | 0.012724 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
164 | MV_370_0_line_164 |  | 157 | 158 | 0.13342 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
165 | MV_370_0_line_165 |  | 158 | 159 | 0.19301 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
166 | MV_370_0_line_166 |  | 158 | 160 | 0.01656 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
167 | MV_370_0_line_167 |  | 159 | 161 | 0.16122 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
168 | MV_370_0_line_168 |  | 159 | 162 | 0.047967 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
169 | MV_370_0_line_169 |  | 160 | 168 | 0.022331 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
170 | MV_370_0_line_170 |  | 161 | 165 | 0.077168 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
171 | MV_370_0_line_171 |  | 161 | 163 | 0.11437 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
172 | MV_370_0_line_172 |  | 163 | 164 | 0.04431 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
173 | MV_370_0_line_173 |  | 165 | 169 | 0.030939 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
174 | MV_370_0_line_174 |  | 165 | 170 | 0.088055 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
175 | MV_370_0_line_175 |  | 166 | 171 | 0.014507 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
176 | MV_370_0_line_176 |  | 169 | 175 | 0.015596 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
177 | MV_370_0_line_177 |  | 172 | 173 | 0.068695 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
178 | MV_370_0_line_178 |  | 175 | 176 | 0.016143 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
179 | MV_370_0_line_179 |  | 177 | 178 | 0.062904 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
180 | MV_370_0_line_180 |  | 178 | 179 | 0.22467 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
181 | MV_370_0_line_181 |  | 179 | 180 | 0.065215 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
182 | MV_370_0_line_182 |  | 181 | 182 | 0.0078623 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
183 | MV_370_0_line_183 |  | 183 | 184 | 0.010192 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_370_0_trafo_34 | 25 MVA 110/20 kV | 185 | 37 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2693608.7776 | 1258831.0528
1 | 2693509.7057 | 1258851.3029
2 | 2694989.5259 | 1259580.7727
3 | 2693380.2385 | 1258795.9261
4 | 2695024.8852 | 1259604.0145
5 | 2693379.2562 | 1258793.6755
6 | 2693325.587 | 1258819.6719
7 | 2694704.3328 | 1259999.3486
8 | 2694765.1027 | 1259937.8276
9 | 2695812.0806 | 1260990.7683
10 | 2695785.2281 | 1260988.3761
11 | 2695755.9413 | 1261138.1342
12 | 2695671.5233 | 1260989.1371
13 | 2695744.4799 | 1261149.658
14 | 2695911.3643 | 1261246.6394
15 | 2695516.7367 | 1260858.2751
16 | 2695602.4953 | 1261061.2907
17 | 2695749.3295 | 1261350.9214
18 | 2695732.0362 | 1261411.257
19 | 2696047.1642 | 1261327.341
20 | 2696070.9832 | 1261085.0094
21 | 2695911.38 | 1261244.2822
22 | 2696230.2356 | 1260908.9216
23 | 2696387.4547 | 1260696.3198
24 | 2696211.3229 | 1260876.809
25 | 2696248.0154 | 1260946.4078
26 | 2695754.3959 | 1260730.0574
27 | 2695906.7853 | 1260480.3017
28 | 2695650.7631 | 1260740.6119
29 | 2695977.8376 | 1260738.1952
30 | 2695770.7497 | 1260720.6696
31 | 2695924.8362 | 1260467.3727
32 | 2695693.1976 | 1260021.4965
33 | 2695635.5246 | 1260711.1641
34 | 2695583.057 | 1260767.673
35 | 2696020.2933 | 1260770.7325
36 | 2696084.9636 | 1261101.2496
37 | 2696431.8572 | 1260657.9122
38 | 2695315.8845 | 1261062.5787
39 | 2695036.0458 | 1261304.1387
40 | 2695326.9506 | 1261000.2734
41 | 2695429.3526 | 1261272.9331
42 | 2695437.097 | 1260754.4285
43 | 2695446.5542 | 1260763.4105
44 | 2695283.2983 | 1261379.454
45 | 2695242.8232 | 1261311.4919
46 | 2695289.3709 | 1261395.594
47 | 2695239.6316 | 1261307.7818
48 | 2695423.8566 | 1261275.3909
49 | 2695032.9627 | 1261342.6313
50 | 2695508.31 | 1260867.051
51 | 2695982.6528 | 1261411.3621
52 | 2696054.58 | 1261319.455
53 | 2695964.0069 | 1261410.9704
54 | 2696181.5818 | 1260986.938
55 | 2696314.7664 | 1261063.6333
56 | 2695782.8828 | 1260045.3666
57 | 2695785.9748 | 1260086.6944
58 | 2695567.996 | 1260120.9977
59 | 2695691.0919 | 1259978.3388
60 | 2695419.402 | 1260614.6638
61 | 2696140.7821 | 1261063.1255
62 | 2698846.237 | 1260550.3651
63 | 2695820.7927 | 1260084.8232
64 | 2695540.3208 | 1260097.4318
65 | 2695408.8295 | 1260281.9477
66 | 2695281.4132 | 1260038.1987
67 | 2695588.3914 | 1259971.4179
68 | 2695582.5672 | 1260127.1039
69 | 2695418.463 | 1260287.0627
70 | 2695269.6108 | 1260092.3411
71 | 2695037.4204 | 1259584.8672
72 | 2695234.8311 | 1259343.4137
73 | 2695383.0759 | 1259233.5463
74 | 2695173.0555 | 1259390.858
75 | 2695308.38 | 1258930.8339
76 | 2695290.9444 | 1258881.5137
77 | 2694964.396 | 1260011.4481
78 | 2695357.1333 | 1259190.1157
79 | 2694950.3339 | 1259980.2308
80 | 2699512.561 | 1258337.6339
81 | 2699476.0582 | 1258295.4974
82 | 2700527.3545 | 1258638.9818
83 | 2699543.5123 | 1258060.8525
84 | 2699375.2281 | 1258099.3784
85 | 2699556.4826 | 1258034.8496
86 | 2699330.8893 | 1258159.0936
87 | 2699313.8421 | 1258072.7489
88 | 2699845.9543 | 1259896.0774
89 | 2699795.3216 | 1259913.5091
90 | 2699493.9292 | 1259880.5073
91 | 2699599.6441 | 1260083.8625
92 | 2700187.7926 | 1259354.0843
93 | 2699437.3676 | 1259683.3405
94 | 2699486.146 | 1259879.3755
95 | 2699590.0094 | 1260095.1095
96 | 2700118.6793 | 1259731.3779
97 | 2700198.1597 | 1259313.9827
98 | 2700055.1949 | 1259637.4943
99 | 2700128.5436 | 1259758.3112
100 | 2700064.418 | 1259625.2736
101 | 2700448.8222 | 1259844.209
102 | 2700450.5721 | 1259576.5646
103 | 2700448.1568 | 1259862.9686
104 | 2700776.321 | 1259496.2037
105 | 2700466.3083 | 1259555.9927
106 | 2699494.0858 | 1259673.1744
107 | 2699729.4675 | 1260165.5267
108 | 2699727.9564 | 1260161.7093
109 | 2699722.853 | 1260278.8188
110 | 2699980.5734 | 1260330.4877
111 | 2699935.3897 | 1260284.6759
112 | 2700185.6569 | 1260107.0404
113 | 2700405.3685 | 1260583.4098
114 | 2699985.1192 | 1260326.4501
115 | 2699930.0798 | 1260270.1521
116 | 2700181.8937 | 1260137.3904
117 | 2700348.2666 | 1260557.9647
118 | 2700596.9414 | 1260261.8112
119 | 2699595.4651 | 1260099.2491
120 | 2699767.5385 | 1260219.3105
121 | 2699485.7703 | 1260394.9562
122 | 2699683.7924 | 1260698.1255
123 | 2699745.4288 | 1260450.3951
124 | 2699369.3567 | 1259980.1509
125 | 2699338.9324 | 1260068.9902
126 | 2699255.9771 | 1260248.5112
127 | 2699331.8752 | 1260073.1196
128 | 2699226.3031 | 1260195.348
129 | 2699225.119 | 1260217.8464
130 | 2701150.9098 | 1258871.9174
131 | 2701155.0935 | 1258873.29
132 | 2702205.6951 | 1259036.0833
133 | 2700772.2546 | 1259500.3601
134 | 2700620.5625 | 1259900.0724
135 | 2700621.8322 | 1259904.3085
136 | 2700665.8627 | 1260162.9579
137 | 2699021.5098 | 1260649.154
138 | 2698991.6466 | 1260571.7356
139 | 2699426.2226 | 1260527.1744
140 | 2698848.762 | 1260553.9769
141 | 2699521.4472 | 1260686.4053
142 | 2699565.2743 | 1260678.5029
143 | 2699648.2985 | 1260702.6313
144 | 2699453.8925 | 1260394.1086
145 | 2699458.3486 | 1260527.1143
146 | 2699940.1533 | 1260857.2358
147 | 2699970.7267 | 1260853.5048
148 | 2700912.1064 | 1258042.7548
149 | 2700941.8179 | 1257792.1577
150 | 2700913.4079 | 1258031.8792
151 | 2700995.2975 | 1257827.5986
152 | 2699160.3083 | 1257990.7977
153 | 2695040.8583 | 1261360.5948
154 | 2695030.5895 | 1261359.9294
155 | 2695311.4422 | 1260634.0617
156 | 2695313.9394 | 1260631.5777
157 | 2695272.8683 | 1260574.5592
158 | 2695375.8482 | 1260572.8279
159 | 2695468.4169 | 1260507.7572
160 | 2695387.6904 | 1260584.4393
161 | 2695582.715 | 1260482.9824
162 | 2695515.174 | 1260497.0524
163 | 2695650.4923 | 1260512.2901
164 | 2695684.7597 | 1260484.1993
165 | 2695576.9314 | 1260406.1938
166 | 2695274.2206 | 1260577.172
167 | 2695267.7668 | 1260562.9029
168 | 2695403.8578 | 1260599.8432
169 | 2695607.7059 | 1260403.0106
170 | 2695523.5021 | 1260336.2012
171 | 2695261.2002 | 1260583.5429
172 | 2693180.2648 | 1258817.2249
173 | 2693242.1029 | 1258792.3901
174 | 2696317.7283 | 1261062.0917
175 | 2695606.0421 | 1260387.5046
176 | 2695604.3268 | 1260371.4528
177 | 2695843.8408 | 1260036.2252
178 | 2695859.7807 | 1260095.8747
179 | 2695898.7464 | 1259999.5395
180 | 2695886.5018 | 1260044.5209
181 | 2695188.3487 | 1261401.8919
182 | 2695191.7126 | 1261408.7812
183 | 2694925.5976 | 1261418.3688
184 | 2694920.2508 | 1261427.0456
185 | 2696431.8572 | 1260657.9122

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9945 | -0.11956 | 0.37428 | 0.18127
1 | 0.99448 | -0.11983 | 0 | 0
2 | 0.995 | -0.089703 | 0 | 0
3 | 0.99446 | -0.12026 | 0 | 0
4 | 0.99501 | -0.089664 | 0.27281 | 0.13213
5 | 0.99446 | -0.12026 | 0.19267 | 0.093316
6 | 0.99445 | -0.12037 | 0 | 0
7 | 0.99488 | -0.092705 | 0.40065 | 0.19405
8 | 0.9949 | -0.092131 | 0 | 0
9 | 0.99719 | -0.066146 | 0.31641 | 0.15324
10 | 0.9972 | -0.066043 | 0 | 0
11 | 0.99731 | -0.065061 | 0 | 0
12 | 0.99713 | -0.066671 | 0 | 0
13 | 0.99731 | -0.065069 | 0.12472 | 0.060403
14 | 0.99749 | -0.063422 | 0 | 0
15 | 0.99705 | -0.067349 | 0 | 0
16 | 0.99712 | -0.067233 | 0.29745 | 0.14406
17 | 0.99748 | -0.063487 | 0 | 0
18 | 0.99747 | -0.063797 | 0.26127 | 0.12654
19 | 0.99747 | -0.063543 | 0 | 0
20 | 0.99785 | -0.0599 | 0 | 0
21 | 0.99749 | -0.063417 | 0.17821 | 0.086312
22 | 0.99876 | -0.012036 | 0 | 0
23 | 0.99988 | -0.0011933 | 0 | 0
24 | 0.99876 | -0.011965 | 0.16061 | 0.077787
25 | 0.99861 | -0.022318 | 0.23025 | 0.11151
26 | 0.99636 | -0.074095 | 0 | 0
27 | 0.9961 | -0.077105 | 0 | 0
28 | 0.99625 | -0.074719 | 0 | 0
29 | 0.99691 | -0.068949 | 0 | 0
30 | 0.99636 | -0.074059 | 0.1606 | 0.077783
31 | 0.99609 | -0.077009 | 0.36066 | 0.17468
32 | 0.99565 | -0.082168 | 0 | 0
33 | 0.99624 | -0.074617 | 0.25603 | 0.124
34 | 0.99619 | -0.078656 | 0 | 0
35 | 0.99688 | -0.068706 | 0.3681 | 0.17828
36 | 0.99789 | -0.059508 | 0.29786 | 0.14426
37 | 1 | 0 | -21.8863 | -8.6482
38 | 0.99696 | -0.068189 | 0 | 0
39 | 0.99689 | -0.069744 | 0 | 0
40 | 0.99695 | -0.068436 | 0.20686 | 0.10019
41 | 0.99692 | -0.068966 | 0 | 0
42 | 0.99688 | -0.065798 | 0 | 0
43 | 0.99687 | -0.065736 | 0.39626 | 0.19192
44 | 0.9969 | -0.069066 | 0 | 0
45 | 0.99688 | -0.0689 | 0 | 0
46 | 0.9969 | -0.069041 | 0.12158 | 0.058882
47 | 0.99688 | -0.068894 | 0.10266 | 0.049722
48 | 0.99692 | -0.068941 | 0.34649 | 0.16781
49 | 0.99688 | -0.069832 | 0.25448 | 0.12325
50 | 0.99705 | -0.067337 | 0.085948 | 0.041627
51 | 0.99746 | -0.063577 | 0 | 0
52 | 0.99746 | -0.063507 | 0.2789 | 0.13508
53 | 0.99746 | -0.063695 | 0.33465 | 0.16208
54 | 0.99834 | -0.04111 | 0 | 0
55 | 0.99858 | -0.022502 | 0 | 0
56 | 0.99563 | -0.082479 | 0 | 0
57 | 0.99563 | -0.082587 | 0.26792 | 0.12976
58 | 0.99551 | -0.083814 | 0 | 0
59 | 0.99563 | -0.081998 | 0.3273 | 0.15852
60 | 0.99609 | -0.079219 | 0 | 0
61 | 0.99813 | -0.043181 | 0 | 0
62 | 0.99269 | -0.42969 | 0.29353 | 0.14216
63 | 0.99562 | -0.082641 | 0 | 0
64 | 0.99548 | -0.084093 | 0 | 0
65 | 0.99546 | -0.08466 | 0 | 0
66 | 0.99531 | -0.086222 | 0 | 0
67 | 0.99548 | -0.08416 | 0.11794 | 0.057121
68 | 0.9955 | -0.083784 | 0.15509 | 0.075116
69 | 0.99546 | -0.084673 | 0.32247 | 0.15618
70 | 0.9953 | -0.086334 | 0.35455 | 0.17172
71 | 0.99501 | -0.089639 | 0 | 0
72 | 0.99497 | -0.090541 | 0 | 0
73 | 0.99496 | -0.090761 | 0 | 0
74 | 0.99496 | -0.090858 | 0.24581 | 0.11905
75 | 0.99494 | -0.090998 | 0 | 0
76 | 0.99494 | -0.091168 | 0.17206 | 0.083333
77 | 0.99472 | -0.090812 | 0 | 0
78 | 0.99496 | -0.090782 | 0.073891 | 0.035787
79 | 0.99471 | -0.090721 | 0.2223 | 0.10766
80 | 0.98565 | -0.7799 | 0.30596 | 0.14818
81 | 0.9856 | -0.78153 | 0 | 0
82 | 0.98606 | -0.75614 | 0.10095 | 0.048892
83 | 0.98555 | -0.7812 | 0 | 0
84 | 0.98546 | -0.78302 | 0 | 0
85 | 0.98555 | -0.78123 | 0.0962 | 0.046592
86 | 0.98542 | -0.78259 | 0.47365 | 0.2294
87 | 0.98545 | -0.78312 | 0.16872 | 0.081717
88 | 0.98866 | -0.54428 | 0.40623 | 0.19675
89 | 0.98869 | -0.54454 | 0 | 0
90 | 0.98853 | -0.54346 | 0 | 0
91 | 0.98932 | -0.54905 | 0 | 0
92 | 0.98787 | -0.53868 | 0 | 0
93 | 0.98843 | -0.54268 | 0 | 0
94 | 0.98853 | -0.54344 | 0.18884 | 0.091461
95 | 0.98935 | -0.54923 | 0.30664 | 0.14851
96 | 0.98755 | -0.53607 | 0 | 0
97 | 0.98785 | -0.53858 | 0.2095 | 0.10146
98 | 0.9875 | -0.53562 | 0 | 0
99 | 0.98754 | -0.53613 | 0.14882 | 0.072075
100 | 0.9875 | -0.53557 | 0.26926 | 0.13041
101 | 0.98735 | -0.70451 | 0 | 0
102 | 0.98719 | -0.70554 | 0 | 0
103 | 0.98736 | -0.70446 | 0.16406 | 0.079459
104 | 0.98691 | -0.70703 | 0 | 0
105 | 0.98717 | -0.70564 | 0.31887 | 0.15443
106 | 0.98841 | -0.54279 | 0.15588 | 0.075497
107 | 0.98982 | -0.55239 | 0.39481 | 0.19122
108 | 0.98982 | -0.55241 | 0 | 0
109 | 0.98999 | -0.55394 | 0 | 0
110 | 0.98694 | -0.66103 | 0 | 0
111 | 0.98691 | -0.66082 | 0 | 0
112 | 0.98662 | -0.65829 | 0 | 0
113 | 0.98807 | -0.67017 | 0 | 0
114 | 0.98693 | -0.66101 | 0.29408 | 0.14243
115 | 0.98691 | -0.66086 | 0.21055 | 0.10197
116 | 0.9866 | -0.65845 | 0.41201 | 0.19955
117 | 0.98815 | -0.66513 | 0.2985 | 0.14457
118 | 0.98769 | -0.69358 | 0.22786 | 0.11036
119 | 0.98936 | -0.54934 | 0 | 0
120 | 0.98997 | -0.55375 | 0.19626 | 0.095054
121 | 0.99066 | -0.5142 | 0 | 0
122 | 0.9893 | -0.59588 | 0.30134 | 0.14594
123 | 0.98988 | -0.55468 | 0.34494 | 0.16706
124 | 0.99161 | -0.43667 | 0 | 0
125 | 0.99152 | -0.43724 | 0.2407 | 0.11658
126 | 0.99186 | -0.43488 | 0 | 0
127 | 0.99152 | -0.43723 | 0 | 0
128 | 0.99145 | -0.43662 | 0 | 0
129 | 0.99144 | -0.43668 | 0.2128 | 0.10306
130 | 0.98644 | -0.73408 | 0.13276 | 0.064299
131 | 0.98644 | -0.73408 | 0 | 0
132 | 0.98628 | -0.73513 | 0.07548 | 0.036557
133 | 0.98691 | -0.70701 | 0.35106 | 0.17002
134 | 0.98751 | -0.69486 | 0.17443 | 0.084479
135 | 0.98751 | -0.69484 | 0 | 0
136 | 0.98764 | -0.69399 | 0 | 0
137 | 0.992 | -0.44596 | 0.32964 | 0.15965
138 | 0.99223 | -0.43231 | 0 | 0
139 | 0.99088 | -0.51294 | 0 | 0
140 | 0.99269 | -0.42972 | 0 | 0
141 | 0.98928 | -0.59569 | 0.096165 | 0.046575
142 | 0.98928 | -0.59574 | 0 | 0
143 | 0.9893 | -0.59585 | 0 | 0
144 | 0.99065 | -0.5141 | 0.221 | 0.10703
145 | 0.99086 | -0.51302 | 0.19914 | 0.096449
146 | 0.98884 | -0.62365 | 0.30494 | 0.14769
147 | 0.98882 | -0.62379 | 0 | 0
148 | 0.9859 | -0.7616 | 0.21324 | 0.10328
149 | 0.98581 | -0.76081 | 0 | 0
150 | 0.98589 | -0.76157 | 0 | 0
151 | 0.98578 | -0.761 | 0.235 | 0.11381
152 | 0.98543 | -0.78367 | 0.10477 | 0.050743
153 | 0.99688 | -0.069805 | 0 | 0
154 | 0.99688 | -0.069845 | 0 | 0
155 | 0.99603 | -0.080679 | 0.15831 | 0.076674
156 | 0.99604 | -0.080686 | 0 | 0
157 | 0.99604 | -0.080655 | 0 | 0
158 | 0.99605 | -0.080473 | 0 | 0
159 | 0.99598 | -0.08081 | 0 | 0
160 | 0.99606 | -0.080437 | 0.26344 | 0.12759
161 | 0.99593 | -0.081041 | 0 | 0
162 | 0.99598 | -0.080849 | 0.20944 | 0.10144
163 | 0.99593 | -0.08107 | 0 | 0
164 | 0.99592 | -0.081365 | 0.35046 | 0.16973
165 | 0.99591 | -0.081512 | 0.79734 | 0.38617
166 | 0.99604 | -0.080656 | 0 | 0
167 | 0.99604 | -0.080661 | 0.082474 | 0.039944
168 | 0.99608 | -0.07927 | 0.07865 | 0.038092
169 | 0.99591 | -0.081542 | 0 | 0
170 | 0.9959 | -0.081691 | 0.52463 | 0.25409
171 | 0.99604 | -0.080661 | 0.082506 | 0.03996
172 | 0.99444 | -0.12069 | 0.41481 | 0.2009
173 | 0.99444 | -0.12058 | 0 | 0
174 | 0.99858 | -0.022498 | 0.1118 | 0.054148
175 | 0.9959 | -0.081557 | 0 | 0
176 | 0.9959 | -0.081562 | 0.24443 | 0.11838
177 | 0.9956 | -0.082564 | 0.24442 | 0.11838
178 | 0.99562 | -0.082747 | 0 | 0
179 | 0.99561 | -0.082855 | 0 | 0
180 | 0.99561 | -0.082881 | 0.095476 | 0.046241
181 | 0.99684 | -0.069462 | 0.12644 | 0.06124
182 | 0.99684 | -0.069474 | 0 | 0
183 | 0.99688 | -0.069931 | 0 | 0
184 | 0.99688 | -0.069958 | 0.16231 | 0.078612
185 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.60751 | 0.2546 | -0.6075 | -0.26238 | 6.9224e-06 | -0.0077764 | 0.01912 | 0.019209 | 0.019209 | 0.9945 | -0.11956 | 0.99448 | -0.11983 | 2.2813
1 | -0.98179 | -0.43588 | 0.98206 | 0.43231 | 0.00027223 | -0.0035661 | 0.031181 | 0.031131 | 0.031181 | 0.9945 | -0.11956 | 0.995 | -0.089703 | 2.4171
2 | 0.6075 | 0.26238 | -0.60749 | -0.2749 | 1.128e-05 | -0.012517 | 0.019209 | 0.019356 | 0.019356 | 0.99448 | -0.11983 | 0.99446 | -0.12026 | 2.2988
3 | -0.98206 | -0.43231 | 0.98207 | 0.42706 | 6.3099e-06 | -0.0052497 | 0.031131 | 0.03107 | 0.031131 | 0.995 | -0.089703 | 0.99501 | -0.089664 | 2.4397
4 | 0.60749 | 0.2749 | -0.60749 | -0.27508 | 1.6844e-07 | -0.00018534 | 0.019356 | 0.019358 | 0.019358 | 0.99446 | -0.12026 | 0.99446 | -0.12026 | 2.2991
5 | -1.2549 | -0.55919 | 1.2549 | 0.55635 | 5.6082e-06 | -0.0028419 | 0.039858 | 0.039825 | 0.039858 | 0.99501 | -0.089664 | 0.99501 | -0.089639 | 3.1237
6 | 0.41481 | 0.18176 | -0.41481 | -0.18626 | 1.8893e-06 | -0.0044936 | 0.013147 | 0.0132 | 0.0132 | 0.99446 | -0.12026 | 0.99445 | -0.12037 | 1.5676
7 | 0.41481 | 0.18626 | -0.41481 | -0.19571 | 4.0252e-06 | -0.0094535 | 0.0132 | 0.013314 | 0.013314 | 0.99445 | -0.12037 | 0.99444 | -0.12058 | 1.5813
8 | -0.40065 | -0.19405 | 0.40066 | 0.19383 | 5.1412e-06 | -0.00021413 | 0.012917 | 0.012914 | 0.012917 | 0.99488 | -0.092705 | 0.9949 | -0.092131 | 1.5753
9 | 0.22234 | 0.092532 | -0.2223 | -0.10686 | 4.0486e-05 | -0.014323 | 0.0069877 | 0.0071578 | 0.0071578 | 0.9949 | -0.092131 | 0.99472 | -0.090812 | 3.2536
10 | -0.623 | -0.28636 | 0.62306 | 0.2195 | 6.1628e-05 | -0.066864 | 0.019895 | 0.019165 | 0.019895 | 0.9949 | -0.092131 | 0.99501 | -0.089639 | 2.3628
11 | -0.31641 | -0.15324 | 0.31641 | 0.15321 | 4.975e-06 | -2.8887e-05 | 0.010177 | 0.010177 | 0.010177 | 0.99719 | -0.066146 | 0.9972 | -0.066043 | 4.8464
12 | -2.4174 | -0.93128 | 2.4177 | 0.89454 | 0.00025516 | -0.036741 | 0.074995 | 0.074617 | 0.074995 | 0.9972 | -0.066043 | 0.99731 | -0.065061 | 5.8773
13 | 2.101 | 0.77807 | -2.1009 | -0.80503 | 0.00014127 | -0.026967 | 0.064858 | 0.065134 | 0.065134 | 0.9972 | -0.066043 | 0.99713 | -0.066671 | 5.1046
14 | 0.12472 | 0.05917 | -0.12472 | -0.060403 | 4.7617e-08 | -0.0012333 | 0.0039956 | 0.0040111 | 0.0040111 | 0.99731 | -0.065061 | 0.99731 | -0.065069 | 0.47637
15 | -2.5424 | -0.95371 | 2.5428 | 0.89927 | 0.00041452 | -0.05444 | 0.078598 | 0.078056 | 0.078598 | 0.99731 | -0.065061 | 0.99749 | -0.063422 | 6.1597
16 | 1.8034 | 0.66124 | -1.8033 | -0.695 | 0.00013017 | -0.033758 | 0.055609 | 0.055954 | 0.055954 | 0.99713 | -0.066671 | 0.99705 | -0.067349 | 4.3851
17 | 0.29746 | 0.14379 | -0.29745 | -0.14406 | 1.6313e-06 | -0.00027009 | 0.0095649 | 0.0095684 | 0.0095684 | 0.99713 | -0.066671 | 0.99712 | -0.067233 | 0.74174
18 | 0.61356 | 0.25437 | -0.61355 | -0.28036 | 1.2053e-05 | -0.025992 | 0.019222 | 0.019523 | 0.019523 | 0.99749 | -0.063422 | 0.99747 | -0.063543 | 1.53
19 | -3.5959 | -1.3358 | 3.5971 | 1.255 | 0.0012311 | -0.080768 | 0.11101 | 0.11021 | 0.11101 | 0.99749 | -0.063422 | 0.99785 | -0.0599 | 8.7001
20 | 0.17821 | 0.086256 | -0.17821 | -0.086312 | 1.0329e-07 | -5.5963e-05 | 0.0057298 | 0.0057306 | 0.0057306 | 0.99749 | -0.063422 | 0.99749 | -0.063417 | 2.6048
21 | 0.26127 | 0.095859 | -0.26127 | -0.12637 | 2.5453e-06 | -0.030509 | 0.0080541 | 0.0083993 | 0.0083993 | 0.99749 | -0.063422 | 0.99748 | -0.063487 | 0.65825
22 | 0.085948 | 0.041338 | -0.085948 | -0.041627 | 1.2401e-07 | -0.00028875 | 0.0027613 | 0.0027649 | 0.0027649 | 0.99705 | -0.067349 | 0.99705 | -0.067337 | 1.2568
23 | 1.321 | 0.47023 | -1.3209 | -0.52791 | 0.00011938 | -0.057671 | 0.040598 | 0.041189 | 0.041189 | 0.99705 | -0.067349 | 0.99696 | -0.068189 | 3.228
24 | 0.39633 | 0.18343 | -0.39626 | -0.19161 | 7.4371e-05 | -0.0081816 | 0.012644 | 0.012746 | 0.012746 | 0.99705 | -0.067349 | 0.99688 | -0.065798 | 5.7936
25 | 0.26127 | 0.12637 | -0.26127 | -0.12654 | 7.9059e-07 | -0.00017052 | 0.0083993 | 0.0084015 | 0.0084015 | 0.99748 | -0.063487 | 0.99747 | -0.063797 | 0.65128
26 | 0.33465 | 0.14554 | -0.33465 | -0.16203 | 2.3149e-06 | -0.016487 | 0.010561 | 0.010761 | 0.010761 | 0.99747 | -0.063543 | 0.99746 | -0.063577 | 0.84331
27 | 0.2789 | 0.13482 | -0.2789 | -0.13508 | 1.1605e-06 | -0.00025647 | 0.0089652 | 0.0089685 | 0.0089685 | 0.99747 | -0.063543 | 0.99746 | -0.063507 | 4.0766
28 | -11.806 | -4.1803 | 11.8065 | 4.1779 | 0.00043404 | -0.0024335 | 0.36232 | 0.3623 | 0.36232 | 0.99785 | -0.0599 | 0.99789 | -0.059508 | 28.3953
29 | 8.2089 | 2.9253 | -8.2016 | -3.0136 | 0.0072844 | -0.088295 | 0.25211 | 0.25302 | 0.25302 | 0.99785 | -0.0599 | 0.99691 | -0.068949 | 19.8292
30 | -12.6141 | -4.5638 | 12.6273 | 4.4997 | 0.013215 | -0.064094 | 0.38772 | 0.38702 | 0.38772 | 0.99876 | -0.012036 | 0.99988 | -0.0011933 | 30.3853
31 | 0.16061 | 0.0769 | -0.16061 | -0.077787 | 1.3208e-06 | -0.00088722 | 0.0051469 | 0.005158 | 0.005158 | 0.99876 | -0.012036 | 0.99876 | -0.011965 | 2.3445
32 | 12.4535 | 4.4869 | -12.4524 | -4.4841 | 0.0010841 | 0.0028007 | 0.3826 | 0.3826 | 0.3826 | 0.99876 | -0.012036 | 0.99861 | -0.022318 | 29.6586
33 | -12.6273 | -4.4997 | 12.6287 | 4.4928 | 0.0014313 | -0.006967 | 0.38702 | 0.38694 | 0.38702 | 0.99988 | -0.0011933 | 1 | 0 | 30.3305
34 | 12.1103 | 4.3187 | -12.1084 | -4.3138 | 0.001919 | 0.0049457 | 0.37167 | 0.37168 | 0.37168 | 0.99861 | -0.022318 | 0.99834 | -0.04111 | 28.8121
35 | 0.1118 | 0.05391 | -0.1118 | -0.054069 | 3.0961e-06 | -0.00015865 | 0.0035881 | 0.0035901 | 0.0035901 | 0.99861 | -0.022318 | 0.99858 | -0.022502 | 1.7096
36 | 4.6202 | 1.4959 | -4.619 | -1.5419 | 0.0011478 | -0.046017 | 0.1407 | 0.14112 | 0.14112 | 0.99636 | -0.074095 | 0.9961 | -0.077105 | 11.0598
37 | 3.0487 | 1.3171 | -3.0484 | -1.3441 | 0.00031227 | -0.026966 | 0.096221 | 0.096536 | 0.096536 | 0.99636 | -0.074095 | 0.99625 | -0.074719 | 7.5655
38 | -7.8295 | -2.8903 | 7.8335 | 2.8367 | 0.0040383 | -0.053653 | 0.24181 | 0.24125 | 0.24181 | 0.99636 | -0.074095 | 0.99691 | -0.068949 | 18.9504
39 | 0.1606 | 0.077336 | -0.1606 | -0.077783 | 6.7216e-07 | -0.00044675 | 0.0051645 | 0.0051701 | 0.0051701 | 0.99636 | -0.074095 | 0.99636 | -0.074059 | 2.35
40 | 0.36067 | 0.17415 | -0.36066 | -0.17468 | 3.9904e-06 | -0.00052411 | 0.011607 | 0.011614 | 0.011614 | 0.9961 | -0.077105 | 0.99609 | -0.077009 | 5.2789
41 | 4.2584 | 1.3678 | -4.2566 | -1.4527 | 0.0018004 | -0.084914 | 0.12962 | 0.1304 | 0.1304 | 0.9961 | -0.077105 | 0.99565 | -0.082168 | 10.2196
42 | 0.25603 | 0.12321 | -0.25603 | -0.124 | 3.0105e-06 | -0.00078652 | 0.0082331 | 0.008243 | 0.008243 | 0.99625 | -0.074719 | 0.99624 | -0.074617 | 3.7468
43 | 2.7924 | 1.2208 | -2.7923 | -1.2208 | 0.0001015 | 7.2878e-05 | 0.088308 | 0.08831 | 0.08831 | 0.99625 | -0.074719 | 0.99619 | -0.078656 | 6.8457
44 | 0.36811 | 0.17697 | -0.3681 | -0.17828 | 1.0346e-05 | -0.0013097 | 0.011827 | 0.011844 | 0.011844 | 0.99691 | -0.068949 | 0.99688 | -0.068706 | 5.3835
45 | 3.3214 | 1.044 | -3.321 | -1.0778 | 0.00043156 | -0.033799 | 0.10095 | 0.10125 | 0.10125 | 0.99565 | -0.082168 | 0.99551 | -0.083814 | 7.9346
46 | 0.32731 | 0.1575 | -0.3273 | -0.15852 | 6.4059e-06 | -0.0010209 | 0.010531 | 0.010544 | 0.010544 | 0.99565 | -0.082168 | 0.99563 | -0.081998 | 4.7928
47 | 0.60784 | 0.25112 | -0.60784 | -0.25995 | 7.8048e-06 | -0.0088308 | 0.019068 | 0.019168 | 0.019168 | 0.99565 | -0.082168 | 0.99563 | -0.082479 | 2.2765
48 | 2.7923 | 1.2208 | -2.792 | -1.2486 | 0.00027096 | -0.027786 | 0.08831 | 0.088637 | 0.088637 | 0.99619 | -0.078656 | 0.99609 | -0.079219 | 6.9465
49 | -12.1043 | -4.3221 | 12.106 | 4.3264 | 0.001668 | 0.0042994 | 0.37181 | 0.37181 | 0.37181 | 0.99789 | -0.059508 | 0.99813 | -0.043181 | 28.8229
50 | 9.2436 | 4.1449 | -9.2067 | -4.0523 | 0.036903 | 0.092602 | 0.29244 | 0.29252 | 0.29252 | 1 | 0 | 0.99269 | -0.42969 | 22.6757
51 | 0.54328 | 0.19429 | -0.54325 | -0.24215 | 3.3173e-05 | -0.047864 | 0.016707 | 0.017223 | 0.017223 | 0.99696 | -0.068189 | 0.99689 | -0.069744 | 2.0455
52 | 0.20686 | 0.10001 | -0.20686 | -0.10019 | 5.0016e-07 | -0.00017254 | 0.0066532 | 0.0066554 | 0.0066554 | 0.99696 | -0.068189 | 0.99695 | -0.068436 | 0.51592
53 | 0.57076 | 0.2336 | -0.57074 | -0.25771 | 1.8825e-05 | -0.024113 | 0.017857 | 0.018133 | 0.018133 | 0.99696 | -0.068189 | 0.99692 | -0.068966 | 2.1536
54 | 0.54325 | 0.24215 | -0.54325 | -0.24512 | 2.1305e-06 | -0.0029718 | 0.017223 | 0.017259 | 0.017259 | 0.99689 | -0.069744 | 0.99688 | -0.069832 | 2.0497
55 | 0.34649 | 0.16767 | -0.34649 | -0.16781 | 9.9634e-07 | -0.00014222 | 0.011146 | 0.011148 | 0.011148 | 0.99692 | -0.068966 | 0.99692 | -0.068941 | 5.0673
56 | 0.22424 | 0.090043 | -0.22424 | -0.10454 | 3.5954e-06 | -0.0145 | 0.0069973 | 0.0071644 | 0.0071644 | 0.99692 | -0.068966 | 0.9969 | -0.069066 | 1.1229
57 | 0.39626 | 0.19161 | -0.39626 | -0.19192 | 2.8251e-06 | -0.00030814 | 0.012746 | 0.01275 | 0.01275 | 0.99688 | -0.065798 | 0.99687 | -0.065736 | 5.7953
58 | 0.10266 | 0.04607 | -0.10266 | -0.049606 | 2.1403e-06 | -0.0035358 | 0.0032585 | 0.0033017 | 0.0033017 | 0.9969 | -0.069066 | 0.99688 | -0.0689 | 1.5008
59 | 0.12158 | 0.058473 | -0.12158 | -0.058882 | 3.5179e-07 | -0.00040908 | 0.0039065 | 0.0039117 | 0.0039117 | 0.9969 | -0.069066 | 0.9969 | -0.069041 | 1.778
60 | 0.10266 | 0.049606 | -0.10266 | -0.049722 | 7.1261e-08 | -0.0001161 | 0.0033017 | 0.0033032 | 0.0033032 | 0.99688 | -0.0689 | 0.99688 | -0.068894 | 1.5015
61 | 0.12645 | 0.054516 | -0.12645 | -0.055097 | 5.209e-07 | -0.00058112 | 0.0039876 | 0.0039942 | 0.0039942 | 0.99688 | -0.069832 | 0.99688 | -0.069805 | 1.8156
62 | 0.16231 | 0.067357 | -0.16231 | -0.068723 | 8.5495e-08 | -0.0013657 | 0.0050889 | 0.0051042 | 0.0051042 | 0.99688 | -0.069832 | 0.99688 | -0.069845 | 0.6062
63 | 0.33465 | 0.16203 | -0.33465 | -0.16208 | 3.8549e-07 | -5.0261e-05 | 0.010761 | 0.010761 | 0.010761 | 0.99746 | -0.063577 | 0.99746 | -0.063695 | 0.8342
64 | 12.1084 | 4.3138 | -12.106 | -4.3264 | 0.0023925 | -0.012684 | 0.37168 | 0.37181 | 0.37181 | 0.99834 | -0.04111 | 0.99813 | -0.043181 | 29.139
65 | 0.1118 | 0.054069 | -0.1118 | -0.054148 | 5.7465e-08 | -7.948e-05 | 0.0035901 | 0.0035911 | 0.0035911 | 0.99858 | -0.022502 | 0.99858 | -0.022498 | 1.6323
66 | 0.60784 | 0.25995 | -0.60783 | -0.26309 | 2.7918e-06 | -0.0031364 | 0.019168 | 0.019204 | 0.019204 | 0.99563 | -0.082479 | 0.99563 | -0.082587 | 2.2807
67 | 0.33991 | 0.13333 | -0.33991 | -0.13596 | 7.1489e-07 | -0.0026323 | 0.010586 | 0.010615 | 0.010615 | 0.99563 | -0.082587 | 0.99562 | -0.082641 | 1.2606
68 | 0.1551 | 0.074742 | -0.15509 | -0.075116 | 5.2619e-07 | -0.00037368 | 0.0049924 | 0.0049971 | 0.0049971 | 0.99551 | -0.083814 | 0.9955 | -0.083784 | 2.2714
69 | 3.1659 | 1.0031 | -3.1658 | -1.0091 | 6.9181e-05 | -0.0059706 | 0.096301 | 0.096354 | 0.096354 | 0.99551 | -0.083814 | 0.99548 | -0.084093 | 7.5513
70 | 2.792 | 1.2486 | -2.792 | -1.2512 | 2.6079e-05 | -0.0026631 | 0.088637 | 0.088669 | 0.088669 | 0.99609 | -0.079219 | 0.99608 | -0.07927 | 6.949
71 | 8.9132 | 3.9101 | -8.9131 | -3.9107 | 5.4497e-05 | -0.00051455 | 0.28304 | 0.28304 | 0.28304 | 0.99269 | -0.42969 | 0.99269 | -0.42972 | 22.1822
72 | 0.33991 | 0.13596 | -0.33991 | -0.14118 | 1.4293e-06 | -0.005221 | 0.010615 | 0.010672 | 0.010672 | 0.99562 | -0.082641 | 0.99562 | -0.082747 | 1.2674
73 | 0.32248 | 0.1242 | -0.32247 | -0.15536 | 7.8247e-06 | -0.031157 | 0.010021 | 0.01038 | 0.01038 | 0.99548 | -0.084093 | 0.99546 | -0.08466 | 1.2328
74 | 2.7254 | 0.83797 | -2.7249 | -0.89085 | 0.00045326 | -0.052879 | 0.082683 | 0.083149 | 0.083149 | 0.99548 | -0.084093 | 0.99531 | -0.086222 | 6.5164
75 | 0.11794 | 0.046909 | -0.11794 | -0.057121 | 3.4485e-07 | -0.010211 | 0.0036807 | 0.0038001 | 0.0038001 | 0.99548 | -0.084093 | 0.99548 | -0.08416 | 0.45132
76 | 0.32247 | 0.15536 | -0.32247 | -0.15618 | 2.1482e-07 | -0.00082369 | 0.01038 | 0.01039 | 0.01039 | 0.99546 | -0.08466 | 0.99546 | -0.084673 | 1.234
77 | 0.35455 | 0.16983 | -0.35455 | -0.17172 | 3.487e-06 | -0.0018808 | 0.011402 | 0.011426 | 0.011426 | 0.99531 | -0.086222 | 0.9953 | -0.086334 | 3.1563
78 | 2.3704 | 0.72101 | -2.3697 | -0.82204 | 0.00065805 | -0.10103 | 0.07186 | 0.07277 | 0.07277 | 0.99531 | -0.086222 | 0.99501 | -0.089639 | 5.703
79 | 0.49179 | 0.046196 | -0.49177 | -0.12485 | 2.0488e-05 | -0.07865 | 0.014331 | 0.014721 | 0.014721 | 0.99501 | -0.089639 | 0.99497 | -0.090541 | 1.1536
80 | 0.24596 | 0.0059931 | -0.24596 | -0.037385 | 2.0009e-06 | -0.031392 | 0.0071382 | 0.0072181 | 0.0072181 | 0.99497 | -0.090541 | 0.99496 | -0.090761 | 0.56568
81 | 0.24581 | 0.11885 | -0.24581 | -0.11905 | 1.7426e-06 | -0.00019709 | 0.0079217 | 0.0079242 | 0.0079242 | 0.99497 | -0.090541 | 0.99496 | -0.090858 | 0.96637
82 | 0.073892 | 0.030497 | -0.073891 | -0.035787 | 7.0664e-08 | -0.00529 | 0.0023193 | 0.0023821 | 0.0023821 | 0.99496 | -0.090761 | 0.99496 | -0.090782 | 0.28291
83 | 0.17206 | 0.0068881 | -0.17206 | -0.083191 | 2.5237e-06 | -0.076303 | 0.0049962 | 0.0055451 | 0.0055451 | 0.99496 | -0.090761 | 0.99494 | -0.090998 | 0.43457
84 | 0.17206 | 0.083191 | -0.17206 | -0.083333 | 2.8721e-07 | -0.00014239 | 0.0055451 | 0.005547 | 0.005547 | 0.99494 | -0.090998 | 0.99494 | -0.091168 | 0.43
85 | 0.2223 | 0.10686 | -0.2223 | -0.10766 | 2.3441e-06 | -0.00080779 | 0.0071578 | 0.007168 | 0.007168 | 0.99472 | -0.090812 | 0.99471 | -0.090721 | 3.2582
86 | 0.8435 | 0.38481 | -0.84347 | -0.38484 | 2.9301e-05 | -2.7676e-05 | 0.027154 | 0.027155 | 0.027155 | 0.98565 | -0.7799 | 0.9856 | -0.78153 | 6.6231
87 | -1.1495 | -0.53299 | 1.1497 | 0.53085 | 0.00025996 | -0.0021453 | 0.037108 | 0.037073 | 0.037108 | 0.98565 | -0.7799 | 0.98606 | -0.75614 | 2.8766
88 | 0.096206 | 0.037999 | -0.096201 | -0.046559 | 4.6686e-06 | -0.0085599 | 0.0030296 | 0.0031304 | 0.0031304 | 0.9856 | -0.78153 | 0.98555 | -0.7812 | 1.4229
89 | 0.74726 | 0.34684 | -0.74717 | -0.35771 | 9.2825e-05 | -0.010869 | 0.02413 | 0.024266 | 0.024266 | 0.9856 | -0.78153 | 0.98546 | -0.78302 | 6.7034
90 | 0.44832 | 0.20843 | -0.44827 | -0.21013 | 5.3062e-05 | -0.0017089 | 0.014474 | 0.014496 | 0.014496 | 0.98606 | -0.75614 | 0.9859 | -0.7616 | 1.7678
91 | -1.699 | -0.78816 | 1.6993 | 0.78733 | 0.00035707 | -0.0008298 | 0.05483 | 0.054808 | 0.05483 | 0.98606 | -0.75614 | 0.98644 | -0.73408 | 4.2504
92 | 0.096201 | 0.046559 | -0.0962 | -0.046592 | 5.0743e-07 | -3.3377e-05 | 0.0031304 | 0.0031309 | 0.0031309 | 0.98555 | -0.7812 | 0.98555 | -0.78123 | 1.4909
93 | 0.47367 | 0.22768 | -0.47365 | -0.2294 | 2.3553e-05 | -0.0017165 | 0.015395 | 0.015417 | 0.015417 | 0.98546 | -0.78302 | 0.98542 | -0.78259 | 7.0078
94 | 0.2735 | 0.13003 | -0.2735 | -0.13225 | 2.5454e-06 | -0.0022221 | 0.0088711 | 0.0088992 | 0.0088992 | 0.98546 | -0.78302 | 0.98545 | -0.78312 | 2.4584
95 | 0.10477 | 0.050533 | -0.10477 | -0.050743 | 1.8565e-06 | -0.00021026 | 0.0034075 | 0.0034102 | 0.0034102 | 0.98545 | -0.78312 | 0.98543 | -0.78367 | 0.97435
96 | -0.40623 | -0.19675 | 0.40625 | 0.1955 | 1.2402e-05 | -0.0012461 | 0.013179 | 0.013164 | 0.013179 | 0.98866 | -0.54428 | 0.98869 | -0.54454 | 5.9906
97 | 0.3448 | 0.14669 | -0.34474 | -0.1547 | 5.5446e-05 | -0.008012 | 0.010941 | 0.011035 | 0.011035 | 0.98869 | -0.54454 | 0.98853 | -0.54346 | 5.0157
98 | -1.3793 | -0.60405 | 1.3803 | 0.59585 | 0.00093419 | -0.0081963 | 0.043966 | 0.043867 | 0.043966 | 0.98869 | -0.54454 | 0.98932 | -0.54905 | 19.9845
99 | 0.62828 | 0.26186 | -0.62773 | -0.28563 | 0.00054879 | -0.023776 | 0.019874 | 0.020153 | 0.020153 | 0.98869 | -0.54454 | 0.98787 | -0.53868 | 9.1606
100 | 0.1559 | 0.063426 | -0.15588 | -0.075431 | 1.7069e-05 | -0.012005 | 0.004915 | 0.0050576 | 0.0050576 | 0.98853 | -0.54346 | 0.98843 | -0.54268 | 2.2989
101 | 0.18884 | 0.091278 | -0.18884 | -0.091461 | 3.9292e-07 | -0.00018285 | 0.0061251 | 0.0061274 | 0.0061274 | 0.98853 | -0.54346 | 0.98853 | -0.54344 | 2.7852
102 | -1.3803 | -0.59585 | 1.3803 | 0.59552 | 3.7997e-05 | -0.00033441 | 0.043867 | 0.043863 | 0.043867 | 0.98932 | -0.54905 | 0.98935 | -0.54923 | 19.9397
103 | 0.41823 | 0.18513 | -0.41809 | -0.1988 | 0.00014208 | -0.013666 | 0.013365 | 0.013533 | 0.013533 | 0.98787 | -0.53868 | 0.98755 | -0.53607 | 6.1512
104 | 0.2095 | 0.1005 | -0.2095 | -0.10146 | 2.5537e-06 | -0.00096426 | 0.0067899 | 0.0068022 | 0.0068022 | 0.98787 | -0.53868 | 0.98785 | -0.53858 | 3.0919
105 | 0.15588 | 0.075431 | -0.15588 | -0.075497 | 2.6266e-06 | -6.5561e-05 | 0.0050576 | 0.0050585 | 0.0050585 | 0.98843 | -0.54268 | 0.98841 | -0.54279 | 2.4088
106 | -1.6869 | -0.74404 | 1.687 | 0.74388 | 2.6407e-05 | -0.0001519 | 0.053797 | 0.053795 | 0.053797 | 0.98935 | -0.54923 | 0.98936 | -0.54934 | 24.4532
107 | 0.26927 | 0.12676 | -0.26926 | -0.13005 | 1.4377e-05 | -0.0032933 | 0.0086997 | 0.0087412 | 0.0087412 | 0.98755 | -0.53607 | 0.9875 | -0.53562 | 3.9733
108 | 0.14882 | 0.072042 | -0.14882 | -0.072075 | 1.1938e-06 | -3.2646e-05 | 0.0048331 | 0.0048335 | 0.0048335 | 0.98755 | -0.53607 | 0.98754 | -0.53613 | 2.3017
109 | 0.26926 | 0.13005 | -0.26926 | -0.13041 | 1.561e-06 | -0.00035565 | 0.0087412 | 0.0087457 | 0.0087457 | 0.9875 | -0.53562 | 0.9875 | -0.53557 | 3.9753
110 | 2.579 | 1.0722 | -2.5786 | -1.1186 | 0.00039468 | -0.046398 | 0.081661 | 0.082193 | 0.082193 | 0.98735 | -0.70451 | 0.98719 | -0.70554 | 6.4415
111 | -2.579 | -1.0722 | 2.579 | 1.0699 | 1.9335e-05 | -0.0022889 | 0.081661 | 0.081635 | 0.081661 | 0.98735 | -0.70451 | 0.98736 | -0.70446 | 6.3997
112 | 2.2598 | 0.96417 | -2.2591 | -1.0561 | 0.0006102 | -0.091945 | 0.071844 | 0.072945 | 0.072945 | 0.98719 | -0.70554 | 0.98691 | -0.70703 | 5.7167
113 | 0.31887 | 0.15441 | -0.31887 | -0.15443 | 4.9533e-06 | -2.703e-05 | 0.01036 | 0.010361 | 0.010361 | 0.98719 | -0.70554 | 0.98717 | -0.70564 | 4.9336
114 | -2.7431 | -1.1493 | 2.7433 | 1.1495 | 0.00023801 | 0.00016466 | 0.086956 | 0.086951 | 0.086956 | 0.98736 | -0.70446 | 0.98751 | -0.69486 | 6.7408
115 | 1.9081 | 0.88623 | -1.9076 | -0.88686 | 0.00049233 | -0.00063555 | 0.061538 | 0.061563 | 0.061563 | 0.98691 | -0.70703 | 0.98644 | -0.73408 | 4.7723
116 | 0.35106 | 0.16989 | -0.35106 | -0.17002 | 1.009e-06 | -0.00013474 | 0.011408 | 0.01141 | 0.01141 | 0.98691 | -0.70703 | 0.98691 | -0.70701 | 5.1861
117 | -0.39481 | -0.19122 | 0.39481 | 0.19112 | 8.967e-07 | -9.5737e-05 | 0.012794 | 0.012793 | 0.012794 | 0.98982 | -0.55239 | 0.98982 | -0.55241 | 5.8154
118 | -0.39481 | -0.19112 | 0.39489 | 0.18326 | 7.3069e-05 | -0.0078645 | 0.012793 | 0.012694 | 0.012793 | 0.98982 | -0.55241 | 0.98999 | -0.55394 | 5.8148
119 | 1.6881 | 0.73733 | -1.687 | -0.74388 | 0.0011362 | -0.0065507 | 0.053714 | 0.053795 | 0.053795 | 0.98999 | -0.55394 | 0.98936 | -0.54934 | 24.4524
120 | 0.19627 | 0.093155 | -0.19626 | -0.095054 | 4.3662e-06 | -0.0018986 | 0.0063349 | 0.0063589 | 0.0063589 | 0.98999 | -0.55394 | 0.98997 | -0.55375 | 2.8904
121 | -7.6949 | -3.3709 | 7.6978 | 3.3778 | 0.0028277 | 0.0068881 | 0.24496 | 0.24496 | 0.24496 | 0.98999 | -0.55394 | 0.99066 | -0.5142 | 18.9895
122 | 5.0707 | 2.1903 | -5.0688 | -2.1862 | 0.0019502 | 0.0041039 | 0.16106 | 0.16108 | 0.16108 | 0.98999 | -0.55394 | 0.9893 | -0.59588 | 12.4865
123 | 0.34497 | 0.16688 | -0.34494 | -0.16706 | 3.8509e-05 | -0.00017834 | 0.011174 | 0.011177 | 0.011177 | 0.98999 | -0.55394 | 0.98988 | -0.55468 | 5.3224
124 | 0.21056 | 0.10007 | -0.21055 | -0.10196 | 5.072e-06 | -0.0018921 | 0.0068189 | 0.0068428 | 0.0068428 | 0.98694 | -0.66103 | 0.98691 | -0.66082 | 3.1104
125 | 0.41216 | 0.18573 | -0.41202 | -0.19952 | 0.00014057 | -0.013782 | 0.013223 | 0.013394 | 0.013394 | 0.98694 | -0.66103 | 0.98662 | -0.65829 | 6.0883
126 | -0.9168 | -0.42809 | 0.91792 | 0.40597 | 0.0011173 | -0.022123 | 0.029595 | 0.029324 | 0.029595 | 0.98694 | -0.66103 | 0.98807 | -0.67017 | 13.4524
127 | 0.29408 | 0.14229 | -0.29408 | -0.14243 | 7.4008e-07 | -0.00014095 | 0.0095557 | 0.0095574 | 0.0095574 | 0.98694 | -0.66103 | 0.98693 | -0.66101 | 4.3443
128 | 0.21055 | 0.10196 | -0.21055 | -0.10197 | 1.2901e-06 | -1.7173e-05 | 0.0068428 | 0.006843 | 0.006843 | 0.98691 | -0.66082 | 0.98691 | -0.66086 | 3.2586
129 | 0.41202 | 0.19952 | -0.41201 | -0.19955 | 9.7761e-06 | -2.9415e-05 | 0.013394 | 0.013395 | 0.013395 | 0.98662 | -0.65829 | 0.9866 | -0.65845 | 6.3785
130 | -4.0647 | -1.7038 | 4.0649 | 1.7041 | 0.00018502 | 0.00032879 | 0.12877 | 0.12876 | 0.12877 | 0.98807 | -0.67017 | 0.98815 | -0.66513 | 9.9818
131 | 3.1468 | 1.2978 | -3.1461 | -1.297 | 0.00066092 | 0.00076732 | 0.099449 | 0.099461 | 0.099461 | 0.98807 | -0.67017 | 0.98769 | -0.69358 | 7.7101
132 | -4.3634 | -1.8487 | 4.365 | 1.8518 | 0.0016401 | 0.0031151 | 0.13844 | 0.13843 | 0.13844 | 0.98815 | -0.66513 | 0.98882 | -0.62379 | 10.7318
133 | 2.9183 | 1.1867 | -2.9181 | -1.2014 | 0.00015799 | -0.01467 | 0.092075 | 0.092239 | 0.092239 | 0.98769 | -0.69358 | 0.98764 | -0.69399 | 7.2287
134 | -7.9188 | -3.484 | 7.9204 | 3.4639 | 0.0016714 | -0.020077 | 0.2521 | 0.25185 | 0.2521 | 0.99066 | -0.5142 | 0.99088 | -0.51294 | 19.7568
135 | 0.221 | 0.10615 | -0.221 | -0.10703 | 2.5896e-06 | -0.00088838 | 0.0071442 | 0.0071555 | 0.0071555 | 0.99066 | -0.5142 | 0.99065 | -0.5141 | 3.2525
136 | 4.6713 | 1.9981 | -4.6701 | -1.9958 | 0.0011838 | 0.0023673 | 0.14825 | 0.14826 | 0.14826 | 0.9893 | -0.59588 | 0.98884 | -0.62365 | 11.4932
137 | 0.096167 | 0.042149 | -0.096167 | -0.042983 | 4.4849e-07 | -0.00083349 | 0.0030638 | 0.0030737 | 0.0030737 | 0.9893 | -0.59588 | 0.9893 | -0.59585 | 1.3971
138 | 0.45355 | 0.2134 | -0.45352 | -0.21349 | 3.563e-05 | -8.7904e-05 | 0.014592 | 0.014594 | 0.014594 | 0.99161 | -0.43667 | 0.99152 | -0.43724 | 6.9494
139 | -0.45355 | -0.2134 | 0.45367 | 0.21313 | 0.00011049 | -0.00027285 | 0.014592 | 0.014588 | 0.014592 | 0.99161 | -0.43667 | 0.99186 | -0.43488 | 6.9487
140 | 0.21282 | 0.096911 | -0.21282 | -0.097109 | 5.2151e-07 | -0.00019761 | 0.0068082 | 0.0068106 | 0.0068106 | 0.99152 | -0.43724 | 0.99152 | -0.43723 | 3.0957
141 | -0.45367 | -0.21313 | 0.45382 | 0.21274 | 0.00015825 | -0.00039145 | 0.014588 | 0.014582 | 0.014588 | 0.99186 | -0.43488 | 0.99223 | -0.43231 | 6.9467
142 | 0.21282 | 0.097109 | -0.2128 | -0.10304 | 1.5822e-05 | -0.0059292 | 0.0068106 | 0.0068841 | 0.0068841 | 0.99152 | -0.43723 | 0.99145 | -0.43662 | 3.1291
143 | 0.2128 | 0.10304 | -0.2128 | -0.10306 | 1.9024e-06 | -2.5246e-05 | 0.0068841 | 0.0068844 | 0.0068844 | 0.99145 | -0.43662 | 0.99144 | -0.43668 | 3.2783
144 | 0.075492 | 0.035227 | -0.075491 | -0.035329 | 3.4867e-08 | -0.00010201 | 0.0024379 | 0.0024392 | 0.0024392 | 0.98644 | -0.73408 | 0.98644 | -0.73408 | 1.1087
145 | 0.075491 | 0.035329 | -0.07548 | -0.036557 | 1.1341e-05 | -0.0012277 | 0.0024392 | 0.0024547 | 0.0024547 | 0.98644 | -0.73408 | 0.98628 | -0.73513 | 1.1689
146 | -2.9178 | -1.234 | 2.9178 | 1.2335 | 5.8578e-06 | -0.00053847 | 0.092608 | 0.092602 | 0.092608 | 0.98751 | -0.69486 | 0.98751 | -0.69484 | 7.2577
147 | -2.9178 | -1.2335 | 2.9181 | 1.2014 | 0.00034779 | -0.032105 | 0.092602 | 0.092239 | 0.092602 | 0.98751 | -0.69484 | 0.98764 | -0.69399 | 7.2572
148 | -8.4543 | -3.7324 | 8.4553 | 3.735 | 0.0010712 | 0.0026548 | 0.26893 | 0.26893 | 0.26893 | 0.992 | -0.44596 | 0.99223 | -0.43231 | 20.8473
149 | 8.1246 | 3.5727 | -8.1196 | -3.5603 | 0.0050334 | 0.012387 | 0.25828 | 0.25829 | 0.25829 | 0.992 | -0.44596 | 0.99088 | -0.51294 | 20.0226
150 | -8.9092 | -3.9477 | 8.9131 | 3.9107 | 0.0039364 | -0.037083 | 0.28351 | 0.28304 | 0.28351 | 0.99223 | -0.43231 | 0.99269 | -0.42972 | 22.2183
151 | 0.19914 | 0.096413 | -0.19914 | -0.096449 | 2.3784e-06 | -3.6165e-05 | 0.0064459 | 0.0064464 | 0.0064464 | 0.99088 | -0.51294 | 0.99086 | -0.51302 | 3.0697
152 | -0.096165 | -0.046575 | 0.096165 | 0.045537 | 5.7388e-07 | -0.0010375 | 0.0031179 | 0.0031048 | 0.0031179 | 0.98928 | -0.59569 | 0.98928 | -0.59574 | 1.4172
153 | -0.096165 | -0.045537 | 0.096167 | 0.042983 | 1.3929e-06 | -0.0025546 | 0.0031048 | 0.0030737 | 0.0031048 | 0.98928 | -0.59574 | 0.9893 | -0.59585 | 1.4113
154 | 4.3651 | 1.8481 | -4.365 | -1.8518 | 9.0887e-05 | -0.0037222 | 0.13838 | 0.13843 | 0.13843 | 0.98884 | -0.62365 | 0.98882 | -0.62379 | 10.8484
155 | 0.23503 | 0.10686 | -0.23502 | -0.10711 | 8.4969e-07 | -0.00025811 | 0.0075595 | 0.0075627 | 0.0075627 | 0.9859 | -0.7616 | 0.98589 | -0.76157 | 3.4376
156 | -0.235 | -0.11374 | 0.23502 | 0.10711 | 2.2069e-05 | -0.0066287 | 0.0076453 | 0.0075627 | 0.0076453 | 0.98581 | -0.76081 | 0.98589 | -0.76157 | 3.4751
157 | 0.235 | 0.11374 | -0.235 | -0.11381 | 6.6822e-06 | -7.0245e-05 | 0.0076453 | 0.0076463 | 0.0076463 | 0.98581 | -0.76081 | 0.98578 | -0.761 | 3.6411
158 | 0.12645 | 0.055097 | -0.12645 | -0.061054 | 5.4429e-06 | -0.0059562 | 0.0039942 | 0.0040662 | 0.0040662 | 0.99688 | -0.069805 | 0.99684 | -0.069474 | 1.8483
159 | 0.16231 | 0.068723 | -0.16231 | -0.078586 | 6.334e-07 | -0.0098636 | 0.0051042 | 0.0052222 | 0.0052222 | 0.99688 | -0.069845 | 0.99688 | -0.069931 | 0.62021
160 | -0.15831 | -0.076674 | 0.15831 | 0.076591 | 1.2201e-07 | -8.3271e-05 | 0.0050981 | 0.005097 | 0.0050981 | 0.99603 | -0.080679 | 0.99604 | -0.080686 | 2.3173
161 | -0.15831 | -0.076591 | 0.15831 | 0.068785 | 9.8638e-07 | -0.0078057 | 0.005097 | 0.0050026 | 0.005097 | 0.99604 | -0.080686 | 0.99604 | -0.080655 | 0.79891
162 | 0.082506 | 0.038637 | -0.082506 | -0.03886 | 3.8181e-09 | -0.00022285 | 0.0026404 | 0.0026432 | 0.0026432 | 0.99604 | -0.080655 | 0.99604 | -0.080656 | 0.31392
163 | 0.082474 | 0.039511 | -0.082474 | -0.039944 | 4.3269e-08 | -0.00043302 | 0.0026504 | 0.0026559 | 0.0026559 | 0.99604 | -0.080655 | 0.99604 | -0.080661 | 0.73366
164 | -0.32329 | -0.14693 | 0.3233 | 0.13682 | 2.5563e-06 | -0.010111 | 0.010292 | 0.010174 | 0.010292 | 0.99604 | -0.080655 | 0.99605 | -0.080473 | 1.2223
165 | 2.1266 | 0.95076 | -2.1264 | -0.97474 | 0.00013649 | -0.023985 | 0.067511 | 0.067799 | 0.067799 | 0.99605 | -0.080473 | 0.99598 | -0.08081 | 5.3134
166 | -2.4499 | -1.0876 | 2.4499 | 1.0855 | 1.5435e-05 | -0.0020559 | 0.077684 | 0.077659 | 0.077684 | 0.99605 | -0.080473 | 0.99606 | -0.080437 | 6.0881
167 | 1.917 | 0.87694 | -1.9169 | -0.89698 | 9.3359e-05 | -0.020044 | 0.061099 | 0.061344 | 0.061344 | 0.99598 | -0.08081 | 0.99593 | -0.081041 | 4.8075
168 | 0.20944 | 0.097801 | -0.20944 | -0.10144 | 3.9664e-07 | -0.0036351 | 0.0066996 | 0.0067448 | 0.0067448 | 0.99598 | -0.08081 | 0.99598 | -0.080849 | 0.80105
169 | -2.7133 | -1.2131 | 2.7133 | 1.2131 | 2.9575e-05 | 1.828e-05 | 0.086138 | 0.086138 | 0.086138 | 0.99606 | -0.080437 | 0.99608 | -0.07927 | 6.6774
170 | 1.5664 | 0.74162 | -1.5664 | -0.74744 | 3.5689e-05 | -0.0058151 | 0.050235 | 0.050308 | 0.050308 | 0.99593 | -0.081041 | 0.99591 | -0.081512 | 5.9748
171 | 0.35046 | 0.15536 | -0.35046 | -0.16961 | 2.2154e-06 | -0.014255 | 0.011112 | 0.011285 | 0.011285 | 0.99593 | -0.081041 | 0.99593 | -0.08107 | 0.88443
172 | 0.35046 | 0.16961 | -0.35046 | -0.16973 | 1.0075e-06 | -0.00011879 | 0.011285 | 0.011287 | 0.011287 | 0.99593 | -0.08107 | 0.99592 | -0.081365 | 0.87495
173 | 0.24443 | 0.11385 | -0.24443 | -0.11619 | 3.4714e-07 | -0.0023442 | 0.0078159 | 0.0078448 | 0.0078448 | 0.99591 | -0.081512 | 0.99591 | -0.081542 | 0.93169
174 | 0.52463 | 0.24742 | -0.52463 | -0.25409 | 4.5778e-06 | -0.0066685 | 0.016813 | 0.016897 | 0.016897 | 0.99591 | -0.081512 | 0.9959 | -0.081691 | 2.0067
175 | 0.082506 | 0.03886 | -0.082506 | -0.03996 | 1.8661e-08 | -0.0010996 | 0.0026432 | 0.0026569 | 0.0026569 | 0.99604 | -0.080656 | 0.99604 | -0.080661 | 0.31555
176 | 0.24443 | 0.11619 | -0.24443 | -0.11738 | 1.7596e-07 | -0.0011817 | 0.0078448 | 0.0078596 | 0.0078596 | 0.99591 | -0.081542 | 0.9959 | -0.081557 | 0.93344
177 | -0.41481 | -0.2009 | 0.41481 | 0.19571 | 2.2394e-06 | -0.0051883 | 0.013379 | 0.013314 | 0.013379 | 0.99444 | -0.12069 | 0.99444 | -0.12058 | 1.589
178 | 0.24443 | 0.11738 | -0.24443 | -0.11838 | 3.0861e-07 | -0.0010058 | 0.0078596 | 0.0078722 | 0.0078722 | 0.9959 | -0.081557 | 0.9959 | -0.081562 | 1.2339
179 | -0.24442 | -0.11838 | 0.24443 | 0.11689 | 5.1949e-06 | -0.0014872 | 0.0078746 | 0.0078559 | 0.0078746 | 0.9956 | -0.082564 | 0.99562 | -0.082747 | 3.5794
180 | 0.095476 | 0.024287 | -0.095476 | -0.041302 | 3.5226e-07 | -0.017015 | 0.0028564 | 0.0030162 | 0.0030162 | 0.99562 | -0.082747 | 0.99561 | -0.082855 | 0.35822
181 | 0.095476 | 0.041302 | -0.095476 | -0.046241 | 1.1067e-07 | -0.004939 | 0.0030162 | 0.0030759 | 0.0030759 | 0.99561 | -0.082855 | 0.99561 | -0.082881 | 0.36531
182 | -0.12644 | -0.06124 | 0.12645 | 0.061054 | 1.7364e-07 | -0.00018649 | 0.0040686 | 0.0040662 | 0.0040686 | 0.99684 | -0.069462 | 0.99684 | -0.069474 | 1.8494
183 | 0.16231 | 0.078586 | -0.16231 | -0.078612 | 9.9061e-08 | -2.6076e-05 | 0.0052222 | 0.0052225 | 0.0052225 | 0.99688 | -0.069931 | 0.99688 | -0.069958 | 0.63689

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 22.0997 | 8.7515

## res_load
| p_mw | q_mvar
0 | 0.37428 | 0.18127
1 | 0.27281 | 0.13213
2 | 0.19267 | 0.093316
3 | 0.40065 | 0.19405
4 | 0.31641 | 0.15324
5 | 0.12472 | 0.060403
6 | 0.29745 | 0.14406
7 | 0.26127 | 0.12654
8 | 0.17821 | 0.086312
9 | 0.16061 | 0.077787
10 | 0.23025 | 0.11151
11 | 0.1606 | 0.077783
12 | 0.36066 | 0.17468
13 | 0.25603 | 0.124
14 | 0.3681 | 0.17828
15 | 0.29786 | 0.14426
16 | 0.21338 | 0.10335
17 | 0.20686 | 0.10019
18 | 0.39626 | 0.19192
19 | 0.12158 | 0.058882
20 | 0.10266 | 0.049722
21 | 0.34649 | 0.16781
22 | 0.25448 | 0.12325
23 | 0.085948 | 0.041627
24 | 0.2789 | 0.13508
25 | 0.33465 | 0.16208
26 | 0.26792 | 0.12976
27 | 0.3273 | 0.15852
28 | 0.29353 | 0.14216
29 | 0.11794 | 0.057121
30 | 0.15509 | 0.075116
31 | 0.32247 | 0.15618
32 | 0.35455 | 0.17172
33 | 0.24581 | 0.11905
34 | 0.17206 | 0.083333
35 | 0.073891 | 0.035787
36 | 0.2223 | 0.10766
37 | 0.30596 | 0.14818
38 | 0.10095 | 0.048892
39 | 0.0962 | 0.046592
40 | 0.47365 | 0.2294
41 | 0.16872 | 0.081717
42 | 0.40623 | 0.19675
43 | 0.18884 | 0.091461
44 | 0.30664 | 0.14851
45 | 0.2095 | 0.10146
46 | 0.14882 | 0.072075
47 | 0.26926 | 0.13041
48 | 0.16406 | 0.079459
49 | 0.31887 | 0.15443
50 | 0.15588 | 0.075497
51 | 0.39481 | 0.19122
52 | 0.29408 | 0.14243
53 | 0.21055 | 0.10197
54 | 0.41201 | 0.19955
55 | 0.2985 | 0.14457
56 | 0.22786 | 0.11036
57 | 0.19626 | 0.095054
58 | 0.30134 | 0.14594
59 | 0.34494 | 0.16706
60 | 0.2407 | 0.11658
61 | 0.2128 | 0.10306
62 | 0.13276 | 0.064299
63 | 0.07548 | 0.036557
64 | 0.35106 | 0.17002
65 | 0.17443 | 0.084479
66 | 0.32964 | 0.15965
67 | 0.096165 | 0.046575
68 | 0.221 | 0.10703
69 | 0.19914 | 0.096449
70 | 0.30494 | 0.14769
71 | 0.21324 | 0.10328
72 | 0.235 | 0.11381
73 | 0.10477 | 0.050743
74 | 0.15831 | 0.076674
75 | 0.26344 | 0.12759
76 | 0.20944 | 0.10144
77 | 0.35046 | 0.16973
78 | 0.79734 | 0.38617
79 | 0.082474 | 0.039944
80 | 0.07865 | 0.038092
81 | 0.52463 | 0.25409
82 | 0.082506 | 0.03996
83 | 0.41481 | 0.2009
84 | 0.1118 | 0.054148
85 | 0.24443 | 0.11838
86 | 0.24442 | 0.11838
87 | 0.095476 | 0.046241
88 | 0.12644 | 0.06124
89 | 0.16231 | 0.078612

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1