## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_375_1_node_15 | 20 | n |  | TRUE
1 | bus_MV_375_1_node_16 | 20 | n |  | TRUE
2 | bus_MV_375_1_node_17 | 20 | n |  | TRUE
3 | bus_MV_375_1_node_37 | 20 | n |  | TRUE
4 | bus_MV_375_1_node_86 | 20 | n |  | TRUE
5 | bus_MV_375_1_node_36 | 20 | n |  | TRUE
6 | bus_MV_375_1_node_19 | 20 | n |  | TRUE
7 | bus_MV_375_1_node_20 | 20 | n |  | TRUE
8 | bus_MV_375_1_node_24 | 20 | n |  | TRUE
9 | bus_MV_375_1_node_21 | 20 | n |  | TRUE
10 | bus_MV_375_1_node_90 | 20 | n |  | TRUE
11 | bus_MV_375_1_node_23 | 20 | n |  | TRUE
12 | bus_MV_375_1_node_22 | 20 | n |  | TRUE
13 | bus_MV_375_1_node_25 | 20 | n |  | TRUE
14 | bus_MV_375_1_node_91 | 20 | n |  | TRUE
15 | bus_MV_375_1_node_46 | 20 | n |  | TRUE
16 | bus_MV_375_1_node_26 | 20 | n |  | TRUE
17 | bus_MV_375_1_node_27 | 20 | n |  | TRUE
18 | bus_MV_375_1_node_45 | 20 | n |  | TRUE
19 | bus_MV_375_1_node_88 | 20 | n |  | TRUE
20 | bus_MV_375_1_node_87 | 20 | n |  | TRUE
21 | bus_MV_375_1_node_47 | 20 | n |  | TRUE
22 | bus_MV_375_1_node_94 | 20 | n |  | TRUE
23 | bus_MV_375_1_node_49 | 20 | n |  | TRUE
24 | bus_MV_375_1_node_54 | 20 | n |  | TRUE
25 | bus_MV_375_1_node_50 | 20 | n |  | TRUE
26 | bus_MV_375_1_node_51 | 20 | n |  | TRUE
27 | bus_MV_375_1_node_53 | 20 | n |  | TRUE
28 | bus_MV_375_1_node_55 | 20 | n |  | TRUE
29 | bus_MV_375_1_node_41 | 20 | n |  | TRUE
30 | bus_MV_375_1_node_28 | 20 | n |  | TRUE
31 | bus_MV_375_1_node_30 | 20 | n |  | TRUE
32 | bus_MV_375_1_node_99 | 20 | n |  | TRUE
33 | bus_MV_375_1_node_33 | 20 | n |  | TRUE
34 | bus_MV_375_1_node_31 | 20 | n |  | TRUE
35 | bus_MV_375_1_node_32 | 20 | n |  | TRUE
36 | bus_MV_375_1_node_48 | 20 | n |  | TRUE
37 | bus_MV_375_1_node_66 | 20 | n |  | TRUE
38 | bus_MV_375_1_node_34 | 20 | n |  | TRUE
39 | bus_MV_375_1_node_92 | 20 | n |  | TRUE
40 | bus_MV_375_1_node_93 | 20 | n |  | TRUE
41 | bus_MV_375_1_node_61 | 20 | n |  | TRUE
42 | bus_MV_375_1_node_62 | 20 | n |  | TRUE
43 | bus_MV_375_1_node_38 | 20 | n |  | TRUE
44 | bus_MV_375_1_node_39 | 20 | n |  | TRUE
45 | bus_MV_375_1_node_42 | 20 | n |  | TRUE
46 | bus_MV_375_1_node_43 | 20 | n |  | TRUE
47 | bus_MV_375_1_node_44 | 20 | n |  | TRUE
48 | bus_MV_375_1_node_65 | 20 | n |  | TRUE
49 | bus_HV_375_1_node_43 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_375_1_load_15 | 0 | 0.17423 | 0.084382 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_375_1_load_86 | 4 | 0.076424 | 0.037014 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_375_1_load_36 | 5 | 0.25277 | 0.12242 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_375_1_load_19 | 6 | 0.1422 | 0.068872 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_375_1_load_90 | 10 | 0.39411 | 0.19088 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_375_1_load_91 | 14 | 0.34821 | 0.16864 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_375_1_load_46 | 15 | 0.12928 | 0.062615 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_375_1_load_26 | 16 | 0.17122 | 0.082923 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_375_1_load_45 | 18 | 0.23219 | 0.11246 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_375_1_load_88 | 19 | 0.12355 | 0.05984 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_375_1_load_87 | 20 | 0.08468 | 0.041012 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_375_1_load_94 | 22 | 0.38157 | 0.1848 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_375_1_load_50 | 25 | 0.34656 | 0.16785 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_375_1_load_53 | 27 | 0.31256 | 0.15138 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_375_1_load_55 | 28 | 0.21606 | 0.10464 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_375_1_load_28 | 30 | 0.26476 | 0.12823 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_375_1_load_99 | 32 | 0.16397 | 0.079416 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_375_1_load_48 | 36 | 0.16264 | 0.078772 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_375_1_load_34 | 38 | 0.054036 | 0.026171 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_375_1_load_93 | 40 | 0.17282 | 0.083698 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_375_1_load_61 | 41 | 0.18146 | 0.087886 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_375_1_load_38 | 43 | 0.2398 | 0.11614 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_375_1_load_42 | 45 | 0.39046 | 0.18911 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_375_1_load_65 | 48 | 0.16512 | 0.079971 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 46 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_375_1_line_0 |  | 0 | 1 | 0.049049 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_375_1_line_1 |  | 1 | 2 | 0.60374 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_375_1_line_2 |  | 2 | 3 | 0.70339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_375_1_line_3 |  | 2 | 4 | 0.026854 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_375_1_line_4 |  | 3 | 5 | 0.058976 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_375_1_line_5 |  | 5 | 23 | 1.8576 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_375_1_line_6 |  | 6 | 7 | 0.035735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_375_1_line_7 |  | 7 | 8 | 0.49654 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_375_1_line_8 |  | 8 | 16 | 0.07082 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_375_1_line_9 |  | 8 | 9 | 0.31458 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_375_1_line_10 |  | 9 | 10 | 0.00832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_375_1_line_11 |  | 9 | 11 | 0.85167 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_375_1_line_12 |  | 11 | 15 | 0.042017 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_375_1_line_13 |  | 11 | 12 | 0.42098 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_375_1_line_14 |  | 12 | 13 | 0.54111 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_375_1_line_15 |  | 12 | 14 | 0.06395 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_375_1_line_16 |  | 13 | 17 | 0.28483 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_375_1_line_17 |  | 13 | 18 | 0.052003 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_375_1_line_18 |  | 13 | 19 | 0.23315 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_375_1_line_19 |  | 16 | 24 | 1.1429 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_375_1_line_20 |  | 17 | 20 | 0.03691 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_375_1_line_21 |  | 19 | 35 | 0.023616 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_375_1_line_22 |  | 20 | 29 | 0.026146 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_375_1_line_23 |  | 21 | 22 | 0.064307 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
24 | MV_375_1_line_24 |  | 21 | 23 | 0.58127 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
25 | MV_375_1_line_25 |  | 22 | 47 | 0.075792 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
26 | MV_375_1_line_26 |  | 23 | 36 | 0.038384 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_375_1_line_27 |  | 24 | 28 | 0.65219 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_375_1_line_28 |  | 24 | 27 | 0.13333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_375_1_line_29 |  | 25 | 26 | 0.069143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_375_1_line_30 |  | 26 | 27 | 0.49083 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_375_1_line_31 |  | 29 | 44 | 0.76136 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_375_1_line_32 |  | 30 | 31 | 0.015181 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_375_1_line_33 |  | 30 | 32 | 0.50678 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_375_1_line_34 |  | 31 | 33 | 0.34835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_375_1_line_35 |  | 32 | 37 | 1.4764 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_375_1_line_36 |  | 32 | 34 | 0.043985 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_375_1_line_37 |  | 33 | 36 | 0.081963 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_375_1_line_38 |  | 34 | 35 | 0.35928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_375_1_line_39 |  | 37 | 48 | 0.13864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_375_1_line_40 |  | 38 | 39 | 0.70373 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_375_1_line_41 |  | 39 | 40 | 0.031044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_375_1_line_42 |  | 40 | 41 | 2.5344 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_375_1_line_43 |  | 41 | 42 | 0.15022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_375_1_line_44 |  | 42 | 48 | 1.0272 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_375_1_line_45 |  | 43 | 44 | 0.099781 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_375_1_line_46 |  | 45 | 46 | 0.058852 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_375_1_line_47 |  | 46 | 47 | 0.62697 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_375_1_trafo_43 | 25 MVA 110/20 kV | 49 | 46 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2576852.8213 | 1187320.9329
1 | 2576898.4794 | 1187303.0132
2 | 2576964.4572 | 1187722.3898
3 | 2577072.7154 | 1188153.8666
4 | 2576939.6048 | 1187716.7051
5 | 2577048.4444 | 1188207.5438
6 | 2576694.6444 | 1190836.2173
7 | 2576717.2599 | 1190863.9325
8 | 2576772.8319 | 1191145.0761
9 | 2576523.2079 | 1191249.9095
10 | 2576515.2615 | 1191247.3728
11 | 2576272.7131 | 1190869.588
12 | 2576014.5792 | 1191061.9785
13 | 2575951.3723 | 1190806.175
14 | 2575972.2298 | 1191109.8967
15 | 2576236.7168 | 1190847.9149
16 | 2576809.6093 | 1191205.5984
17 | 2575886.6549 | 1191035.8028
18 | 2575990.3681 | 1190795.9013
19 | 2575810.0057 | 1190620.7684
20 | 2575851.616 | 1191047.4041
21 | 2576468.25 | 1190298.6435
22 | 2576406.0987 | 1190281.5022
23 | 2576250.3999 | 1189884.9657
24 | 2577761.2193 | 1191838.4864
25 | 2578180.5653 | 1191373.9677
26 | 2578172.2621 | 1191442.3677
27 | 2577894.0674 | 1191846.7411
28 | 2577273.7028 | 1192271.7075
29 | 2575837.2974 | 1191026.72
30 | 2575944.2988 | 1190060.4522
31 | 2575952.842 | 1190047.8889
32 | 2575568.0501 | 1190399.9619
33 | 2576133.8433 | 1189856.6493
34 | 2575562.9527 | 1190443.6504
35 | 2575788.6879 | 1190610.6072
36 | 2576212.8043 | 1189877.6869
37 | 2574302.4659 | 1189639.7101
38 | 2572965.5077 | 1192983.9603
39 | 2572315.7894 | 1192713.5851
40 | 2572325.0727 | 1192683.9595
41 | 2573237.6852 | 1190319.6202
42 | 2573279.9952 | 1190178.0329
43 | 2575184.3507 | 1191391.7402
44 | 2575283.8267 | 1191399.5312
45 | 2576137.9461 | 1190462.3763
46 | 2576114.2427 | 1190516.2442
47 | 2576334.0231 | 1190257.6974
48 | 2574209.9237 | 1189741.6747
49 | 2576114.2427 | 1190516.2442

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99451 | -0.055972 | 0.17423 | 0.084382
1 | 0.99452 | -0.055867 | 0 | 0
2 | 0.99466 | -0.05686 | 0 | 0
3 | 0.99488 | -0.057938 | 0 | 0
4 | 0.99465 | -0.056836 | 0.076424 | 0.037014
5 | 0.99489 | -0.057994 | 0.25277 | 0.12242
6 | 0.9835 | -0.012954 | 0.1422 | 0.068872
7 | 0.98351 | -0.013016 | 0 | 0
8 | 0.9836 | -0.013674 | 0 | 0
9 | 0.98408 | -0.017827 | 0 | 0
10 | 0.98408 | -0.017786 | 0.39411 | 0.19088
11 | 0.98582 | -0.032417 | 0 | 0
12 | 0.98674 | -0.039845 | 0 | 0
13 | 0.98817 | -0.051284 | 0 | 0
14 | 0.9867 | -0.040122 | 0.34821 | 0.16864
15 | 0.98581 | -0.032352 | 0.12928 | 0.062615
16 | 0.98345 | -0.014646 | 0.17122 | 0.082923
17 | 0.98806 | -0.050573 | 0 | 0
18 | 0.98816 | -0.051138 | 0.23219 | 0.11246
19 | 0.98935 | -0.041704 | 0.12355 | 0.05984
20 | 0.98804 | -0.050471 | 0.08468 | 0.041012
21 | 0.99804 | -0.02421 | 0 | 0
22 | 0.99819 | -0.022321 | 0.38157 | 0.1848
23 | 0.99665 | -0.041165 | 0 | 0
24 | 0.98149 | -0.027838 | 0 | 0
25 | 0.98101 | -0.0287 | 0.34656 | 0.16785
26 | 0.98104 | -0.028995 | 0 | 0
27 | 0.98137 | -0.026778 | 0.31256 | 0.15138
28 | 0.98121 | -0.029627 | 0.21606 | 0.10464
29 | 0.98803 | -0.050425 | 0 | 0
30 | 0.99433 | -0.022998 | 0.26476 | 0.12823
31 | 0.9944 | -0.023573 | 0 | 0
32 | 0.99093 | -0.050101 | 0.16397 | 0.079416
33 | 0.99607 | -0.036631 | 0 | 0
34 | 0.99069 | -0.052008 | 0 | 0
35 | 0.98943 | -0.042347 | 0 | 0
36 | 0.99646 | -0.03967 | 0.16264 | 0.078772
37 | 0.98929 | -0.062245 | 0 | 0
38 | 0.9871 | -0.074897 | 0.054036 | 0.026171
39 | 0.98717 | -0.0744 | 0 | 0
40 | 0.98717 | -0.074419 | 0.17282 | 0.083698
41 | 0.98829 | -0.066631 | 0.18146 | 0.087886
42 | 0.98837 | -0.067322 | 0 | 0
43 | 0.98775 | -0.048931 | 0.2398 | 0.11614
44 | 0.9878 | -0.048634 | 0 | 0
45 | 0.99996 | -0.00027787 | 0.39046 | 0.18911
46 | 1 | 0 | -5.2502 | -2.3342
47 | 0.99838 | -0.019928 | 0 | 0
48 | 0.98918 | -0.061369 | 0.16512 | 0.079971
49 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.17423 | -0.084382 | 0.17423 | 0.084325 | 2.759e-06 | -5.6186e-05 | 0.0056192 | 0.0056185 | 0.0056192 | 0.99451 | -0.055972 | 0.99452 | -0.055867 | 2.6758
1 | -0.17423 | -0.084325 | 0.17425 | 0.070073 | 2.4661e-05 | -0.014252 | 0.0056185 | 0.0054509 | 0.0056185 | 0.99452 | -0.055867 | 0.99466 | -0.05686 | 2.5538
2 | -0.25068 | -0.10645 | 0.25073 | 0.089851 | 5.7322e-05 | -0.016602 | 0.0079041 | 0.0077284 | 0.0079041 | 0.99466 | -0.05686 | 0.99488 | -0.057938 | 3.5928
3 | 0.076424 | 0.036379 | -0.076424 | -0.037014 | 2.1704e-07 | -0.00063428 | 0.0024565 | 0.0024645 | 0.0024645 | 0.99466 | -0.05686 | 0.99465 | -0.056836 | 1.1202
4 | -0.25073 | -0.089851 | 0.25074 | 0.088459 | 4.6943e-06 | -0.0013924 | 0.0077284 | 0.0077149 | 0.0077284 | 0.99488 | -0.057938 | 0.99489 | -0.057994 | 3.5129
5 | -0.50351 | -0.21088 | 0.50434 | 0.2092 | 0.00082904 | -0.0016796 | 0.015839 | 0.015815 | 0.015839 | 0.99489 | -0.057994 | 0.99665 | -0.041165 | 7.5425
6 | -0.1422 | -0.068872 | 0.1422 | 0.068047 | 1.0237e-06 | -0.00082499 | 0.0046377 | 0.0046272 | 0.0046377 | 0.9835 | -0.012954 | 0.98351 | -0.013016 | 2.108
7 | -0.1422 | -0.068047 | 0.14222 | 0.056583 | 1.3766e-05 | -0.011465 | 0.0046272 | 0.0044922 | 0.0046272 | 0.98351 | -0.013016 | 0.9836 | -0.013674 | 2.1033
8 | 1.0485 | 0.50069 | -1.0483 | -0.50068 | 0.00014673 | 1.0123e-05 | 0.0341 | 0.034101 | 0.034101 | 0.9836 | -0.013674 | 0.98345 | -0.014646 | 16.2386
9 | -1.1907 | -0.55727 | 1.1913 | 0.55019 | 0.00062372 | -0.0070851 | 0.038583 | 0.038493 | 0.038583 | 0.9836 | -0.013674 | 0.98408 | -0.017827 | 17.5378
10 | 0.39411 | 0.19068 | -0.39411 | -0.19088 | 1.8324e-06 | -0.00019183 | 0.012843 | 0.012846 | 0.012846 | 0.98408 | -0.017827 | 0.98408 | -0.017786 | 5.8389
11 | -1.5854 | -0.74087 | 1.5884 | 0.72203 | 0.002982 | -0.018842 | 0.051335 | 0.051093 | 0.051335 | 0.98408 | -0.017827 | 0.98582 | -0.032417 | 23.334
12 | 0.12929 | 0.061641 | -0.12928 | -0.062615 | 9.8962e-07 | -0.00097465 | 0.0041941 | 0.0042065 | 0.0042065 | 0.98582 | -0.032417 | 0.98581 | -0.032352 | 1.912
13 | -1.7177 | -0.78367 | 1.7194 | 0.7744 | 0.0017141 | -0.0092689 | 0.055286 | 0.055168 | 0.055286 | 0.98582 | -0.032417 | 0.98674 | -0.039845 | 25.1301
14 | -2.0676 | -0.94298 | 2.0708 | 0.93133 | 0.0031856 | -0.011653 | 0.066483 | 0.066331 | 0.066483 | 0.98674 | -0.039845 | 0.98817 | -0.051284 | 30.2195
15 | 0.34822 | 0.16858 | -0.34821 | -0.16864 | 1.4597e-05 | -6.5186e-05 | 0.011318 | 0.011319 | 0.011319 | 0.98674 | -0.039845 | 0.9867 | -0.040122 | 5.3901
16 | 0.3246 | 0.13122 | -0.32456 | -0.13785 | 4.0065e-05 | -0.006628 | 0.010228 | 0.010302 | 0.010302 | 0.98817 | -0.051284 | 0.98806 | -0.050573 | 4.6829
17 | 0.2322 | 0.11125 | -0.23219 | -0.11246 | 3.9355e-06 | -0.0012112 | 0.0075215 | 0.0075369 | 0.0075369 | 0.98817 | -0.051284 | 0.98816 | -0.051138 | 3.4259
18 | -2.6276 | -1.1738 | 2.6305 | 1.1754 | 0.002936 | 0.0015669 | 0.084071 | 0.084068 | 0.084071 | 0.98817 | -0.051284 | 0.98935 | -0.041704 | 40.0338
19 | 0.8771 | 0.41776 | -0.87545 | -0.41804 | 0.0016569 | -0.00027913 | 0.028517 | 0.028534 | 0.028534 | 0.98345 | -0.014646 | 0.98149 | -0.027838 | 13.5874
20 | 0.32456 | 0.13785 | -0.32455 | -0.13871 | 5.2349e-06 | -0.00085876 | 0.010302 | 0.010312 | 0.010312 | 0.98806 | -0.050573 | 0.98804 | -0.050471 | 4.6874
21 | -2.7541 | -1.2352 | 2.7543 | 1.2347 | 0.00024452 | -0.00047942 | 0.088072 | 0.088065 | 0.088072 | 0.98935 | -0.041704 | 0.98943 | -0.042347 | 40.0326
22 | 0.23987 | 0.097699 | -0.23987 | -0.098307 | 2.0006e-06 | -0.00060882 | 0.0075674 | 0.0075741 | 0.0075741 | 0.98804 | -0.050471 | 0.98803 | -0.050425 | 3.4428
23 | -4.4556 | -1.9699 | 4.4562 | 1.9681 | 0.0006166 | -0.0017497 | 0.14091 | 0.14088 | 0.14091 | 0.99804 | -0.02421 | 0.99819 | -0.022321 | 38.9251
24 | 4.4556 | 1.9699 | -4.45 | -1.9857 | 0.0055837 | -0.015778 | 0.14091 | 0.14114 | 0.14114 | 0.99804 | -0.02421 | 0.99665 | -0.041165 | 38.9895
25 | -4.8378 | -2.1529 | 4.8386 | 2.151 | 0.00085831 | -0.0019675 | 0.15314 | 0.15311 | 0.15314 | 0.99819 | -0.022321 | 0.99838 | -0.019928 | 42.3031
26 | 3.9457 | 1.7765 | -3.9449 | -1.7771 | 0.00080502 | -0.00067137 | 0.12533 | 0.12534 | 0.12534 | 0.99665 | -0.041165 | 0.99646 | -0.03967 | 56.9747
27 | 0.21612 | 0.10393 | -0.21606 | -0.10464 | 5.7886e-05 | -0.00071356 | 0.0070532 | 0.0070628 | 0.0070628 | 0.98149 | -0.027838 | 0.98121 | -0.029627 | 3.3632
28 | 0.65933 | 0.31411 | -0.65925 | -0.31715 | 8.2278e-05 | -0.0030419 | 0.02148 | 0.021519 | 0.021519 | 0.98149 | -0.027838 | 0.98137 | -0.026778 | 9.7815
29 | -0.34656 | -0.16785 | 0.34657 | 0.16626 | 1.183e-05 | -0.0015853 | 0.011331 | 0.011311 | 0.011331 | 0.98101 | -0.0287 | 0.98104 | -0.028995 | 5.1505
30 | -0.34657 | -0.16626 | 0.34668 | 0.16577 | 0.00011181 | -0.0004941 | 0.011311 | 0.011304 | 0.011311 | 0.98104 | -0.028995 | 0.98137 | -0.026778 | 5.3861
31 | 0.23987 | 0.098307 | -0.23981 | -0.11603 | 5.989e-05 | -0.017724 | 0.0075741 | 0.0077855 | 0.0077855 | 0.98803 | -0.050425 | 0.9878 | -0.048634 | 3.5389
32 | -3.7736 | -1.7064 | 3.7739 | 1.7061 | 0.00029298 | -0.00027148 | 0.12024 | 0.12023 | 0.12024 | 0.99433 | -0.022998 | 0.9944 | -0.023573 | 54.653
33 | 3.5089 | 1.5781 | -3.4976 | -1.5717 | 0.011266 | 0.0064608 | 0.1117 | 0.11171 | 0.11171 | 0.99433 | -0.022998 | 0.99093 | -0.050101 | 53.1936
34 | -3.7739 | -1.7061 | 3.7807 | 1.6998 | 0.0067171 | -0.0062456 | 0.12023 | 0.12013 | 0.12023 | 0.9944 | -0.023573 | 0.99607 | -0.036631 | 54.6511
35 | 0.57499 | 0.26451 | -0.57409 | -0.26567 | 0.00089526 | -0.001167 | 0.018438 | 0.018459 | 0.018459 | 0.99093 | -0.050101 | 0.98929 | -0.062245 | 8.79
36 | 2.7587 | 1.2277 | -2.7581 | -1.2274 | 0.00060639 | 0.00032828 | 0.087964 | 0.087965 | 0.087965 | 0.99093 | -0.050101 | 0.99069 | -0.052008 | 41.8881
37 | -3.7807 | -1.6998 | 3.7822 | 1.6984 | 0.0015789 | -0.001474 | 0.12013 | 0.12011 | 0.12013 | 0.99607 | -0.036631 | 0.99646 | -0.03967 | 54.6064
38 | 2.7581 | 1.2274 | -2.7543 | -1.2347 | 0.0037156 | -0.0073064 | 0.087965 | 0.088065 | 0.088065 | 0.99069 | -0.052008 | 0.98943 | -0.042347 | 40.0296
39 | 0.57409 | 0.26567 | -0.57403 | -0.26889 | 6.3202e-05 | -0.0032206 | 0.018459 | 0.018499 | 0.018499 | 0.98929 | -0.062245 | 0.98918 | -0.061369 | 8.4086
40 | -0.054036 | -0.026171 | 0.054039 | 0.025354 | 3.8428e-06 | -0.00081623 | 0.0017558 | 0.0017455 | 0.0017558 | 0.9871 | -0.074897 | 0.98717 | -0.0744 | 0.83612
41 | -0.054039 | -0.025354 | 0.054039 | 0.024632 | 1.2563e-07 | -0.00072228 | 0.0017455 | 0.0017367 | 0.0017455 | 0.98717 | -0.0744 | 0.98717 | -0.074419 | 0.79343
42 | -0.22686 | -0.10833 | 0.2271 | 0.10553 | 0.0002428 | -0.0027997 | 0.0073514 | 0.0073146 | 0.0073514 | 0.98717 | -0.074419 | 0.98829 | -0.066631 | 3.5007
43 | -0.40856 | -0.19342 | 0.40859 | 0.18992 | 3.4846e-05 | -0.0034931 | 0.013204 | 0.01316 | 0.013204 | 0.98829 | -0.066631 | 0.98837 | -0.067322 | 6.0016
44 | -0.40859 | -0.18992 | 0.40891 | 0.18892 | 0.00031661 | -0.0010006 | 0.01316 | 0.013145 | 0.01316 | 0.98837 | -0.067322 | 0.98918 | -0.061369 | 6.2667
45 | -0.2398 | -0.11614 | 0.23981 | 0.11603 | 1.0778e-05 | -0.00010947 | 0.007787 | 0.0077855 | 0.007787 | 0.98775 | -0.048931 | 0.9878 | -0.048634 | 3.7081
46 | -0.39046 | -0.18911 | 0.39047 | 0.18905 | 1.6447e-05 | -5.9953e-05 | 0.012524 | 0.012524 | 0.012524 | 0.99996 | -0.00027787 | 1 | 0 | 5.964
47 | 4.8457 | 2.1346 | -4.8386 | -2.151 | 0.0070871 | -0.016324 | 0.15286 | 0.15311 | 0.15311 | 1 | 0 | 0.99838 | -0.019928 | 42.2947

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 5.2502 | 2.3342

## res_load
| p_mw | q_mvar
0 | 0.17423 | 0.084382
1 | 0.076424 | 0.037014
2 | 0.25277 | 0.12242
3 | 0.1422 | 0.068872
4 | 0.39411 | 0.19088
5 | 0.34821 | 0.16864
6 | 0.12928 | 0.062615
7 | 0.17122 | 0.082923
8 | 0.23219 | 0.11246
9 | 0.12355 | 0.05984
10 | 0.08468 | 0.041012
11 | 0.38157 | 0.1848
12 | 0.34656 | 0.16785
13 | 0.31256 | 0.15138
14 | 0.21606 | 0.10464
15 | 0.26476 | 0.12823
16 | 0.16397 | 0.079416
17 | 0.16264 | 0.078772
18 | 0.054036 | 0.026171
19 | 0.17282 | 0.083698
20 | 0.18146 | 0.087886
21 | 0.2398 | 0.11614
22 | 0.39046 | 0.18911
23 | 0.16512 | 0.079971

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1