## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_381_1_node_4 | 20 | n |  | TRUE
1 | bus_MV_381_1_node_186 | 20 | n |  | TRUE
2 | bus_MV_381_1_node_8 | 20 | n |  | TRUE
3 | bus_MV_381_1_node_9 | 20 | n |  | TRUE
4 | bus_MV_381_1_node_10 | 20 | n |  | TRUE
5 | bus_MV_381_1_node_11 | 20 | n |  | TRUE
6 | bus_MV_381_1_node_183 | 20 | n |  | TRUE
7 | bus_MV_381_1_node_12 | 20 | n |  | TRUE
8 | bus_MV_381_1_node_140 | 20 | n |  | TRUE
9 | bus_MV_381_1_node_141 | 20 | n |  | TRUE
10 | bus_MV_381_1_node_153 | 20 | n |  | TRUE
11 | bus_MV_381_1_node_142 | 20 | n |  | TRUE
12 | bus_MV_381_1_node_15 | 20 | n |  | TRUE
13 | bus_MV_381_1_node_17 | 20 | n |  | TRUE
14 | bus_MV_381_1_node_16 | 20 | n |  | TRUE
15 | bus_MV_381_1_node_150 | 20 | n |  | TRUE
16 | bus_MV_381_1_node_18 | 20 | n |  | TRUE
17 | bus_MV_381_1_node_21 | 20 | n |  | TRUE
18 | bus_MV_381_1_node_23 | 20 | n |  | TRUE
19 | bus_MV_381_1_node_19 | 20 | n |  | TRUE
20 | bus_MV_381_1_node_20 | 20 | n |  | TRUE
21 | bus_MV_381_1_node_22 | 20 | n |  | TRUE
22 | bus_MV_381_1_node_27 | 20 | n |  | TRUE
23 | bus_MV_381_1_node_159 | 20 | n |  | TRUE
24 | bus_MV_381_1_node_158 | 20 | n |  | TRUE
25 | bus_MV_381_1_node_24 | 20 | n |  | TRUE
26 | bus_MV_381_1_node_25 | 20 | n |  | TRUE
27 | bus_MV_381_1_node_26 | 20 | n |  | TRUE
28 | bus_MV_381_1_node_149 | 20 | n |  | TRUE
29 | bus_MV_381_1_node_151 | 20 | n |  | TRUE
30 | bus_MV_381_1_node_152 | 20 | n |  | TRUE
31 | bus_MV_381_1_node_184 | 20 | n |  | TRUE
32 | bus_MV_381_1_node_185 | 20 | n |  | TRUE
33 | bus_HV_381_1_node_19 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_381_1_load_4 | 0 | 0.06918 | 0.033505 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_381_1_load_8 | 2 | 0.14851 | 0.071927 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_381_1_load_183 | 6 | 0.30279 | 0.14665 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_381_1_load_12 | 7 | 0.1835 | 0.088874 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_381_1_load_140 | 8 | 0.069346 | 0.033586 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_381_1_load_153 | 10 | 0.11599 | 0.056178 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_381_1_load_15 | 12 | 0.35146 | 0.17022 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_381_1_load_16 | 14 | 0.09833 | 0.047623 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_381_1_load_23 | 18 | 0.15663 | 0.075857 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_381_1_load_19 | 19 | 0.30311 | 0.1468 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_381_1_load_27 | 22 | 0.35998 | 0.17434 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_381_1_load_158 | 24 | 0.071891 | 0.034818 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_381_1_load_24 | 25 | 0.1583 | 0.076667 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_381_1_load_149 | 28 | 0.11712 | 0.056726 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_381_1_load_184 | 31 | 0.22412 | 0.10855 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_381_1_load_185 | 32 | 0.122 | 0.059085 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_381_1_line_0 |  | 0 | 1 | 1.2385 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_381_1_line_1 |  | 1 | 32 | 0.12339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_381_1_line_2 |  | 2 | 3 | 0.007853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_381_1_line_3 |  | 3 | 4 | 0.87473 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_381_1_line_4 |  | 3 | 5 | 1.0578 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_381_1_line_5 |  | 4 | 6 | 0.034287 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_381_1_line_6 |  | 5 | 7 | 0.032383 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_381_1_line_7 |  | 6 | 21 | 1.1955 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_381_1_line_8 |  | 8 | 9 | 0.088303 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_381_1_line_9 |  | 8 | 10 | 1.4446 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_381_1_line_10 |  | 9 | 11 | 0.57002 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_381_1_line_11 |  | 10 | 30 | 0.097697 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_381_1_line_12 |  | 11 | 32 | 0.11588 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_381_1_line_13 |  | 12 | 13 | 0.64102 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_381_1_line_14 |  | 13 | 16 | 0.95018 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_381_1_line_15 |  | 13 | 17 | 1.2714 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_381_1_line_16 |  | 13 | 14 | 0.55716 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_381_1_line_17 |  | 14 | 15 | 1.5122 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_381_1_line_18 |  | 15 | 28 | 0.045802 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_381_1_line_19 |  | 16 | 18 | 0.081917 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_381_1_line_20 |  | 17 | 22 | 0.039979 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_381_1_line_21 |  | 17 | 20 | 0.21211 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_381_1_line_22 |  | 19 | 20 | 0.048804 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_381_1_line_23 |  | 20 | 21 | 1.4151 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_381_1_line_24 |  | 21 | 23 | 0.99977 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_381_1_line_25 |  | 21 | 24 | 0.01908 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_381_1_line_26 |  | 22 | 27 | 0.075205 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_381_1_line_27 |  | 23 | 31 | 0.049033 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_381_1_line_28 |  | 25 | 26 | 0.071271 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_381_1_line_29 |  | 26 | 27 | 1.085 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_381_1_line_30 |  | 28 | 29 | 0.050024 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_381_1_line_31 |  | 29 | 30 | 0.25764 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_381_1_trafo_19 | 25 MVA 110/20 kV | 33 | 19 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2586490.6222 | 1203835.0168
1 | 2585280.8491 | 1204100.293
2 | 2584493.7138 | 1199222.3271
3 | 2584490.5886 | 1199215.1202
4 | 2585220.7241 | 1199326.0086
5 | 2583879.4235 | 1199166.6643
6 | 2585254.1205 | 1199318.2437
7 | 2583869.0531 | 1199197.3423
8 | 2584885.2025 | 1203825.3922
9 | 2584806.7507 | 1203834.1082
10 | 2584787.3258 | 1202384.1124
11 | 2585131.0572 | 1203923.414
12 | 2587320.7905 | 1202046.2463
13 | 2586830.7315 | 1201633.0226
14 | 2586436.6744 | 1202026.9121
15 | 2584927.8711 | 1202127.6816
16 | 2587685.4102 | 1201339.0958
17 | 2586558.2395 | 1200391.1507
18 | 2587746.2112 | 1201393.0658
19 | 2586397.2774 | 1200333.2081
20 | 2586404.7259 | 1200284.9761
21 | 2586445.7333 | 1199414.7024
22 | 2586576.0098 | 1200355.7247
23 | 2586443.8344 | 1198886.4004
24 | 2586464.1485 | 1199409.7081
25 | 2587280.7805 | 1199480.4686
26 | 2587256.5384 | 1199547.1898
27 | 2586565.3617 | 1200282.3203
28 | 2584901.9613 | 1202164.3784
29 | 2584863.4759 | 1202196.3604
30 | 2584708.8123 | 1202325.9713
31 | 2586425.7257 | 1198928.6311
32 | 2585223.4436 | 1203993.366
33 | 2586397.2774 | 1200333.2081

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99332 | -0.048613 | 0.06918 | 0.033505
1 | 0.99349 | -0.047486 | 0 | 0
2 | 0.99632 | -0.0074041 | 0.14851 | 0.071927
3 | 0.99633 | -0.0074181 | 0 | 0
4 | 0.99669 | -0.0089152 | 0 | 0
5 | 0.99608 | -0.0059319 | 0 | 0
6 | 0.99671 | -0.0086414 | 0.30279 | 0.14665
7 | 0.99607 | -0.0060044 | 0.1835 | 0.088874
8 | 0.9937 | -0.048255 | 0.069346 | 0.033586
9 | 0.99368 | -0.048158 | 0 | 0
10 | 0.99441 | -0.041055 | 0.11599 | 0.056178
11 | 0.99354 | -0.04725 | 0 | 0
12 | 0.99625 | -0.025565 | 0.35146 | 0.17022
13 | 0.99669 | -0.022802 | 0 | 0
14 | 0.99606 | -0.028361 | 0.09833 | 0.047623
15 | 0.99465 | -0.041506 | 0 | 0
16 | 0.9965 | -0.021815 | 0 | 0
17 | 0.99934 | 0.00053706 | 0 | 0
18 | 0.99648 | -0.021666 | 0.15663 | 0.075857
19 | 1 | 0 | -2.5714 | -1.048
20 | 0.99977 | -0.0023437 | 0 | 0
21 | 0.99813 | 0.0053646 | 0 | 0
22 | 0.99931 | 0.00070916 | 0.35998 | 0.17434
23 | 0.99785 | 0.0072212 | 0 | 0
24 | 0.99813 | 0.0053808 | 0.071891 | 0.034818
25 | 0.99907 | 0.0018914 | 0.1583 | 0.076667
26 | 0.99908 | 0.0017601 | 0 | 0
27 | 0.9993 | 0.00071517 | 0 | 0
28 | 0.99462 | -0.04132 | 0.11712 | 0.056726
29 | 0.9946 | -0.041184 | 0 | 0
30 | 0.99448 | -0.040422 | 0 | 0
31 | 0.99783 | 0.0073514 | 0.22412 | 0.10855
32 | 0.9935 | -0.047566 | 0.122 | 0.059085
33 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.06918 | -0.033505 | 0.069191 | 0.032053 | 1.0921e-05 | -0.0014523 | 0.0022339 | 0.0022157 | 0.0022339 | 0.99332 | -0.048613 | 0.99349 | -0.047486 | 1.0637
1 | -0.069191 | -0.032053 | 0.069192 | 0.029146 | 7.9603e-07 | -0.0029076 | 0.0022157 | 0.0021815 | 0.0022157 | 0.99349 | -0.047486 | 0.9935 | -0.047566 | 1.0071
2 | -0.14851 | -0.071927 | 0.14851 | 0.071741 | 2.3953e-07 | -0.00018605 | 0.004781 | 0.0047787 | 0.004781 | 0.99632 | -0.0074041 | 0.99633 | -0.0074181 | 2.1732
3 | -0.33206 | -0.13553 | 0.33219 | 0.11483 | 0.00012345 | -0.020703 | 0.010392 | 0.01018 | 0.010392 | 0.99633 | -0.0074181 | 0.99669 | -0.0089152 | 4.7235
4 | 0.18355 | 0.063788 | -0.1835 | -0.088837 | 4.6845e-05 | -0.02505 | 0.0056302 | 0.0059086 | 0.0059086 | 0.99633 | -0.0074181 | 0.99608 | -0.0059319 | 2.6857
5 | -0.33219 | -0.11483 | 0.33219 | 0.11479 | 6.3304e-06 | -3.6697e-05 | 0.01018 | 0.010179 | 0.01018 | 0.99669 | -0.0089152 | 0.99671 | -0.0086414 | 4.8475
6 | 0.1835 | 0.088837 | -0.1835 | -0.088874 | 2.0145e-06 | -3.7095e-05 | 0.0059086 | 0.0059091 | 0.0059091 | 0.99608 | -0.0059319 | 0.99607 | -0.0060044 | 2.8138
7 | -0.63499 | -0.26144 | 0.63583 | 0.26055 | 0.00084191 | -0.0008925 | 0.019889 | 0.019873 | 0.019889 | 0.99671 | -0.0086414 | 0.99813 | 0.0053646 | 9.4709
8 | 0.19123 | 0.07259 | -0.19122 | -0.07467 | 4.1773e-06 | -0.0020806 | 0.005942 | 0.0059637 | 0.0059637 | 0.9937 | -0.048255 | 0.99368 | -0.048158 | 2.7108
9 | -0.26057 | -0.10618 | 0.26074 | 0.10458 | 0.00017158 | -0.0015967 | 0.008174 | 0.0081555 | 0.008174 | 0.9937 | -0.048255 | 0.99441 | -0.041055 | 3.8924
10 | 0.19122 | 0.07467 | -0.19119 | -0.088099 | 2.7739e-05 | -0.013428 | 0.0059637 | 0.0061165 | 0.0061165 | 0.99368 | -0.048158 | 0.99354 | -0.04725 | 2.7802
11 | -0.37674 | -0.16076 | 0.37676 | 0.16066 | 2.4608e-05 | -9.9925e-05 | 0.011891 | 0.011889 | 0.011891 | 0.99441 | -0.041055 | 0.99448 | -0.040422 | 5.6622
12 | 0.19119 | 0.088099 | -0.19119 | -0.08823 | 7.7264e-06 | -0.00013171 | 0.0061165 | 0.0061182 | 0.0061182 | 0.99354 | -0.04725 | 0.9935 | -0.047566 | 2.9134
13 | -0.35146 | -0.17022 | 0.35161 | 0.16955 | 0.00014611 | -0.00066834 | 0.011316 | 0.011306 | 0.011316 | 0.99625 | -0.025565 | 0.99669 | -0.022802 | 5.3884
14 | 0.15666 | 0.051393 | -0.15663 | -0.073916 | 3.0294e-05 | -0.022523 | 0.0047753 | 0.0050172 | 0.0050172 | 0.99669 | -0.022802 | 0.9965 | -0.021815 | 2.2806
15 | -1.1016 | -0.4758 | 1.1043 | 0.476 | 0.0027347 | 0.00020115 | 0.034754 | 0.034737 | 0.034754 | 0.99669 | -0.022802 | 0.99934 | 0.00053706 | 16.5495
16 | 0.59329 | 0.25486 | -0.59294 | -0.2553 | 0.00034735 | -0.00044276 | 0.018702 | 0.01871 | 0.01871 | 0.99669 | -0.022802 | 0.99606 | -0.028361 | 8.9093
17 | 0.49461 | 0.20768 | -0.49396 | -0.20906 | 0.00065206 | -0.0013801 | 0.015547 | 0.015567 | 0.015567 | 0.99606 | -0.028361 | 0.99465 | -0.041506 | 7.4129
18 | 0.49396 | 0.20906 | -0.49394 | -0.21013 | 1.4829e-05 | -0.0010775 | 0.015567 | 0.015579 | 0.015579 | 0.99465 | -0.041506 | 0.99462 | -0.04132 | 7.0815
19 | 0.15663 | 0.073916 | -0.15663 | -0.075857 | 2.7661e-06 | -0.0019413 | 0.0050172 | 0.0050415 | 0.0050415 | 0.9965 | -0.021815 | 0.99648 | -0.021666 | 2.2916
20 | 0.51833 | 0.22072 | -0.51831 | -0.22167 | 1.4144e-05 | -0.00094905 | 0.016274 | 0.016285 | 0.016285 | 0.99934 | 0.00053706 | 0.99931 | 0.00070916 | 7.4021
21 | -1.6226 | -0.69672 | 1.6234 | 0.69188 | 0.00073599 | -0.0048416 | 0.05101 | 0.050953 | 0.05101 | 0.99934 | 0.00053706 | 0.99977 | -0.0023437 | 23.1865
22 | 2.5574 | 1.0375 | -2.5568 | -1.0372 | 0.00055191 | 0.00028745 | 0.079669 | 0.07967 | 0.07967 | 1 | 0 | 0.99977 | -0.0023437 | 37.938
23 | 0.93349 | 0.34529 | -0.93191 | -0.37854 | 0.0015791 | -0.033248 | 0.028739 | 0.029091 | 0.029091 | 0.99977 | -0.0023437 | 0.99813 | 0.0053646 | 13.2232
24 | 0.22419 | 0.083629 | -0.22413 | -0.10738 | 6.6301e-05 | -0.023755 | 0.0069205 | 0.0071898 | 0.0071898 | 0.99813 | 0.0053646 | 0.99785 | 0.0072212 | 3.2681
25 | 0.071891 | 0.034364 | -0.071891 | -0.034818 | 1.3562e-07 | -0.00045382 | 0.0023045 | 0.0023102 | 0.0023102 | 0.99813 | 0.0053646 | 0.99813 | 0.0053808 | 1.0501
26 | 0.15834 | 0.047323 | -0.15834 | -0.049116 | 2.2953e-06 | -0.0017924 | 0.0047739 | 0.004789 | 0.004789 | 0.99931 | 0.00070916 | 0.9993 | 0.00071517 | 2.1768
27 | 0.22413 | 0.10738 | -0.22412 | -0.10855 | 3.3906e-06 | -0.0011647 | 0.0071898 | 0.0072044 | 0.0072044 | 0.99785 | 0.0072212 | 0.99783 | 0.0073514 | 3.2747
28 | -0.1583 | -0.076667 | 0.1583 | 0.074969 | 2.4472e-06 | -0.0016978 | 0.0050821 | 0.0050609 | 0.0050821 | 0.99907 | 0.0018914 | 0.99908 | 0.0017601 | 2.3101
29 | -0.1583 | -0.074969 | 0.15834 | 0.049116 | 3.4958e-05 | -0.025854 | 0.0050609 | 0.004789 | 0.0050609 | 0.99908 | 0.0017601 | 0.9993 | 0.00071517 | 2.3004
30 | 0.37682 | 0.15341 | -0.37681 | -0.15459 | 9.322e-06 | -0.0011788 | 0.011808 | 0.011821 | 0.011821 | 0.99462 | -0.04132 | 0.9946 | -0.041184 | 5.3733
31 | 0.37681 | 0.15459 | -0.37676 | -0.16066 | 4.8338e-05 | -0.00607 | 0.011821 | 0.011889 | 0.011889 | 0.9946 | -0.041184 | 0.99448 | -0.040422 | 5.4043

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 2.8745 | 1.1948

## res_load
| p_mw | q_mvar
0 | 0.06918 | 0.033505
1 | 0.14851 | 0.071927
2 | 0.30279 | 0.14665
3 | 0.1835 | 0.088874
4 | 0.069346 | 0.033586
5 | 0.11599 | 0.056178
6 | 0.35146 | 0.17022
7 | 0.09833 | 0.047623
8 | 0.15663 | 0.075857
9 | 0.30311 | 0.1468
10 | 0.35998 | 0.17434
11 | 0.071891 | 0.034818
12 | 0.1583 | 0.076667
13 | 0.11712 | 0.056726
14 | 0.22412 | 0.10855
15 | 0.122 | 0.059085

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1