## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_383_1_node_41 | 20 | n |  | TRUE
1 | bus_MV_383_1_node_42 | 20 | n |  | TRUE
2 | bus_MV_383_1_node_43 | 20 | n |  | TRUE
3 | bus_MV_383_1_node_85 | 20 | n |  | TRUE
4 | bus_MV_383_1_node_45 | 20 | n |  | TRUE
5 | bus_MV_383_1_node_44 | 20 | n |  | TRUE
6 | bus_MV_383_1_node_104 | 20 | n |  | TRUE
7 | bus_MV_383_1_node_79 | 20 | n |  | TRUE
8 | bus_MV_383_1_node_80 | 20 | n |  | TRUE
9 | bus_MV_383_1_node_84 | 20 | n |  | TRUE
10 | bus_MV_383_1_node_78 | 20 | n |  | TRUE
11 | bus_MV_383_1_node_102 | 20 | n |  | TRUE
12 | bus_MV_383_1_node_103 | 20 | n |  | TRUE
13 | bus_MV_383_1_node_110 | 20 | n |  | TRUE
14 | bus_MV_383_1_node_83 | 20 | n |  | TRUE
15 | bus_MV_383_1_node_46 | 20 | n |  | TRUE
16 | bus_MV_383_1_node_48 | 20 | n |  | TRUE
17 | bus_MV_383_1_node_47 | 20 | n |  | TRUE
18 | bus_MV_383_1_node_50 | 20 | n |  | TRUE
19 | bus_MV_383_1_node_49 | 20 | n |  | TRUE
20 | bus_MV_383_1_node_57 | 20 | n |  | TRUE
21 | bus_MV_383_1_node_59 | 20 | n |  | TRUE
22 | bus_MV_383_1_node_51 | 20 | n |  | TRUE
23 | bus_MV_383_1_node_53 | 20 | n |  | TRUE
24 | bus_MV_383_1_node_52 | 20 | n |  | TRUE
25 | bus_MV_383_1_node_56 | 20 | n |  | TRUE
26 | bus_MV_383_1_node_54 | 20 | n |  | TRUE
27 | bus_MV_383_1_node_55 | 20 | n |  | TRUE
28 | bus_MV_383_1_node_96 | 20 | n |  | TRUE
29 | bus_MV_383_1_node_114 | 20 | n |  | TRUE
30 | bus_MV_383_1_node_92 | 20 | n |  | TRUE
31 | bus_MV_383_1_node_97 | 20 | n |  | TRUE
32 | bus_MV_383_1_node_94 | 20 | n |  | TRUE
33 | bus_MV_383_1_node_91 | 20 | n |  | TRUE
34 | bus_MV_383_1_node_62 | 20 | n |  | TRUE
35 | bus_MV_383_1_node_58 | 20 | n |  | TRUE
36 | bus_MV_383_1_node_60 | 20 | n |  | TRUE
37 | bus_MV_383_1_node_61 | 20 | n |  | TRUE
38 | bus_MV_383_1_node_66 | 20 | n |  | TRUE
39 | bus_MV_383_1_node_65 | 20 | n |  | TRUE
40 | bus_MV_383_1_node_67 | 20 | n |  | TRUE
41 | bus_MV_383_1_node_63 | 20 | n |  | TRUE
42 | bus_MV_383_1_node_64 | 20 | n |  | TRUE
43 | bus_MV_383_1_node_111 | 20 | n |  | TRUE
44 | bus_MV_383_1_node_71 | 20 | n |  | TRUE
45 | bus_MV_383_1_node_68 | 20 | n |  | TRUE
46 | bus_MV_383_1_node_69 | 20 | n |  | TRUE
47 | bus_MV_383_1_node_70 | 20 | n |  | TRUE
48 | bus_MV_383_1_node_72 | 20 | n |  | TRUE
49 | bus_MV_383_1_node_93 | 20 | n |  | TRUE
50 | bus_MV_383_1_node_73 | 20 | n |  | TRUE
51 | bus_MV_383_1_node_75 | 20 | n |  | TRUE
52 | bus_MV_383_1_node_76 | 20 | n |  | TRUE
53 | bus_MV_383_1_node_77 | 20 | n |  | TRUE
54 | bus_MV_383_1_node_112 | 20 | n |  | TRUE
55 | bus_MV_383_1_node_99 | 20 | n |  | TRUE
56 | bus_MV_383_1_node_101 | 20 | n |  | TRUE
57 | bus_MV_383_1_node_81 | 20 | n |  | TRUE
58 | bus_MV_383_1_node_82 | 20 | n |  | TRUE
59 | bus_MV_383_1_node_95 | 20 | n |  | TRUE
60 | bus_MV_383_1_node_98 | 20 | n |  | TRUE
61 | bus_HV_383_1_node_75 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_383_1_load_41 | 0 | 0.19424 | 0.094074 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_383_1_load_85 | 3 | 0.092258 | 0.044683 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_383_1_load_44 | 5 | 0.37621 | 0.18221 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_383_1_load_84 | 9 | 0.29426 | 0.14252 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_383_1_load_102 | 11 | 0.14507 | 0.070259 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_383_1_load_110 | 13 | 0.30965 | 0.14997 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_383_1_load_46 | 15 | 0.25798 | 0.12495 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_383_1_load_50 | 18 | 0.085244 | 0.041285 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_383_1_load_57 | 20 | 0.23377 | 0.11322 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_383_1_load_51 | 22 | 0.3091 | 0.1497 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_383_1_load_56 | 25 | 0.07898 | 0.038252 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_383_1_load_114 | 29 | 0.25755 | 0.12474 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_383_1_load_92 | 30 | 0.13218 | 0.064018 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_383_1_load_94 | 32 | 0.39975 | 0.19361 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_383_1_load_58 | 35 | 0.22036 | 0.10673 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_383_1_load_60 | 36 | 0.0689 | 0.03337 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_383_1_load_66 | 38 | 0.38096 | 0.18451 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_383_1_load_63 | 41 | 0.13913 | 0.067383 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_383_1_load_111 | 43 | 0.39997 | 0.19371 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_383_1_load_68 | 45 | 0.28421 | 0.13765 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_383_1_load_93 | 49 | 0.14689 | 0.071143 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_383_1_load_73 | 50 | 0.35003 | 0.16953 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_383_1_load_76 | 52 | 0.051601 | 0.024991 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_383_1_load_112 | 54 | 0.07744 | 0.037506 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_383_1_load_99 | 55 | 0.30045 | 0.14551 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_383_1_load_101 | 56 | 0.07666 | 0.037128 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_383_1_load_81 | 57 | 0.35297 | 0.17095 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_383_1_load_95 | 59 | 0.072151 | 0.034944 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_383_1_load_98 | 60 | 0.069571 | 0.033695 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 51 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_383_1_line_0 |  | 0 | 1 | 0.018155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_383_1_line_1 |  | 1 | 2 | 0.51834 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
2 | MV_383_1_line_2 |  | 1 | 3 | 1.3866 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
3 | MV_383_1_line_3 |  | 2 | 4 | 0.074616 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
4 | MV_383_1_line_4 |  | 3 | 7 | 0.082502 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
5 | MV_383_1_line_5 |  | 4 | 5 | 0.047232 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
6 | MV_383_1_line_6 |  | 5 | 6 | 1.1266 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
7 | MV_383_1_line_7 |  | 6 | 13 | 0.068408 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
8 | MV_383_1_line_8 |  | 7 | 8 | 0.64027 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
9 | MV_383_1_line_9 |  | 8 | 9 | 0.072968 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_383_1_line_10 |  | 8 | 10 | 0.71921 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
11 | MV_383_1_line_11 |  | 10 | 53 | 0.47064 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
12 | MV_383_1_line_12 |  | 11 | 12 | 0.022378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_383_1_line_13 |  | 12 | 13 | 0.10655 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_383_1_line_14 |  | 13 | 14 | 0.11852 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
15 | MV_383_1_line_15 |  | 14 | 54 | 1.6405 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
16 | MV_383_1_line_16 |  | 14 | 58 | 0.42178 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_383_1_line_17 |  | 15 | 16 | 0.14211 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_383_1_line_18 |  | 15 | 17 | 0.16863 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_383_1_line_19 |  | 16 | 18 | 0.0096863 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_383_1_line_20 |  | 17 | 19 | 1.0641 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_383_1_line_21 |  | 19 | 20 | 0.052937 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_383_1_line_22 |  | 20 | 21 | 0.034921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_383_1_line_23 |  | 21 | 34 | 0.15142 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_383_1_line_24 |  | 22 | 23 | 0.055377 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_383_1_line_25 |  | 22 | 24 | 0.045153 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_383_1_line_26 |  | 23 | 25 | 0.034033 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_383_1_line_27 |  | 24 | 26 | 0.26336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_383_1_line_28 |  | 24 | 27 | 0.5834 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_383_1_line_29 |  | 26 | 28 | 0.52598 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_383_1_line_30 |  | 26 | 29 | 0.02336 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_383_1_line_31 |  | 27 | 30 | 0.055219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_383_1_line_32 |  | 28 | 31 | 0.1004 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_383_1_line_33 |  | 28 | 32 | 0.15432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_383_1_line_34 |  | 30 | 33 | 0.0019354 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_383_1_line_35 |  | 31 | 60 | 0.065952 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_383_1_line_36 |  | 32 | 59 | 0.057131 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_383_1_line_37 |  | 33 | 37 | 0.12921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_383_1_line_38 |  | 34 | 38 | 0.05968 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_383_1_line_39 |  | 35 | 36 | 0.015201 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_383_1_line_40 |  | 36 | 37 | 0.027554 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_383_1_line_41 |  | 38 | 39 | 0.01763 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_383_1_line_42 |  | 39 | 40 | 0.15887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_383_1_line_43 |  | 40 | 45 | 0.06799 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_383_1_line_44 |  | 41 | 42 | 0.13359 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_383_1_line_45 |  | 42 | 43 | 0.31622 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_383_1_line_46 |  | 43 | 44 | 0.031338 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_383_1_line_47 |  | 44 | 46 | 0.1766 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_383_1_line_48 |  | 45 | 46 | 0.040517 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_383_1_line_49 |  | 45 | 47 | 0.043283 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_383_1_line_50 |  | 47 | 48 | 0.19646 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_383_1_line_51 |  | 47 | 49 | 0.30936 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_383_1_line_52 |  | 48 | 50 | 0.07749 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_383_1_line_53 |  | 49 | 51 | 0.070871 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_383_1_line_54 |  | 51 | 52 | 1.4479 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
55 | MV_383_1_line_55 |  | 52 | 53 | 0.006278 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
56 | MV_383_1_line_56 |  | 54 | 55 | 0.9773 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
57 | MV_383_1_line_57 |  | 54 | 56 | 0.26776 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_383_1_line_58 |  | 55 | 59 | 0.054774 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
59 | MV_383_1_line_59 |  | 57 | 58 | 0.031098 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_383_1_trafo_75 | 25 MVA 110/20 kV | 61 | 51 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2679040.1228 | 1272204.5199
1 | 2679027.6078 | 1272217.6724
2 | 2679328.3698 | 1272185.7009
3 | 2679574.0331 | 1273492.0363
4 | 2679386.4251 | 1272232.5742
5 | 2679416.0689 | 1272196.7773
6 | 2680409.4877 | 1272728.2138
7 | 2679655.7899 | 1273493.9401
8 | 2680079.4576 | 1273225.2086
9 | 2680142.0876 | 1273262.9666
10 | 2680404.1346 | 1273361.1305
11 | 2680498.0758 | 1272713.1769
12 | 2680502.3105 | 1272735.1506
13 | 2680415.1172 | 1272796.39
14 | 2680424.2995 | 1272914.5549
15 | 2683644.1897 | 1274419.5038
16 | 2683764.7279 | 1274495.364
17 | 2683550.5966 | 1274559.7715
18 | 2683772.971 | 1274500.4507
19 | 2683115.1754 | 1274115.4391
20 | 2683063.1701 | 1274104.7541
21 | 2683028.8271 | 1274097.8876
22 | 2682986.1999 | 1273709.6821
23 | 2682961.1026 | 1273759.0809
24 | 2683006.627 | 1273669.4141
25 | 2682945.6911 | 1273789.4241
26 | 2682896.3096 | 1273494.7217
27 | 2683187.0477 | 1273923.4387
28 | 2682965.9262 | 1273094.0839
29 | 2682905.3061 | 1273473.1638
30 | 2683171.7258 | 1273976.4896
31 | 2682889.8211 | 1273028.3394
32 | 2682863.6193 | 1273078.4761
33 | 2683171.1888 | 1273978.3491
34 | 2682882.8985 | 1274101.8961
35 | 2683073.3996 | 1274055.4208
36 | 2683076.486 | 1274040.5364
37 | 2683082.0804 | 1274013.5566
38 | 2682823.2217 | 1274102.537
39 | 2682805.8284 | 1274099.3571
40 | 2682647.5895 | 1274088.9537
41 | 2682660.7869 | 1274729.0846
42 | 2682618.7208 | 1274602.2918
43 | 2682515.8717 | 1274303.2643
44 | 2682533.8642 | 1274278.0841
45 | 2682583.0396 | 1274067.5997
46 | 2682576.7193 | 1274107.6217
47 | 2682542.6249 | 1274051.7883
48 | 2682556.0725 | 1273856.0053
49 | 2682233.5986 | 1274037.4962
50 | 2682479.7038 | 1273842.8717
51 | 2682169.5749 | 1274007.1039
52 | 2680776.0561 | 1273613.9336
53 | 2680770.1682 | 1273611.7068
54 | 2681990.9385 | 1272427.7923
55 | 2682772.7222 | 1273014.252
56 | 2682053.9755 | 1272167.5586
57 | 2680423.5724 | 1273320.4845
58 | 2680395.348 | 1273307.245
59 | 2682820.5646 | 1273040.9223
60 | 2682839.3023 | 1272985.943
61 | 2682169.5749 | 1274007.1039

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9908 | -0.41549 | 0.19424 | 0.094074
1 | 0.9908 | -0.41554 | 0 | 0
2 | 0.99025 | -0.41811 | 0 | 0
3 | 0.99401 | -0.23065 | 0.092258 | 0.044683
4 | 0.99008 | -0.4275 | 0 | 0
5 | 0.99003 | -0.42772 | 0.37621 | 0.18221
6 | 0.98784 | -0.5535 | 0 | 0
7 | 0.99411 | -0.2302 | 0 | 0
8 | 0.99485 | -0.22654 | 0 | 0
9 | 0.99482 | -0.22629 | 0.29426 | 0.14252
10 | 0.99575 | -0.22172 | 0 | 0
11 | 0.98767 | -0.56131 | 0.14507 | 0.070259
12 | 0.98767 | -0.56135 | 0 | 0
13 | 0.9877 | -0.56115 | 0.30965 | 0.14997
14 | 0.98761 | -0.5616 | 0 | 0
15 | 0.9973 | -0.0033154 | 0.25798 | 0.12495
16 | 0.99729 | -0.0031871 | 0 | 0
17 | 0.99741 | -0.0025589 | 0 | 0
18 | 0.99729 | -0.0031773 | 0.085244 | 0.041285
19 | 0.99787 | -0.0058292 | 0 | 0
20 | 0.9979 | -0.0059468 | 0.23377 | 0.11322
21 | 0.99792 | -0.0061201 | 0 | 0
22 | 0.98258 | -0.75944 | 0.3091 | 0.1497
23 | 0.98258 | -0.75939 | 0 | 0
24 | 0.98262 | -0.75921 | 0 | 0
25 | 0.98257 | -0.75936 | 0.07898 | 0.038252
26 | 0.98289 | -0.76144 | 0 | 0
27 | 0.9823 | -0.75663 | 0 | 0
28 | 0.98361 | -0.76724 | 0 | 0
29 | 0.98288 | -0.76151 | 0.25755 | 0.12474
30 | 0.98227 | -0.75635 | 0.13218 | 0.064018
31 | 0.9836 | -0.76717 | 0 | 0
32 | 0.98384 | -0.76895 | 0.39975 | 0.19361
33 | 0.98227 | -0.75635 | 0 | 0
34 | 0.99803 | -0.0068501 | 0 | 0
35 | 0.98221 | -0.75577 | 0.22036 | 0.10673
36 | 0.98221 | -0.75581 | 0.0689 | 0.03337
37 | 0.98222 | -0.75591 | 0 | 0
38 | 0.9981 | -0.0062545 | 0.38096 | 0.18451
39 | 0.99812 | -0.0064178 | 0 | 0
40 | 0.99831 | -0.0078677 | 0 | 0
41 | 0.99814 | -0.0060672 | 0.13913 | 0.067383
42 | 0.99818 | -0.0058409 | 0 | 0
43 | 0.99826 | -0.005298 | 0.39997 | 0.19371
44 | 0.99829 | -0.005499 | 0 | 0
45 | 0.99843 | -0.0068504 | 0.28421 | 0.13765
46 | 0.99841 | -0.0066037 | 0 | 0
47 | 0.99853 | -0.0076482 | 0 | 0
48 | 0.99844 | -0.0068534 | 0 | 0
49 | 0.9998 | 0.0016985 | 0.14689 | 0.071143
50 | 0.99839 | -0.0071825 | 0.35003 | 0.16953
51 | 1 | 0 | -6.2099 | -2.7745
52 | 0.99634 | -0.21826 | 0.051601 | 0.024991
53 | 0.99633 | -0.21831 | 0 | 0
54 | 0.98532 | -0.69389 | 0.07744 | 0.037506
55 | 0.98405 | -0.76711 | 0.30045 | 0.14551
56 | 0.98528 | -0.69415 | 0.07666 | 0.037128
57 | 0.98741 | -0.55979 | 0.35297 | 0.17095
58 | 0.98742 | -0.55993 | 0 | 0
59 | 0.98395 | -0.76986 | 0.072151 | 0.034944
60 | 0.9836 | -0.76712 | 0.069571 | 0.033695
61 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.19424 | -0.094074 | 0.19424 | 0.093649 | 9.5752e-07 | -0.00042525 | 0.0062881 | 0.0062827 | 0.0062881 | 0.9908 | -0.41549 | 0.9908 | -0.41554 | 2.8582
1 | 3.259 | 1.489 | -3.2572 | -1.5199 | 0.001752 | -0.030967 | 0.10439 | 0.10478 | 0.10478 | 0.9908 | -0.41554 | 0.99025 | -0.41811 | 16.4236
2 | -3.4532 | -1.5826 | 3.4593 | 1.597 | 0.0060619 | 0.014413 | 0.11067 | 0.11065 | 0.11067 | 0.9908 | -0.41554 | 0.99401 | -0.23065 | 17.1587
3 | 3.2572 | 1.5199 | -3.2569 | -1.5192 | 0.00029247 | 0.00068535 | 0.10478 | 0.10478 | 0.10478 | 0.99025 | -0.41811 | 0.99008 | -0.4275 | 16.2456
4 | -3.5515 | -1.6417 | 3.5518 | 1.6368 | 0.00032896 | -0.0049371 | 0.11363 | 0.11356 | 0.11363 | 0.99401 | -0.23065 | 0.99411 | -0.2302 | 17.8099
5 | 3.2569 | 1.5192 | -3.2567 | -1.5221 | 0.0001603 | -0.0028187 | 0.10478 | 0.10482 | 0.10482 | 0.99008 | -0.4275 | 0.99003 | -0.42772 | 16.4294
6 | 2.8805 | 1.3399 | -2.8771 | -1.3321 | 0.003452 | 0.0077596 | 0.092633 | 0.092651 | 0.092651 | 0.99003 | -0.42772 | 0.98784 | -0.5535 | 14.3646
7 | 2.8771 | 1.3321 | -2.8769 | -1.3316 | 0.00020965 | 0.00047149 | 0.092651 | 0.092653 | 0.092653 | 0.98784 | -0.5535 | 0.9877 | -0.56115 | 14.3647
8 | -3.5518 | -1.6368 | 3.5544 | 1.5984 | 0.0025408 | -0.038355 | 0.11356 | 0.11309 | 0.11356 | 0.99411 | -0.2302 | 0.99485 | -0.22654 | 17.8001
9 | 0.29427 | 0.1408 | -0.29426 | -0.14252 | 8.7485e-06 | -0.0017216 | 0.009466 | 0.0094877 | 0.0094877 | 0.99485 | -0.22654 | 0.99482 | -0.22629 | 4.3126
10 | -3.8487 | -1.7392 | 3.852 | 1.6963 | 0.0033232 | -0.042894 | 0.12255 | 0.12202 | 0.12255 | 0.99485 | -0.22654 | 0.99575 | -0.22172 | 19.2084
11 | -3.852 | -1.6963 | 3.8541 | 1.6682 | 0.0021592 | -0.028122 | 0.12202 | 0.12168 | 0.12202 | 0.99575 | -0.22172 | 0.99633 | -0.21831 | 19.1255
12 | -0.14507 | -0.070259 | 0.14507 | 0.069738 | 6.6212e-07 | -0.00052101 | 0.0047111 | 0.0047045 | 0.0047111 | 0.98767 | -0.56131 | 0.98767 | -0.56135 | 2.1414
13 | -0.14507 | -0.069738 | 0.14507 | 0.069617 | 4.2002e-06 | -0.00012146 | 0.0047045 | 0.0047029 | 0.0047045 | 0.98767 | -0.56135 | 0.9877 | -0.56115 | 2.2402
14 | 2.4222 | 1.112 | -2.4219 | -1.1192 | 0.00022248 | -0.007139 | 0.077896 | 0.077985 | 0.077985 | 0.9877 | -0.56115 | 0.98761 | -0.5616 | 12.2234
15 | 2.0689 | 0.95874 | -2.0663 | -0.95395 | 0.0026028 | 0.0047923 | 0.06665 | 0.066678 | 0.066678 | 0.98761 | -0.5616 | 0.98532 | -0.69389 | 10.3376
16 | 0.35305 | 0.16043 | -0.35298 | -0.17023 | 7.3116e-05 | -0.0097988 | 0.011335 | 0.011457 | 0.011457 | 0.98761 | -0.5616 | 0.98742 | -0.55993 | 5.2077
17 | 0.085245 | 0.037681 | -0.085244 | -0.041055 | 1.4014e-06 | -0.0033743 | 0.0026978 | 0.0027387 | 0.0027387 | 0.9973 | -0.0033154 | 0.99729 | -0.0031871 | 1.2449
18 | -0.34322 | -0.16263 | 0.34326 | 0.16245 | 3.6303e-05 | -0.00017751 | 0.010994 | 0.010991 | 0.010994 | 0.9973 | -0.0033154 | 0.99741 | -0.0025589 | 5.2351
19 | 0.085244 | 0.041055 | -0.085244 | -0.041285 | 9.7091e-08 | -0.00022999 | 0.0027387 | 0.0027416 | 0.0027416 | 0.99729 | -0.0031871 | 0.99729 | -0.0031773 | 1.2462
20 | -0.34326 | -0.16245 | 0.34343 | 0.13721 | 0.00016691 | -0.025236 | 0.010991 | 0.010699 | 0.010991 | 0.99741 | -0.0025589 | 0.99787 | -0.0058292 | 4.996
21 | -0.34343 | -0.13721 | 0.34344 | 0.13596 | 8.0789e-06 | -0.0012562 | 0.010699 | 0.010685 | 0.010699 | 0.99787 | -0.0058292 | 0.9979 | -0.0059468 | 4.863
22 | -0.57721 | -0.24918 | 0.57722 | 0.24835 | 1.5412e-05 | -0.00082572 | 0.018187 | 0.018178 | 0.018187 | 0.9979 | -0.0059468 | 0.99792 | -0.0061201 | 8.2669
23 | -0.57722 | -0.24835 | 0.57729 | 0.24477 | 6.6642e-05 | -0.0035808 | 0.018178 | 0.018137 | 0.018178 | 0.99792 | -0.0061201 | 0.99803 | -0.0068501 | 8.2626
24 | 0.07898 | 0.036191 | -0.07898 | -0.037467 | 4.8459e-07 | -0.0012764 | 0.0025524 | 0.0025682 | 0.0025682 | 0.98258 | -0.75944 | 0.98258 | -0.75939 | 1.1674
25 | -0.38808 | -0.18589 | 0.38809 | 0.18585 | 1.2857e-05 | -4.3991e-05 | 0.012642 | 0.012641 | 0.012642 | 0.98258 | -0.75944 | 0.98262 | -0.75921 | 6.02
26 | 0.07898 | 0.037467 | -0.07898 | -0.038252 | 3.0083e-07 | -0.00078441 | 0.0025682 | 0.0025782 | 0.0025782 | 0.98258 | -0.75939 | 0.98257 | -0.75936 | 1.1719
27 | -0.80971 | -0.37129 | 0.80995 | 0.36529 | 0.00024011 | -0.0060019 | 0.02617 | 0.026096 | 0.02617 | 0.98262 | -0.75921 | 0.98289 | -0.76144 | 11.8953
28 | 0.42162 | 0.18544 | -0.42148 | -0.19885 | 0.00014432 | -0.013402 | 0.013532 | 0.013695 | 0.013695 | 0.98262 | -0.75921 | 0.9823 | -0.75663 | 6.2252
29 | -1.0675 | -0.49 | 1.0683 | 0.47811 | 0.00083209 | -0.011894 | 0.034498 | 0.034351 | 0.034498 | 0.98289 | -0.76144 | 0.98361 | -0.76724 | 15.6808
30 | 0.25755 | 0.12471 | -0.25755 | -0.12474 | 2.9399e-06 | -2.5099e-05 | 0.0084044 | 0.0084047 | 0.0084047 | 0.98289 | -0.76144 | 0.98288 | -0.76151 | 4.0022
31 | 0.42148 | 0.19885 | -0.42146 | -0.20011 | 1.3843e-05 | -0.001268 | 0.013695 | 0.013711 | 0.013711 | 0.9823 | -0.75663 | 0.98227 | -0.75635 | 6.2325
32 | 0.069572 | 0.029852 | -0.069571 | -0.032171 | 6.6981e-07 | -0.002319 | 0.0022219 | 0.0022496 | 0.0022496 | 0.98361 | -0.76724 | 0.9836 | -0.76717 | 1.0225
33 | -1.1379 | -0.50796 | 1.1382 | 0.50448 | 0.00027523 | -0.0034839 | 0.036572 | 0.03653 | 0.036572 | 0.98361 | -0.76724 | 0.98384 | -0.76895 | 16.6237
34 | 0.28928 | 0.1361 | -0.28928 | -0.13614 | 2.281e-07 | -4.4519e-05 | 0.0093955 | 0.009396 | 0.009396 | 0.98227 | -0.75635 | 0.98227 | -0.75635 | 4.2709
35 | 0.069571 | 0.032171 | -0.069571 | -0.033695 | 4.4932e-07 | -0.0015233 | 0.0022496 | 0.0022687 | 0.0022687 | 0.9836 | -0.76717 | 0.9836 | -0.76712 | 1.0312
36 | -1.5379 | -0.69809 | 1.5381 | 0.69682 | 0.00018725 | -0.0012649 | 0.049557 | 0.049541 | 0.049557 | 0.98384 | -0.76895 | 0.98395 | -0.76986 | 22.5259
37 | 0.28928 | 0.13614 | -0.28927 | -0.13911 | 1.529e-05 | -0.002972 | 0.009396 | 0.0094336 | 0.0094336 | 0.98227 | -0.75635 | 0.98222 | -0.75591 | 4.288
38 | -0.57729 | -0.24477 | 0.57733 | 0.24472 | 3.4976e-05 | -4.9063e-05 | 0.018137 | 0.018136 | 0.018137 | 0.99803 | -0.0068501 | 0.9981 | -0.0062545 | 8.6366
39 | -0.22036 | -0.10673 | 0.22036 | 0.10638 | 1.0502e-06 | -0.00034983 | 0.0071962 | 0.0071917 | 0.0071962 | 0.98221 | -0.75577 | 0.98221 | -0.75581 | 3.271
40 | -0.28926 | -0.13975 | 0.28927 | 0.13911 | 3.2763e-06 | -0.00063371 | 0.0094417 | 0.0094336 | 0.0094417 | 0.98221 | -0.75581 | 0.98222 | -0.75591 | 4.2917
41 | -0.95829 | -0.42923 | 0.95831 | 0.42882 | 2.1704e-05 | -0.00041291 | 0.03037 | 0.030365 | 0.03037 | 0.9981 | -0.0062545 | 0.99812 | -0.0064178 | 13.8043
42 | -0.95831 | -0.42882 | 0.95851 | 0.4251 | 0.00019526 | -0.0037217 | 0.030365 | 0.03032 | 0.030365 | 0.99812 | -0.0064178 | 0.99831 | -0.0078677 | 13.8021
43 | -0.95851 | -0.4251 | 0.95862 | 0.42509 | 0.00011136 | -1.1151e-05 | 0.03032 | 0.030319 | 0.03032 | 0.99831 | -0.0078677 | 0.99843 | -0.0068504 | 14.4381
44 | -0.13913 | -0.067383 | 0.13913 | 0.067227 | 4.7554e-06 | -0.00015591 | 0.0044708 | 0.0044688 | 0.0044708 | 0.99814 | -0.0060672 | 0.99818 | -0.0058409 | 2.129
45 | -0.13913 | -0.067227 | 0.13914 | 0.066857 | 1.124e-05 | -0.00036912 | 0.0044688 | 0.0044641 | 0.0044688 | 0.99818 | -0.0058409 | 0.99826 | -0.005298 | 2.128
46 | -0.53911 | -0.26057 | 0.53912 | 0.25983 | 1.2537e-05 | -0.00074193 | 0.017315 | 0.017306 | 0.017315 | 0.99826 | -0.005298 | 0.99829 | -0.005499 | 7.8706
47 | -0.53912 | -0.25983 | 0.53919 | 0.25565 | 7.0393e-05 | -0.0041816 | 0.017306 | 0.017254 | 0.017306 | 0.99829 | -0.005499 | 0.99841 | -0.0066037 | 7.8663
48 | 0.53921 | 0.25469 | -0.53919 | -0.25565 | 1.6091e-05 | -0.00095956 | 0.017242 | 0.017254 | 0.017254 | 0.99843 | -0.0068504 | 0.99841 | -0.0066037 | 7.8425
49 | -1.782 | -0.81742 | 1.7822 | 0.81645 | 0.00018563 | -0.00097523 | 0.056686 | 0.056673 | 0.056686 | 0.99843 | -0.0068504 | 0.99853 | -0.0076482 | 25.7661
50 | 0.35008 | 0.16478 | -0.35005 | -0.16945 | 3.2987e-05 | -0.0046666 | 0.011186 | 0.011244 | 0.011244 | 0.99853 | -0.0076482 | 0.99844 | -0.0068534 | 5.111
51 | -2.1323 | -0.98123 | 2.1348 | 0.98245 | 0.0025379 | 0.001221 | 0.067859 | 0.067854 | 0.067859 | 0.99853 | -0.0076482 | 0.9998 | 0.0016985 | 32.3136
52 | 0.35005 | 0.16945 | -0.35003 | -0.16953 | 1.7458e-05 | -8.128e-05 | 0.011244 | 0.011245 | 0.011245 | 0.99844 | -0.0068534 | 0.99839 | -0.0071825 | 5.355
53 | -2.2817 | -1.0536 | 2.2822 | 1.052 | 0.00049807 | -0.001544 | 0.072566 | 0.072545 | 0.072566 | 0.9998 | 0.0016985 | 1 | 0 | 32.9845
54 | 3.9136 | 1.712 | -3.9058 | -1.6928 | 0.0078616 | 0.019146 | 0.12331 | 0.12334 | 0.12334 | 1 | 0 | 0.99634 | -0.21826 | 19.1218
55 | 3.8542 | 1.6678 | -3.8541 | -1.6682 | 2.8721e-05 | -0.0003754 | 0.12168 | 0.12168 | 0.12168 | 0.99634 | -0.21826 | 0.99633 | -0.21831 | 19.0722
56 | 1.9122 | 0.87962 | -1.9109 | -0.87737 | 0.0013271 | 0.0022588 | 0.061666 | 0.061682 | 0.061682 | 0.98532 | -0.69389 | 0.98405 | -0.76711 | 9.5631
57 | 0.076663 | 0.03682 | -0.07666 | -0.037128 | 2.9665e-06 | -0.00030846 | 0.0024917 | 0.0024956 | 0.0024956 | 0.98532 | -0.69389 | 0.98528 | -0.69415 | 1.1884
58 | 1.6104 | 0.73185 | -1.6103 | -0.73176 | 0.0001354 | 8.8221e-05 | 0.051891 | 0.051892 | 0.051892 | 0.98405 | -0.76711 | 0.98395 | -0.76986 | 14.8263
59 | -0.35297 | -0.17095 | 0.35298 | 0.17023 | 5.4537e-06 | -0.00072231 | 0.011466 | 0.011457 | 0.011466 | 0.98741 | -0.55979 | 0.98742 | -0.55993 | 5.2118

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 6.2099 | 2.7745

## res_load
| p_mw | q_mvar
0 | 0.19424 | 0.094074
1 | 0.092258 | 0.044683
2 | 0.37621 | 0.18221
3 | 0.29426 | 0.14252
4 | 0.14507 | 0.070259
5 | 0.30965 | 0.14997
6 | 0.25798 | 0.12495
7 | 0.085244 | 0.041285
8 | 0.23377 | 0.11322
9 | 0.3091 | 0.1497
10 | 0.07898 | 0.038252
11 | 0.25755 | 0.12474
12 | 0.13218 | 0.064018
13 | 0.39975 | 0.19361
14 | 0.22036 | 0.10673
15 | 0.0689 | 0.03337
16 | 0.38096 | 0.18451
17 | 0.13913 | 0.067383
18 | 0.39997 | 0.19371
19 | 0.28421 | 0.13765
20 | 0.14689 | 0.071143
21 | 0.35003 | 0.16953
22 | 0.051601 | 0.024991
23 | 0.07744 | 0.037506
24 | 0.30045 | 0.14551
25 | 0.07666 | 0.037128
26 | 0.35297 | 0.17095
27 | 0.072151 | 0.034944
28 | 0.069571 | 0.033695

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1