## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_385_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_385_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_385_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_385_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_385_0_node_126 | 20 | n |  | TRUE
5 | bus_MV_385_0_node_128 | 20 | n |  | TRUE
6 | bus_MV_385_0_node_127 | 20 | n |  | TRUE
7 | bus_MV_385_0_node_227 | 20 | n |  | TRUE
8 | bus_MV_385_0_node_187 | 20 | n |  | TRUE
9 | bus_MV_385_0_node_4 | 20 | n |  | TRUE
10 | bus_MV_385_0_node_48 | 20 | n |  | TRUE
11 | bus_MV_385_0_node_181 | 20 | n |  | TRUE
12 | bus_MV_385_0_node_53 | 20 | n |  | TRUE
13 | bus_MV_385_0_node_47 | 20 | n |  | TRUE
14 | bus_MV_385_0_node_44 | 20 | n |  | TRUE
15 | bus_MV_385_0_node_201 | 20 | n |  | TRUE
16 | bus_MV_385_0_node_46 | 20 | n |  | TRUE
17 | bus_MV_385_0_node_200 | 20 | n |  | TRUE
18 | bus_MV_385_0_node_45 | 20 | n |  | TRUE
19 | bus_MV_385_0_node_217 | 20 | n |  | TRUE
20 | bus_MV_385_0_node_216 | 20 | n |  | TRUE
21 | bus_MV_385_0_node_52 | 20 | n |  | TRUE
22 | bus_MV_385_0_node_49 | 20 | n |  | TRUE
23 | bus_MV_385_0_node_50 | 20 | n |  | TRUE
24 | bus_MV_385_0_node_54 | 20 | n |  | TRUE
25 | bus_MV_385_0_node_55 | 20 | n |  | TRUE
26 | bus_MV_385_0_node_56 | 20 | n |  | TRUE
27 | bus_MV_385_0_node_57 | 20 | n |  | TRUE
28 | bus_MV_385_0_node_60 | 20 | n |  | TRUE
29 | bus_MV_385_0_node_58 | 20 | n |  | TRUE
30 | bus_MV_385_0_node_221 | 20 | n |  | TRUE
31 | bus_MV_385_0_node_59 | 20 | n |  | TRUE
32 | bus_MV_385_0_node_220 | 20 | n |  | TRUE
33 | bus_MV_385_0_node_61 | 20 | n |  | TRUE
34 | bus_MV_385_0_node_62 | 20 | n |  | TRUE
35 | bus_MV_385_0_node_202 | 20 | n |  | TRUE
36 | bus_MV_385_0_node_108 | 20 | n |  | TRUE
37 | bus_MV_385_0_node_109 | 20 | n |  | TRUE
38 | bus_MV_385_0_node_110 | 20 | n |  | TRUE
39 | bus_MV_385_0_node_111 | 20 | n |  | TRUE
40 | bus_MV_385_0_node_159 | 20 | n |  | TRUE
41 | bus_MV_385_0_node_231 | 20 | n |  | TRUE
42 | bus_MV_385_0_node_114 | 20 | n |  | TRUE
43 | bus_MV_385_0_node_122 | 20 | n |  | TRUE
44 | bus_MV_385_0_node_149 | 20 | n |  | TRUE
45 | bus_MV_385_0_node_158 | 20 | n |  | TRUE
46 | bus_MV_385_0_node_141 | 20 | n |  | TRUE
47 | bus_MV_385_0_node_148 | 20 | n |  | TRUE
48 | bus_MV_385_0_node_176 | 20 | n |  | TRUE
49 | bus_MV_385_0_node_123 | 20 | n |  | TRUE
50 | bus_MV_385_0_node_125 | 20 | n |  | TRUE
51 | bus_MV_385_0_node_112 | 20 | n |  | TRUE
52 | bus_MV_385_0_node_113 | 20 | n |  | TRUE
53 | bus_MV_385_0_node_115 | 20 | n |  | TRUE
54 | bus_MV_385_0_node_132 | 20 | n |  | TRUE
55 | bus_MV_385_0_node_164 | 20 | n |  | TRUE
56 | bus_MV_385_0_node_124 | 20 | n |  | TRUE
57 | bus_MV_385_0_node_230 | 20 | n |  | TRUE
58 | bus_MV_385_0_node_117 | 20 | n |  | TRUE
59 | bus_MV_385_0_node_160 | 20 | n |  | TRUE
60 | bus_MV_385_0_node_129 | 20 | n |  | TRUE
61 | bus_MV_385_0_node_163 | 20 | n |  | TRUE
62 | bus_MV_385_0_node_116 | 20 | n |  | TRUE
63 | bus_MV_385_0_node_118 | 20 | n |  | TRUE
64 | bus_MV_385_0_node_119 | 20 | n |  | TRUE
65 | bus_MV_385_0_node_175 | 20 | n |  | TRUE
66 | bus_MV_385_0_node_145 | 20 | n |  | TRUE
67 | bus_MV_385_0_node_131 | 20 | n |  | TRUE
68 | bus_MV_385_0_node_136 | 20 | n |  | TRUE
69 | bus_MV_385_0_node_146 | 20 | n |  | TRUE
70 | bus_MV_385_0_node_120 | 20 | n |  | TRUE
71 | bus_MV_385_0_node_144 | 20 | n |  | TRUE
72 | bus_MV_385_0_node_186 | 20 | n |  | TRUE
73 | bus_MV_385_0_node_135 | 20 | n |  | TRUE
74 | bus_MV_385_0_node_130 | 20 | n |  | TRUE
75 | bus_MV_385_0_node_133 | 20 | n |  | TRUE
76 | bus_MV_385_0_node_134 | 20 | n |  | TRUE
77 | bus_MV_385_0_node_137 | 20 | n |  | TRUE
78 | bus_MV_385_0_node_138 | 20 | n |  | TRUE
79 | bus_MV_385_0_node_229 | 20 | n |  | TRUE
80 | bus_MV_385_0_node_182 | 20 | n |  | TRUE
81 | bus_MV_385_0_node_177 | 20 | n |  | TRUE
82 | bus_MV_385_0_node_178 | 20 | n |  | TRUE
83 | bus_MV_385_0_node_180 | 20 | n |  | TRUE
84 | bus_MV_385_0_node_183 | 20 | n |  | TRUE
85 | bus_MV_385_0_node_185 | 20 | n |  | TRUE
86 | bus_MV_385_0_node_223 | 20 | n |  | TRUE
87 | bus_MV_385_0_node_139 | 20 | n |  | TRUE
88 | bus_MV_385_0_node_140 | 20 | n |  | TRUE
89 | bus_MV_385_0_node_142 | 20 | n |  | TRUE
90 | bus_MV_385_0_node_215 | 20 | n |  | TRUE
91 | bus_MV_385_0_node_147 | 20 | n |  | TRUE
92 | bus_MV_385_0_node_214 | 20 | n |  | TRUE
93 | bus_MV_385_0_node_150 | 20 | n |  | TRUE
94 | bus_MV_385_0_node_151 | 20 | n |  | TRUE
95 | bus_MV_385_0_node_152 | 20 | n |  | TRUE
96 | bus_MV_385_0_node_153 | 20 | n |  | TRUE
97 | bus_MV_385_0_node_154 | 20 | n |  | TRUE
98 | bus_MV_385_0_node_157 | 20 | n |  | TRUE
99 | bus_MV_385_0_node_155 | 20 | n |  | TRUE
100 | bus_MV_385_0_node_166 | 20 | n |  | TRUE
101 | bus_MV_385_0_node_156 | 20 | n |  | TRUE
102 | bus_MV_385_0_node_165 | 20 | n |  | TRUE
103 | bus_MV_385_0_node_167 | 20 | n |  | TRUE
104 | bus_MV_385_0_node_209 | 20 | n |  | TRUE
105 | bus_MV_385_0_node_210 | 20 | n |  | TRUE
106 | bus_MV_385_0_node_161 | 20 | n |  | TRUE
107 | bus_MV_385_0_node_208 | 20 | n |  | TRUE
108 | bus_MV_385_0_node_174 | 20 | n |  | TRUE
109 | bus_MV_385_0_node_168 | 20 | n |  | TRUE
110 | bus_MV_385_0_node_169 | 20 | n |  | TRUE
111 | bus_MV_385_0_node_170 | 20 | n |  | TRUE
112 | bus_MV_385_0_node_171 | 20 | n |  | TRUE
113 | bus_MV_385_0_node_172 | 20 | n |  | TRUE
114 | bus_MV_385_0_node_173 | 20 | n |  | TRUE
115 | bus_MV_385_0_node_213 | 20 | n |  | TRUE
116 | bus_MV_385_0_node_211 | 20 | n |  | TRUE
117 | bus_MV_385_0_node_212 | 20 | n |  | TRUE
118 | bus_HV_385_0_node_216 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_385_0_load_0 | 0 | 0.2325 | 0.1126 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_385_0_load_126 | 4 | 0.1473 | 0.07134 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_385_0_load_227 | 7 | 0.33445 | 0.16198 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_385_0_load_187 | 8 | 0.10198 | 0.04939 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_385_0_load_4 | 9 | 0.15292 | 0.074064 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_385_0_load_53 | 12 | 0.36882 | 0.17863 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_385_0_load_44 | 14 | 0.33567 | 0.16257 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_385_0_load_46 | 16 | 0.16521 | 0.080015 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_385_0_load_200 | 17 | 0.19252 | 0.09324 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_385_0_load_45 | 18 | 0.14071 | 0.06815 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_385_0_load_217 | 19 | 2.0706 | 1.0028 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_385_0_load_49 | 22 | 0.24685 | 0.11955 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_385_0_load_54 | 24 | 0.39588 | 0.19174 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_385_0_load_60 | 28 | 0.38058 | 0.18432 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_385_0_load_221 | 30 | 0.1635 | 0.079189 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_385_0_load_220 | 32 | 0.30753 | 0.14894 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_385_0_load_202 | 35 | 0.10429 | 0.050511 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_385_0_load_108 | 36 | 0.12064 | 0.058429 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_385_0_load_231 | 41 | 0.11875 | 0.057512 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_385_0_load_122 | 43 | 0.092805 | 0.044948 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_385_0_load_158 | 45 | 0.10675 | 0.051699 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_385_0_load_176 | 48 | 0.15878 | 0.0769 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_385_0_load_125 | 50 | 0.14862 | 0.071981 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_385_0_load_112 | 51 | 0.13327 | 0.064543 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_385_0_load_164 | 55 | 0.081378 | 0.039413 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_385_0_load_230 | 57 | 0.15111 | 0.073185 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_385_0_load_160 | 59 | 0.076798 | 0.037195 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_385_0_load_116 | 62 | 0.085957 | 0.041631 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_385_0_load_175 | 65 | 0.15081 | 0.073038 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_385_0_load_145 | 66 | 0.14465 | 0.070056 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_385_0_load_131 | 67 | 0.14168 | 0.068621 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_385_0_load_120 | 70 | 0.162 | 0.078459 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_385_0_load_144 | 71 | 0.1392 | 0.06742 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_385_0_load_186 | 72 | 0.11656 | 0.056455 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_385_0_load_133 | 75 | 0.13777 | 0.066727 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_385_0_load_137 | 77 | 0.10841 | 0.052507 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_385_0_load_229 | 79 | 0.14754 | 0.071457 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_385_0_load_177 | 81 | 0.14794 | 0.071651 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_385_0_load_183 | 84 | 0.13541 | 0.065584 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_385_0_load_223 | 86 | 0.098145 | 0.047534 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_385_0_load_139 | 87 | 0.14504 | 0.070245 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_385_0_load_215 | 90 | 0.07056 | 0.034174 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_385_0_load_147 | 91 | 0.12561 | 0.060836 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_385_0_load_214 | 92 | 2.7101 | 1.3126 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_385_0_load_150 | 93 | 0.081853 | 0.039643 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_385_0_load_157 | 98 | 0.091589 | 0.044358 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_385_0_load_165 | 102 | 0.10929 | 0.052932 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_385_0_load_167 | 103 | 0.11702 | 0.056677 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_385_0_load_210 | 105 | 0.053913 | 0.026111 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_385_0_load_161 | 106 | 0.072504 | 0.035115 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_385_0_load_208 | 107 | 0.18995 | 0.091997 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_385_0_load_168 | 109 | 0.11126 | 0.053887 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_385_0_load_169 | 110 | 0.096647 | 0.046808 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_385_0_load_172 | 113 | 0.087221 | 0.042243 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_385_0_load_213 | 115 | 0.18129 | 0.087803 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_385_0_load_211 | 116 | 0.11975 | 0.058 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_385_0_load_212 | 117 | 0.095832 | 0.046413 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_385_0_line_0 |  | 0 | 1 | 0.002414 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_385_0_line_1 |  | 1 | 2 | 0.64065 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
2 | MV_385_0_line_2 |  | 1 | 3 | 0.4469 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
3 | MV_385_0_line_3 |  | 2 | 7 | 0.15425 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_385_0_line_4 |  | 2 | 8 | 1.7657 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
5 | MV_385_0_line_5 |  | 3 | 9 | 0.054424 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_385_0_line_6 |  | 3 | 10 | 2.0675 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
7 | MV_385_0_line_7 |  | 4 | 5 | 0.076636 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
8 | MV_385_0_line_8 |  | 4 | 6 | 0.09807 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
9 | MV_385_0_line_9 |  | 5 | 74 | 0.084242 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
10 | MV_385_0_line_10 |  | 6 | 60 | 0.071987 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
11 | MV_385_0_line_11 |  | 8 | 11 | 0.037768 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
12 | MV_385_0_line_12 |  | 10 | 12 | 0.03918 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_385_0_line_13 |  | 10 | 13 | 0.68562 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
14 | MV_385_0_line_14 |  | 11 | 83 | 0.3208 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
15 | MV_385_0_line_15 |  | 12 | 21 | 0.013814 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_385_0_line_16 |  | 13 | 18 | 0.068924 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
17 | MV_385_0_line_17 |  | 14 | 15 | 1.3189 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
18 | MV_385_0_line_18 |  | 14 | 16 | 1.3234 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
19 | MV_385_0_line_19 |  | 15 | 17 | 0.035702 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_385_0_line_20 |  | 16 | 18 | 0.11532 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
21 | MV_385_0_line_21 |  | 17 | 27 | 0.13145 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_385_0_line_22 |  | 19 | 20 | 0.020655 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_385_0_line_23 |  | 20 | 92 | 0.088704 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
24 | MV_385_0_line_24 |  | 21 | 23 | 0.32313 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_385_0_line_25 |  | 22 | 23 | 0.11497 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_385_0_line_26 |  | 24 | 25 | 0.072755 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_385_0_line_27 |  | 25 | 26 | 0.042935 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_385_0_line_28 |  | 25 | 27 | 0.41135 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_385_0_line_29 |  | 26 | 28 | 0.090011 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_385_0_line_30 |  | 27 | 29 | 0.30531 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_385_0_line_31 |  | 28 | 33 | 0.0778 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_385_0_line_32 |  | 29 | 30 | 0.028315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_385_0_line_33 |  | 29 | 31 | 0.40415 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_385_0_line_34 |  | 31 | 32 | 0.010515 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_385_0_line_35 |  | 33 | 34 | 0.017199 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_385_0_line_36 |  | 34 | 35 | 0.029823 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_385_0_line_37 |  | 36 | 37 | 0.043409 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_385_0_line_38 |  | 37 | 38 | 0.079323 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_385_0_line_39 |  | 38 | 39 | 0.20253 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
40 | MV_385_0_line_40 |  | 38 | 40 | 0.18426 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
41 | MV_385_0_line_41 |  | 38 | 41 | 0.057686 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_385_0_line_42 |  | 39 | 42 | 0.064732 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
43 | MV_385_0_line_43 |  | 39 | 43 | 0.049384 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_385_0_line_44 |  | 40 | 48 | 0.027829 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_385_0_line_45 |  | 40 | 44 | 0.19018 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
46 | MV_385_0_line_46 |  | 42 | 49 | 0.050101 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_385_0_line_47 |  | 42 | 50 | 0.043675 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
48 | MV_385_0_line_48 |  | 44 | 45 | 0.038431 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_385_0_line_49 |  | 44 | 46 | 0.19783 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_385_0_line_50 |  | 44 | 47 | 0.10932 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
51 | MV_385_0_line_51 |  | 46 | 87 | 0.005676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_385_0_line_52 |  | 47 | 91 | 0.028314 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_385_0_line_53 |  | 47 | 88 | 0.1489 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
54 | MV_385_0_line_54 |  | 48 | 97 | 0.014146 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_385_0_line_55 |  | 49 | 56 | 0.84252 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_385_0_line_56 |  | 50 | 58 | 0.14821 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
57 | MV_385_0_line_57 |  | 51 | 52 | 0.07598 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_385_0_line_58 |  | 52 | 53 | 0.16814 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_385_0_line_59 |  | 53 | 54 | 0.13697 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_385_0_line_60 |  | 53 | 55 | 0.08345 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_385_0_line_61 |  | 54 | 59 | 0.13026 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_385_0_line_62 |  | 54 | 60 | 0.49146 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_385_0_line_63 |  | 55 | 61 | 0.052902 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_385_0_line_64 |  | 56 | 57 | 0.039081 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_385_0_line_65 |  | 58 | 63 | 0.14328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_385_0_line_66 |  | 58 | 64 | 0.15248 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
67 | MV_385_0_line_67 |  | 58 | 62 | 0.030505 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_385_0_line_68 |  | 60 | 67 | 0.070388 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
69 | MV_385_0_line_69 |  | 61 | 106 | 0.071864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_385_0_line_70 |  | 63 | 65 | 0.093466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_385_0_line_71 |  | 64 | 66 | 0.012462 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
72 | MV_385_0_line_72 |  | 66 | 69 | 0.031244 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
73 | MV_385_0_line_73 |  | 67 | 68 | 0.092551 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
74 | MV_385_0_line_74 |  | 68 | 77 | 0.024603 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
75 | MV_385_0_line_75 |  | 69 | 78 | 0.089875 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
76 | MV_385_0_line_76 |  | 70 | 71 | 0.2865 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
77 | MV_385_0_line_77 |  | 71 | 72 | 1.8105 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
78 | MV_385_0_line_78 |  | 71 | 73 | 0.036112 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
79 | MV_385_0_line_79 |  | 72 | 85 | 0.048743 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
80 | MV_385_0_line_80 |  | 73 | 76 | 0.29723 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
81 | MV_385_0_line_81 |  | 74 | 75 | 0.11345 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
82 | MV_385_0_line_82 |  | 75 | 76 | 0.048418 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
83 | MV_385_0_line_83 |  | 77 | 78 | 0.034439 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
84 | MV_385_0_line_84 |  | 79 | 80 | 1.5855 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_385_0_line_85 |  | 80 | 86 | 0.051069 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_385_0_line_86 |  | 80 | 82 | 0.26301 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
87 | MV_385_0_line_87 |  | 81 | 82 | 0.032003 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
88 | MV_385_0_line_88 |  | 82 | 83 | 0.19406 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_385_0_line_89 |  | 83 | 84 | 0.024068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_385_0_line_90 |  | 83 | 85 | 0.30041 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
91 | MV_385_0_line_91 |  | 88 | 89 | 0.074397 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
92 | MV_385_0_line_92 |  | 89 | 90 | 0.05591 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
93 | MV_385_0_line_93 |  | 90 | 92 | 0.073013 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
94 | MV_385_0_line_94 |  | 93 | 94 | 0.05472 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_385_0_line_95 |  | 93 | 95 | 0.10378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_385_0_line_96 |  | 94 | 96 | 0.15376 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_385_0_line_97 |  | 95 | 97 | 0.17241 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_385_0_line_98 |  | 96 | 98 | 0.042793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_385_0_line_99 |  | 97 | 99 | 0.50112 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_385_0_line_100 |  | 99 | 100 | 0.30421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_385_0_line_101 |  | 99 | 101 | 0.54955 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_385_0_line_102 |  | 99 | 102 | 0.02787 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_385_0_line_103 |  | 100 | 104 | 0.007208 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_385_0_line_104 |  | 100 | 105 | 0.021705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_385_0_line_105 |  | 101 | 103 | 0.02864 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
106 | MV_385_0_line_106 |  | 104 | 107 | 0.057687 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_385_0_line_107 |  | 105 | 108 | 0.04578 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_385_0_line_108 |  | 108 | 112 | 0.11336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_385_0_line_109 |  | 109 | 110 | 0.03075 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_385_0_line_110 |  | 109 | 111 | 0.032863 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_385_0_line_111 |  | 111 | 112 | 0.026944 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_385_0_line_112 |  | 112 | 113 | 0.027222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_385_0_line_113 |  | 112 | 114 | 0.16677 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_385_0_line_114 |  | 114 | 115 | 0.067444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_385_0_line_115 |  | 115 | 116 | 0.03254 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_385_0_line_116 |  | 116 | 117 | 0.032523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_385_0_trafo_216 | 25 MVA 110/20 kV | 118 | 20 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2596530.509 | 1217633.1846
1 | 2596528.603 | 1217631.696
2 | 2596342.5148 | 1218065.234
3 | 2596211.0035 | 1217598.2967
4 | 2595379.3022 | 1220663.8014
5 | 2595449.6734 | 1220694.5196
6 | 2595282.1948 | 1220650.0932
7 | 2596205.9927 | 1217993.4469
8 | 2597403.8266 | 1219476.3909
9 | 2596242.4972 | 1217554.4959
10 | 2594145.5976 | 1217504.1632
11 | 2597438.0098 | 1219460.1219
12 | 2594108.2271 | 1217515.7182
13 | 2594139.4235 | 1216945.163
14 | 2592676.0168 | 1217220.3127
15 | 2592215.9327 | 1218456.339
16 | 2593961.3054 | 1216905.1872
17 | 2592238.0888 | 1218484.2781
18 | 2594075.7019 | 1216919.7347
19 | 2594145.173 | 1220506.2944
20 | 2594163.5424 | 1220515.7327
21 | 2594095.1689 | 1217520.3339
22 | 2593914.8915 | 1217908.0047
23 | 2593967.0191 | 1217805.5261
24 | 2592694.4186 | 1218593.1048
25 | 2592643.9724 | 1218645.5308
26 | 2592666.1472 | 1218682.3242
27 | 2592325.9826 | 1218579.3873
28 | 2592712.1324 | 1218759.767
29 | 2592205.8721 | 1218687.84
30 | 2592186.1447 | 1218667.4767
31 | 2592396.098 | 1218862.825
32 | 2592402.8395 | 1218870.9098
33 | 2592784.1354 | 1218730.1615
34 | 2592790.438 | 1218745.7404
35 | 2592790.6121 | 1218775.5603
36 | 2594756.0249 | 1221030.0473
37 | 2594713.5214 | 1221021.2248
38 | 2594728.611 | 1220946.8462
39 | 2594904.9892 | 1220997.8087
40 | 2594569.9587 | 1220962.0329
41 | 2594713.7152 | 1220891.1165
42 | 2594968.8304 | 1220987.7144
43 | 2594906.5189 | 1221047.1691
44 | 2594448.9406 | 1220881.055
45 | 2594419.7128 | 1220906.0082
46 | 2594579.4261 | 1220732.3587
47 | 2594355.4502 | 1220824.8784
48 | 2594556.8503 | 1220986.5925
49 | 2594980.6131 | 1221034.2089
50 | 2595011.4258 | 1220978.697
51 | 2594960.7938 | 1220931.0443
52 | 2594969.4605 | 1220855.5712
53 | 2594937.9627 | 1220775.6746
54 | 2595041.1929 | 1220702.1775
55 | 2594854.9318 | 1220767.3161
56 | 2595046.3995 | 1221737.2802
57 | 2595084.0167 | 1221741.74
58 | 2595158.1481 | 1220957.7712
59 | 2594936.3077 | 1220624.9338
60 | 2595210.2043 | 1220644.6484
61 | 2594802.2959 | 1220762.0187
62 | 2595161.4609 | 1220927.451
63 | 2595296.6408 | 1220982.8729
64 | 2595258.1434 | 1220890.1061
65 | 2595265.3061 | 1221070.404
66 | 2595263.5052 | 1220878.8508
67 | 2595207.7204 | 1220714.9797
68 | 2595183.2601 | 1220804.24
69 | 2595234.502 | 1220867.0231
70 | 2595794.6397 | 1221325.5134
71 | 2595852.1047 | 1221044.8331
72 | 2597402.677 | 1220110.2098
73 | 2595832.8314 | 1221015.8968
74 | 2595506.4877 | 1220735.666
75 | 2595599.611 | 1220800.4659
76 | 2595643.8543 | 1220802.2338
77 | 2595158.7472 | 1220801.4252
78 | 2595155.4908 | 1220835.7032
79 | 2598359.0521 | 1218089.4036
80 | 2597826.4062 | 1219582.7884
81 | 2597612.2994 | 1219676.182
82 | 2597580.3026 | 1219675.5505
83 | 2597459.8983 | 1219766.0429
84 | 2597484.019 | 1219766.9773
85 | 2597406.0465 | 1220061.5916
86 | 2597871.6055 | 1219602.8052
87 | 2594575.5003 | 1220728.2489
88 | 2594370.8444 | 1220676.7785
89 | 2594342.4825 | 1220632.6248
90 | 2594295.5703 | 1220602.8086
91 | 2594338.3882 | 1220847.5079
92 | 2594241.1837 | 1220558.6306
93 | 2594315.424 | 1221088.9912
94 | 2594265.6311 | 1221111.9973
95 | 2594409.2771 | 1221044.1309
96 | 2594146.1422 | 1221135.5175
97 | 2594550.5203 | 1220999.2501
98 | 2594162.3362 | 1221095.9675
99 | 2594348.7223 | 1221361.794
100 | 2594190.3082 | 1221344.9721
101 | 2594711.827 | 1221312.6274
102 | 2594353.4971 | 1221389.2496
103 | 2594730.2095 | 1221290.6649
104 | 2594194.8043 | 1221350.6153
105 | 2594169.6994 | 1221338.0774
106 | 2594804.3715 | 1220690.1978
107 | 2594214.185 | 1221404.5829
108 | 2594174.2134 | 1221292.8914
109 | 2594035.9291 | 1221351.0302
110 | 2594006.4018 | 1221342.4461
111 | 2594068.8873 | 1221350.7967
112 | 2594087.3852 | 1221332.9345
113 | 2594060.1759 | 1221333.7723
114 | 2593971.8799 | 1221300.9667
115 | 2593942.7596 | 1221361.8005
116 | 2593928.7099 | 1221391.1509
117 | 2593914.6674 | 1221420.4863
118 | 2594163.5424 | 1220515.7327

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9914 | -0.39086 | 0.2325 | 0.1126
1 | 0.9914 | -0.39087 | 0 | 0
2 | 0.99173 | -0.38851 | 0 | 0
3 | 0.99119 | -0.39222 | 0 | 0
4 | 0.99731 | -0.07331 | 0.1473 | 0.07134
5 | 0.99726 | -0.073741 | 0 | 0
6 | 0.99746 | -0.063946 | 0 | 0
7 | 0.99163 | -0.38915 | 0.33445 | 0.16198
8 | 0.99368 | -0.26539 | 0.10198 | 0.04939
9 | 0.99118 | -0.39212 | 0.15292 | 0.074064
10 | 0.9893 | -0.50599 | 0 | 0
11 | 0.99371 | -0.26524 | 0 | 0
12 | 0.98927 | -0.50572 | 0.36882 | 0.17863
13 | 0.98906 | -0.50736 | 0 | 0
14 | 0.98811 | -0.56042 | 0.33567 | 0.16257
15 | 0.98709 | -0.59557 | 0 | 0
16 | 0.98895 | -0.51205 | 0.16521 | 0.080015
17 | 0.98702 | -0.59498 | 0.19252 | 0.09324
18 | 0.98903 | -0.50747 | 0.14071 | 0.06815
19 | 0.99995 | 0.00051137 | 2.0706 | 1.0028
20 | 1 | 0 | -13.2593 | -5.724
21 | 0.98926 | -0.50568 | 0 | 0
22 | 0.98911 | -0.50514 | 0.24685 | 0.11955
23 | 0.98916 | -0.50479 | 0 | 0
24 | 0.98627 | -0.58929 | 0.39588 | 0.19174
25 | 0.98632 | -0.58894 | 0 | 0
26 | 0.9863 | -0.58869 | 0 | 0
27 | 0.98679 | -0.5931 | 0 | 0
28 | 0.98624 | -0.58818 | 0.38058 | 0.18432
29 | 0.98661 | -0.59161 | 0 | 0
30 | 0.9866 | -0.59155 | 0.1635 | 0.079189
31 | 0.98645 | -0.59021 | 0 | 0
32 | 0.98644 | -0.59017 | 0.30753 | 0.14894
33 | 0.98623 | -0.58809 | 0 | 0
34 | 0.98623 | -0.58807 | 0 | 0
35 | 0.98622 | -0.58803 | 0.10429 | 0.050511
36 | 0.99859 | -0.03165 | 0.12064 | 0.058429
37 | 0.9986 | -0.031587 | 0 | 0
38 | 0.99861 | -0.031696 | 0 | 0
39 | 0.99841 | -0.03323 | 0 | 0
40 | 0.9988 | -0.03024 | 0 | 0
41 | 0.9986 | -0.03178 | 0.11875 | 0.057512
42 | 0.99835 | -0.033709 | 0 | 0
43 | 0.9984 | -0.033286 | 0.092805 | 0.044948
44 | 0.99904 | -0.028451 | 0 | 0
45 | 0.99903 | -0.0285 | 0.10675 | 0.051699
46 | 0.99898 | -0.028802 | 0 | 0
47 | 0.99918 | -0.027391 | 0 | 0
48 | 0.99875 | -0.029851 | 0.15878 | 0.0769
49 | 0.99834 | -0.033688 | 0 | 0
50 | 0.9983 | -0.034019 | 0.14862 | 0.071981
51 | 0.9972 | -0.061297 | 0.13327 | 0.064543
52 | 0.99721 | -0.061415 | 0 | 0
53 | 0.99724 | -0.061643 | 0 | 0
54 | 0.99729 | -0.062008 | 0 | 0
55 | 0.99723 | -0.06151 | 0.081378 | 0.039413
56 | 0.99818 | -0.032749 | 0 | 0
57 | 0.99817 | -0.03268 | 0.15111 | 0.073185
58 | 0.99803 | -0.051056 | 0 | 0
59 | 0.99727 | -0.06213 | 0.076798 | 0.037195
60 | 0.99752 | -0.06353 | 0 | 0
61 | 0.99722 | -0.061472 | 0 | 0
62 | 0.99803 | -0.051025 | 0.085957 | 0.041631
63 | 0.99801 | -0.050833 | 0 | 0
64 | 0.9979 | -0.052085 | 0 | 0
65 | 0.99799 | -0.05067 | 0.15081 | 0.073038
66 | 0.99789 | -0.052168 | 0.14465 | 0.070056
67 | 0.99758 | -0.06309 | 0.14168 | 0.068621
68 | 0.99773 | -0.053338 | 0 | 0
69 | 0.99786 | -0.052374 | 0 | 0
70 | 0.99666 | -0.087291 | 0.162 | 0.078459
71 | 0.99675 | -0.086723 | 0.1392 | 0.06742
72 | 0.99432 | -0.23895 | 0.11656 | 0.056455
73 | 0.99677 | -0.086538 | 0 | 0
74 | 0.99719 | -0.074209 | 0 | 0
75 | 0.99702 | -0.084711 | 0.13777 | 0.066727
76 | 0.99699 | -0.084974 | 0 | 0
77 | 0.99775 | -0.053181 | 0.10841 | 0.052507
78 | 0.99778 | -0.052959 | 0 | 0
79 | 0.99321 | -0.26684 | 0.14754 | 0.071457
80 | 0.99367 | -0.26384 | 0 | 0
81 | 0.99378 | -0.26304 | 0.14794 | 0.071651
82 | 0.99379 | -0.26298 | 0 | 0
83 | 0.99389 | -0.26383 | 0 | 0
84 | 0.99389 | -0.2638 | 0.13541 | 0.065584
85 | 0.99428 | -0.23919 | 0 | 0
86 | 0.99366 | -0.26379 | 0.098145 | 0.047534
87 | 0.99898 | -0.028792 | 0.14504 | 0.070245
88 | 0.99957 | -0.0030429 | 0 | 0
89 | 0.99967 | -0.0023123 | 0 | 0
90 | 0.99974 | -0.0017599 | 0.07056 | 0.034174
91 | 0.99918 | -0.027349 | 0.12561 | 0.060836
92 | 0.99984 | -0.0010313 | 2.7101 | 1.3126
93 | 0.99866 | -0.029269 | 0.081853 | 0.039643
94 | 0.99866 | -0.029228 | 0 | 0
95 | 0.99869 | -0.029437 | 0 | 0
96 | 0.99864 | -0.029087 | 0 | 0
97 | 0.99872 | -0.02968 | 0 | 0
98 | 0.99863 | -0.029041 | 0.091589 | 0.044358
99 | 0.99799 | -0.024058 | 0 | 0
100 | 0.99763 | -0.021014 | 0 | 0
101 | 0.99791 | -0.023516 | 0 | 0
102 | 0.99798 | -0.024022 | 0.10929 | 0.052932
103 | 0.9979 | -0.023557 | 0.11702 | 0.056677
104 | 0.99762 | -0.020998 | 0 | 0
105 | 0.99761 | -0.020839 | 0.053913 | 0.026111
106 | 0.99722 | -0.061413 | 0.072504 | 0.035115
107 | 0.99761 | -0.020869 | 0.18995 | 0.091997
108 | 0.99757 | -0.020496 | 0 | 0
109 | 0.99745 | -0.019491 | 0.11126 | 0.053887
110 | 0.99745 | -0.019456 | 0.096647 | 0.046808
111 | 0.99746 | -0.019571 | 0 | 0
112 | 0.99747 | -0.019635 | 0 | 0
113 | 0.99746 | -0.019607 | 0.087221 | 0.042243
114 | 0.99738 | -0.018894 | 0 | 0
115 | 0.99735 | -0.018582 | 0.18129 | 0.087803
116 | 0.99734 | -0.0185 | 0.11975 | 0.058
117 | 0.99733 | -0.018463 | 0.095832 | 0.046413
118 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.2325 | -0.1126 | 0.2325 | 0.11255 | 1.8234e-07 | -5.6596e-05 | 0.0075221 | 0.0075214 | 0.0075221 | 0.9914 | -0.39086 | 0.9914 | -0.39087 | 3.4191
1 | -3.1944 | -1.3488 | 3.1954 | 1.2702 | 0.0010002 | -0.078591 | 0.10097 | 0.10009 | 0.10097 | 0.9914 | -0.39087 | 0.99173 | -0.38851 | 7.9126
2 | 2.9619 | 1.2362 | -2.9613 | -1.2911 | 0.00060707 | -0.054844 | 0.093454 | 0.094085 | 0.094085 | 0.9914 | -0.39087 | 0.99119 | -0.39222 | 7.3734
3 | 0.33448 | 0.16182 | -0.33445 | -0.16198 | 3.2156e-05 | -0.00016095 | 0.010816 | 0.010818 | 0.010818 | 0.99173 | -0.38851 | 0.99163 | -0.38915 | 5.1515
4 | -3.5299 | -1.432 | 3.5338 | 1.4376 | 0.0038732 | 0.0056048 | 0.11088 | 0.11083 | 0.11088 | 0.99173 | -0.38851 | 0.99368 | -0.26539 | 8.5955
5 | 0.15292 | 0.072788 | -0.15292 | -0.074064 | 1.7735e-06 | -0.0012761 | 0.0049326 | 0.0049487 | 0.0049487 | 0.99119 | -0.39222 | 0.99118 | -0.39212 | 2.2494
6 | 2.8084 | 1.2183 | -2.8054 | -1.216 | 0.0029357 | 0.0022893 | 0.089155 | 0.08922 | 0.08922 | 0.99119 | -0.39222 | 0.9893 | -0.50599 | 6.9163
7 | 4.7302 | 1.8998 | -4.73 | -1.9092 | 0.00025795 | -0.0094329 | 0.14755 | 0.14765 | 0.14765 | 0.99731 | -0.07331 | 0.99726 | -0.073741 | 11.5715
8 | -4.8775 | -1.9711 | 4.8779 | 1.9719 | 0.0004059 | 0.00082179 | 0.15227 | 0.15227 | 0.15227 | 0.99731 | -0.07331 | 0.99746 | -0.063946 | 11.8042
9 | 4.73 | 1.9092 | -4.7297 | -1.9196 | 0.00028397 | -0.010368 | 0.14765 | 0.14777 | 0.14777 | 0.99726 | -0.073741 | 0.99719 | -0.074209 | 11.5804
10 | -4.8779 | -1.9719 | 4.8782 | 1.9631 | 0.00025772 | -0.0088557 | 0.15227 | 0.15217 | 0.15227 | 0.99746 | -0.063946 | 0.99752 | -0.06353 | 11.9335
11 | -3.6357 | -1.487 | 3.6358 | 1.4823 | 7.5951e-05 | -0.0046436 | 0.11411 | 0.11406 | 0.11411 | 0.99368 | -0.26539 | 0.99371 | -0.26524 | 8.9431
12 | 0.61573 | 0.28928 | -0.61571 | -0.29019 | 2.0623e-05 | -0.00090941 | 0.019851 | 0.019862 | 0.019862 | 0.9893 | -0.50599 | 0.98927 | -0.50572 | 9.0283
13 | 2.1897 | 0.92669 | -2.1892 | -1.0107 | 0.00051712 | -0.084011 | 0.069381 | 0.070376 | 0.070376 | 0.9893 | -0.50599 | 0.98906 | -0.50736 | 5.5154
14 | -3.6358 | -1.4823 | 3.6364 | 1.4429 | 0.00064238 | -0.039452 | 0.11406 | 0.11363 | 0.11406 | 0.99371 | -0.26524 | 0.99389 | -0.26383 | 8.9391
15 | 0.24689 | 0.11156 | -0.24689 | -0.11189 | 1.1532e-06 | -0.00032244 | 0.0079058 | 0.0079097 | 0.0079097 | 0.98927 | -0.50572 | 0.98926 | -0.50568 | 3.5953
16 | 2.1892 | 1.0107 | -2.1891 | -1.0191 | 5.282e-05 | -0.0084428 | 0.070376 | 0.07048 | 0.07048 | 0.98906 | -0.50736 | 0.98903 | -0.50747 | 5.5235
17 | 1.5466 | 0.70972 | -1.5454 | -0.71137 | 0.0011626 | -0.0016467 | 0.049714 | 0.049754 | 0.049754 | 0.98811 | -0.56042 | 0.98709 | -0.59557 | 6.0676
18 | -1.8823 | -0.8723 | 1.8831 | 0.87105 | 0.00086708 | -0.0012435 | 0.060608 | 0.060564 | 0.060608 | 0.98811 | -0.56042 | 0.98895 | -0.51205 | 4.6983
19 | 1.5454 | 0.71137 | -1.5453 | -0.71216 | 0.00011801 | -0.00079549 | 0.049754 | 0.049764 | 0.049764 | 0.98709 | -0.59557 | 0.98702 | -0.59498 | 22.6201
20 | -2.0483 | -0.95107 | 2.0484 | 0.951 | 8.9447e-05 | -7.1299e-05 | 0.065922 | 0.065918 | 0.065922 | 0.98895 | -0.51205 | 0.98903 | -0.50747 | 5.1102
21 | 1.3528 | 0.61893 | -1.3525 | -0.62188 | 0.00033249 | -0.0029582 | 0.043509 | 0.043547 | 0.043547 | 0.98702 | -0.59498 | 0.98679 | -0.5931 | 19.794
22 | -2.0706 | -1.0028 | 2.0707 | 1.0024 | 0.00012163 | -0.00045705 | 0.066418 | 0.066412 | 0.066418 | 0.99995 | 0.00051137 | 1 | 0 | 30.1899
23 | 11.1746 | 4.7111 | -11.173 | -4.7213 | 0.0016802 | -0.010199 | 0.35008 | 0.3502 | 0.3502 | 1 | 0 | 0.99984 | -0.0010313 | 27.4455
24 | 0.24689 | 0.11189 | -0.24686 | -0.11943 | 2.7304e-05 | -0.0075415 | 0.0079097 | 0.0080031 | 0.0080031 | 0.98926 | -0.50568 | 0.98916 | -0.50479 | 3.6378
25 | -0.24685 | -0.11955 | 0.24686 | 0.11943 | 1.3123e-05 | -0.00012607 | 0.0080048 | 0.0080031 | 0.0080048 | 0.98911 | -0.50514 | 0.98916 | -0.50479 | 3.8118
26 | -0.39588 | -0.19174 | 0.39591 | 0.19166 | 2.1485e-05 | -7.1034e-05 | 0.012875 | 0.012874 | 0.012875 | 0.98627 | -0.58929 | 0.98632 | -0.58894 | 6.1308
27 | 0.48492 | 0.22886 | -0.4849 | -0.22985 | 1.4128e-05 | -0.00099306 | 0.015694 | 0.015706 | 0.015706 | 0.98632 | -0.58894 | 0.9863 | -0.58869 | 7.1392
28 | -0.88082 | -0.42053 | 0.88127 | 0.4111 | 0.00044627 | -0.0094269 | 0.028567 | 0.028448 | 0.028567 | 0.98632 | -0.58894 | 0.98679 | -0.5931 | 12.985
29 | 0.4849 | 0.22985 | -0.48487 | -0.23194 | 2.9692e-05 | -0.0020817 | 0.015706 | 0.015732 | 0.015732 | 0.9863 | -0.58869 | 0.98624 | -0.58818 | 7.1511
30 | 0.47118 | 0.21079 | -0.47109 | -0.21785 | 9.3465e-05 | -0.0070693 | 0.0151 | 0.015186 | 0.015186 | 0.98679 | -0.5931 | 0.98661 | -0.59161 | 6.9029
31 | 0.10429 | 0.047613 | -0.10429 | -0.049419 | 1.1774e-06 | -0.0018064 | 0.0033558 | 0.0033781 | 0.0033781 | 0.98624 | -0.58818 | 0.98623 | -0.58809 | 1.5355
32 | 0.16351 | 0.078531 | -0.1635 | -0.079189 | 1.0664e-06 | -0.00065774 | 0.0053073 | 0.0053156 | 0.0053156 | 0.98661 | -0.59161 | 0.9866 | -0.59155 | 2.4162
33 | 0.30758 | 0.13932 | -0.30753 | -0.1487 | 5.328e-05 | -0.0093754 | 0.0098799 | 0.0099964 | 0.0099964 | 0.98661 | -0.59161 | 0.98645 | -0.59021 | 4.5438
34 | 0.30753 | 0.1487 | -0.30753 | -0.14894 | 1.4032e-06 | -0.00024388 | 0.0099964 | 0.0099995 | 0.0099995 | 0.98645 | -0.59021 | 0.98644 | -0.59017 | 4.5452
35 | 0.10429 | 0.049419 | -0.10429 | -0.049819 | 2.6241e-07 | -0.00039934 | 0.0033781 | 0.0033831 | 0.0033831 | 0.98623 | -0.58809 | 0.98623 | -0.58807 | 1.5378
36 | 0.10429 | 0.049819 | -0.10429 | -0.050511 | 4.5687e-07 | -0.00069244 | 0.0033831 | 0.0033919 | 0.0033919 | 0.98623 | -0.58807 | 0.98622 | -0.58803 | 1.5418
37 | -0.12064 | -0.058429 | 0.12064 | 0.058378 | 1.1612e-06 | -5.0949e-05 | 0.003875 | 0.0038744 | 0.003875 | 0.99859 | -0.03165 | 0.9986 | -0.031587 | 1.8452
38 | -0.12064 | -0.058378 | 0.12064 | 0.05649 | 1.5799e-06 | -0.0018882 | 0.0038744 | 0.0038509 | 0.0038744 | 0.9986 | -0.031587 | 0.99861 | -0.031696 | 1.7611
39 | 6.2714 | 2.4951 | -6.2702 | -2.5198 | 0.0011929 | -0.024704 | 0.19511 | 0.19539 | 0.19539 | 0.99861 | -0.031696 | 0.99841 | -0.03323 | 15.3123
40 | -6.5108 | -2.609 | 6.512 | 2.5866 | 0.0011689 | -0.022436 | 0.20276 | 0.20251 | 0.20276 | 0.99861 | -0.031696 | 0.9988 | -0.03024 | 15.8904
41 | 0.11875 | 0.057445 | -0.11875 | -0.057512 | 1.4949e-06 | -6.7737e-05 | 0.0038133 | 0.0038142 | 0.0038142 | 0.99861 | -0.031696 | 0.9986 | -0.03178 | 1.8163
42 | 6.1774 | 2.4749 | -6.177 | -2.4828 | 0.00037043 | -0.0078995 | 0.19241 | 0.1925 | 0.1925 | 0.99841 | -0.03323 | 0.99835 | -0.033709 | 15.0861
43 | 0.092806 | 0.044889 | -0.092805 | -0.044948 | 7.8196e-07 | -5.8277e-05 | 0.0029808 | 0.0029815 | 0.0029815 | 0.99841 | -0.03323 | 0.9984 | -0.033286 | 1.4198
44 | 1.496 | 0.66202 | -1.4959 | -0.66266 | 8.307e-05 | -0.00063818 | 0.047282 | 0.04729 | 0.04729 | 0.9988 | -0.03024 | 0.99875 | -0.029851 | 21.4954
45 | -8.008 | -3.2486 | 8.0098 | 3.2258 | 0.0018311 | -0.022816 | 0.24977 | 0.24951 | 0.24977 | 0.9988 | -0.03024 | 0.99904 | -0.028451 | 19.5742
46 | 0.15114 | 0.051026 | -0.15114 | -0.052217 | 1.4264e-06 | -0.0011918 | 0.0046125 | 0.0046236 | 0.0046236 | 0.99835 | -0.033709 | 0.99834 | -0.033688 | 2.1017
47 | 6.0259 | 2.4318 | -6.0256 | -2.4371 | 0.0002383 | -0.0053358 | 0.18789 | 0.18795 | 0.18795 | 0.99835 | -0.033709 | 0.9983 | -0.034019 | 14.7299
48 | 0.10675 | 0.051654 | -0.10675 | -0.051699 | 8.0411e-07 | -4.5287e-05 | 0.0034266 | 0.0034272 | 0.0034272 | 0.99904 | -0.028451 | 0.99903 | -0.0285 | 1.632
49 | 0.14505 | 0.069879 | -0.14504 | -0.07011 | 7.6333e-06 | -0.00023092 | 0.0046522 | 0.0046551 | 0.0046551 | 0.99904 | -0.028451 | 0.99898 | -0.028802 | 2.2167
50 | -8.2616 | -3.3473 | 8.2627 | 3.3342 | 0.0011199 | -0.013083 | 0.25757 | 0.25742 | 0.25757 | 0.99904 | -0.028451 | 0.99918 | -0.027391 | 20.1858
51 | 0.14504 | 0.07011 | -0.14504 | -0.070245 | 1.6426e-07 | -0.0001352 | 0.0046551 | 0.0046568 | 0.0046568 | 0.99898 | -0.028802 | 0.99898 | -0.028792 | 2.1167
52 | 0.12561 | 0.060161 | -0.12561 | -0.060836 | 6.1329e-07 | -0.00067474 | 0.0040238 | 0.0040323 | 0.0040323 | 0.99918 | -0.027391 | 0.99918 | -0.027349 | 1.8328
53 | -8.3883 | -3.3944 | 8.3901 | 3.3989 | 0.0018166 | 0.0044738 | 0.26144 | 0.26143 | 0.26144 | 0.99918 | -0.027391 | 0.99957 | -0.0030429 | 20.2665
54 | 1.3371 | 0.58576 | -1.3371 | -0.58608 | 3.3624e-05 | -0.00032692 | 0.042194 | 0.042198 | 0.042198 | 0.99875 | -0.029851 | 0.99872 | -0.02968 | 19.1808
55 | 0.15114 | 0.052217 | -0.15111 | -0.072256 | 2.5124e-05 | -0.020039 | 0.0046236 | 0.004844 | 0.004844 | 0.99834 | -0.033688 | 0.99818 | -0.032749 | 2.2018
56 | 5.877 | 2.3651 | -5.8761 | -2.3631 | 0.0008878 | 0.0019791 | 0.18319 | 0.18319 | 0.18319 | 0.9983 | -0.034019 | 0.99803 | -0.051056 | 14.201
57 | -0.13327 | -0.064543 | 0.13327 | 0.06274 | 1.8539e-06 | -0.0018034 | 0.0042865 | 0.004264 | 0.0042865 | 0.9972 | -0.061297 | 0.99721 | -0.061415 | 1.9484
58 | -0.13327 | -0.06274 | 0.13327 | 0.058749 | 4.0349e-06 | -0.0039912 | 0.004264 | 0.0042161 | 0.004264 | 0.99721 | -0.061415 | 0.99724 | -0.061643 | 1.9382
59 | -0.28716 | -0.12833 | 0.28717 | 0.12509 | 1.5095e-05 | -0.003248 | 0.0091048 | 0.0090668 | 0.0091048 | 0.99724 | -0.061643 | 0.99729 | -0.062008 | 4.1385
60 | 0.15389 | 0.069586 | -0.15388 | -0.071567 | 2.6757e-06 | -0.0019807 | 0.0048889 | 0.0049128 | 0.0049128 | 0.99724 | -0.061643 | 0.99723 | -0.06151 | 2.2331
61 | 0.0768 | 0.037041 | -0.076798 | -0.037195 | 1.4148e-06 | -0.00015377 | 0.0024681 | 0.00247 | 0.00247 | 0.99729 | -0.062008 | 0.99727 | -0.06213 | 1.1762
62 | -0.36397 | -0.16213 | 0.36406 | 0.15048 | 8.6254e-05 | -0.011648 | 0.011533 | 0.0114 | 0.011533 | 0.99729 | -0.062008 | 0.99752 | -0.06353 | 5.2425
63 | 0.072505 | 0.032153 | -0.072505 | -0.033409 | 3.7472e-07 | -0.001256 | 0.002296 | 0.002311 | 0.002311 | 0.99723 | -0.06151 | 0.99722 | -0.061472 | 1.0504
64 | 0.15111 | 0.072256 | -0.15111 | -0.073185 | 1.2272e-06 | -0.00092933 | 0.004844 | 0.0048557 | 0.0048557 | 0.99818 | -0.032749 | 0.99817 | -0.03268 | 2.2071
65 | 0.15081 | 0.06741 | -0.15081 | -0.070816 | 4.4041e-06 | -0.0034061 | 0.0047781 | 0.0048191 | 0.0048191 | 0.99803 | -0.051056 | 0.99801 | -0.050833 | 2.1905
66 | 5.6394 | 2.2548 | -5.6386 | -2.2735 | 0.00072784 | -0.018673 | 0.17567 | 0.17588 | 0.17588 | 0.99803 | -0.051056 | 0.9979 | -0.052085 | 13.7834
67 | 0.085957 | 0.040905 | -0.085957 | -0.041631 | 3.0976e-07 | -0.00072539 | 0.0027534 | 0.0027625 | 0.0027625 | 0.99803 | -0.051056 | 0.99803 | -0.051025 | 1.2557
68 | -5.2423 | -2.1136 | 5.2426 | 2.1049 | 0.00029081 | -0.0086381 | 0.16357 | 0.16348 | 0.16357 | 0.99752 | -0.06353 | 0.99758 | -0.06309 | 12.8193
69 | 0.072505 | 0.033409 | -0.072504 | -0.035115 | 5.1701e-07 | -0.0017061 | 0.002311 | 0.0023321 | 0.0023321 | 0.99722 | -0.061472 | 0.99722 | -0.061413 | 1.06
70 | 0.15081 | 0.070816 | -0.15081 | -0.073038 | 2.9144e-06 | -0.0022218 | 0.0048191 | 0.0048468 | 0.0048468 | 0.99801 | -0.050833 | 0.99799 | -0.05067 | 2.2031
71 | 5.6386 | 2.2735 | -5.6386 | -2.275 | 5.9563e-05 | -0.0015259 | 0.17588 | 0.17589 | 0.17589 | 0.9979 | -0.052085 | 0.99789 | -0.052168 | 13.7847
72 | 5.4939 | 2.205 | -5.4938 | -2.2088 | 0.00014161 | -0.0038298 | 0.17125 | 0.1713 | 0.1713 | 0.99789 | -0.052168 | 0.99786 | -0.052374 | 13.4245
73 | -5.3842 | -2.1736 | 5.3847 | 2.1746 | 0.0004664 | 0.00099951 | 0.16802 | 0.16802 | 0.16802 | 0.99758 | -0.06309 | 0.99773 | -0.053338 | 13.0251
74 | -5.3847 | -2.1746 | 5.3848 | 2.1715 | 0.00010729 | -0.0030173 | 0.16802 | 0.16799 | 0.16802 | 0.99773 | -0.053338 | 0.99775 | -0.053181 | 13.1678
75 | 5.4938 | 2.2088 | -5.4934 | -2.2198 | 0.00040773 | -0.011015 | 0.1713 | 0.17142 | 0.17142 | 0.99786 | -0.052374 | 0.99778 | -0.052959 | 13.434
76 | -0.162 | -0.078459 | 0.16201 | 0.078128 | 1.3863e-05 | -0.00033109 | 0.0052135 | 0.0052093 | 0.0052135 | 0.99666 | -0.087291 | 0.99675 | -0.086723 | 2.4826
77 | 4.2891 | 1.7534 | -4.2832 | -1.7427 | 0.0058223 | 0.010696 | 0.1342 | 0.13425 | 0.13425 | 0.99675 | -0.086723 | 0.99432 | -0.23895 | 10.4071
78 | -4.5903 | -1.899 | 4.5904 | 1.8945 | 0.00011544 | -0.0044436 | 0.14387 | 0.14382 | 0.14387 | 0.99675 | -0.086723 | 0.99677 | -0.086538 | 11.275
79 | 4.1667 | 1.6863 | -4.1665 | -1.6923 | 0.00012832 | -0.0059833 | 0.1305 | 0.13057 | 0.13057 | 0.99432 | -0.23895 | 0.99428 | -0.23919 | 10.2325
80 | -4.5904 | -1.8945 | 4.5913 | 1.8579 | 0.00094717 | -0.036585 | 0.14382 | 0.14341 | 0.14382 | 0.99677 | -0.086538 | 0.99699 | -0.084974 | 11.2711
81 | 4.7297 | 1.9196 | -4.7293 | -1.9187 | 0.00044218 | 0.00087723 | 0.14777 | 0.14777 | 0.14777 | 0.99719 | -0.074209 | 0.99702 | -0.084711 | 11.455
82 | 4.5915 | 1.852 | -4.5913 | -1.8579 | 0.00015378 | -0.0059614 | 0.14335 | 0.14341 | 0.14341 | 0.99702 | -0.084711 | 0.99699 | -0.084974 | 11.2392
83 | -5.4932 | -2.224 | 5.4934 | 2.2198 | 0.00015639 | -0.0042204 | 0.17147 | 0.17142 | 0.17147 | 0.99775 | -0.053181 | 0.99778 | -0.052959 | 13.4377
84 | -0.14754 | -0.071457 | 0.1476 | 0.069629 | 6.3816e-05 | -0.0018281 | 0.0047647 | 0.0047413 | 0.0047647 | 0.99321 | -0.26684 | 0.99367 | -0.26384 | 2.2689
85 | 0.098146 | 0.04633 | -0.098145 | -0.047534 | 6.8101e-07 | -0.0012037 | 0.003153 | 0.0031681 | 0.0031681 | 0.99367 | -0.26384 | 0.99366 | -0.26379 | 1.44
86 | -0.24575 | -0.11596 | 0.24578 | 0.11567 | 2.9189e-05 | -0.00029177 | 0.0078943 | 0.0078904 | 0.0078943 | 0.99367 | -0.26384 | 0.99379 | -0.26298 | 3.7592
87 | -0.14794 | -0.071651 | 0.14794 | 0.071614 | 1.2999e-06 | -3.6918e-05 | 0.0047749 | 0.0047744 | 0.0047749 | 0.99378 | -0.26304 | 0.99379 | -0.26298 | 2.2737
88 | -0.39372 | -0.18728 | 0.39376 | 0.18272 | 4.1367e-05 | -0.0045643 | 0.012665 | 0.012608 | 0.012665 | 0.99379 | -0.26298 | 0.99389 | -0.26383 | 5.7567
89 | 0.13542 | 0.065017 | -0.13541 | -0.065584 | 6.1263e-07 | -0.00056747 | 0.004363 | 0.0043701 | 0.0043701 | 0.99389 | -0.26383 | 0.99389 | -0.2638 | 1.9864
90 | -4.1656 | -1.6906 | 4.1665 | 1.6923 | 0.00091422 | 0.0016377 | 0.13058 | 0.13057 | 0.13058 | 0.99389 | -0.26383 | 0.99428 | -0.23919 | 10.1221
91 | -8.3901 | -3.3989 | 8.3909 | 3.39 | 0.0007853 | -0.0088997 | 0.26143 | 0.26133 | 0.26143 | 0.99957 | -0.0030429 | 0.99967 | -0.0023123 | 20.4885
92 | -8.3909 | -3.39 | 8.3915 | 3.3833 | 0.00058976 | -0.0066897 | 0.26133 | 0.26126 | 0.26133 | 0.99967 | -0.0023123 | 0.99974 | -0.0017599 | 20.4806
93 | -8.4621 | -3.4175 | 8.4628 | 3.4087 | 0.00078302 | -0.0087303 | 0.26351 | 0.26342 | 0.26351 | 0.99974 | -0.0017599 | 0.99984 | -0.0010313 | 20.6516
94 | 0.091591 | 0.038376 | -0.091591 | -0.039679 | 6.0503e-07 | -0.0013028 | 0.0028706 | 0.0028853 | 0.0028853 | 0.99866 | -0.029269 | 0.99866 | -0.029228 | 1.3115
95 | -0.17344 | -0.078019 | 0.17345 | 0.075549 | 4.1652e-06 | -0.0024701 | 0.0054975 | 0.0054686 | 0.0054975 | 0.99866 | -0.029269 | 0.99869 | -0.029437 | 2.4989
96 | 0.091591 | 0.039679 | -0.091589 | -0.04334 | 1.7343e-06 | -0.0036607 | 0.0028853 | 0.002929 | 0.002929 | 0.99866 | -0.029228 | 0.99864 | -0.029087 | 1.3314
97 | -0.17345 | -0.075549 | 0.17346 | 0.071446 | 6.8244e-06 | -0.0041038 | 0.0054686 | 0.0054223 | 0.0054686 | 0.99869 | -0.029437 | 0.99872 | -0.02968 | 2.4857
98 | 0.091589 | 0.04334 | -0.091589 | -0.044358 | 4.9223e-07 | -0.0010188 | 0.002929 | 0.0029417 | 0.0029417 | 0.99864 | -0.029087 | 0.99863 | -0.029041 | 1.3371
99 | 1.1636 | 0.51464 | -1.1627 | -0.5263 | 0.00090831 | -0.011656 | 0.036777 | 0.036918 | 0.036918 | 0.99872 | -0.02968 | 0.99799 | -0.024058 | 16.7809
100 | 0.93641 | 0.43045 | -0.93605 | -0.43757 | 0.00036198 | -0.0071241 | 0.029811 | 0.029899 | 0.029899 | 0.99799 | -0.024058 | 0.99763 | -0.021014 | 13.5905
101 | 0.11703 | 0.043579 | -0.11702 | -0.056644 | 9.9494e-06 | -0.013064 | 0.0036124 | 0.003761 | 0.003761 | 0.99799 | -0.024058 | 0.99791 | -0.023516 | 1.7096
102 | 0.10929 | 0.05227 | -0.10929 | -0.052932 | 4.5798e-07 | -0.00066261 | 0.0035043 | 0.0035126 | 0.0035126 | 0.99799 | -0.024058 | 0.99798 | -0.024022 | 1.5966
103 | 0.18995 | 0.090455 | -0.18995 | -0.090627 | 3.5677e-07 | -0.00017118 | 0.0060879 | 0.00609 | 0.00609 | 0.99763 | -0.021014 | 0.99762 | -0.020998 | 2.7682
104 | 0.7461 | 0.34711 | -0.74608 | -0.34763 | 1.6433e-05 | -0.00051089 | 0.023811 | 0.023818 | 0.023818 | 0.99763 | -0.021014 | 0.99761 | -0.020839 | 10.8262
105 | 0.11702 | 0.056644 | -0.11702 | -0.056677 | 7.2189e-07 | -3.3596e-05 | 0.003761 | 0.0037614 | 0.0037614 | 0.99791 | -0.023516 | 0.9979 | -0.023557 | 1.7912
106 | 0.18995 | 0.090627 | -0.18995 | -0.091997 | 2.8643e-06 | -0.0013699 | 0.00609 | 0.0061072 | 0.0061072 | 0.99762 | -0.020998 | 0.99761 | -0.020869 | 2.776
107 | 0.69217 | 0.32151 | -0.69214 | -0.32259 | 2.9826e-05 | -0.0010789 | 0.022084 | 0.022098 | 0.022098 | 0.99761 | -0.020839 | 0.99757 | -0.020496 | 10.0444
108 | 0.69214 | 0.32259 | -0.69206 | -0.32526 | 7.4009e-05 | -0.0026712 | 0.022098 | 0.022131 | 0.022131 | 0.99757 | -0.020496 | 0.99747 | -0.019635 | 10.0594
109 | 0.096647 | 0.046078 | -0.096647 | -0.046808 | 3.9534e-07 | -0.00073032 | 0.0030987 | 0.0031079 | 0.0031079 | 0.99745 | -0.019491 | 0.99745 | -0.019456 | 1.4127
110 | -0.20791 | -0.099965 | 0.20791 | 0.099184 | 1.9528e-06 | -0.00078007 | 0.0066766 | 0.0066668 | 0.0066766 | 0.99745 | -0.019491 | 0.99746 | -0.019571 | 3.0348
111 | -0.20791 | -0.099184 | 0.20791 | 0.098545 | 1.5968e-06 | -0.00063958 | 0.0066668 | 0.0066588 | 0.0066668 | 0.99746 | -0.019571 | 0.99747 | -0.019635 | 3.0304
112 | 0.087221 | 0.041596 | -0.087221 | -0.042243 | 2.8505e-07 | -0.00064658 | 0.0027966 | 0.0028047 | 0.0028047 | 0.99747 | -0.019635 | 0.99746 | -0.019607 | 1.2749
113 | 0.39693 | 0.18512 | -0.39689 | -0.18907 | 3.5909e-05 | -0.0039508 | 0.012675 | 0.012724 | 0.012724 | 0.99747 | -0.019635 | 0.99738 | -0.018894 | 5.7838
114 | 0.39689 | 0.18907 | -0.39688 | -0.19067 | 1.4601e-05 | -0.0015975 | 0.012724 | 0.012744 | 0.012744 | 0.99738 | -0.018894 | 0.99735 | -0.018582 | 5.7929
115 | 0.21559 | 0.10287 | -0.21559 | -0.10364 | 2.0795e-06 | -0.00077218 | 0.006914 | 0.0069237 | 0.0069237 | 0.99735 | -0.018582 | 0.99734 | -0.0185 | 3.1471
116 | 0.095832 | 0.045641 | -0.095832 | -0.046413 | 4.1113e-07 | -0.00077227 | 0.0030723 | 0.003082 | 0.003082 | 0.99734 | -0.0185 | 0.99733 | -0.018463 | 1.4009

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 13.2593 | 5.724

## res_load
| p_mw | q_mvar
0 | 0.2325 | 0.1126
1 | 0.1473 | 0.07134
2 | 0.33445 | 0.16198
3 | 0.10198 | 0.04939
4 | 0.15292 | 0.074064
5 | 0.36882 | 0.17863
6 | 0.33567 | 0.16257
7 | 0.16521 | 0.080015
8 | 0.19252 | 0.09324
9 | 0.14071 | 0.06815
10 | 2.0706 | 1.0028
11 | 0.24685 | 0.11955
12 | 0.39588 | 0.19174
13 | 0.38058 | 0.18432
14 | 0.1635 | 0.079189
15 | 0.30753 | 0.14894
16 | 0.10429 | 0.050511
17 | 0.12064 | 0.058429
18 | 0.11875 | 0.057512
19 | 0.092805 | 0.044948
20 | 0.10675 | 0.051699
21 | 0.15878 | 0.0769
22 | 0.14862 | 0.071981
23 | 0.13327 | 0.064543
24 | 0.081378 | 0.039413
25 | 0.15111 | 0.073185
26 | 0.076798 | 0.037195
27 | 0.085957 | 0.041631
28 | 0.15081 | 0.073038
29 | 0.14465 | 0.070056
30 | 0.14168 | 0.068621
31 | 0.162 | 0.078459
32 | 0.1392 | 0.06742
33 | 0.11656 | 0.056455
34 | 0.13777 | 0.066727
35 | 0.10841 | 0.052507
36 | 0.14754 | 0.071457
37 | 0.14794 | 0.071651
38 | 0.13541 | 0.065584
39 | 0.098145 | 0.047534
40 | 0.14504 | 0.070245
41 | 0.07056 | 0.034174
42 | 0.12561 | 0.060836
43 | 2.7101 | 1.3126
44 | 0.081853 | 0.039643
45 | 0.091589 | 0.044358
46 | 0.10929 | 0.052932
47 | 0.11702 | 0.056677
48 | 0.053913 | 0.026111
49 | 0.072504 | 0.035115
50 | 0.18995 | 0.091997
51 | 0.11126 | 0.053887
52 | 0.096647 | 0.046808
53 | 0.087221 | 0.042243
54 | 0.18129 | 0.087803
55 | 0.11975 | 0.058
56 | 0.095832 | 0.046413

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1