## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_387_1_node_3 | 20 | n |  | TRUE
1 | bus_MV_387_1_node_5 | 20 | n |  | TRUE
2 | bus_MV_387_1_node_7 | 20 | n |  | TRUE
3 | bus_MV_387_1_node_6 | 20 | n |  | TRUE
4 | bus_MV_387_1_node_10 | 20 | n |  | TRUE
5 | bus_MV_387_1_node_8 | 20 | n |  | TRUE
6 | bus_MV_387_1_node_9 | 20 | n |  | TRUE
7 | bus_MV_387_1_node_177 | 20 | n |  | TRUE
8 | bus_MV_387_1_node_24 | 20 | n |  | TRUE
9 | bus_MV_387_1_node_25 | 20 | n |  | TRUE
10 | bus_MV_387_1_node_215 | 20 | n |  | TRUE
11 | bus_MV_387_1_node_26 | 20 | n |  | TRUE
12 | bus_MV_387_1_node_27 | 20 | n |  | TRUE
13 | bus_MV_387_1_node_28 | 20 | n |  | TRUE
14 | bus_MV_387_1_node_30 | 20 | n |  | TRUE
15 | bus_MV_387_1_node_29 | 20 | n |  | TRUE
16 | bus_MV_387_1_node_216 | 20 | n |  | TRUE
17 | bus_MV_387_1_node_31 | 20 | n |  | TRUE
18 | bus_MV_387_1_node_32 | 20 | n |  | TRUE
19 | bus_MV_387_1_node_201 | 20 | n |  | TRUE
20 | bus_MV_387_1_node_33 | 20 | n |  | TRUE
21 | bus_MV_387_1_node_34 | 20 | n |  | TRUE
22 | bus_MV_387_1_node_35 | 20 | n |  | TRUE
23 | bus_MV_387_1_node_36 | 20 | n |  | TRUE
24 | bus_MV_387_1_node_42 | 20 | n |  | TRUE
25 | bus_MV_387_1_node_194 | 20 | n |  | TRUE
26 | bus_MV_387_1_node_43 | 20 | n |  | TRUE
27 | bus_MV_387_1_node_37 | 20 | n |  | TRUE
28 | bus_MV_387_1_node_39 | 20 | n |  | TRUE
29 | bus_MV_387_1_node_195 | 20 | n |  | TRUE
30 | bus_MV_387_1_node_167 | 20 | n |  | TRUE
31 | bus_MV_387_1_node_38 | 20 | n |  | TRUE
32 | bus_MV_387_1_node_40 | 20 | n |  | TRUE
33 | bus_MV_387_1_node_41 | 20 | n |  | TRUE
34 | bus_MV_387_1_node_166 | 20 | n |  | TRUE
35 | bus_MV_387_1_node_168 | 20 | n |  | TRUE
36 | bus_MV_387_1_node_193 | 20 | n |  | TRUE
37 | bus_MV_387_1_node_196 | 20 | n |  | TRUE
38 | bus_MV_387_1_node_187 | 20 | n |  | TRUE
39 | bus_MV_387_1_node_188 | 20 | n |  | TRUE
40 | bus_MV_387_1_node_189 | 20 | n |  | TRUE
41 | bus_MV_387_1_node_199 | 20 | n |  | TRUE
42 | bus_MV_387_1_node_72 | 20 | n |  | TRUE
43 | bus_MV_387_1_node_202 | 20 | n |  | TRUE
44 | bus_MV_387_1_node_203 | 20 | n |  | TRUE
45 | bus_MV_387_1_node_204 | 20 | n |  | TRUE
46 | bus_HV_387_1_node_30 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_387_1_load_3 | 0 | 0.28593 | 0.13848 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_387_1_load_10 | 4 | 0.13819 | 0.066929 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_387_1_load_8 | 5 | 0.30146 | 0.146 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_387_1_load_177 | 7 | 0.15425 | 0.074708 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_387_1_load_24 | 8 | 0.051469 | 0.024928 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_387_1_load_215 | 10 | 0.27397 | 0.13269 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_387_1_load_26 | 11 | 0.28017 | 0.13569 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_387_1_load_30 | 14 | 0.1678 | 0.081269 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_387_1_load_29 | 15 | 0.0727 | 0.03521 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_387_1_load_33 | 20 | 0.37323 | 0.18076 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_387_1_load_42 | 24 | 0.093412 | 0.045241 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_387_1_load_194 | 25 | 0.13615 | 0.065942 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_387_1_load_43 | 26 | 0.10654 | 0.051601 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_387_1_load_37 | 27 | 0.12914 | 0.062546 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_387_1_load_39 | 28 | 0.10613 | 0.051399 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_387_1_load_195 | 29 | 0.099084 | 0.047989 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_387_1_load_167 | 30 | 0.24061 | 0.11653 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_387_1_load_38 | 31 | 0.18987 | 0.091958 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_387_1_load_41 | 33 | 0.12529 | 0.060683 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_387_1_load_166 | 34 | 0.081833 | 0.039633 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_387_1_load_193 | 36 | 0.21484 | 0.10405 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_387_1_load_187 | 38 | 0.10831 | 0.052456 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_387_1_load_199 | 41 | 0.1239 | 0.060007 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_387_1_load_72 | 42 | 0.13633 | 0.066027 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_387_1_load_204 | 45 | 0.1642 | 0.079524 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_387_1_line_0 |  | 0 | 1 | 0.063303 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_387_1_line_1 |  | 1 | 2 | 0.47045 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_387_1_line_2 |  | 1 | 3 | 0.31459 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_387_1_line_3 |  | 2 | 5 | 0.13733 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_387_1_line_4 |  | 3 | 4 | 0.02722 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_387_1_line_5 |  | 5 | 6 | 0.11418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_387_1_line_6 |  | 6 | 7 | 0.91578 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_387_1_line_7 |  | 7 | 37 | 1.5155 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_387_1_line_8 |  | 8 | 9 | 0.007667 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_387_1_line_9 |  | 9 | 10 | 0.66576 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_387_1_line_10 |  | 10 | 44 | 0.028346 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_387_1_line_11 |  | 11 | 12 | 0.051355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_387_1_line_12 |  | 11 | 13 | 0.070688 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_387_1_line_13 |  | 12 | 14 | 1.2036 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_387_1_line_14 |  | 13 | 15 | 1.5238 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_387_1_line_15 |  | 13 | 16 | 1.4573 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_387_1_line_16 |  | 14 | 17 | 0.022278 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_387_1_line_17 |  | 16 | 45 | 0.24253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_387_1_line_18 |  | 17 | 18 | 0.32557 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_387_1_line_19 |  | 17 | 19 | 1.4946 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_387_1_line_20 |  | 18 | 20 | 0.077587 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_387_1_line_21 |  | 19 | 40 | 0.068378 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_387_1_line_22 |  | 20 | 21 | 0.021265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_387_1_line_23 |  | 21 | 22 | 1.378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_387_1_line_24 |  | 22 | 23 | 0.89495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_387_1_line_25 |  | 22 | 24 | 0.063982 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_387_1_line_26 |  | 23 | 25 | 0.020545 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_387_1_line_27 |  | 23 | 26 | 0.69166 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_387_1_line_28 |  | 24 | 28 | 0.023679 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_387_1_line_29 |  | 27 | 28 | 0.033095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_387_1_line_30 |  | 27 | 29 | 1.345 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_387_1_line_31 |  | 27 | 30 | 0.082163 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_387_1_line_32 |  | 29 | 37 | 0.0224 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_387_1_line_33 |  | 30 | 35 | 0.022788 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_387_1_line_34 |  | 31 | 32 | 0.031056 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_387_1_line_35 |  | 32 | 33 | 0.002857 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_387_1_line_36 |  | 33 | 34 | 0.027206 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_387_1_line_37 |  | 34 | 35 | 0.02165 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_387_1_line_38 |  | 35 | 36 | 1.4278 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_387_1_line_39 |  | 36 | 42 | 2.0494 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_387_1_line_40 |  | 38 | 39 | 0.055307 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_387_1_line_41 |  | 39 | 40 | 1.2516 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_387_1_line_42 |  | 40 | 41 | 0.044781 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_387_1_line_43 |  | 43 | 44 | 0.66625 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_387_1_line_44 |  | 43 | 45 | 0.069084 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_387_1_trafo_30 | 25 MVA 110/20 kV | 46 | 14 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2600603.9822 | 1215350.4965
1 | 2600566.8025 | 1215401.8
2 | 2600225.0159 | 1215597.6697
3 | 2600814.8933 | 1215595.2348
4 | 2600807.9124 | 1215621.2153
5 | 2600101.619 | 1215657.9462
6 | 2600025.8832 | 1215742.0938
7 | 2599255.0379 | 1215247.6821
8 | 2600031.2891 | 1210254.4481
9 | 2600023.644 | 1210255.2709
10 | 2599618.8838 | 1209726.6843
11 | 2599155.6613 | 1211613.4841
12 | 2599115.7019 | 1211644.0074
13 | 2599191.8786 | 1211552.7449
14 | 2598104.3003 | 1212296.4635
15 | 2600713.6383 | 1211632.1807
16 | 2599266.0647 | 1210097.36
17 | 2598091.3491 | 1212278.3132
18 | 2597898.2803 | 1212381.6382
19 | 2597797.8289 | 1210812.836
20 | 2597880.1592 | 1212456.8646
21 | 2597858.8576 | 1212455.8163
22 | 2597616.3801 | 1213141.9947
23 | 2597234.3795 | 1212476.0145
24 | 2597593.9664 | 1213201.9221
25 | 2597254.9584 | 1212474.9708
26 | 2596545.3396 | 1212415.8934
27 | 2597574.4074 | 1213255.22
28 | 2597585.8088 | 1213224.1513
29 | 2598808.593 | 1213789.8186
30 | 2597542.1109 | 1213330.769
31 | 2597500.1275 | 1213304.7792
32 | 2597485.6846 | 1213330.8668
33 | 2597488.3003 | 1213332.0161
34 | 2597513.2081 | 1213342.9602
35 | 2597533.0292 | 1213351.6692
36 | 2597280.8089 | 1214757.0262
37 | 2598830.8621 | 1213792.7712
38 | 2597253.9847 | 1209822.1749
39 | 2597262.3706 | 1209876.8123
40 | 2597738.3929 | 1210779.0291
41 | 2597774.8726 | 1210753.0561
42 | 2595275.2369 | 1215178.8079
43 | 2599253.0505 | 1209796.095
44 | 2599635.4885 | 1209703.6925
45 | 2599249.7464 | 1209865.1003
46 | 2598104.3003 | 1212296.4635

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98659 | 0.007938 | 0.28593 | 0.13848
1 | 0.98661 | 0.0077185 | 0 | 0
2 | 0.98687 | 0.0055112 | 0 | 0
3 | 0.98653 | 0.0071564 | 0 | 0
4 | 0.98652 | 0.0072021 | 0.13819 | 0.066929
5 | 0.98698 | 0.006396 | 0.30146 | 0.146
6 | 0.98709 | 0.0054898 | 0 | 0
7 | 0.98838 | 0.015063 | 0.15425 | 0.074708
8 | 0.99606 | -0.023708 | 0.051469 | 0.024928
9 | 0.99606 | -0.023712 | 0 | 0
10 | 0.99613 | -0.023262 | 0.27397 | 0.13269
11 | 0.99801 | -0.014982 | 0.28017 | 0.13569
12 | 0.99807 | -0.015407 | 0 | 0
13 | 0.99796 | -0.014629 | 0 | 0
14 | 1 | 0 | -4.0281 | -1.7917
15 | 0.99775 | -0.016091 | 0.0727 | 0.03521
16 | 0.99661 | -0.026313 | 0 | 0
17 | 0.99991 | 0.00065762 | 0 | 0
18 | 0.9987 | 0.010147 | 0 | 0
19 | 0.99928 | -0.0076349 | 0 | 0
20 | 0.99842 | 0.012436 | 0.37323 | 0.18076
21 | 0.99835 | 0.01297 | 0 | 0
22 | 0.99389 | 0.049196 | 0 | 0
23 | 0.99361 | 0.051143 | 0 | 0
24 | 0.9937 | 0.050861 | 0.093412 | 0.045241
25 | 0.99361 | 0.051177 | 0.13615 | 0.065942
26 | 0.99347 | 0.050217 | 0.10654 | 0.051601
27 | 0.99354 | 0.052236 | 0.12914 | 0.062546
28 | 0.99363 | 0.051451 | 0.10613 | 0.051399
29 | 0.99099 | 0.033701 | 0.099084 | 0.047989
30 | 0.99339 | 0.051195 | 0.24061 | 0.11653
31 | 0.99333 | 0.051673 | 0.18987 | 0.091958
32 | 0.99334 | 0.051603 | 0 | 0
33 | 0.99334 | 0.051596 | 0.12529 | 0.060683
34 | 0.99335 | 0.051494 | 0.081833 | 0.039633
35 | 0.99336 | 0.051392 | 0 | 0
36 | 0.99239 | 0.044846 | 0.21484 | 0.10405
37 | 0.99096 | 0.033914 | 0 | 0
38 | 0.99908 | -0.0076123 | 0.10831 | 0.052456
39 | 0.99909 | -0.0076818 | 0 | 0
40 | 0.99925 | -0.0080091 | 0 | 0
41 | 0.99924 | -0.0080763 | 0.1239 | 0.060007
42 | 0.99185 | 0.041203 | 0.13633 | 0.066027
43 | 0.99642 | -0.025577 | 0 | 0
44 | 0.99614 | -0.023371 | 0 | 0
45 | 0.99646 | -0.025199 | 0.1642 | 0.079524
46 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.28593 | -0.13848 | 0.28593 | 0.13701 | 7.2878e-06 | -0.001469 | 0.0092957 | 0.009277 | 0.0092957 | 0.98659 | 0.007938 | 0.98661 | 0.0077185 | 4.2253
1 | -0.42414 | -0.20295 | 0.42425 | 0.19205 | 0.00011769 | -0.010902 | 0.013757 | 0.013622 | 0.013757 | 0.98661 | 0.0077185 | 0.98687 | 0.0055112 | 6.2534
2 | 0.1382 | 0.065938 | -0.13819 | -0.066296 | 1.1263e-05 | -0.00035848 | 0.0044804 | 0.004485 | 0.004485 | 0.98661 | 0.0077185 | 0.98653 | 0.0071564 | 2.1357
3 | -0.42425 | -0.19205 | 0.4243 | 0.19192 | 4.5399e-05 | -0.00013125 | 0.013622 | 0.01362 | 0.013622 | 0.98687 | 0.0055112 | 0.98698 | 0.006396 | 6.4868
4 | 0.13819 | 0.066296 | -0.13819 | -0.066929 | 7.3226e-07 | -0.00063229 | 0.004485 | 0.004493 | 0.004493 | 0.98653 | 0.0071564 | 0.98652 | 0.0072021 | 2.0423
5 | -0.72576 | -0.33792 | 0.72584 | 0.33529 | 8.3457e-05 | -0.0026312 | 0.023415 | 0.023383 | 0.023415 | 0.98698 | 0.006396 | 0.98709 | 0.0054898 | 10.6433
6 | -0.72584 | -0.33529 | 0.72673 | 0.33478 | 0.0008916 | -0.00050813 | 0.023383 | 0.02337 | 0.023383 | 0.98709 | 0.0054898 | 0.98838 | 0.015063 | 11.1346
7 | -0.88099 | -0.40949 | 0.88316 | 0.40908 | 0.0021723 | -0.00041137 | 0.028375 | 0.028353 | 0.028375 | 0.98838 | 0.015063 | 0.99096 | 0.033914 | 13.5118
8 | -0.051469 | -0.024928 | 0.051469 | 0.024746 | 2.806e-08 | -0.00018161 | 0.0016574 | 0.0016551 | 0.0016574 | 0.99606 | -0.023708 | 0.99606 | -0.023712 | 0.75336
9 | -0.051469 | -0.024746 | 0.051472 | 0.023959 | 3.2301e-06 | -0.00078657 | 0.0016551 | 0.0016453 | 0.0016551 | 0.99606 | -0.023712 | 0.99613 | -0.023262 | 0.78815
10 | -0.32545 | -0.15665 | 0.32545 | 0.15598 | 4.1426e-06 | -0.00067034 | 0.010467 | 0.010459 | 0.010467 | 0.99613 | -0.023262 | 0.99614 | -0.023371 | 4.7577
11 | -0.84337 | -0.38003 | 0.84342 | 0.37883 | 4.9057e-05 | -0.0012068 | 0.026757 | 0.026742 | 0.026757 | 0.99801 | -0.014982 | 0.99807 | -0.015407 | 12.1622
12 | 0.5632 | 0.24434 | -0.56317 | -0.24601 | 2.979e-05 | -0.0016721 | 0.017758 | 0.017777 | 0.017777 | 0.99801 | -0.014982 | 0.99796 | -0.014629 | 8.0804
13 | -0.84342 | -0.37883 | 0.84496 | 0.37835 | 0.0015326 | -0.00047408 | 0.026742 | 0.026725 | 0.026742 | 0.99807 | -0.015407 | 1 | 0 | 12.7345
14 | 0.072715 | 0.033408 | -0.0727 | -0.03521 | 1.4687e-05 | -0.0018022 | 0.0023148 | 0.0023371 | 0.0023371 | 0.99796 | -0.014629 | 0.99775 | -0.016091 | 1.1129
15 | 0.49045 | 0.2126 | -0.48983 | -0.21394 | 0.00062159 | -0.0013409 | 0.015463 | 0.015483 | 0.015483 | 0.99796 | -0.014629 | 0.99661 | -0.026313 | 7.3727
16 | 3.1692 | 1.4029 | -3.1689 | -1.4033 | 0.00029772 | -0.00044355 | 0.10005 | 0.10006 | 0.10006 | 1 | 0 | 0.99991 | 0.00065762 | 45.4798
17 | 0.48983 | 0.21394 | -0.48975 | -0.21967 | 7.7951e-05 | -0.0057275 | 0.015483 | 0.01555 | 0.01555 | 0.99661 | -0.026313 | 0.99646 | -0.025199 | 7.0682
18 | 2.9365 | 1.3238 | -2.9328 | -1.3305 | 0.0037625 | -0.0066466 | 0.092994 | 0.093087 | 0.093087 | 0.99991 | 0.00065762 | 0.9987 | 0.010147 | 42.3122
19 | 0.23237 | 0.079487 | -0.23223 | -0.081185 | 0.00013418 | -0.0016988 | 0.0070901 | 0.0071069 | 0.0071069 | 0.99991 | 0.00065762 | 0.99928 | -0.0076349 | 3.3842
20 | 2.9328 | 1.3305 | -2.9319 | -1.3321 | 0.00089774 | -0.0015809 | 0.093087 | 0.093109 | 0.093109 | 0.9987 | 0.010147 | 0.99842 | 0.012436 | 42.3223
21 | 0.23223 | 0.081185 | -0.23223 | -0.081263 | 6.154e-06 | -7.7656e-05 | 0.0071069 | 0.0071077 | 0.0071077 | 0.99928 | -0.0076349 | 0.99925 | -0.0080091 | 3.3846
22 | 2.5586 | 1.1513 | -2.5585 | -1.1517 | 0.00018684 | -0.00045066 | 0.081123 | 0.081129 | 0.081129 | 0.99842 | 0.012436 | 0.99835 | 0.01297 | 36.8768
23 | 2.5585 | 1.1517 | -2.5463 | -1.1808 | 0.012167 | -0.029038 | 0.081129 | 0.081522 | 0.081522 | 0.99835 | 0.01297 | 0.99389 | 0.049196 | 37.0555
24 | 0.24278 | 0.095172 | -0.24271 | -0.11625 | 7.0676e-05 | -0.021081 | 0.0075741 | 0.0078187 | 0.0078187 | 0.99389 | 0.049196 | 0.99361 | 0.051143 | 3.5539
25 | 2.3035 | 1.0856 | -2.303 | -1.087 | 0.00046739 | -0.0013701 | 0.073963 | 0.073982 | 0.073982 | 0.99389 | 0.049196 | 0.9937 | 0.050861 | 33.6282
26 | 0.13615 | 0.065458 | -0.13615 | -0.065942 | 5.2911e-07 | -0.00048413 | 0.0043891 | 0.0043952 | 0.0043952 | 0.99361 | 0.051143 | 0.99361 | 0.051177 | 1.9978
27 | 0.10656 | 0.050795 | -0.10654 | -0.051601 | 1.4538e-05 | -0.00080597 | 0.0034295 | 0.0034398 | 0.0034398 | 0.99361 | 0.051143 | 0.99347 | 0.050217 | 1.638
28 | 2.2096 | 1.0417 | -2.2095 | -1.0422 | 0.00015922 | -0.00051099 | 0.070967 | 0.070974 | 0.070974 | 0.9937 | 0.050861 | 0.99363 | 0.051451 | 32.2609
29 | -2.1031 | -0.99157 | 2.1033 | 0.99085 | 0.00020162 | -0.00072026 | 0.067558 | 0.067548 | 0.067558 | 0.99354 | 0.052236 | 0.99363 | 0.051451 | 30.7082
30 | 0.98465 | 0.45646 | -0.98227 | -0.45655 | 0.0023844 | -8.7438e-05 | 0.031534 | 0.031553 | 0.031553 | 0.99354 | 0.052236 | 0.99099 | 0.033701 | 15.0253
31 | 0.98935 | 0.47256 | -0.9892 | -0.47257 | 0.00014857 | -3.7513e-06 | 0.031856 | 0.031858 | 0.031858 | 0.99354 | 0.052236 | 0.99339 | 0.051195 | 15.1703
32 | 0.88318 | 0.40856 | -0.88316 | -0.40908 | 2.4034e-05 | -0.00051809 | 0.028347 | 0.028353 | 0.028353 | 0.99099 | 0.033701 | 0.99096 | 0.033914 | 12.8877
33 | 0.74859 | 0.35603 | -0.74857 | -0.35657 | 1.7658e-05 | -0.00053167 | 0.024089 | 0.024096 | 0.024096 | 0.99339 | 0.051195 | 0.99336 | 0.051392 | 10.9525
34 | -0.18987 | -0.091958 | 0.18987 | 0.091227 | 1.556e-06 | -0.00073118 | 0.006131 | 0.0061217 | 0.006131 | 0.99333 | 0.051673 | 0.99334 | 0.051603 | 2.7868
35 | -0.18987 | -0.091227 | 0.18987 | 0.09116 | 1.4294e-07 | -6.7267e-05 | 0.0061217 | 0.0061209 | 0.0061217 | 0.99334 | 0.051603 | 0.99334 | 0.051596 | 2.7826
36 | -0.31517 | -0.15184 | 0.31517 | 0.1512 | 3.7511e-06 | -0.00063985 | 0.010167 | 0.010159 | 0.010167 | 0.99334 | 0.051596 | 0.99335 | 0.051494 | 4.6212
37 | -0.397 | -0.19084 | 0.39701 | 0.19033 | 4.7337e-06 | -0.00050867 | 0.012801 | 0.012794 | 0.012801 | 0.99335 | 0.051494 | 0.99336 | 0.051392 | 5.8186
38 | 0.35157 | 0.16624 | -0.35124 | -0.16772 | 0.00032551 | -0.0014764 | 0.011301 | 0.011322 | 0.011322 | 0.99336 | 0.051392 | 0.99239 | 0.044846 | 5.3915
39 | 0.1364 | 0.063663 | -0.13633 | -0.066027 | 7.0484e-05 | -0.0023641 | 0.0043786 | 0.0044087 | 0.0044087 | 0.99239 | 0.044846 | 0.99185 | 0.041203 | 2.0994
40 | -0.10831 | -0.052456 | 0.10831 | 0.051138 | 8.8848e-07 | -0.0013178 | 0.0034772 | 0.0034607 | 0.0034772 | 0.99908 | -0.0076123 | 0.99909 | -0.0076818 | 1.5805
41 | -0.10831 | -0.051138 | 0.10833 | 0.021309 | 1.8195e-05 | -0.029829 | 0.0034607 | 0.0031894 | 0.0034607 | 0.99909 | -0.0076818 | 0.99925 | -0.0080091 | 1.5731
42 | 0.1239 | 0.059954 | -0.1239 | -0.060007 | 1.2618e-06 | -5.259e-05 | 0.0039764 | 0.0039771 | 0.0039771 | 0.99925 | -0.0080091 | 0.99924 | -0.0080763 | 1.8938
43 | 0.32555 | 0.14022 | -0.32545 | -0.15598 | 9.5496e-05 | -0.015761 | 0.010269 | 0.010459 | 0.010459 | 0.99642 | -0.025577 | 0.99614 | -0.023371 | 4.7539
44 | -0.32555 | -0.14022 | 0.32556 | 0.14015 | 1.2979e-05 | -7.3757e-05 | 0.010269 | 0.010268 | 0.010269 | 0.99642 | -0.025577 | 0.99646 | -0.025199 | 4.8901

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 4.1959 | 1.873

## res_load
| p_mw | q_mvar
0 | 0.28593 | 0.13848
1 | 0.13819 | 0.066929
2 | 0.30146 | 0.146
3 | 0.15425 | 0.074708
4 | 0.051469 | 0.024928
5 | 0.27397 | 0.13269
6 | 0.28017 | 0.13569
7 | 0.1678 | 0.081269
8 | 0.0727 | 0.03521
9 | 0.37323 | 0.18076
10 | 0.093412 | 0.045241
11 | 0.13615 | 0.065942
12 | 0.10654 | 0.051601
13 | 0.12914 | 0.062546
14 | 0.10613 | 0.051399
15 | 0.099084 | 0.047989
16 | 0.24061 | 0.11653
17 | 0.18987 | 0.091958
18 | 0.12529 | 0.060683
19 | 0.081833 | 0.039633
20 | 0.21484 | 0.10405
21 | 0.10831 | 0.052456
22 | 0.1239 | 0.060007
23 | 0.13633 | 0.066027
24 | 0.1642 | 0.079524

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1