## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_389_1_node_2 | 20 | n |  | TRUE
1 | bus_MV_389_1_node_4 | 20 | n |  | TRUE
2 | bus_MV_389_1_node_104 | 20 | n |  | TRUE
3 | bus_MV_389_1_node_10 | 20 | n |  | TRUE
4 | bus_MV_389_1_node_103 | 20 | n |  | TRUE
5 | bus_MV_389_1_node_8 | 20 | n |  | TRUE
6 | bus_MV_389_1_node_3 | 20 | n |  | TRUE
7 | bus_MV_389_1_node_9 | 20 | n |  | TRUE
8 | bus_MV_389_1_node_5 | 20 | n |  | TRUE
9 | bus_MV_389_1_node_122 | 20 | n |  | TRUE
10 | bus_MV_389_1_node_6 | 20 | n |  | TRUE
11 | bus_MV_389_1_node_179 | 20 | n |  | TRUE
12 | bus_MV_389_1_node_159 | 20 | n |  | TRUE
13 | bus_MV_389_1_node_7 | 20 | n |  | TRUE
14 | bus_MV_389_1_node_132 | 20 | n |  | TRUE
15 | bus_MV_389_1_node_93 | 20 | n |  | TRUE
16 | bus_MV_389_1_node_182 | 20 | n |  | TRUE
17 | bus_MV_389_1_node_68 | 20 | n |  | TRUE
18 | bus_MV_389_1_node_156 | 20 | n |  | TRUE
19 | bus_MV_389_1_node_169 | 20 | n |  | TRUE
20 | bus_MV_389_1_node_170 | 20 | n |  | TRUE
21 | bus_MV_389_1_node_155 | 20 | n |  | TRUE
22 | bus_MV_389_1_node_131 | 20 | n |  | TRUE
23 | bus_MV_389_1_node_152 | 20 | n |  | TRUE
24 | bus_MV_389_1_node_80 | 20 | n |  | TRUE
25 | bus_MV_389_1_node_77 | 20 | n |  | TRUE
26 | bus_MV_389_1_node_78 | 20 | n |  | TRUE
27 | bus_MV_389_1_node_30 | 20 | n |  | TRUE
28 | bus_MV_389_1_node_167 | 20 | n |  | TRUE
29 | bus_MV_389_1_node_32 | 20 | n |  | TRUE
30 | bus_MV_389_1_node_94 | 20 | n |  | TRUE
31 | bus_MV_389_1_node_102 | 20 | n |  | TRUE
32 | bus_MV_389_1_node_143 | 20 | n |  | TRUE
33 | bus_MV_389_1_node_174 | 20 | n |  | TRUE
34 | bus_MV_389_1_node_66 | 20 | n |  | TRUE
35 | bus_MV_389_1_node_67 | 20 | n |  | TRUE
36 | bus_MV_389_1_node_73 | 20 | n |  | TRUE
37 | bus_MV_389_1_node_74 | 20 | n |  | TRUE
38 | bus_MV_389_1_node_75 | 20 | n |  | TRUE
39 | bus_MV_389_1_node_82 | 20 | n |  | TRUE
40 | bus_MV_389_1_node_76 | 20 | n |  | TRUE
41 | bus_MV_389_1_node_173 | 20 | n |  | TRUE
42 | bus_MV_389_1_node_177 | 20 | n |  | TRUE
43 | bus_MV_389_1_node_79 | 20 | n |  | TRUE
44 | bus_MV_389_1_node_176 | 20 | n |  | TRUE
45 | bus_MV_389_1_node_183 | 20 | n |  | TRUE
46 | bus_MV_389_1_node_81 | 20 | n |  | TRUE
47 | bus_MV_389_1_node_136 | 20 | n |  | TRUE
48 | bus_MV_389_1_node_113 | 20 | n |  | TRUE
49 | bus_MV_389_1_node_175 | 20 | n |  | TRUE
50 | bus_MV_389_1_node_135 | 20 | n |  | TRUE
51 | bus_MV_389_1_node_97 | 20 | n |  | TRUE
52 | bus_MV_389_1_node_84 | 20 | n |  | TRUE
53 | bus_MV_389_1_node_85 | 20 | n |  | TRUE
54 | bus_MV_389_1_node_86 | 20 | n |  | TRUE
55 | bus_MV_389_1_node_87 | 20 | n |  | TRUE
56 | bus_MV_389_1_node_147 | 20 | n |  | TRUE
57 | bus_MV_389_1_node_133 | 20 | n |  | TRUE
58 | bus_MV_389_1_node_142 | 20 | n |  | TRUE
59 | bus_MV_389_1_node_98 | 20 | n |  | TRUE
60 | bus_MV_389_1_node_88 | 20 | n |  | TRUE
61 | bus_MV_389_1_node_89 | 20 | n |  | TRUE
62 | bus_MV_389_1_node_90 | 20 | n |  | TRUE
63 | bus_MV_389_1_node_91 | 20 | n |  | TRUE
64 | bus_MV_389_1_node_92 | 20 | n |  | TRUE
65 | bus_MV_389_1_node_123 | 20 | n |  | TRUE
66 | bus_MV_389_1_node_112 | 20 | n |  | TRUE
67 | bus_MV_389_1_node_96 | 20 | n |  | TRUE
68 | bus_MV_389_1_node_146 | 20 | n |  | TRUE
69 | bus_MV_389_1_node_110 | 20 | n |  | TRUE
70 | bus_MV_389_1_node_111 | 20 | n |  | TRUE
71 | bus_MV_389_1_node_105 | 20 | n |  | TRUE
72 | bus_MV_389_1_node_106 | 20 | n |  | TRUE
73 | bus_MV_389_1_node_107 | 20 | n |  | TRUE
74 | bus_MV_389_1_node_108 | 20 | n |  | TRUE
75 | bus_MV_389_1_node_109 | 20 | n |  | TRUE
76 | bus_MV_389_1_node_163 | 20 | n |  | TRUE
77 | bus_MV_389_1_node_141 | 20 | n |  | TRUE
78 | bus_MV_389_1_node_118 | 20 | n |  | TRUE
79 | bus_MV_389_1_node_119 | 20 | n |  | TRUE
80 | bus_MV_389_1_node_120 | 20 | n |  | TRUE
81 | bus_MV_389_1_node_121 | 20 | n |  | TRUE
82 | bus_MV_389_1_node_162 | 20 | n |  | TRUE
83 | bus_MV_389_1_node_161 | 20 | n |  | TRUE
84 | bus_MV_389_1_node_145 | 20 | n |  | TRUE
85 | bus_MV_389_1_node_140 | 20 | n |  | TRUE
86 | bus_MV_389_1_node_134 | 20 | n |  | TRUE
87 | bus_MV_389_1_node_137 | 20 | n |  | TRUE
88 | bus_MV_389_1_node_138 | 20 | n |  | TRUE
89 | bus_MV_389_1_node_139 | 20 | n |  | TRUE
90 | bus_MV_389_1_node_144 | 20 | n |  | TRUE
91 | bus_MV_389_1_node_148 | 20 | n |  | TRUE
92 | bus_MV_389_1_node_149 | 20 | n |  | TRUE
93 | bus_MV_389_1_node_150 | 20 | n |  | TRUE
94 | bus_MV_389_1_node_151 | 20 | n |  | TRUE
95 | bus_MV_389_1_node_153 | 20 | n |  | TRUE
96 | bus_MV_389_1_node_154 | 20 | n |  | TRUE
97 | bus_MV_389_1_node_185 | 20 | n |  | TRUE
98 | bus_HV_389_1_node_10 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_389_1_load_2 | 0 | 0.25605 | 0.12401 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_389_1_load_104 | 2 | 0.10195 | 0.049377 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_389_1_load_122 | 9 | 0.22444 | 0.1087 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_389_1_load_179 | 11 | 0.40816 | 0.19768 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_389_1_load_132 | 14 | 0.13874 | 0.067195 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_389_1_load_93 | 15 | 0.082332 | 0.039875 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_389_1_load_182 | 16 | 0.40159 | 0.1945 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_389_1_load_68 | 17 | 0.10087 | 0.048854 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_389_1_load_156 | 18 | 0.10803 | 0.052321 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_389_1_load_169 | 19 | 0.15944 | 0.077222 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_389_1_load_131 | 22 | 0.62457 | 0.30249 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_389_1_load_152 | 23 | 0.35635 | 0.17259 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_389_1_load_167 | 28 | 0.38871 | 0.18826 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_389_1_load_94 | 30 | 0.59224 | 0.28684 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_389_1_load_102 | 31 | 0.076723 | 0.037159 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_389_1_load_174 | 33 | 0.065896 | 0.031915 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_389_1_load_66 | 34 | 0.20302 | 0.098328 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_389_1_load_67 | 35 | 0.1242 | 0.060152 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_389_1_load_73 | 36 | 0.098438 | 0.047676 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_389_1_load_82 | 39 | 0.13057 | 0.063237 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_389_1_load_173 | 41 | 0.20541 | 0.099487 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_389_1_load_177 | 42 | 0.37243 | 0.18038 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_389_1_load_183 | 45 | 0.26585 | 0.12876 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_389_1_load_136 | 47 | 0.21863 | 0.10589 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_389_1_load_113 | 48 | 0.23328 | 0.11298 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_389_1_load_175 | 49 | 0.34612 | 0.16764 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_389_1_load_135 | 50 | 0.15585 | 0.07548 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_389_1_load_84 | 52 | 0.075162 | 0.036403 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_389_1_load_147 | 56 | 0.30957 | 0.14993 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_389_1_load_133 | 57 | 0.20649 | 0.10001 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_389_1_load_88 | 60 | 0.15443 | 0.074794 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_389_1_load_90 | 62 | 0.22321 | 0.1081 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_389_1_load_123 | 65 | 0.28517 | 0.13811 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_389_1_load_146 | 68 | 0.1024 | 0.049595 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_389_1_load_110 | 69 | 0.5381 | 0.26062 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_389_1_load_105 | 71 | 0.15814 | 0.07659 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_389_1_load_108 | 74 | 0.10425 | 0.050493 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_389_1_load_163 | 76 | 0.34108 | 0.16519 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_389_1_load_118 | 78 | 0.28424 | 0.13766 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_389_1_load_162 | 82 | 0.097275 | 0.047112 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_389_1_load_161 | 83 | 0.080748 | 0.039108 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_389_1_load_145 | 84 | 0.12235 | 0.059256 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_389_1_load_134 | 86 | 0.16868 | 0.081693 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_389_1_load_137 | 87 | 0.11898 | 0.057623 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_389_1_load_144 | 90 | 0.15589 | 0.075503 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_389_1_load_148 | 91 | 0.071657 | 0.034705 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_389_1_load_153 | 95 | 0.30365 | 0.14707 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_389_1_load_154 | 96 | 1.3802 | 0.66848 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_389_1_load_185 | 97 | 0.72473 | 0.351 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_389_1_line_0 |  | 0 | 1 | 0.026372 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
1 | MV_389_1_line_1 |  | 0 | 2 | 0.023065 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
2 | MV_389_1_line_2 |  | 1 | 3 | 0.25794 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
3 | MV_389_1_line_3 |  | 1 | 4 | 0.030588 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_389_1_line_4 |  | 2 | 5 | 0.074645 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
5 | MV_389_1_line_5 |  | 3 | 16 | 0.024431 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
6 | MV_389_1_line_6 |  | 4 | 17 | 0.024808 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_389_1_line_7 |  | 5 | 6 | 0.30849 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_389_1_line_8 |  | 5 | 8 | 0.22001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_389_1_line_9 |  | 5 | 10 | 0.24616 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_389_1_line_10 |  | 6 | 7 | 0.21471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_389_1_line_11 |  | 7 | 15 | 0.041658 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_389_1_line_12 |  | 7 | 13 | 0.23868 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_389_1_line_13 |  | 8 | 9 | 0.036097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_389_1_line_14 |  | 10 | 11 | 0.007478 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_389_1_line_15 |  | 10 | 12 | 0.35787 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_389_1_line_16 |  | 11 | 18 | 0.099578 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_389_1_line_17 |  | 12 | 19 | 0.037075 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_389_1_line_18 |  | 12 | 20 | 0.65226 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_389_1_line_19 |  | 13 | 14 | 0.08675 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_389_1_line_20 |  | 14 | 22 | 0.12244 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_389_1_line_21 |  | 16 | 24 | 0.025159 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
22 | MV_389_1_line_22 |  | 17 | 35 | 0.030026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_389_1_line_23 |  | 20 | 33 | 0.12428 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_389_1_line_24 |  | 21 | 22 | 0.058075 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_389_1_line_25 |  | 21 | 23 | 0.039308 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_389_1_line_26 |  | 23 | 92 | 0.023813 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_389_1_line_27 |  | 24 | 25 | 0.45821 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
28 | MV_389_1_line_28 |  | 24 | 26 | 0.50618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_389_1_line_29 |  | 25 | 42 | 0.003658 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_389_1_line_30 |  | 25 | 43 | 0.08289 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
31 | MV_389_1_line_31 |  | 25 | 44 | 0.32733 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_389_1_line_32 |  | 26 | 45 | 0.061754 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_389_1_line_33 |  | 26 | 40 | 0.37352 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_389_1_line_34 |  | 27 | 28 | 0.00508 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_389_1_line_35 |  | 27 | 29 | 0.14127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_389_1_line_36 |  | 27 | 30 | 0.13671 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_389_1_line_37 |  | 29 | 31 | 0.034685 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_389_1_line_38 |  | 31 | 32 | 0.1404 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_389_1_line_39 |  | 32 | 90 | 0.028774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_389_1_line_40 |  | 32 | 89 | 0.030225 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_389_1_line_41 |  | 34 | 35 | 0.024547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_389_1_line_42 |  | 36 | 37 | 0.033572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_389_1_line_43 |  | 37 | 38 | 0.097522 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_389_1_line_44 |  | 38 | 39 | 0.12556 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_389_1_line_45 |  | 38 | 40 | 0.34356 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_389_1_line_46 |  | 40 | 41 | 0.039339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_389_1_line_47 |  | 43 | 46 | 0.045659 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
48 | MV_389_1_line_48 |  | 43 | 47 | 0.048671 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_389_1_line_49 |  | 44 | 49 | 0.00631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_389_1_line_50 |  | 46 | 48 | 0.015255 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
51 | MV_389_1_line_51 |  | 47 | 50 | 0.043414 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_389_1_line_52 |  | 48 | 51 | 0.022856 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
53 | MV_389_1_line_53 |  | 50 | 86 | 0.051388 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_389_1_line_54 |  | 51 | 59 | 0.035733 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_389_1_line_55 |  | 51 | 69 | 0.04952 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_389_1_line_56 |  | 51 | 67 | 0.26966 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_389_1_line_57 |  | 52 | 53 | 0.078182 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_389_1_line_58 |  | 53 | 54 | 0.021664 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_389_1_line_59 |  | 54 | 55 | 0.14155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_389_1_line_60 |  | 54 | 56 | 0.045422 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_389_1_line_61 |  | 55 | 57 | 0.070438 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_389_1_line_62 |  | 56 | 58 | 0.02017 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_389_1_line_63 |  | 57 | 59 | 0.037234 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_389_1_line_64 |  | 58 | 77 | 0.057068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_389_1_line_65 |  | 60 | 61 | 0.013789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_389_1_line_66 |  | 61 | 62 | 0.014626 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_389_1_line_67 |  | 62 | 63 | 0.010509 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_389_1_line_68 |  | 63 | 64 | 0.029176 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_389_1_line_69 |  | 64 | 65 | 0.023004 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_389_1_line_70 |  | 65 | 66 | 0.026845 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_389_1_line_71 |  | 66 | 70 | 0.018474 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_389_1_line_72 |  | 67 | 68 | 0.031451 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_389_1_line_73 |  | 69 | 70 | 0.010249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_389_1_line_74 |  | 71 | 72 | 0.012972 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_389_1_line_75 |  | 71 | 73 | 0.034606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_389_1_line_76 |  | 72 | 74 | 0.033646 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_389_1_line_77 |  | 73 | 75 | 0.027977 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_389_1_line_78 |  | 75 | 76 | 0.029877 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_389_1_line_79 |  | 76 | 77 | 0.044596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_389_1_line_80 |  | 77 | 88 | 0.059462 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_389_1_line_81 |  | 78 | 79 | 0.020251 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_389_1_line_82 |  | 79 | 80 | 0.14738 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_389_1_line_83 |  | 79 | 81 | 0.18943 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_389_1_line_84 |  | 80 | 82 | 0.037829 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_389_1_line_85 |  | 80 | 83 | 0.061636 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_389_1_line_86 |  | 81 | 84 | 0.023574 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_389_1_line_87 |  | 84 | 85 | 0.017059 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_389_1_line_88 |  | 85 | 88 | 0.01741 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_389_1_line_89 |  | 87 | 88 | 0.023273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_389_1_line_90 |  | 87 | 89 | 0.024752 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_389_1_line_91 |  | 91 | 92 | 0.009793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_389_1_line_92 |  | 91 | 93 | 0.014998 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_389_1_line_93 |  | 92 | 94 | 0.015984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_389_1_line_94 |  | 93 | 95 | 0.009965 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_389_1_line_95 |  | 94 | 96 | 0.000948 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_389_1_line_96 |  | 96 | 97 | 0.017115 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_389_1_trafo_10 | 25 MVA 110/20 kV | 98 | 3 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2679143.5498 | 1249978.8689
1 | 2679168.412 | 1249969.872
2 | 2679122.5589 | 1249969.3091
3 | 2679328.9429 | 1249973.9543
4 | 2679187.0156 | 1249945.5916
5 | 2679052.4827 | 1249995.0212
6 | 2679152.5135 | 1250004.1738
7 | 2679273.5219 | 1250061.0213
8 | 2678943.045 | 1249894.5781
9 | 2678908.4308 | 1249903.9435
10 | 2678891.6875 | 1250091.3277
11 | 2678887.5501 | 1250085.0903
12 | 2678649.2709 | 1250354.5886
13 | 2679287.7133 | 1250174.6168
14 | 2679347.5356 | 1250237.4412
15 | 2679312.5651 | 1250046.4951
16 | 2679351.0308 | 1249964.6764
17 | 2679178.9293 | 1249922.1391
18 | 2678835.2719 | 1250000.3389
19 | 2678663.6072 | 1250388.7483
20 | 2678208.0546 | 1250640.2496
21 | 2679489.6139 | 1250205.0319
22 | 2679468.0552 | 1250258.957
23 | 2679517.8126 | 1250215.2062
24 | 2679374.6653 | 1249956.0532
25 | 2679406.8718 | 1249726.4381
26 | 2679562.1184 | 1250129.5157
27 | 2678994.9418 | 1249461.1185
28 | 2678990.337 | 1249463.292
29 | 2678953.1653 | 1249539.1302
30 | 2679127.1385 | 1249495.9725
31 | 2678987.1583 | 1249532.3114
32 | 2679013.6961 | 1249670.1771
33 | 2678083.4284 | 1250642.6862
34 | 2679161.0485 | 1249870.5786
35 | 2679169.0252 | 1249893.7936
36 | 2679767.3965 | 1250264.6071
37 | 2679734.7941 | 1250272.6188
38 | 2679800.0531 | 1250302.4633
39 | 2679922.9855 | 1250276.9847
40 | 2679822.5571 | 1250127.2373
41 | 2679802.6446 | 1250093.2776
42 | 2679404.8819 | 1249723.3648
43 | 2679337.4184 | 1249744.1879
44 | 2679456.9219 | 1249616.8394
45 | 2679576.0959 | 1250188.9136
46 | 2679327.8481 | 1249709.5122
47 | 2679311.6606 | 1249774.6439
48 | 2679322.5733 | 1249695.1986
49 | 2679451.0243 | 1249619.1287
50 | 2679270.4803 | 1249788.3815
51 | 2679310.5929 | 1249677.5246
52 | 2679205.4909 | 1249711.7723
53 | 2679132.9051 | 1249740.8188
54 | 2679125.3875 | 1249727.0528
55 | 2679220.1954 | 1249755.5843
56 | 2679082.9547 | 1249743.257
57 | 2679259.8408 | 1249709.7526
58 | 2679064.1123 | 1249750.4525
59 | 2679286.6774 | 1249683.9427
60 | 2679310.447 | 1249589.1578
61 | 2679305.4847 | 1249576.2931
62 | 2679319.2026 | 1249571.2196
63 | 2679329.0323 | 1249567.5017
64 | 2679347.6898 | 1249588.956
65 | 2679350.6096 | 1249610.0546
66 | 2679360.2096 | 1249635.1241
67 | 2679121.7353 | 1249625.6853
68 | 2679091.6239 | 1249634.3748
69 | 2679355.1886 | 1249656.3412
70 | 2679364.7031 | 1249652.5303
71 | 2679083.1745 | 1249847.695
72 | 2679095.4285 | 1249843.4384
73 | 2679050.4842 | 1249859.0504
74 | 2679121.9035 | 1249827.1298
75 | 2679042.1955 | 1249832.3314
76 | 2679027.6006 | 1249812.2264
77 | 2679010.8351 | 1249770.9016
78 | 2678838.7878 | 1249800.078
79 | 2678846.3366 | 1249818.869
80 | 2678805.3514 | 1249863.8348
81 | 2678947.5854 | 1249745.9296
82 | 2678770.3753 | 1249878.2472
83 | 2678788.0409 | 1249806.1628
84 | 2678969.7105 | 1249737.7931
85 | 2678985.7212 | 1249731.9051
86 | 2679221.4357 | 1249803.7229
87 | 2678994.0654 | 1249704.0387
88 | 2679002.0576 | 1249725.8961
89 | 2678985.3445 | 1249680.8738
90 | 2679024.151 | 1249696.9846
91 | 2679541.0138 | 1250204.0035
92 | 2679541.5833 | 1250213.7799
93 | 2679540.1414 | 1250189.0312
94 | 2679550.2514 | 1250227.2172
95 | 2679549.9658 | 1250187.2061
96 | 2679550.7997 | 1250227.9918
97 | 2679555.4547 | 1250244.4611
98 | 2679328.9429 | 1249973.9543

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99933 | -0.012023 | 0.25605 | 0.12401
1 | 0.99938 | -0.010988 | 0 | 0
2 | 0.9992 | -0.015272 | 0.10195 | 0.049377
3 | 1 | 0 | -12.5002 | -5.8645
4 | 0.99936 | -0.011152 | 0 | 0
5 | 0.99901 | -0.01733 | 0 | 0
6 | 0.99756 | -0.0040991 | 0 | 0
7 | 0.99655 | 0.0052178 | 0 | 0
8 | 0.99895 | -0.016787 | 0 | 0
9 | 0.99894 | -0.01669 | 0.22444 | 0.1087
10 | 0.99878 | -0.015503 | 0 | 0
11 | 0.99877 | -0.015457 | 0.40816 | 0.19768
12 | 0.99863 | -0.017078 | 0 | 0
13 | 0.99545 | 0.015457 | 0 | 0
14 | 0.99484 | 0.011594 | 0.13874 | 0.067195
15 | 0.99654 | 0.0052578 | 0.082332 | 0.039875
16 | 0.99993 | -0.0013522 | 0.40159 | 0.1945
17 | 0.99935 | -0.011027 | 0.10087 | 0.048854
18 | 0.99875 | -0.015587 | 0.10803 | 0.052321
19 | 0.99862 | -0.017008 | 0.15944 | 0.077222
20 | 0.99858 | -0.017009 | 0 | 0
21 | 0.99398 | 0.014654 | 0 | 0
22 | 0.9943 | 0.016685 | 0.62457 | 0.30249
23 | 0.99383 | 0.015998 | 0.35635 | 0.17259
24 | 0.99976 | -0.0069216 | 0 | 0
25 | 0.99857 | -0.028116 | 0 | 0
26 | 0.99931 | -0.003699 | 0 | 0
27 | 0.99594 | -0.018444 | 0 | 0
28 | 0.99594 | -0.01842 | 0.38871 | 0.18826
29 | 0.99612 | -0.020097 | 0 | 0
30 | 0.99578 | -0.019431 | 0.59224 | 0.28684
31 | 0.99616 | -0.020499 | 0.076723 | 0.037159
32 | 0.99645 | -0.018635 | 0 | 0
33 | 0.99857 | -0.016923 | 0.065896 | 0.031915
34 | 0.99933 | -0.010852 | 0.20302 | 0.098328
35 | 0.99933 | -0.010911 | 0.1242 | 0.060152
36 | 0.99899 | -0.0013636 | 0.098438 | 0.047676
37 | 0.999 | -0.0014023 | 0 | 0
38 | 0.99901 | -0.0015052 | 0 | 0
39 | 0.99899 | -0.0013207 | 0.13057 | 0.063237
40 | 0.99911 | -0.0022242 | 0 | 0
41 | 0.9991 | -0.0021286 | 0.20541 | 0.099487
42 | 0.99857 | -0.028099 | 0.37243 | 0.18038
43 | 0.99838 | -0.031475 | 0 | 0
44 | 0.99843 | -0.026841 | 0 | 0
45 | 0.99929 | -0.0035052 | 0.26585 | 0.12876
46 | 0.99829 | -0.033133 | 0 | 0
47 | 0.99835 | -0.031167 | 0.21863 | 0.10589
48 | 0.99826 | -0.033687 | 0.23328 | 0.11298
49 | 0.99843 | -0.026815 | 0.34612 | 0.16764
50 | 0.99833 | -0.031003 | 0.15585 | 0.07548
51 | 0.9982 | -0.03428 | 0 | 0
52 | 0.99712 | -0.024679 | 0.075162 | 0.036403
53 | 0.99713 | -0.024746 | 0 | 0
54 | 0.99713 | -0.024762 | 0 | 0
55 | 0.99766 | -0.029418 | 0 | 0
56 | 0.99697 | -0.023295 | 0.30957 | 0.14993
57 | 0.99792 | -0.031722 | 0.20649 | 0.10001
58 | 0.9969 | -0.022717 | 0 | 0
59 | 0.99806 | -0.033029 | 0 | 0
60 | 0.99805 | -0.032816 | 0.15443 | 0.074794
61 | 0.99805 | -0.032842 | 0 | 0
62 | 0.99805 | -0.032868 | 0.22321 | 0.1081
63 | 0.99806 | -0.032915 | 0 | 0
64 | 0.99807 | -0.033045 | 0 | 0
65 | 0.99808 | -0.033147 | 0.28517 | 0.13811
66 | 0.9981 | -0.033356 | 0 | 0
67 | 0.99817 | -0.034017 | 0 | 0
68 | 0.99817 | -0.033979 | 0.1024 | 0.049595
69 | 0.99813 | -0.033579 | 0.5381 | 0.26062
70 | 0.99812 | -0.0335 | 0 | 0
71 | 0.99665 | -0.020487 | 0.15814 | 0.07659
72 | 0.99665 | -0.020471 | 0 | 0
73 | 0.99667 | -0.020593 | 0 | 0
74 | 0.99665 | -0.02043 | 0.10425 | 0.050493
75 | 0.99668 | -0.020677 | 0 | 0
76 | 0.99669 | -0.020766 | 0.34108 | 0.16519
77 | 0.99672 | -0.021079 | 0 | 0
78 | 0.99642 | -0.018431 | 0.28424 | 0.13766
79 | 0.99642 | -0.0185 | 0 | 0
80 | 0.99639 | -0.018223 | 0 | 0
81 | 0.99654 | -0.019451 | 0 | 0
82 | 0.99639 | -0.01818 | 0.097275 | 0.047112
83 | 0.99638 | -0.018166 | 0.080748 | 0.039108
84 | 0.99655 | -0.019566 | 0.12235 | 0.059256
85 | 0.99656 | -0.019673 | 0 | 0
86 | 0.99832 | -0.030901 | 0.16868 | 0.081693
87 | 0.99653 | -0.019419 | 0.11898 | 0.057623
88 | 0.99657 | -0.019782 | 0 | 0
89 | 0.9965 | -0.019067 | 0 | 0
90 | 0.99644 | -0.018582 | 0.15589 | 0.075503
91 | 0.99375 | 0.016755 | 0.071657 | 0.034705
92 | 0.99376 | 0.01671 | 0 | 0
93 | 0.99375 | 0.016809 | 0 | 0
94 | 0.99371 | 0.017117 | 0 | 0
95 | 0.99374 | 0.016846 | 0.30365 | 0.14707
96 | 0.99371 | 0.017142 | 1.3802 | 0.66848
97 | 0.9937 | 0.017292 | 0.72473 | 0.351
98 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -5.0276 | -2.3728 | 5.0279 | 2.3721 | 0.00024892 | -0.00077764 | 0.1606 | 0.16058 | 0.1606 | 0.99933 | -0.012023 | 0.99938 | -0.010988 | 38.1462
1 | 4.7716 | 2.2488 | -4.7711 | -2.2483 | 0.00049164 | 0.00053339 | 0.15238 | 0.15238 | 0.15238 | 0.99933 | -0.012023 | 0.9992 | -0.015272 | 43.5367
2 | -5.456 | -2.5775 | 5.4589 | 2.5702 | 0.0028661 | -0.0072166 | 0.1743 | 0.17418 | 0.1743 | 0.99938 | -0.010988 | 1 | 0 | 41.4012
3 | 0.42811 | 0.20541 | -0.4281 | -0.20544 | 1.0253e-05 | -3.0048e-05 | 0.013716 | 0.013716 | 0.013716 | 0.99938 | -0.010988 | 0.99936 | -0.011152 | 6.5316
4 | 4.6692 | 2.1989 | -4.6684 | -2.2009 | 0.00080173 | -0.0019736 | 0.14911 | 0.14914 | 0.14914 | 0.9992 | -0.015272 | 0.99901 | -0.01733 | 41.1981
5 | 7.0273 | 3.2837 | -7.0269 | -3.2843 | 0.00044835 | -0.00052164 | 0.22392 | 0.22393 | 0.22393 | 1 | 0 | 0.99993 | -0.0013522 | 53.1894
6 | 0.4281 | 0.20544 | -0.4281 | -0.20603 | 6.2342e-06 | -0.00058969 | 0.013716 | 0.013724 | 0.013724 | 0.99936 | -0.011152 | 0.99935 | -0.011027 | 6.2381
7 | 3.7021 | 1.765 | -3.6964 | -1.7706 | 0.0057888 | -0.0056231 | 0.11851 | 0.11861 | 0.11861 | 0.99901 | -0.01733 | 0.99756 | -0.0040991 | 53.9114
8 | 0.22446 | 0.10261 | -0.22445 | -0.10784 | 1.5071e-05 | -0.0052377 | 0.0071316 | 0.0071959 | 0.0071959 | 0.99901 | -0.01733 | 0.99895 | -0.016787 | 3.2709
9 | 0.74175 | 0.33326 | -0.74157 | -0.33907 | 0.00018199 | -0.0058105 | 0.023498 | 0.023568 | 0.023568 | 0.99901 | -0.01733 | 0.99878 | -0.015503 | 10.7125
10 | 3.6964 | 1.7706 | -3.6923 | -1.7745 | 0.0040344 | -0.0038996 | 0.11861 | 0.11867 | 0.11867 | 0.99756 | -0.0040991 | 0.99655 | 0.0052178 | 53.9404
11 | 0.082333 | 0.038888 | -0.082332 | -0.039875 | 3.8871e-07 | -0.00098765 | 0.0026376 | 0.00265 | 0.00265 | 0.99655 | 0.0052178 | 0.99654 | 0.0052578 | 1.2045
12 | 3.61 | 1.7357 | -3.6057 | -1.74 | 0.0042925 | -0.0043799 | 0.11603 | 0.1161 | 0.1161 | 0.99655 | 0.0052178 | 0.99545 | 0.015457 | 52.7739
13 | 0.22445 | 0.10784 | -0.22444 | -0.1087 | 2.499e-06 | -0.00085928 | 0.0071959 | 0.0072067 | 0.0072067 | 0.99895 | -0.016787 | 0.99894 | -0.01669 | 3.2758
14 | 0.51619 | 0.24971 | -0.51619 | -0.24988 | 2.7425e-06 | -0.00017729 | 0.016573 | 0.016576 | 0.016576 | 0.99878 | -0.015503 | 0.99877 | -0.015457 | 7.5344
15 | 0.22538 | 0.08936 | -0.22535 | -0.089767 | 3.1329e-05 | -0.0004065 | 0.0070074 | 0.0070119 | 0.0070119 | 0.99878 | -0.015503 | 0.99863 | -0.017078 | 3.339
16 | 0.10803 | 0.052204 | -0.10803 | -0.052321 | 2.1346e-06 | -0.00011725 | 0.0034679 | 0.0034694 | 0.0034694 | 0.99877 | -0.015457 | 0.99875 | -0.015587 | 1.6521
17 | 0.15944 | 0.07634 | -0.15944 | -0.077222 | 1.2953e-06 | -0.00088239 | 0.0051101 | 0.0051212 | 0.0051212 | 0.99863 | -0.017078 | 0.99862 | -0.017008 | 2.3278
18 | 0.065901 | 0.013427 | -0.065897 | -0.028956 | 3.4868e-06 | -0.015529 | 0.0019441 | 0.0020808 | 0.0020808 | 0.99863 | -0.017078 | 0.99858 | -0.017009 | 0.94582
19 | 3.6057 | 1.74 | -3.6036 | -1.7388 | 0.0020835 | 0.0012025 | 0.1161 | 0.1161 | 0.1161 | 0.99545 | 0.015457 | 0.99484 | 0.011594 | 55.2875
20 | 3.4649 | 1.6716 | -3.4628 | -1.6739 | 0.0020375 | -0.0022872 | 0.11163 | 0.11167 | 0.11167 | 0.99484 | 0.011594 | 0.9943 | 0.016685 | 50.7578
21 | 6.6253 | 3.0898 | -6.6245 | -3.0886 | 0.00079875 | 0.0011239 | 0.21105 | 0.21105 | 0.21105 | 0.99993 | -0.0013522 | 0.99976 | -0.0069216 | 51.4749
22 | 0.32723 | 0.15718 | -0.32722 | -0.1579 | 4.4116e-06 | -0.00071465 | 0.010486 | 0.010495 | 0.010495 | 0.99935 | -0.011027 | 0.99933 | -0.010911 | 4.7706
23 | 0.065897 | 0.028956 | -0.065896 | -0.031915 | 7.3056e-07 | -0.0029587 | 0.0020808 | 0.0021167 | 0.0021167 | 0.99858 | -0.017009 | 0.99857 | -0.016923 | 0.96212
24 | -2.8374 | -1.371 | 2.8383 | 1.3714 | 0.00086666 | 0.00047433 | 0.09152 | 0.091519 | 0.09152 | 0.99398 | 0.014654 | 0.9943 | 0.016685 | 43.5809
25 | 2.8374 | 1.371 | -2.837 | -1.3718 | 0.00043959 | -0.00079672 | 0.09152 | 0.091532 | 0.091532 | 0.99398 | 0.014654 | 0.99383 | 0.015998 | 41.6053
26 | 2.4806 | 1.1992 | -2.4804 | -1.1997 | 0.00020364 | -0.00050113 | 0.080031 | 0.080038 | 0.080038 | 0.99383 | 0.015998 | 0.99376 | 0.01671 | 36.3808
27 | 5.9237 | 2.787 | -5.9177 | -2.799 | 0.0059994 | -0.011968 | 0.18903 | 0.18925 | 0.18925 | 0.99976 | -0.0069216 | 0.99857 | -0.028116 | 44.9515
28 | 0.70073 | 0.3016 | -0.7004 | -0.31358 | 0.00032997 | -0.011977 | 0.022028 | 0.022168 | 0.022168 | 0.99976 | -0.0069216 | 0.99931 | -0.003699 | 10.0764
29 | 0.37243 | 0.18029 | -0.37243 | -0.18038 | 6.9877e-07 | -8.6882e-05 | 0.011962 | 0.011963 | 0.011963 | 0.99857 | -0.028116 | 0.99857 | -0.028099 | 5.4376
30 | 5.1991 | 2.459 | -5.1983 | -2.4614 | 0.00083884 | -0.0023868 | 0.16626 | 0.1663 | 0.1663 | 0.99857 | -0.028116 | 0.99838 | -0.031475 | 39.5018
31 | 0.34618 | 0.15971 | -0.34613 | -0.16749 | 5.354e-05 | -0.007776 | 0.011021 | 0.011118 | 0.011118 | 0.99857 | -0.028116 | 0.99843 | -0.026841 | 5.0534
32 | 0.26586 | 0.12729 | -0.26585 | -0.12876 | 5.9902e-06 | -0.0014706 | 0.0085149 | 0.0085333 | 0.0085333 | 0.99931 | -0.003699 | 0.99929 | -0.0035052 | 3.8788
33 | 0.43454 | 0.18629 | -0.43445 | -0.19517 | 9.3713e-05 | -0.0088763 | 0.013658 | 0.013761 | 0.013761 | 0.99931 | -0.003699 | 0.99911 | -0.0022242 | 6.2551
34 | 0.38871 | 0.18814 | -0.38871 | -0.18826 | 1.0627e-06 | -0.00011999 | 0.012517 | 0.012519 | 0.012519 | 0.99594 | -0.018444 | 0.99594 | -0.01842 | 5.6904
35 | -0.98105 | -0.47487 | 0.98124 | 0.47158 | 0.00018798 | -0.0032906 | 0.031592 | 0.03155 | 0.031592 | 0.99594 | -0.018444 | 0.99612 | -0.020097 | 14.36
36 | 0.59233 | 0.28673 | -0.59224 | -0.28684 | 8.8635e-05 | -0.00010634 | 0.019075 | 0.019077 | 0.019077 | 0.99594 | -0.018444 | 0.99578 | -0.019431 | 9.0841
37 | -0.98124 | -0.47158 | 0.98128 | 0.47077 | 4.6076e-05 | -0.0008081 | 0.03155 | 0.031539 | 0.03155 | 0.99612 | -0.020097 | 0.99616 | -0.020499 | 14.3408
38 | -1.058 | -0.50793 | 1.0583 | 0.50795 | 0.00028932 | 1.4849e-05 | 0.03401 | 0.034008 | 0.03401 | 0.99616 | -0.020499 | 0.99645 | -0.018635 | 16.1952
39 | 0.15589 | 0.074821 | -0.15589 | -0.075503 | 9.6566e-07 | -0.00068185 | 0.0050096 | 0.0050181 | 0.0050181 | 0.99645 | -0.018635 | 0.99644 | -0.018582 | 2.281
40 | -1.2142 | -0.58277 | 1.2143 | 0.58207 | 6.1413e-05 | -0.00069836 | 0.039017 | 0.039008 | 0.039017 | 0.99645 | -0.018635 | 0.9965 | -0.019067 | 17.7352
41 | -0.20302 | -0.098328 | 0.20302 | 0.097744 | 1.39e-06 | -0.0005849 | 0.0065163 | 0.006509 | 0.0065163 | 0.99933 | -0.010852 | 0.99933 | -0.010911 | 2.962
42 | -0.098438 | -0.047676 | 0.098439 | 0.046876 | 4.4629e-07 | -0.00079984 | 0.0031606 | 0.0031506 | 0.0031606 | 0.99899 | -0.0013636 | 0.999 | -0.0014023 | 1.4366
43 | -0.098439 | -0.046876 | 0.09844 | 0.044553 | 1.2806e-06 | -0.0023234 | 0.0031506 | 0.0031223 | 0.0031506 | 0.999 | -0.0014023 | 0.99901 | -0.0015052 | 1.4321
44 | 0.13057 | 0.060246 | -0.13057 | -0.063237 | 2.9196e-06 | -0.0029909 | 0.0041552 | 0.0041922 | 0.0041922 | 0.99901 | -0.0015052 | 0.99899 | -0.0013207 | 1.9055
45 | -0.22901 | -0.1048 | 0.22903 | 0.096618 | 2.3969e-05 | -0.0081804 | 0.0072775 | 0.0071823 | 0.0072775 | 0.99901 | -0.0015052 | 0.99911 | -0.0022242 | 3.3079
46 | 0.20542 | 0.09855 | -0.20541 | -0.099487 | 2.2798e-06 | -0.0009369 | 0.0065828 | 0.0065946 | 0.0065946 | 0.99911 | -0.0022242 | 0.9991 | -0.0021286 | 2.9975
47 | 4.6551 | 2.2017 | -4.6547 | -2.2031 | 0.00037053 | -0.0013983 | 0.1489 | 0.14892 | 0.14892 | 0.99838 | -0.031475 | 0.99829 | -0.033133 | 35.3721
48 | 0.54318 | 0.25965 | -0.54316 | -0.26081 | 1.9706e-05 | -0.0011524 | 0.017408 | 0.017422 | 0.017422 | 0.99838 | -0.031475 | 0.99835 | -0.031167 | 7.9192
49 | 0.34613 | 0.16749 | -0.34612 | -0.16764 | 1.0414e-06 | -0.00014988 | 0.011118 | 0.011119 | 0.011119 | 0.99843 | -0.026841 | 0.99843 | -0.026815 | 5.0543
50 | 4.6547 | 2.2031 | -4.6546 | -2.2036 | 0.00012382 | -0.00046707 | 0.14892 | 0.14892 | 0.14892 | 0.99829 | -0.033133 | 0.99826 | -0.033687 | 35.3738
51 | 0.32453 | 0.15492 | -0.32452 | -0.15595 | 6.2744e-06 | -0.0010313 | 0.010398 | 0.010411 | 0.010411 | 0.99835 | -0.031167 | 0.99833 | -0.031003 | 4.7323
52 | 4.4213 | 2.0906 | -4.4211 | -2.0912 | 0.00022083 | -0.00062086 | 0.14143 | 0.14144 | 0.14144 | 0.99826 | -0.033687 | 0.9982 | -0.03428 | 39.0713
53 | 0.16868 | 0.080471 | -0.16868 | -0.081693 | 2.0091e-06 | -0.0012222 | 0.0054041 | 0.0054194 | 0.0054194 | 0.99833 | -0.031003 | 0.99832 | -0.030901 | 2.4634
54 | 3.1177 | 1.4718 | -3.1172 | -1.4725 | 0.00047426 | -0.00070931 | 0.099703 | 0.099713 | 0.099713 | 0.9982 | -0.03428 | 0.99806 | -0.033029 | 45.3242
55 | 1.2011 | 0.577 | -1.201 | -0.57815 | 9.8202e-05 | -0.0011489 | 0.038534 | 0.038549 | 0.038549 | 0.9982 | -0.03428 | 0.99813 | -0.033579 | 17.5222
56 | 0.10241 | 0.042433 | -0.1024 | -0.048847 | 3.7845e-06 | -0.0064139 | 0.0032057 | 0.0032812 | 0.0032812 | 0.9982 | -0.03428 | 0.99817 | -0.034017 | 1.4915
57 | -0.075162 | -0.036403 | 0.075163 | 0.034547 | 6.043e-07 | -0.0018558 | 0.0024178 | 0.0023949 | 0.0024178 | 0.99712 | -0.024679 | 0.99713 | -0.024746 | 1.099
58 | -0.075163 | -0.034547 | 0.075163 | 0.034033 | 1.6545e-07 | -0.00051424 | 0.0023949 | 0.0023887 | 0.0023949 | 0.99713 | -0.024746 | 0.99713 | -0.024762 | 1.0886
59 | -2.9077 | -1.3776 | 2.9094 | 1.3747 | 0.001639 | -0.002876 | 0.09315 | 0.093108 | 0.09315 | 0.99713 | -0.024762 | 0.99766 | -0.029418 | 42.3409
60 | 2.8326 | 1.3435 | -2.8321 | -1.3445 | 0.00049959 | -0.00092991 | 0.090762 | 0.090775 | 0.090775 | 0.99713 | -0.024762 | 0.99697 | -0.023295 | 41.2614
61 | -2.9094 | -1.3747 | 2.9102 | 1.3733 | 0.00081502 | -0.0014326 | 0.093108 | 0.093088 | 0.093108 | 0.99766 | -0.029418 | 0.99792 | -0.031722 | 42.322
62 | 2.5225 | 1.1945 | -2.5223 | -1.195 | 0.00017587 | -0.00042645 | 0.080816 | 0.080822 | 0.080822 | 0.99697 | -0.023295 | 0.9969 | -0.022717 | 36.7372
63 | -3.1167 | -1.4733 | 3.1172 | 1.4725 | 0.00049428 | -0.00073881 | 0.099724 | 0.099713 | 0.099724 | 0.99792 | -0.031722 | 0.99806 | -0.033029 | 45.3292
64 | 2.5223 | 1.195 | -2.5218 | -1.1962 | 0.00049776 | -0.0012062 | 0.080822 | 0.080839 | 0.080839 | 0.9969 | -0.022717 | 0.99672 | -0.021079 | 36.7448
65 | -0.15443 | -0.074794 | 0.15443 | 0.074466 | 4.5304e-07 | -0.0003278 | 0.004963 | 0.0049589 | 0.004963 | 0.99805 | -0.032816 | 0.99805 | -0.032842 | 2.2559
66 | -0.15443 | -0.074466 | 0.15443 | 0.074118 | 4.7973e-07 | -0.00034771 | 0.0049589 | 0.0049545 | 0.0049589 | 0.99805 | -0.032842 | 0.99805 | -0.032868 | 2.254
67 | -0.37764 | -0.18222 | 0.37764 | 0.18197 | 2.0631e-06 | -0.00024934 | 0.012128 | 0.012125 | 0.012128 | 0.99805 | -0.032868 | 0.99806 | -0.032915 | 5.5127
68 | -0.37764 | -0.18197 | 0.37765 | 0.18128 | 5.7219e-06 | -0.00069221 | 0.012125 | 0.012116 | 0.012125 | 0.99806 | -0.032915 | 0.99807 | -0.033045 | 5.5112
69 | -0.37765 | -0.18128 | 0.37765 | 0.18074 | 4.5057e-06 | -0.0005458 | 0.012116 | 0.012109 | 0.012116 | 0.99807 | -0.033045 | 0.99808 | -0.033147 | 5.5073
70 | -0.66282 | -0.31885 | 0.66283 | 0.31821 | 1.6213e-05 | -0.0006337 | 0.021274 | 0.021266 | 0.021274 | 0.99808 | -0.033147 | 0.9981 | -0.033356 | 9.6698
71 | -0.66283 | -0.31821 | 0.66285 | 0.31778 | 1.115e-05 | -0.00043611 | 0.021266 | 0.02126 | 0.021266 | 0.9981 | -0.033356 | 0.99812 | -0.0335 | 9.6661
72 | 0.1024 | 0.048847 | -0.1024 | -0.049595 | 4.5333e-07 | -0.00074805 | 0.0032812 | 0.0032906 | 0.0032906 | 0.99817 | -0.034017 | 0.99817 | -0.033979 | 1.4957
73 | 0.66285 | 0.31754 | -0.66285 | -0.31778 | 6.1836e-06 | -0.00024196 | 0.021257 | 0.02126 | 0.02126 | 0.99813 | -0.033579 | 0.99812 | -0.0335 | 9.6636
74 | 0.10426 | 0.049387 | -0.10426 | -0.049695 | 1.9358e-07 | -0.0003076 | 0.0033414 | 0.0033452 | 0.0033452 | 0.99665 | -0.020487 | 0.99665 | -0.020471 | 1.5205
75 | -0.26239 | -0.12598 | 0.2624 | 0.12516 | 3.2796e-06 | -0.00081978 | 0.0084306 | 0.0084203 | 0.0084306 | 0.99665 | -0.020487 | 0.99667 | -0.020593 | 3.8321
76 | 0.10426 | 0.049695 | -0.10425 | -0.050493 | 5.0415e-07 | -0.00079782 | 0.0033452 | 0.0033552 | 0.0033552 | 0.99665 | -0.020471 | 0.99665 | -0.02043 | 1.5251
77 | -0.2624 | -0.12516 | 0.2624 | 0.12449 | 2.6456e-06 | -0.00066276 | 0.0084203 | 0.0084121 | 0.0084203 | 0.99667 | -0.020593 | 0.99668 | -0.020677 | 3.8274
78 | -0.2624 | -0.12449 | 0.2624 | 0.12379 | 2.8195e-06 | -0.00070779 | 0.0084121 | 0.0084033 | 0.0084121 | 0.99668 | -0.020677 | 0.99669 | -0.020766 | 3.8237
79 | -0.60349 | -0.28898 | 0.60351 | 0.28793 | 2.2345e-05 | -0.0010511 | 0.01938 | 0.019366 | 0.01938 | 0.99669 | -0.020766 | 0.99672 | -0.021079 | 8.809
80 | 1.9183 | 0.90823 | -1.918 | -0.90955 | 0.00030005 | -0.0013212 | 0.061472 | 0.06149 | 0.06149 | 0.99672 | -0.021079 | 0.99657 | -0.019782 | 27.9498
81 | -0.28424 | -0.13766 | 0.28424 | 0.13718 | 2.2618e-06 | -0.00047938 | 0.0091498 | 0.0091437 | 0.0091498 | 0.99642 | -0.018431 | 0.99642 | -0.0185 | 4.159
82 | 0.17803 | 0.080371 | -0.17802 | -0.083863 | 6.3476e-06 | -0.0034917 | 0.005659 | 0.0057013 | 0.0057013 | 0.99642 | -0.0185 | 0.99639 | -0.018223 | 2.5915
83 | -0.46227 | -0.21756 | 0.46233 | 0.21308 | 5.5199e-05 | -0.0044748 | 0.014802 | 0.014747 | 0.014802 | 0.99642 | -0.0185 | 0.99654 | -0.019451 | 6.728
84 | 0.097275 | 0.046216 | -0.097275 | -0.047112 | 4.9343e-07 | -0.00089655 | 0.0031202 | 0.0031314 | 0.0031314 | 0.99639 | -0.018223 | 0.99639 | -0.01818 | 1.4234
85 | 0.080748 | 0.037647 | -0.080748 | -0.039108 | 5.5207e-07 | -0.0014608 | 0.0025812 | 0.0025994 | 0.0025994 | 0.99639 | -0.018223 | 0.99638 | -0.018166 | 1.1815
86 | -0.46233 | -0.21308 | 0.46233 | 0.21252 | 6.8406e-06 | -0.00055693 | 0.014747 | 0.01474 | 0.014747 | 0.99654 | -0.019451 | 0.99655 | -0.019566 | 6.703
87 | -0.58468 | -0.27178 | 0.58469 | 0.27138 | 7.9422e-06 | -0.00040215 | 0.018677 | 0.018672 | 0.018677 | 0.99655 | -0.019566 | 0.99656 | -0.019673 | 8.4896
88 | -0.58469 | -0.27138 | 0.5847 | 0.27097 | 8.1011e-06 | -0.00041042 | 0.018672 | 0.018667 | 0.018672 | 0.99656 | -0.019673 | 0.99657 | -0.019782 | 8.4874
89 | -1.3333 | -0.63912 | 1.3333 | 0.63859 | 5.6986e-05 | -0.00053494 | 0.04283 | 0.042823 | 0.04283 | 0.99653 | -0.019419 | 0.99657 | -0.019782 | 19.4684
90 | 1.2143 | 0.5815 | -1.2143 | -0.58207 | 5.0273e-05 | -0.00057197 | 0.039001 | 0.039008 | 0.039008 | 0.99653 | -0.019419 | 0.9965 | -0.019067 | 17.7311
91 | -0.37531 | -0.18118 | 0.37532 | 0.18095 | 1.9157e-06 | -0.00023034 | 0.012106 | 0.012104 | 0.012106 | 0.99375 | 0.016755 | 0.99376 | 0.01671 | 5.5029
92 | 0.30366 | 0.14648 | -0.30365 | -0.14683 | 1.9213e-06 | -0.00035305 | 0.0097936 | 0.0097981 | 0.0097981 | 0.99375 | 0.016755 | 0.99375 | 0.016809 | 4.4537
93 | 2.1051 | 1.0187 | -2.105 | -1.0191 | 9.8486e-05 | -0.00034766 | 0.067934 | 0.067939 | 0.067939 | 0.99376 | 0.01671 | 0.99371 | 0.017117 | 30.8814
94 | 0.30365 | 0.14683 | -0.30365 | -0.14707 | 1.2775e-06 | -0.00023458 | 0.0097981 | 0.009801 | 0.009801 | 0.99375 | 0.016809 | 0.99374 | 0.016846 | 4.455
95 | 2.105 | 1.0191 | -2.105 | -1.0191 | 5.8417e-06 | -2.0618e-05 | 0.067939 | 0.067939 | 0.067939 | 0.99371 | 0.017117 | 0.99371 | 0.017142 | 30.8815
96 | 0.72474 | 0.3506 | -0.72473 | -0.351 | 1.2501e-05 | -0.00039979 | 0.023388 | 0.023393 | 0.023393 | 0.99371 | 0.017142 | 0.9937 | 0.017292 | 10.6333

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 12.5002 | 5.8645

## res_load
| p_mw | q_mvar
0 | 0.25605 | 0.12401
1 | 0.10195 | 0.049377
2 | 0.22444 | 0.1087
3 | 0.40816 | 0.19768
4 | 0.13874 | 0.067195
5 | 0.082332 | 0.039875
6 | 0.40159 | 0.1945
7 | 0.10087 | 0.048854
8 | 0.10803 | 0.052321
9 | 0.15944 | 0.077222
10 | 0.62457 | 0.30249
11 | 0.35635 | 0.17259
12 | 0.38871 | 0.18826
13 | 0.59224 | 0.28684
14 | 0.076723 | 0.037159
15 | 0.065896 | 0.031915
16 | 0.20302 | 0.098328
17 | 0.1242 | 0.060152
18 | 0.098438 | 0.047676
19 | 0.13057 | 0.063237
20 | 0.20541 | 0.099487
21 | 0.37243 | 0.18038
22 | 0.26585 | 0.12876
23 | 0.21863 | 0.10589
24 | 0.23328 | 0.11298
25 | 0.34612 | 0.16764
26 | 0.15585 | 0.07548
27 | 0.075162 | 0.036403
28 | 0.30957 | 0.14993
29 | 0.20649 | 0.10001
30 | 0.15443 | 0.074794
31 | 0.22321 | 0.1081
32 | 0.28517 | 0.13811
33 | 0.1024 | 0.049595
34 | 0.5381 | 0.26062
35 | 0.15814 | 0.07659
36 | 0.10425 | 0.050493
37 | 0.34108 | 0.16519
38 | 0.28424 | 0.13766
39 | 0.097275 | 0.047112
40 | 0.080748 | 0.039108
41 | 0.12235 | 0.059256
42 | 0.16868 | 0.081693
43 | 0.11898 | 0.057623
44 | 0.15589 | 0.075503
45 | 0.071657 | 0.034705
46 | 0.30365 | 0.14707
47 | 1.3802 | 0.66848
48 | 0.72473 | 0.351

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1